## LLL_max_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_deg | pf_ikss_to_deg | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_deg | pf_va_to_deg
Line_0 | 0 | 4.283 | 0 | 9.2778 | 0 | 148.3662 | 6.2986e-19 | -1e-07 | -4.9297e-19 | -1e-07 | -77.7798 | 102.2202 | 0 | 0 | 87.328 | 77.7798
Line_1 | 2.4666 | 0 | 4.9647 | 0 | 85.4462 | 0 | -1e-07 | 1.6022e-19 | -1e-07 | -1.2516e-19 | -77.7798 | 0 | 0 | 0 | 73.5107 | 77.7798
Line_2 | 2.4666 | 0 | 4.9647 | 0 | 85.4462 | 0 | -1e-07 | 1.6022e-19 | -1e-07 | -1.2516e-19 | -77.7798 | 0 | 0 | 0 | 73.5107 | 77.7798
Line_4 | 1.2333 | 1.2333 | 2.4824 | 2.4824 | 42.7231 | 42.7231 | -1e-07 | -1e-07 | -1e-07 | -1e-07 | -73.5107 | 106.4893 | 0 | 0 | 73.5107 | 73.5107

## LLL_max_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_deg | pf_ikss_to_deg | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_deg | pf_va_to_deg
Line_0 | 0 | 4.283 | 0 | 9.2778 | 0 | 148.3662 | 6.2984e-19 | -1e-07 | -4.9301e-19 | -1e-07 | -77.7798 | 102.2202 | 0 | 0 | 87.328 | 77.7798
Line_1 | 2.4666 | 0 | 4.9647 | 0 | 85.4462 | 0 | -1e-07 | 1.602e-19 | -1e-07 | -1.2518e-19 | -77.7798 | 0 | 0 | 0 | 73.5107 | 77.7798
Line_2 | 2.4666 | 0 | 4.9647 | 0 | 85.4462 | 0 | -1e-07 | 1.602e-19 | -1e-07 | -1.2518e-19 | -77.7798 | 0 | 0 | 0 | 73.5107 | 77.7798
Line_4 | 1.2333 | 1.2333 | 2.4824 | 2.4824 | 42.7231 | 42.7231 | -1e-07 | -1e-07 | -1e-07 | -1e-07 | -73.5107 | 106.4893 | 0 | 0 | 73.5107 | 73.5107

## LLL_max_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_deg | pf_ikss_to_deg | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_deg | pf_va_to_deg
Line_0 | 0 | 1.3097 | 0 | 2.8371 | 0 | 45.3689 | -6.0676e-09 | -25.7292 | 5.5265e-09 | -25.7292 | -54.5297 | 125.4703 | 0.87234 | 0.80202 | 45 | 45
Line_1 | 0.82856 | 0 | 1.6677 | 0 | 28.7021 | 0 | -15.4464 | -2.495e-09 | -15.4464 | 1.6066e-09 | -54.5297 | 0 | 0.76108 | 0.80202 | 45 | 45
Line_2 | 0.82856 | 0 | 1.6677 | 0 | 28.7021 | 0 | -15.4464 | -2.495e-09 | -15.4464 | 1.6066e-09 | -54.5297 | 0 | 0.76108 | 0.80202 | 45 | 45
Line_4 | 0.41428 | 0.41428 | 0.83384 | 0.83384 | 14.351 | 14.351 | -7.7232 | -7.7232 | -7.7232 | -7.7232 | -54.2264 | 125.7736 | 0.76108 | 0.76108 | 45 | 45

## LLL_max_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_deg | pf_ikss_to_deg | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_deg | pf_va_to_deg
Line_0 | 0 | 1.3097 | 0 | 2.8371 | 0 | 45.3689 | -6.0676e-09 | -25.7292 | 5.5265e-09 | -25.7292 | -54.5297 | 125.4703 | 0.87234 | 0.80202 | 45 | 45
Line_1 | 0.82856 | 0 | 1.6677 | 0 | 28.7021 | 0 | -15.4464 | -2.495e-09 | -15.4464 | 1.6066e-09 | -54.5297 | 0 | 0.76108 | 0.80202 | 45 | 45
Line_2 | 0.82856 | 0 | 1.6677 | 0 | 28.7021 | 0 | -15.4464 | -2.495e-09 | -15.4464 | 1.6066e-09 | -54.5297 | 0 | 0.76108 | 0.80202 | 45 | 45
Line_4 | 0.41428 | 0.41428 | 0.83384 | 0.83384 | 14.351 | 14.351 | -7.7232 | -7.7232 | -7.7232 | -7.7232 | -54.2264 | 125.7736 | 0.76108 | 0.76108 | 45 | 45

## LLL_min_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_deg | pf_ikss_to_deg | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_deg | pf_va_to_deg
Line_0 | 0 | 3.6016 | 0 | 6.8381 | 0 | 124.7634 | 7.2813e-20 | -1e-07 | 2.6701e-19 | -1e-07 | -69.6723 | 110.3277 | 0 | 0 | 87.2669 | 69.6723
Line_1 | 2.0061 | 0 | 3.4722 | 0 | 69.4947 | 0 | -1e-07 | 1.7293e-20 | -1e-07 | 6.3216e-20 | -69.6723 | 0 | 0 | 0 | 62.3733 | 69.6723
Line_2 | 2.0061 | 0 | 3.4722 | 0 | 69.4947 | 0 | -1e-07 | 1.7293e-20 | -1e-07 | 6.3216e-20 | -69.6723 | 0 | 0 | 0 | 62.3733 | 69.6723
Line_4 | 1.0031 | 1.0031 | 1.7361 | 1.7361 | 34.7474 | 34.7474 | -1e-07 | -1e-07 | -1e-07 | -1e-07 | -62.3733 | 117.6267 | 0 | 0 | 62.3733 | 62.3733

## LLL_min_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_deg | pf_ikss_to_deg | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_deg | pf_va_to_deg
Line_0 | 0 | 3.6016 | 0 | 6.8381 | 0 | 124.7634 | 7.2813e-20 | -1e-07 | 2.6704e-19 | -1e-07 | -69.6723 | 110.3277 | 0 | 0 | 87.2669 | 69.6723
Line_1 | 2.0061 | 0 | 3.4722 | 0 | 69.4947 | 0 | -1e-07 | 1.7288e-20 | -1e-07 | 6.3228e-20 | -69.6723 | 0 | 0 | 0 | 62.3733 | 69.6723
Line_2 | 2.0061 | 0 | 3.4722 | 0 | 69.4947 | 0 | -1e-07 | 1.7288e-20 | -1e-07 | 6.3228e-20 | -69.6723 | 0 | 0 | 0 | 62.3733 | 69.6723
Line_4 | 1.0031 | 1.0031 | 1.7361 | 1.7361 | 34.7474 | 34.7474 | -1e-07 | -1e-07 | -1e-07 | -1e-07 | -62.3733 | 117.6267 | 0 | 0 | 62.3733 | 62.3733

## LLL_min_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_deg | pf_ikss_to_deg | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_deg | pf_va_to_deg
Line_0 | 0 | 1.1462 | 0 | 2.1763 | 0 | 39.7072 | -5.1465e-09 | -19.7082 | 4.6775e-09 | -19.7082 | -52.6343 | 127.3657 | 0.78485 | 0.70193 | 45 | 45
Line_1 | 0.71316 | 0 | 1.2343 | 0 | 24.7046 | 0 | -11.4434 | -2.233e-09 | -11.4434 | 1.0258e-09 | -52.6343 | 0 | 0.65508 | 0.70193 | 45 | 45
Line_2 | 0.71316 | 0 | 1.2343 | 0 | 24.7046 | 0 | -11.4434 | -2.233e-09 | -11.4434 | 1.0258e-09 | -52.6343 | 0 | 0.65508 | 0.70193 | 45 | 45
Line_4 | 0.35658 | 0.35658 | 0.61717 | 0.61717 | 12.3523 | 12.3523 | -5.7217 | -5.7217 | -5.7217 | -5.7217 | -51.0933 | 128.9067 | 0.65508 | 0.65508 | 45 | 45

## LLL_min_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_deg | pf_ikss_to_deg | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_deg | pf_va_to_deg
Line_0 | 0 | 1.1462 | 0 | 2.1763 | 0 | 39.7072 | -5.1465e-09 | -19.7082 | 4.6775e-09 | -19.7082 | -52.6343 | 127.3657 | 0.78485 | 0.70193 | 45 | 45
Line_1 | 0.71316 | 0 | 1.2343 | 0 | 24.7046 | 0 | -11.4434 | -2.233e-09 | -11.4434 | 1.0258e-09 | -52.6343 | 0 | 0.65508 | 0.70193 | 45 | 45
Line_2 | 0.71316 | 0 | 1.2343 | 0 | 24.7046 | 0 | -11.4434 | -2.233e-09 | -11.4434 | 1.0258e-09 | -52.6343 | 0 | 0.65508 | 0.70193 | 45 | 45
Line_4 | 0.35658 | 0.35658 | 0.61717 | 0.61717 | 12.3523 | 12.3523 | -5.7217 | -5.7217 | -5.7217 | -5.7217 | -51.0933 | 128.9067 | 0.65508 | 0.65508 | 45 | 45

## LL_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mw | pf_q_b_from_mw | pf_q_c_from_mw | pf_q_a_to_mw | pf_q_b_to_mw | pf_q_c_to_mw | pf_ikss_a_from_deg | pf_ikss_b_from_deg | pf_ikss_c_from_deg | pf_ikss_a_to_deg | pf_ikss_b_to_deg | pf_ikss_c_to_deg | pf_vm_a_from_pu | pf_vm_b_from_bus_pu | pf_vm_c_from_bus_pu | pf_vm_a_to_bus_pu | pf_vm_b_to_bus_pu | pf_vm_c_to_bus_pu | pf_va_a_from_bus_deg | pf_va_b_from_bus_deg | pf_va_c_from_bus_deg | pf_va_a_to_bus_deg | pf_va_b_to_bus_deg | pf_va_c_to_bus_deg
Line_0 | 0 | 0 | 0 | 0 | 3.7092 | 3.7092 | 0 | 0 | 0 | 0 | 42.8296 | 42.8296 | -9.9002e-14 | 5.2106e-14 | 1.0421e-14 | 7.2949e-14 | -23.0225 | 23.0225 | 2.0843e-14 | 5.7634e-09 | -5.7634e-09 | -2.6053e-14 | 4.9861 | -4.9861 | 0 | -167.7798 | 12.2202 | 0 | 12.2202 | -167.7798 | 0.95263 | 0 | 0.95263 | 0.95263 | 0 | 0.95263 | -4.0783e-12 | 0 | -180 | -1.2473e-11 | 0 | -180
Line_1 | 0 | 2.1362 | 2.1362 | 0 | 0 | 0 | 0 | 24.6662 | 24.6662 | 0 | 0 | 0 | 3.1264e-14 | -13.0085 | 13.0085 | -3.6475e-14 | 2.6053e-14 | -5.2106e-15 | 7.3056e-28 | 3.8506 | -3.8506 | -5.2106e-15 | 1.9211e-09 | -1.9211e-09 | 0 | -167.7798 | 12.2202 | 0 | 0 | 0 | 0.95263 | 0 | 0.95263 | 0.95263 | 0 | 0.95263 | -1.4274e-11 | 0 | -180 | -1.2473e-11 | 0 | -180
Line_2 | 0 | 2.1362 | 2.1362 | 0 | 0 | 0 | 0 | 24.6662 | 24.6662 | 0 | 0 | 0 | 3.6475e-14 | -13.0085 | 13.0085 | -3.1264e-14 | 2.6053e-14 | -5.2106e-15 | -1.0421e-14 | 3.8506 | -3.8506 | -8.569e-28 | 1.9211e-09 | -1.9211e-09 | 0 | -167.7798 | 12.2202 | 0 | 0 | 0 | 0.95263 | 0 | 0.95263 | 0.95263 | 0 | 0.95263 | -1.4294e-11 | 0 | -180 | -1.2473e-11 | 0 | -180
Line_4 | 0 | 1.0681 | 1.0681 | 0 | 1.0681 | 1.0681 | 0 | 12.3331 | 12.3331 | 0 | 12.3331 | 12.3331 | -5.2106e-15 | -6.5042 | 6.5042 | -1.0421e-14 | -6.5042 | 6.5042 | 1.5632e-14 | 1.9253 | -1.9253 | -5.2106e-15 | 1.9253 | -1.9253 | 0 | -163.5107 | 16.4893 | 0 | 16.4893 | -163.5107 | 0.95263 | 0 | 0.95263 | 0.95263 | 0 | 0.95263 | -1.4274e-11 | 0 | -180 | -1.4294e-11 | 0 | -180

## LL_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mw | pf_q_b_from_mw | pf_q_c_from_mw | pf_q_a_to_mw | pf_q_b_to_mw | pf_q_c_to_mw | pf_ikss_a_from_deg | pf_ikss_b_from_deg | pf_ikss_c_from_deg | pf_ikss_a_to_deg | pf_ikss_b_to_deg | pf_ikss_c_to_deg | pf_vm_a_from_pu | pf_vm_b_from_bus_pu | pf_vm_c_from_bus_pu | pf_vm_a_to_bus_pu | pf_vm_b_to_bus_pu | pf_vm_c_to_bus_pu | pf_va_a_from_bus_deg | pf_va_b_from_bus_deg | pf_va_c_from_bus_deg | pf_va_a_to_bus_deg | pf_va_b_to_bus_deg | pf_va_c_to_bus_deg
Line_0 | 0 | 0 | 0 | 0 | 3.7092 | 3.7092 | 0 | 0 | 0 | 0 | 42.8296 | 42.8296 | -9.9002e-14 | 5.2106e-14 | 1.0421e-14 | 7.2949e-14 | -23.0225 | 23.0225 | 2.0843e-14 | 5.7634e-09 | -5.7634e-09 | -2.6053e-14 | 4.9861 | -4.9861 | 0 | -167.7798 | 12.2202 | 0 | 12.2202 | -167.7798 | 0.95263 | 0 | 0.95263 | 0.95263 | 0 | 0.95263 | -4.0783e-12 | 0 | -180 | -1.2473e-11 | 0 | -180
Line_1 | 0 | 2.1362 | 2.1362 | 0 | 0 | 0 | 0 | 24.6662 | 24.6662 | 0 | 0 | 0 | 3.1264e-14 | -13.0085 | 13.0085 | -3.6475e-14 | 2.6053e-14 | -5.2106e-15 | 7.3056e-28 | 3.8506 | -3.8506 | -5.2106e-15 | 1.9211e-09 | -1.9211e-09 | 0 | -167.7798 | 12.2202 | 0 | 0 | 0 | 0.95263 | 0 | 0.95263 | 0.95263 | 0 | 0.95263 | -1.4274e-11 | 0 | -180 | -1.2473e-11 | 0 | -180
Line_2 | 0 | 2.1362 | 2.1362 | 0 | 0 | 0 | 0 | 24.6662 | 24.6662 | 0 | 0 | 0 | 3.6475e-14 | -13.0085 | 13.0085 | -3.1264e-14 | 2.6053e-14 | -5.2106e-15 | -1.0421e-14 | 3.8506 | -3.8506 | -8.569e-28 | 1.9211e-09 | -1.9211e-09 | 0 | -167.7798 | 12.2202 | 0 | 0 | 0 | 0.95263 | 0 | 0.95263 | 0.95263 | 0 | 0.95263 | -1.4294e-11 | 0 | -180 | -1.2473e-11 | 0 | -180
Line_4 | 0 | 1.0681 | 1.0681 | 0 | 1.0681 | 1.0681 | 0 | 12.3331 | 12.3331 | 0 | 12.3331 | 12.3331 | -5.2106e-15 | -6.5042 | 6.5042 | -1.0421e-14 | -6.5042 | 6.5042 | 1.5632e-14 | 1.9253 | -1.9253 | -5.2106e-15 | 1.9253 | -1.9253 | 0 | -163.5107 | 16.4893 | 0 | 16.4893 | -163.5107 | 0.95263 | 0 | 0.95263 | 0.95263 | 0 | 0.95263 | -1.4274e-11 | 0 | -180 | -1.4294e-11 | 0 | -180

## LL_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mw | pf_q_b_from_mw | pf_q_c_from_mw | pf_q_a_to_mw | pf_q_b_to_mw | pf_q_c_to_mw | pf_ikss_a_from_deg | pf_ikss_b_from_deg | pf_ikss_c_from_deg | pf_ikss_a_to_deg | pf_ikss_b_to_deg | pf_ikss_c_to_deg | pf_vm_a_from_pu | pf_vm_b_from_bus_pu | pf_vm_c_from_bus_pu | pf_vm_a_to_bus_pu | pf_vm_b_to_bus_pu | pf_vm_c_to_bus_pu | pf_va_a_from_bus_deg | pf_va_b_from_bus_deg | pf_va_c_from_bus_deg | pf_va_a_to_bus_deg | pf_va_b_to_bus_deg | pf_va_c_to_bus_deg
Line_0 | 0 | 0 | 0 | 0 | 1.7631 | 1.7631 | 0 | 0 | 0 | 0 | 20.3584 | 20.3584 | -3.6475e-14 | -9.5545e-10 | -3.075e-09 | 3.3869e-14 | -17.4596 | 1.9173 | 7.816e-15 | 4.0277e-09 | -3.5666e-10 | -1.0421e-14 | -2.1579 | -13.3845 | 0 | -149.913 | 30.087 | 0 | 30.087 | -149.913 | 1.1075 | 0.71098 | 0.91717 | 1.0759 | 0.62335 | 0.92294 | 17.922 | -106.528 | 158.1868 | 16.2567 | -104.913 | 160.9544
Line_1 | 0 | 1.0858 | 1.0858 | 0 | 0 | 0 | 0 | 12.5375 | 12.5375 | 0 | 0 | 0 | 1.3027e-14 | -10.3342 | 1.4923 | -1.5632e-14 | -4.7338e-10 | -1.0337e-09 | 2.6053e-15 | -0.87368 | -7.9682 | -2.6053e-15 | 1.3544e-09 | -3.8387e-10 | 0 | -149.913 | 30.087 | 0 | 0 | 0 | 1.0599 | 0.57582 | 0.92591 | 1.0759 | 0.62335 | 0.92294 | 15.2786 | -104.0411 | 162.4427 | 16.2567 | -104.913 | 160.9544
Line_2 | 0 | 1.0858 | 1.0858 | 0 | 0 | 0 | 0 | 12.5375 | 12.5375 | 0 | 0 | 0 | 2.6053e-15 | -10.3342 | 1.4923 | -1.3027e-14 | -4.7338e-10 | -1.0337e-09 | 2.8943e-29 | -0.87368 | -7.9682 | -1.5745e-28 | 1.3544e-09 | -3.8387e-10 | 0 | -149.913 | 30.087 | 0 | 0 | 0 | 1.0599 | 0.57582 | 0.92591 | 1.0759 | 0.62335 | 0.92294 | 15.2786 | -104.0411 | 162.4427 | 16.2567 | -104.913 | 160.9544
Line_4 | 0 | 0.54289 | 0.54289 | 0 | 0.54289 | 0.54289 | 0 | 6.2688 | 6.2688 | 0 | 6.2688 | 6.2688 | 2.6053e-15 | -5.1671 | 0.74615 | -1.8237e-14 | -5.1671 | 0.74615 | 5.2106e-15 | -0.43684 | -3.9841 | 5.2106e-15 | -0.43684 | -3.9841 | 0 | -149.0411 | 30.9589 | 0 | 30.9589 | -149.0411 | 1.0599 | 0.57582 | 0.92591 | 1.0599 | 0.57582 | 0.92591 | 15.2786 | -104.0411 | 162.4427 | 15.2786 | -104.0411 | 162.4427

## LL_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mw | pf_q_b_from_mw | pf_q_c_from_mw | pf_q_a_to_mw | pf_q_b_to_mw | pf_q_c_to_mw | pf_ikss_a_from_deg | pf_ikss_b_from_deg | pf_ikss_c_from_deg | pf_ikss_a_to_deg | pf_ikss_b_to_deg | pf_ikss_c_to_deg | pf_vm_a_from_pu | pf_vm_b_from_bus_pu | pf_vm_c_from_bus_pu | pf_vm_a_to_bus_pu | pf_vm_b_to_bus_pu | pf_vm_c_to_bus_pu | pf_va_a_from_bus_deg | pf_va_b_from_bus_deg | pf_va_c_from_bus_deg | pf_va_a_to_bus_deg | pf_va_b_to_bus_deg | pf_va_c_to_bus_deg
Line_0 | 0 | 0 | 0 | 0 | 1.7631 | 1.7631 | 0 | 0 | 0 | 0 | 20.3584 | 20.3584 | -3.6475e-14 | -9.5545e-10 | -3.075e-09 | 3.3869e-14 | -17.4596 | 1.9173 | 7.816e-15 | 4.0277e-09 | -3.5666e-10 | -1.0421e-14 | -2.1579 | -13.3845 | 0 | -149.913 | 30.087 | 0 | 30.087 | -149.913 | 1.1075 | 0.71098 | 0.91717 | 1.0759 | 0.62335 | 0.92294 | 17.922 | -106.528 | 158.1868 | 16.2567 | -104.913 | 160.9544
Line_1 | 0 | 1.0858 | 1.0858 | 0 | 0 | 0 | 0 | 12.5375 | 12.5375 | 0 | 0 | 0 | 1.3027e-14 | -10.3342 | 1.4923 | -1.5632e-14 | -4.7338e-10 | -1.0337e-09 | 2.6053e-15 | -0.87368 | -7.9682 | -2.6053e-15 | 1.3544e-09 | -3.8387e-10 | 0 | -149.913 | 30.087 | 0 | 0 | 0 | 1.0599 | 0.57582 | 0.92591 | 1.0759 | 0.62335 | 0.92294 | 15.2786 | -104.0411 | 162.4427 | 16.2567 | -104.913 | 160.9544
Line_2 | 0 | 1.0858 | 1.0858 | 0 | 0 | 0 | 0 | 12.5375 | 12.5375 | 0 | 0 | 0 | 2.6053e-15 | -10.3342 | 1.4923 | -1.3027e-14 | -4.7338e-10 | -1.0337e-09 | 2.8943e-29 | -0.87368 | -7.9682 | -1.5745e-28 | 1.3544e-09 | -3.8387e-10 | 0 | -149.913 | 30.087 | 0 | 0 | 0 | 1.0599 | 0.57582 | 0.92591 | 1.0759 | 0.62335 | 0.92294 | 15.2786 | -104.0411 | 162.4427 | 16.2567 | -104.913 | 160.9544
Line_4 | 0 | 0.54289 | 0.54289 | 0 | 0.54289 | 0.54289 | 0 | 6.2688 | 6.2688 | 0 | 6.2688 | 6.2688 | 2.6053e-15 | -5.1671 | 0.74615 | -1.8237e-14 | -5.1671 | 0.74615 | 5.2106e-15 | -0.43684 | -3.9841 | 5.2106e-15 | -0.43684 | -3.9841 | 0 | -149.0411 | 30.9589 | 0 | 30.9589 | -149.0411 | 1.0599 | 0.57582 | 0.92591 | 1.0599 | 0.57582 | 0.92591 | 15.2786 | -104.0411 | 162.4427 | 15.2786 | -104.0411 | 162.4427

## LL_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mw | pf_q_b_from_mw | pf_q_c_from_mw | pf_q_a_to_mw | pf_q_b_to_mw | pf_q_c_to_mw | pf_ikss_a_from_deg | pf_ikss_b_from_deg | pf_ikss_c_from_deg | pf_ikss_a_to_deg | pf_ikss_b_to_deg | pf_ikss_c_to_deg | pf_vm_a_from_pu | pf_vm_b_from_bus_pu | pf_vm_c_from_bus_pu | pf_vm_a_to_bus_pu | pf_vm_b_to_bus_pu | pf_vm_c_to_bus_pu | pf_va_a_from_bus_deg | pf_va_b_from_bus_deg | pf_va_c_from_bus_deg | pf_va_a_to_bus_deg | pf_va_b_to_bus_deg | pf_va_c_to_bus_deg
Line_0 | 0 | 0 | 0 | 0 | 3.1191 | 3.1191 | 0 | 0 | 0 | 0 | 36.0161 | 36.0161 | 1.9637e-28 | 1.7764e-14 | -2.3685e-15 | -1.7756e-28 | -16.8865 | 16.8865 | -1.4211e-14 | 4.7631e-09 | -4.7631e-09 | 1.8948e-14 | 6.2558 | -6.2558 | 0 | -159.6723 | 20.3277 | 0 | 20.3277 | -159.6723 | 0.86603 | 0 | 0.86603 | 0.86603 | 0 | 0.86603 | 3.0769e-11 | 0 | 180 | 1.7234e-10 | 0 | 180
Line_1 | 0 | 1.7374 | 1.7374 | 0 | 0 | 0 | 0 | 20.0614 | 20.0614 | 0 | 0 | 0 | -2.3685e-15 | -8.8871 | 8.8871 | 7.1054e-15 | 4.7369e-15 | -2.3685e-15 | 1.6579e-14 | 4.6513 | -4.6513 | -1.8948e-14 | 1.5877e-09 | -1.5877e-09 | 0 | -159.6723 | 20.3277 | 0 | 0 | 0 | 0.86603 | 0 | 0.86603 | 0.86603 | 0 | 0.86603 | 1.9235e-10 | 0 | 180 | 1.7234e-10 | 0 | 180
Line_2 | 0 | 1.7374 | 1.7374 | 0 | 0 | 0 | 0 | 20.0614 | 20.0614 | 0 | 0 | 0 | -8.2897e-15 | -8.8871 | 8.8871 | 1.6579e-14 | 9.4739e-15 | -2.3685e-15 | 1.4211e-14 | 4.6513 | -4.6513 | -1.4211e-14 | 1.5877e-09 | -1.5877e-09 | 0 | -159.6723 | 20.3277 | 0 | 0 | 0 | 0.86603 | 0 | 0.86603 | 0.86603 | 0 | 0.86603 | 1.9236e-10 | 0 | 180 | 1.7234e-10 | 0 | 180
Line_4 | 0 | 0.86868 | 0.86868 | 0 | 0.86868 | 0.86868 | 0 | 10.0307 | 10.0307 | 0 | 10.0307 | 10.0307 | -9.1344e-29 | -4.4435 | 4.4435 | -2.3685e-15 | -4.4435 | 4.4435 | 1.4211e-14 | 2.3257 | -2.3257 | -4.737e-15 | 2.3257 | -2.3257 | 0 | -152.3733 | 27.6267 | 0 | 27.6267 | -152.3733 | 0.86603 | 0 | 0.86603 | 0.86603 | 0 | 0.86603 | 1.9235e-10 | 0 | 180 | 1.9236e-10 | 0 | 180

## LL_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mw | pf_q_b_from_mw | pf_q_c_from_mw | pf_q_a_to_mw | pf_q_b_to_mw | pf_q_c_to_mw | pf_ikss_a_from_deg | pf_ikss_b_from_deg | pf_ikss_c_from_deg | pf_ikss_a_to_deg | pf_ikss_b_to_deg | pf_ikss_c_to_deg | pf_vm_a_from_pu | pf_vm_b_from_bus_pu | pf_vm_c_from_bus_pu | pf_vm_a_to_bus_pu | pf_vm_b_to_bus_pu | pf_vm_c_to_bus_pu | pf_va_a_from_bus_deg | pf_va_b_from_bus_deg | pf_va_c_from_bus_deg | pf_va_a_to_bus_deg | pf_va_b_to_bus_deg | pf_va_c_to_bus_deg
Line_0 | 0 | 0 | 0 | 0 | 3.1191 | 3.1191 | 0 | 0 | 0 | 0 | 36.0161 | 36.0161 | 1.9637e-28 | 1.7764e-14 | -2.3685e-15 | -1.7756e-28 | -16.8865 | 16.8865 | -1.4211e-14 | 4.7631e-09 | -4.7631e-09 | 1.8948e-14 | 6.2558 | -6.2558 | 0 | -159.6723 | 20.3277 | 0 | 20.3277 | -159.6723 | 0.86603 | 0 | 0.86603 | 0.86603 | 0 | 0.86603 | 3.0769e-11 | 0 | 180 | 1.7234e-10 | 0 | 180
Line_1 | 0 | 1.7374 | 1.7374 | 0 | 0 | 0 | 0 | 20.0614 | 20.0614 | 0 | 0 | 0 | -2.3685e-15 | -8.8871 | 8.8871 | 7.1054e-15 | 4.7369e-15 | -2.3685e-15 | 1.6579e-14 | 4.6513 | -4.6513 | -1.8948e-14 | 1.5877e-09 | -1.5877e-09 | 0 | -159.6723 | 20.3277 | 0 | 0 | 0 | 0.86603 | 0 | 0.86603 | 0.86603 | 0 | 0.86603 | 1.9235e-10 | 0 | 180 | 1.7234e-10 | 0 | 180
Line_2 | 0 | 1.7374 | 1.7374 | 0 | 0 | 0 | 0 | 20.0614 | 20.0614 | 0 | 0 | 0 | -8.2897e-15 | -8.8871 | 8.8871 | 1.6579e-14 | 9.4739e-15 | -2.3685e-15 | 1.4211e-14 | 4.6513 | -4.6513 | -1.4211e-14 | 1.5877e-09 | -1.5877e-09 | 0 | -159.6723 | 20.3277 | 0 | 0 | 0 | 0.86603 | 0 | 0.86603 | 0.86603 | 0 | 0.86603 | 1.9236e-10 | 0 | 180 | 1.7234e-10 | 0 | 180
Line_4 | 0 | 0.86868 | 0.86868 | 0 | 0.86868 | 0.86868 | 0 | 10.0307 | 10.0307 | 0 | 10.0307 | 10.0307 | -9.1344e-29 | -4.4435 | 4.4435 | -2.3685e-15 | -4.4435 | 4.4435 | 1.4211e-14 | 2.3257 | -2.3257 | -4.737e-15 | 2.3257 | -2.3257 | 0 | -152.3733 | 27.6267 | 0 | 27.6267 | -152.3733 | 0.86603 | 0 | 0.86603 | 0.86603 | 0 | 0.86603 | 1.9235e-10 | 0 | 180 | 1.9236e-10 | 0 | 180

## LL_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mw | pf_q_b_from_mw | pf_q_c_from_mw | pf_q_a_to_mw | pf_q_b_to_mw | pf_q_c_to_mw | pf_ikss_a_from_deg | pf_ikss_b_from_deg | pf_ikss_c_from_deg | pf_ikss_a_to_deg | pf_ikss_b_to_deg | pf_ikss_c_to_deg | pf_vm_a_from_pu | pf_vm_b_from_bus_pu | pf_vm_c_from_bus_pu | pf_vm_a_to_bus_pu | pf_vm_b_to_bus_pu | pf_vm_c_to_bus_pu | pf_va_a_from_bus_deg | pf_va_b_from_bus_deg | pf_va_c_from_bus_deg | pf_va_a_to_bus_deg | pf_va_b_to_bus_deg | pf_va_c_to_bus_deg
Line_0 | 0 | 0 | 0 | 0 | 1.5183 | 1.5183 | 0 | 0 | 0 | 0 | 17.5318 | 17.5318 | -1.4803e-15 | -8.0025e-10 | -2.5674e-09 | -5.9212e-16 | -13.0917 | 1.5655 | -4.737e-15 | 3.4014e-09 | -3.4064e-10 | 9.4739e-15 | -0.95344 | -10.5727 | 0 | -146.7238 | 33.2762 | 0 | 33.2762 | -146.7238 | 1.0057 | 0.63489 | 0.83074 | 0.95734 | 0.5368 | 0.85298 | 17.5701 | -106.9886 | 158.5648 | 15.9329 | -101.7238 | 162.0554
Line_1 | 0 | 0.9147 | 0.9147 | 0 | 0 | 0 | 0 | 10.5621 | 10.5621 | 0 | 0 | 0 | -1.7764e-15 | -7.4125 | 1.1373 | -5.9212e-16 | -4.7979e-10 | -8.2615e-10 | 4.737e-15 | -0.036791 | -6.2383 | -7.1054e-15 | 1.0532e-09 | -4.5325e-10 | 0 | -146.7238 | 33.2762 | 0 | 0 | 0 | 0.93535 | 0.4851 | 0.86185 | 0.95734 | 0.5368 | 0.85298 | 14.8381 | -99.0449 | 163.8635 | 15.9329 | -101.7238 | 162.0554
Line_2 | 0 | 0.9147 | 0.9147 | 0 | 0 | 0 | 0 | 10.5621 | 10.5621 | 0 | 0 | 0 | -3.5527e-15 | -7.4125 | 1.1373 | -1.1842e-15 | -4.7979e-10 | -8.2616e-10 | -2.3685e-15 | -0.036791 | -6.2383 | -5.3734e-30 | 1.0532e-09 | -4.5325e-10 | 0 | -146.7238 | 33.2762 | 0 | 0 | 0 | 0.93535 | 0.4851 | 0.86185 | 0.95734 | 0.5368 | 0.85298 | 14.8381 | -99.0449 | 163.8635 | 15.9329 | -101.7238 | 162.0554
Line_4 | 0 | 0.45735 | 0.45735 | 0 | 0.45735 | 0.45735 | 0 | 5.2811 | 5.2811 | 0 | 5.2811 | 5.2811 | 5.9212e-16 | -3.7062 | 0.56866 | -5.9212e-15 | -3.7062 | 0.56866 | 2.3685e-15 | -0.018396 | -3.1192 | -2.3685e-15 | -0.018396 | -3.1192 | 0 | -144.0449 | 35.9551 | 0 | 35.9551 | -144.0449 | 0.93535 | 0.4851 | 0.86185 | 0.93535 | 0.4851 | 0.86185 | 14.8381 | -99.0449 | 163.8635 | 14.8381 | -99.0449 | 163.8635

## LL_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mw | pf_q_b_from_mw | pf_q_c_from_mw | pf_q_a_to_mw | pf_q_b_to_mw | pf_q_c_to_mw | pf_ikss_a_from_deg | pf_ikss_b_from_deg | pf_ikss_c_from_deg | pf_ikss_a_to_deg | pf_ikss_b_to_deg | pf_ikss_c_to_deg | pf_vm_a_from_pu | pf_vm_b_from_bus_pu | pf_vm_c_from_bus_pu | pf_vm_a_to_bus_pu | pf_vm_b_to_bus_pu | pf_vm_c_to_bus_pu | pf_va_a_from_bus_deg | pf_va_b_from_bus_deg | pf_va_c_from_bus_deg | pf_va_a_to_bus_deg | pf_va_b_to_bus_deg | pf_va_c_to_bus_deg
Line_0 | 0 | 0 | 0 | 0 | 1.5183 | 1.5183 | 0 | 0 | 0 | 0 | 17.5318 | 17.5318 | -1.4803e-15 | -8.0025e-10 | -2.5674e-09 | -5.9212e-16 | -13.0917 | 1.5655 | -4.737e-15 | 3.4014e-09 | -3.4064e-10 | 9.4739e-15 | -0.95344 | -10.5727 | 0 | -146.7238 | 33.2762 | 0 | 33.2762 | -146.7238 | 1.0057 | 0.63489 | 0.83074 | 0.95734 | 0.5368 | 0.85298 | 17.5701 | -106.9886 | 158.5648 | 15.9329 | -101.7238 | 162.0554
Line_1 | 0 | 0.9147 | 0.9147 | 0 | 0 | 0 | 0 | 10.5621 | 10.5621 | 0 | 0 | 0 | -1.7764e-15 | -7.4125 | 1.1373 | -5.9212e-16 | -4.7979e-10 | -8.2615e-10 | 4.737e-15 | -0.036791 | -6.2383 | -7.1054e-15 | 1.0532e-09 | -4.5325e-10 | 0 | -146.7238 | 33.2762 | 0 | 0 | 0 | 0.93535 | 0.4851 | 0.86185 | 0.95734 | 0.5368 | 0.85298 | 14.8381 | -99.0449 | 163.8635 | 15.9329 | -101.7238 | 162.0554
Line_2 | 0 | 0.9147 | 0.9147 | 0 | 0 | 0 | 0 | 10.5621 | 10.5621 | 0 | 0 | 0 | -3.5527e-15 | -7.4125 | 1.1373 | -1.1842e-15 | -4.7979e-10 | -8.2616e-10 | -2.3685e-15 | -0.036791 | -6.2383 | -5.3734e-30 | 1.0532e-09 | -4.5325e-10 | 0 | -146.7238 | 33.2762 | 0 | 0 | 0 | 0.93535 | 0.4851 | 0.86185 | 0.95734 | 0.5368 | 0.85298 | 14.8381 | -99.0449 | 163.8635 | 15.9329 | -101.7238 | 162.0554
Line_4 | 0 | 0.45735 | 0.45735 | 0 | 0.45735 | 0.45735 | 0 | 5.2811 | 5.2811 | 0 | 5.2811 | 5.2811 | 5.9212e-16 | -3.7062 | 0.56866 | -5.9212e-15 | -3.7062 | 0.56866 | 2.3685e-15 | -0.018396 | -3.1192 | -2.3685e-15 | -0.018396 | -3.1192 | 0 | -144.0449 | 35.9551 | 0 | 35.9551 | -144.0449 | 0.93535 | 0.4851 | 0.86185 | 0.93535 | 0.4851 | 0.86185 | 14.8381 | -99.0449 | 163.8635 | 14.8381 | -99.0449 | 163.8635

## LLG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mw | pf_q_b_from_mw | pf_q_c_from_mw | pf_q_a_to_mw | pf_q_b_to_mw | pf_q_c_to_mw | pf_ikss_a_from_deg | pf_ikss_b_from_deg | pf_ikss_c_from_deg | pf_ikss_a_to_deg | pf_ikss_b_to_deg | pf_ikss_c_to_deg | pf_vm_a_from_pu | pf_vm_b_from_bus_pu | pf_vm_c_from_bus_pu | pf_vm_a_to_bus_pu | pf_vm_b_to_bus_pu | pf_vm_c_to_bus_pu | pf_va_a_from_bus_deg | pf_va_b_from_bus_deg | pf_va_c_from_bus_deg | pf_va_a_to_bus_deg | pf_va_b_to_bus_deg | pf_va_c_to_bus_deg
Line_0 | 0.010681 | 0.010681 | 0.010681 | 0.007957 | 3.6896 | 3.737 | 0.12333 | 0.12333 | 0.12333 | 0.091879 | 42.604 | 43.1515 | 0.0011271 | -6.1786e-14 | -5.4834e-14 | -0.00015604 | 7.7053e-11 | 8.2684e-11 | -0.19915 | -1.0737e-13 | 1.0742e-13 | 0.14764 | -4.719e-11 | 3.3e-11 | 0 | -170.39 | 14.7994 | -89.8584 | 9.4882 | -165.0825 | 0.93227 | 0 | 0.93227 | 0.92771 | 0 | 0.92771 | 0.056497 | 0 | -179.9435 | 0.20213 | 0 | -179.7979
Line_1 | 0.0013113 | 2.1213 | 2.1566 | 0.0039785 | 0.0039785 | 0.0039785 | 0.015142 | 24.4949 | 24.9027 | 0.04594 | 0.04594 | 0.04594 | 0.00033778 | 4.7455e-11 | 5.432e-11 | 7.8017e-05 | -3.6716e-14 | -5.642e-14 | 0.024248 | -3.2823e-11 | 1.7897e-11 | -0.073818 | -9.0246e-14 | 7.6155e-14 | 0 | -170.39 | 14.7994 | 90.1416 | 90.1416 | 90.1416 | 0.92466 | 0 | 0.92466 | 0.92771 | 0 | 0.92771 | 0.27651 | 0 | -179.7235 | 0.20213 | 0 | -179.7979
Line_2 | 0.0013113 | 2.1213 | 2.1566 | 0.0039785 | 0.0039785 | 0.0039785 | 0.015142 | 24.4949 | 24.9027 | 0.04594 | 0.04594 | 0.04594 | 0.00033778 | 4.7506e-11 | 5.4297e-11 | 7.8017e-05 | -3.6716e-14 | -5.642e-14 | 0.024248 | -3.2833e-11 | 1.7949e-11 | -0.073818 | -9.0246e-14 | 7.6155e-14 | 0 | -170.39 | 14.7994 | 90.1416 | 90.1416 | 90.1416 | 0.92466 | 0 | 0.92466 | 0.92771 | 0 | 0.92771 | 0.27651 | 0 | -179.7235 | 0.20213 | 0 | -179.7979
Line_4 | 0.0013113 | 1.0611 | 1.0777 | 0.0013113 | 1.0611 | 1.0777 | 0.015142 | 12.2524 | 12.4442 | 0.015142 | 12.2524 | 12.4442 | -0.00033779 | 2.3707e-11 | 2.7129e-11 | -0.00033779 | 2.3733e-11 | 2.7117e-11 | -0.024248 | -1.6461e-11 | 8.9905e-12 | -0.024248 | -1.6466e-11 | 9.0165e-12 | 0 | -166.4466 | 19.378 | 91.0746 | 13.6225 | -160.6882 | 0.92466 | 0 | 0.92466 | 0.92466 | 0 | 0.92466 | 0.27651 | 0 | -179.7235 | 0.27651 | 0 | -179.7235

## LLG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mw | pf_q_b_from_mw | pf_q_c_from_mw | pf_q_a_to_mw | pf_q_b_to_mw | pf_q_c_to_mw | pf_ikss_a_from_deg | pf_ikss_b_from_deg | pf_ikss_c_from_deg | pf_ikss_a_to_deg | pf_ikss_b_to_deg | pf_ikss_c_to_deg | pf_vm_a_from_pu | pf_vm_b_from_bus_pu | pf_vm_c_from_bus_pu | pf_vm_a_to_bus_pu | pf_vm_b_to_bus_pu | pf_vm_c_to_bus_pu | pf_va_a_from_bus_deg | pf_va_b_from_bus_deg | pf_va_c_from_bus_deg | pf_va_a_to_bus_deg | pf_va_b_to_bus_deg | pf_va_c_to_bus_deg
Line_0 | 0.010681 | 0.010681 | 0.010681 | 0.007957 | 3.6896 | 3.737 | 0.12333 | 0.12333 | 0.12333 | 0.091879 | 42.604 | 43.1515 | 0.0011271 | -6.1786e-14 | -5.4834e-14 | -0.00015604 | 7.7053e-11 | 8.2684e-11 | -0.19915 | -1.0737e-13 | 1.0742e-13 | 0.14764 | -4.719e-11 | 3.3e-11 | 0 | -170.39 | 14.7994 | -89.8584 | 9.4882 | -165.0825 | 0.93227 | 0 | 0.93227 | 0.92771 | 0 | 0.92771 | 0.056497 | 0 | -179.9435 | 0.20213 | 0 | -179.7979
Line_1 | 0.0013113 | 2.1213 | 2.1566 | 0.0039785 | 0.0039785 | 0.0039785 | 0.015142 | 24.4949 | 24.9027 | 0.04594 | 0.04594 | 0.04594 | 0.00033778 | 4.7455e-11 | 5.432e-11 | 7.8017e-05 | -3.6716e-14 | -5.642e-14 | 0.024248 | -3.2823e-11 | 1.7897e-11 | -0.073818 | -9.0246e-14 | 7.6155e-14 | 0 | -170.39 | 14.7994 | 90.1416 | 90.1416 | 90.1416 | 0.92466 | 0 | 0.92466 | 0.92771 | 0 | 0.92771 | 0.27651 | 0 | -179.7235 | 0.20213 | 0 | -179.7979
Line_2 | 0.0013113 | 2.1213 | 2.1566 | 0.0039785 | 0.0039785 | 0.0039785 | 0.015142 | 24.4949 | 24.9027 | 0.04594 | 0.04594 | 0.04594 | 0.00033778 | 4.7506e-11 | 5.4297e-11 | 7.8017e-05 | -3.6716e-14 | -5.642e-14 | 0.024248 | -3.2833e-11 | 1.7949e-11 | -0.073818 | -9.0246e-14 | 7.6155e-14 | 0 | -170.39 | 14.7994 | 90.1416 | 90.1416 | 90.1416 | 0.92466 | 0 | 0.92466 | 0.92771 | 0 | 0.92771 | 0.27651 | 0 | -179.7235 | 0.20213 | 0 | -179.7979
Line_4 | 0.0013113 | 1.0611 | 1.0777 | 0.0013113 | 1.0611 | 1.0777 | 0.015142 | 12.2524 | 12.4442 | 0.015142 | 12.2524 | 12.4442 | -0.00033779 | 2.3707e-11 | 2.7129e-11 | -0.00033779 | 2.3733e-11 | 2.7117e-11 | -0.024248 | -1.6461e-11 | 8.9905e-12 | -0.024248 | -1.6466e-11 | 9.0165e-12 | 0 | -166.4466 | 19.378 | 91.0746 | 13.6225 | -160.6882 | 0.92466 | 0 | 0.92466 | 0.92466 | 0 | 0.92466 | 0.27651 | 0 | -179.7235 | 0.27651 | 0 | -179.7235

## LLG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mw | pf_q_b_from_mw | pf_q_c_from_mw | pf_q_a_to_mw | pf_q_b_to_mw | pf_q_c_to_mw | pf_ikss_a_from_deg | pf_ikss_b_from_deg | pf_ikss_c_from_deg | pf_ikss_a_to_deg | pf_ikss_b_to_deg | pf_ikss_c_to_deg | pf_vm_a_from_pu | pf_vm_b_from_bus_pu | pf_vm_c_from_bus_pu | pf_vm_a_to_bus_pu | pf_vm_b_to_bus_pu | pf_vm_c_to_bus_pu | pf_va_a_from_bus_deg | pf_va_b_from_bus_deg | pf_va_c_from_bus_deg | pf_va_a_to_bus_deg | pf_va_b_to_bus_deg | pf_va_c_to_bus_deg
Line_0 | 0.0093084 | 0.0093084 | 0.0093084 | 0.006916 | 1.0785 | 1.2072 | 0.10748 | 0.10748 | 0.10748 | 0.079859 | 12.4537 | 13.9393 | -0.01336 | -0.07066 | 0.084876 | 0.0092229 | -5.7952 | -7.2958 | -0.16565 | 0.03056 | -0.016167 | 0.12251 | -5.8645 | -7.2282 | 0 | -151.6456 | 41.8613 | -83.7723 | 28.0141 | -137.8719 | 1.098 | 0.87234 | 0.96081 | 1.0729 | 0.80202 | 0.95035 | 22.9504 | -100.051 | 153.3589 | 21.6594 | -99.5297 | 155.4443
Line_1 | 0.0011392 | 0.68583 | 0.76033 | 0.003458 | 0.003458 | 0.003458 | 0.013154 | 7.9193 | 8.7796 | 0.039929 | 0.039929 | 0.039929 | 0.0016976 | -3.5245 | -4.3372 | -0.0046114 | -0.024356 | 0.029027 | 0.020104 | -3.5354 | -4.3267 | -0.061253 | 0.010275 | -0.0047878 | 0 | -151.6456 | 41.8613 | 96.2277 | 96.2277 | 96.2277 | 1.0585 | 0.76108 | 0.94432 | 1.0729 | 0.80202 | 0.95035 | 20.8705 | -99.2264 | 156.6601 | 21.6594 | -99.5297 | 155.4443
Line_2 | 0.0011392 | 0.68583 | 0.76033 | 0.003458 | 0.003458 | 0.003458 | 0.013154 | 7.9193 | 8.7796 | 0.039929 | 0.039929 | 0.039929 | 0.0016976 | -3.5245 | -4.3372 | -0.0046114 | -0.024356 | 0.029027 | 0.020104 | -3.5354 | -4.3267 | -0.061253 | 0.010275 | -0.0047878 | 0 | -151.6456 | 41.8613 | 96.2277 | 96.2277 | 96.2277 | 1.0585 | 0.76108 | 0.94432 | 1.0729 | 0.80202 | 0.95035 | 20.8705 | -99.2264 | 156.6601 | 21.6594 | -99.5297 | 155.4443
Line_4 | 0.0011392 | 0.34355 | 0.37917 | 0.0011392 | 0.34355 | 0.37917 | 0.013154 | 3.967 | 4.3783 | 0.013154 | 3.967 | 4.3783 | -0.0016976 | -1.7737 | -2.155 | -0.0016976 | -1.7737 | -2.155 | -0.020104 | -1.7628 | -2.1656 | -0.020104 | -1.7628 | -2.1656 | 0 | -151.6064 | 42.437 | 96.6611 | 28.57 | -137.7027 | 1.0585 | 0.76108 | 0.94432 | 1.0585 | 0.76108 | 0.94432 | 20.8705 | -99.2264 | 156.6601 | 20.8705 | -99.2264 | 156.6601

## LLG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mw | pf_q_b_from_mw | pf_q_c_from_mw | pf_q_a_to_mw | pf_q_b_to_mw | pf_q_c_to_mw | pf_ikss_a_from_deg | pf_ikss_b_from_deg | pf_ikss_c_from_deg | pf_ikss_a_to_deg | pf_ikss_b_to_deg | pf_ikss_c_to_deg | pf_vm_a_from_pu | pf_vm_b_from_bus_pu | pf_vm_c_from_bus_pu | pf_vm_a_to_bus_pu | pf_vm_b_to_bus_pu | pf_vm_c_to_bus_pu | pf_va_a_from_bus_deg | pf_va_b_from_bus_deg | pf_va_c_from_bus_deg | pf_va_a_to_bus_deg | pf_va_b_to_bus_deg | pf_va_c_to_bus_deg
Line_0 | 0.0093084 | 0.0093084 | 0.0093084 | 0.006916 | 1.0785 | 1.2072 | 0.10748 | 0.10748 | 0.10748 | 0.079859 | 12.4537 | 13.9393 | -0.01336 | -0.07066 | 0.084876 | 0.0092229 | -5.7952 | -7.2958 | -0.16565 | 0.03056 | -0.016167 | 0.12251 | -5.8645 | -7.2282 | 0 | -151.6456 | 41.8613 | -83.7723 | 28.0141 | -137.8719 | 1.098 | 0.87234 | 0.96081 | 1.0729 | 0.80202 | 0.95035 | 22.9504 | -100.051 | 153.3589 | 21.6594 | -99.5297 | 155.4443
Line_1 | 0.0011392 | 0.68583 | 0.76033 | 0.003458 | 0.003458 | 0.003458 | 0.013154 | 7.9193 | 8.7796 | 0.039929 | 0.039929 | 0.039929 | 0.0016976 | -3.5245 | -4.3372 | -0.0046114 | -0.024356 | 0.029027 | 0.020104 | -3.5354 | -4.3267 | -0.061253 | 0.010275 | -0.0047878 | 0 | -151.6456 | 41.8613 | 96.2277 | 96.2277 | 96.2277 | 1.0585 | 0.76108 | 0.94432 | 1.0729 | 0.80202 | 0.95035 | 20.8705 | -99.2264 | 156.6601 | 21.6594 | -99.5297 | 155.4443
Line_2 | 0.0011392 | 0.68583 | 0.76033 | 0.003458 | 0.003458 | 0.003458 | 0.013154 | 7.9193 | 8.7796 | 0.039929 | 0.039929 | 0.039929 | 0.0016976 | -3.5245 | -4.3372 | -0.0046114 | -0.024356 | 0.029027 | 0.020104 | -3.5354 | -4.3267 | -0.061253 | 0.010275 | -0.0047878 | 0 | -151.6456 | 41.8613 | 96.2277 | 96.2277 | 96.2277 | 1.0585 | 0.76108 | 0.94432 | 1.0729 | 0.80202 | 0.95035 | 20.8705 | -99.2264 | 156.6601 | 21.6594 | -99.5297 | 155.4443
Line_4 | 0.0011392 | 0.34355 | 0.37917 | 0.0011392 | 0.34355 | 0.37917 | 0.013154 | 3.967 | 4.3783 | 0.013154 | 3.967 | 4.3783 | -0.0016976 | -1.7737 | -2.155 | -0.0016976 | -1.7737 | -2.155 | -0.020104 | -1.7628 | -2.1656 | -0.020104 | -1.7628 | -2.1656 | 0 | -151.6064 | 42.437 | 96.6611 | 28.57 | -137.7027 | 1.0585 | 0.76108 | 0.94432 | 1.0585 | 0.76108 | 0.94432 | 20.8705 | -99.2264 | 156.6601 | 20.8705 | -99.2264 | 156.6601

## LLG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mw | pf_q_b_from_mw | pf_q_c_from_mw | pf_q_a_to_mw | pf_q_b_to_mw | pf_q_c_to_mw | pf_ikss_a_from_deg | pf_ikss_b_from_deg | pf_ikss_c_from_deg | pf_ikss_a_to_deg | pf_ikss_b_to_deg | pf_ikss_c_to_deg | pf_vm_a_from_pu | pf_vm_b_from_bus_pu | pf_vm_c_from_bus_pu | pf_vm_a_to_bus_pu | pf_vm_b_to_bus_pu | pf_vm_c_to_bus_pu | pf_va_a_from_bus_deg | pf_va_b_from_bus_deg | pf_va_c_from_bus_deg | pf_va_a_to_bus_deg | pf_va_b_to_bus_deg | pf_va_c_to_bus_deg
Line_0 | 0.0096996 | 0.0096996 | 0.0096996 | 0.0072221 | 3.0906 | 3.1555 | 0.112 | 0.112 | 0.112 | 0.083393 | 35.6868 | 36.4361 | 0.0017846 | -1.0542e-13 | 1.1358e-13 | -0.0002468 | -1.3488e-10 | 2.9685e-11 | -0.16424 | 6.4442e-14 | 5.5601e-14 | 0.12162 | -1.3588e-10 | -1.9413e-10 | 0 | -162.4481 | 23.0506 | -89.789 | 17.4241 | -156.8285 | 0.84668 | 0 | 0.84668 | 0.84203 | 0 | 0.84203 | 0.059826 | 0 | -179.9402 | 0.3273 | 0 | -179.6727
Line_1 | 0.0011843 | 1.7165 | 1.7636 | 0.003611 | 0.003611 | 0.003611 | 0.013676 | 19.8206 | 20.3638 | 0.041697 | 0.041697 | 0.041697 | 0.00051309 | -9.2591e-11 | 2.8494e-12 | 0.0001234 | -1.9829e-13 | 1.913e-13 | 0.019858 | -7.338e-11 | -1.2175e-10 | -0.060812 | 1.0356e-13 | 1.1794e-13 | 0 | -162.4481 | 23.0506 | 90.211 | 90.211 | 90.211 | 0.83865 | 0 | 0.83865 | 0.84203 | 0 | 0.84203 | 0.45314 | 0 | -179.5469 | 0.3273 | 0 | -179.6727
Line_2 | 0.0011843 | 1.7165 | 1.7636 | 0.003611 | 0.003611 | 0.003611 | 0.013676 | 19.8206 | 20.3638 | 0.041697 | 0.041697 | 0.041697 | 0.00051309 | -9.2571e-11 | 2.8162e-12 | 0.0001234 | -1.9829e-13 | 1.913e-13 | 0.019858 | -7.3367e-11 | -1.2176e-10 | -0.060812 | 1.0356e-13 | 1.1794e-13 | 0 | -162.4481 | 23.0506 | 90.211 | 90.211 | 90.211 | 0.83865 | 0 | 0.83865 | 0.84203 | 0 | 0.84203 | 0.45314 | 0 | -179.5469 | 0.3273 | 0 | -179.6727
Line_4 | 0.0011843 | 0.85894 | 0.88092 | 0.0011843 | 0.85894 | 0.88092 | 0.013676 | 9.9181 | 10.172 | 0.013676 | 9.9181 | 10.172 | -0.00051309 | -4.6402e-11 | 1.5307e-12 | -0.00051309 | -4.6392e-11 | 1.5142e-12 | -0.019858 | -3.663e-11 | -6.0812e-11 | -0.019858 | -3.6624e-11 | -6.0817e-11 | 0 | -155.5522 | 30.7225 | 91.9332 | 24.5207 | -149.345 | 0.83865 | 0 | 0.83865 | 0.83865 | 0 | 0.83865 | 0.45314 | 0 | -179.5469 | 0.45314 | 0 | -179.5469

## LLG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mw | pf_q_b_from_mw | pf_q_c_from_mw | pf_q_a_to_mw | pf_q_b_to_mw | pf_q_c_to_mw | pf_ikss_a_from_deg | pf_ikss_b_from_deg | pf_ikss_c_from_deg | pf_ikss_a_to_deg | pf_ikss_b_to_deg | pf_ikss_c_to_deg | pf_vm_a_from_pu | pf_vm_b_from_bus_pu | pf_vm_c_from_bus_pu | pf_vm_a_to_bus_pu | pf_vm_b_to_bus_pu | pf_vm_c_to_bus_pu | pf_va_a_from_bus_deg | pf_va_b_from_bus_deg | pf_va_c_from_bus_deg | pf_va_a_to_bus_deg | pf_va_b_to_bus_deg | pf_va_c_to_bus_deg
Line_0 | 0.0096996 | 0.0096996 | 0.0096996 | 0.0072221 | 3.0906 | 3.1555 | 0.112 | 0.112 | 0.112 | 0.083393 | 35.6868 | 36.4361 | 0.0017846 | -1.0542e-13 | 1.1358e-13 | -0.0002468 | -1.3488e-10 | 2.9685e-11 | -0.16424 | 6.4442e-14 | 5.5601e-14 | 0.12162 | -1.3588e-10 | -1.9413e-10 | 0 | -162.4481 | 23.0506 | -89.789 | 17.4241 | -156.8285 | 0.84668 | 0 | 0.84668 | 0.84203 | 0 | 0.84203 | 0.059826 | 0 | -179.9402 | 0.3273 | 0 | -179.6727
Line_1 | 0.0011843 | 1.7165 | 1.7636 | 0.003611 | 0.003611 | 0.003611 | 0.013676 | 19.8206 | 20.3638 | 0.041697 | 0.041697 | 0.041697 | 0.00051309 | -9.2591e-11 | 2.8494e-12 | 0.0001234 | -1.9829e-13 | 1.913e-13 | 0.019858 | -7.338e-11 | -1.2175e-10 | -0.060812 | 1.0356e-13 | 1.1794e-13 | 0 | -162.4481 | 23.0506 | 90.211 | 90.211 | 90.211 | 0.83865 | 0 | 0.83865 | 0.84203 | 0 | 0.84203 | 0.45314 | 0 | -179.5469 | 0.3273 | 0 | -179.6727
Line_2 | 0.0011843 | 1.7165 | 1.7636 | 0.003611 | 0.003611 | 0.003611 | 0.013676 | 19.8206 | 20.3638 | 0.041697 | 0.041697 | 0.041697 | 0.00051309 | -9.2571e-11 | 2.8162e-12 | 0.0001234 | -1.9829e-13 | 1.913e-13 | 0.019858 | -7.3367e-11 | -1.2176e-10 | -0.060812 | 1.0356e-13 | 1.1794e-13 | 0 | -162.4481 | 23.0506 | 90.211 | 90.211 | 90.211 | 0.83865 | 0 | 0.83865 | 0.84203 | 0 | 0.84203 | 0.45314 | 0 | -179.5469 | 0.3273 | 0 | -179.6727
Line_4 | 0.0011843 | 0.85894 | 0.88092 | 0.0011843 | 0.85894 | 0.88092 | 0.013676 | 9.9181 | 10.172 | 0.013676 | 9.9181 | 10.172 | -0.00051309 | -4.6402e-11 | 1.5307e-12 | -0.00051309 | -4.6392e-11 | 1.5142e-12 | -0.019858 | -3.663e-11 | -6.0812e-11 | -0.019858 | -3.6624e-11 | -6.0817e-11 | 0 | -155.5522 | 30.7225 | 91.9332 | 24.5207 | -149.345 | 0.83865 | 0 | 0.83865 | 0.83865 | 0 | 0.83865 | 0.45314 | 0 | -179.5469 | 0.45314 | 0 | -179.5469

## LLG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mw | pf_q_b_from_mw | pf_q_c_from_mw | pf_q_a_to_mw | pf_q_b_to_mw | pf_q_c_to_mw | pf_ikss_a_from_deg | pf_ikss_b_from_deg | pf_ikss_c_from_deg | pf_ikss_a_to_deg | pf_ikss_b_to_deg | pf_ikss_c_to_deg | pf_vm_a_from_pu | pf_vm_b_from_bus_pu | pf_vm_c_from_bus_pu | pf_vm_a_to_bus_pu | pf_vm_b_to_bus_pu | pf_vm_c_to_bus_pu | pf_va_a_from_bus_deg | pf_va_b_from_bus_deg | pf_va_c_from_bus_deg | pf_va_a_to_bus_deg | pf_va_b_to_bus_deg | pf_va_c_to_bus_deg
Line_0 | 0.0084543 | 0.0084543 | 0.0084543 | 0.0062443 | 0.94654 | 1.055 | 0.097622 | 0.097622 | 0.097622 | 0.072103 | 10.9297 | 12.1826 | -0.010301 | -0.057704 | 0.06936 | 0.0067055 | -4.4647 | -5.5708 | -0.13671 | 0.025112 | -0.013175 | 0.10033 | -4.5187 | -5.5193 | 0 | -149.9984 | 44.0113 | -84.3332 | 29.6572 | -135.7227 | 0.99726 | 0.78485 | 0.86933 | 0.95784 | 0.70193 | 0.86997 | 22.6911 | -100.4046 | 153.5481 | 21.434 | -97.6343 | 156.587
Line_1 | 0.0010227 | 0.59317 | 0.65246 | 0.0031222 | 0.0031222 | 0.0031222 | 0.01181 | 6.8493 | 7.5339 | 0.036052 | 0.036052 | 0.036052 | 0.0013799 | -2.6366 | -3.1934 | -0.0033528 | -0.019605 | 0.02305 | 0.01635 | -2.6449 | -3.1857 | -0.050165 | 0.0073945 | -0.0026896 | 0 | -149.9984 | 44.0113 | 95.6668 | 95.6668 | 95.6668 | 0.93662 | 0.65508 | 0.86902 | 0.95784 | 0.70193 | 0.86997 | 20.5976 | -96.0933 | 158.2606 | 21.434 | -97.6343 | 156.587
Line_2 | 0.0010227 | 0.59317 | 0.65246 | 0.0031222 | 0.0031222 | 0.0031222 | 0.01181 | 6.8493 | 7.5339 | 0.036052 | 0.036052 | 0.036052 | 0.0013799 | -2.6366 | -3.1934 | -0.0033528 | -0.019605 | 0.02305 | 0.01635 | -2.6449 | -3.1857 | -0.050165 | 0.0073945 | -0.0026896 | 0 | -149.9984 | 44.0113 | 95.6668 | 95.6668 | 95.6668 | 0.93662 | 0.65508 | 0.86902 | 0.95784 | 0.70193 | 0.86997 | 20.5976 | -96.0933 | 158.2606 | 21.434 | -97.6343 | 156.587
Line_4 | 0.0010227 | 0.29723 | 0.32526 | 0.0010227 | 0.29723 | 0.32526 | 0.01181 | 3.4321 | 3.7557 | 0.01181 | 3.4321 | 3.7557 | -0.0013799 | -1.3274 | -1.5862 | -0.0013799 | -1.3274 | -1.5862 | -0.01635 | -1.3191 | -1.5939 | -0.01635 | -1.3191 | -1.5939 | 0 | -148.7746 | 45.8984 | 96.5216 | 31.4045 | -134.2408 | 0.93662 | 0.65508 | 0.86902 | 0.93662 | 0.65508 | 0.86902 | 20.5976 | -96.0933 | 158.2606 | 20.5976 | -96.0933 | 158.2606

## LLG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mw | pf_q_b_from_mw | pf_q_c_from_mw | pf_q_a_to_mw | pf_q_b_to_mw | pf_q_c_to_mw | pf_ikss_a_from_deg | pf_ikss_b_from_deg | pf_ikss_c_from_deg | pf_ikss_a_to_deg | pf_ikss_b_to_deg | pf_ikss_c_to_deg | pf_vm_a_from_pu | pf_vm_b_from_bus_pu | pf_vm_c_from_bus_pu | pf_vm_a_to_bus_pu | pf_vm_b_to_bus_pu | pf_vm_c_to_bus_pu | pf_va_a_from_bus_deg | pf_va_b_from_bus_deg | pf_va_c_from_bus_deg | pf_va_a_to_bus_deg | pf_va_b_to_bus_deg | pf_va_c_to_bus_deg
Line_0 | 0.0084543 | 0.0084543 | 0.0084543 | 0.0062443 | 0.94654 | 1.055 | 0.097622 | 0.097622 | 0.097622 | 0.072103 | 10.9297 | 12.1826 | -0.010301 | -0.057704 | 0.06936 | 0.0067055 | -4.4647 | -5.5708 | -0.13671 | 0.025112 | -0.013175 | 0.10033 | -4.5187 | -5.5193 | 0 | -149.9984 | 44.0113 | -84.3332 | 29.6572 | -135.7227 | 0.99726 | 0.78485 | 0.86933 | 0.95784 | 0.70193 | 0.86997 | 22.6911 | -100.4046 | 153.5481 | 21.434 | -97.6343 | 156.587
Line_1 | 0.0010227 | 0.59317 | 0.65246 | 0.0031222 | 0.0031222 | 0.0031222 | 0.01181 | 6.8493 | 7.5339 | 0.036052 | 0.036052 | 0.036052 | 0.0013799 | -2.6366 | -3.1934 | -0.0033528 | -0.019605 | 0.02305 | 0.01635 | -2.6449 | -3.1857 | -0.050165 | 0.0073945 | -0.0026896 | 0 | -149.9984 | 44.0113 | 95.6668 | 95.6668 | 95.6668 | 0.93662 | 0.65508 | 0.86902 | 0.95784 | 0.70193 | 0.86997 | 20.5976 | -96.0933 | 158.2606 | 21.434 | -97.6343 | 156.587
Line_2 | 0.0010227 | 0.59317 | 0.65246 | 0.0031222 | 0.0031222 | 0.0031222 | 0.01181 | 6.8493 | 7.5339 | 0.036052 | 0.036052 | 0.036052 | 0.0013799 | -2.6366 | -3.1934 | -0.0033528 | -0.019605 | 0.02305 | 0.01635 | -2.6449 | -3.1857 | -0.050165 | 0.0073945 | -0.0026896 | 0 | -149.9984 | 44.0113 | 95.6668 | 95.6668 | 95.6668 | 0.93662 | 0.65508 | 0.86902 | 0.95784 | 0.70193 | 0.86997 | 20.5976 | -96.0933 | 158.2606 | 21.434 | -97.6343 | 156.587
Line_4 | 0.0010227 | 0.29723 | 0.32526 | 0.0010227 | 0.29723 | 0.32526 | 0.01181 | 3.4321 | 3.7557 | 0.01181 | 3.4321 | 3.7557 | -0.0013799 | -1.3274 | -1.5862 | -0.0013799 | -1.3274 | -1.5862 | -0.01635 | -1.3191 | -1.5939 | -0.01635 | -1.3191 | -1.5939 | 0 | -148.7746 | 45.8984 | 96.5216 | 31.4045 | -134.2408 | 0.93662 | 0.65508 | 0.86902 | 0.93662 | 0.65508 | 0.86902 | 20.5976 | -96.0933 | 158.2606 | 20.5976 | -96.0933 | 158.2606

## LG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mw | pf_q_b_from_mw | pf_q_c_from_mw | pf_q_a_to_mw | pf_q_b_to_mw | pf_q_c_to_mw | pf_ikss_a_from_deg | pf_ikss_b_from_deg | pf_ikss_c_from_deg | pf_ikss_a_to_deg | pf_ikss_b_to_deg | pf_ikss_c_to_deg | pf_vm_a_from_pu | pf_vm_b_from_bus_pu | pf_vm_c_from_bus_pu | pf_vm_a_to_bus_pu | pf_vm_b_to_bus_pu | pf_vm_c_to_bus_pu | pf_va_a_from_bus_deg | pf_va_b_from_bus_deg | pf_va_c_from_bus_deg | pf_va_a_to_bus_deg | pf_va_b_to_bus_deg | pf_va_c_to_bus_deg
Line_0 | 0.020075 | 0.020075 | 0.020075 | 0.64343 | 0.014755 | 0.014755 | 0.2318 | 0.2318 | 0.2318 | 7.4297 | 0.17038 | 0.17038 | -4.0446e-13 | 0.22281 | -0.21883 | 1.1793e-11 | -0.16256 | 0.16203 | 1.2696e-13 | -0.35132 | -0.35218 | -4.9539e-12 | 0.25579 | 0.25188 | -84.7131 | 0 | 0 | 95.1815 | 90.6891 | 90.6891 | 1.0362 | 1.1 | 1.0327 | 1.027 | 1.1 | 1.0149 | 32.2717 | -90 | 148.033 | 33.1268 | -90 | 147.9374
Line_1 | 0.40688 | 0.0024101 | 0.0024101 | 0.0073776 | 0.0073776 | 0.0073776 | 4.6982 | 0.027829 | 0.027829 | 0.085189 | 0.085189 | 0.085189 | 6.9756e-12 | -0.025927 | 0.027068 | -1.3925e-13 | 0.081281 | -0.081013 | -3.3644e-12 | 0.041793 | 0.040114 | 4.6035e-14 | -0.12789 | -0.12594 | -84.7131 | 0 | 0 | -89.3109 | -89.3109 | -89.3109 | 1.0203 | 1.1 | 1.004 | 1.027 | 1.1 | 1.0149 | 33.6286 | -90 | 147.804 | 33.1268 | -90 | 147.9374
Line_2 | 0.40688 | 0.0024101 | 0.0024101 | 0.0073776 | 0.0073776 | 0.0073776 | 4.6982 | 0.027829 | 0.027829 | 0.085189 | 0.085189 | 0.085189 | 6.9733e-12 | -0.025927 | 0.027068 | -1.3925e-13 | 0.081281 | -0.081013 | -3.363e-12 | 0.041793 | 0.040114 | 4.6035e-14 | -0.12789 | -0.12594 | -84.7131 | 0 | 0 | -89.3109 | -89.3109 | -89.3109 | 1.0203 | 1.1 | 1.004 | 1.027 | 1.1 | 1.0149 | 33.6286 | -90 | 147.804 | 33.1268 | -90 | 147.9374
Line_4 | 0.19985 | 0.0024101 | 0.0024101 | 0.19985 | 0.0024101 | 0.0024101 | 2.3076 | 0.027829 | 0.027829 | 2.3076 | 0.027829 | 0.027829 | 3.4229e-12 | 0.025927 | -0.027068 | 3.4218e-12 | 0.025927 | -0.027068 | -1.6593e-12 | -0.041793 | -0.040114 | -1.6586e-12 | -0.041793 | -0.040114 | -81.8327 | 0 | 0 | 98.2437 | -88.1855 | -88.1855 | 1.0203 | 1.1 | 1.004 | 1.0203 | 1.1 | 1.004 | 33.6286 | -90 | 147.804 | 33.6286 | -90 | 147.804

## LG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mw | pf_q_b_from_mw | pf_q_c_from_mw | pf_q_a_to_mw | pf_q_b_to_mw | pf_q_c_to_mw | pf_ikss_a_from_deg | pf_ikss_b_from_deg | pf_ikss_c_from_deg | pf_ikss_a_to_deg | pf_ikss_b_to_deg | pf_ikss_c_to_deg | pf_vm_a_from_pu | pf_vm_b_from_bus_pu | pf_vm_c_from_bus_pu | pf_vm_a_to_bus_pu | pf_vm_b_to_bus_pu | pf_vm_c_to_bus_pu | pf_va_a_from_bus_deg | pf_va_b_from_bus_deg | pf_va_c_from_bus_deg | pf_va_a_to_bus_deg | pf_va_b_to_bus_deg | pf_va_c_to_bus_deg
Line_0 | 0.020075 | 0.020075 | 0.020075 | 0.64343 | 0.014755 | 0.014755 | 0.2318 | 0.2318 | 0.2318 | 7.4297 | 0.17038 | 0.17038 | -4.0446e-13 | 0.22281 | -0.21883 | 1.1793e-11 | -0.16256 | 0.16203 | 1.2696e-13 | -0.35132 | -0.35218 | -4.9539e-12 | 0.25579 | 0.25188 | -84.7131 | 0 | 0 | 95.1815 | 90.6891 | 90.6891 | 1.0362 | 1.1 | 1.0327 | 1.027 | 1.1 | 1.0149 | 32.2717 | -90 | 148.033 | 33.1268 | -90 | 147.9374
Line_1 | 0.40688 | 0.0024101 | 0.0024101 | 0.0073776 | 0.0073776 | 0.0073776 | 4.6982 | 0.027829 | 0.027829 | 0.085189 | 0.085189 | 0.085189 | 6.9756e-12 | -0.025927 | 0.027068 | -1.3925e-13 | 0.081281 | -0.081013 | -3.3644e-12 | 0.041793 | 0.040114 | 4.6035e-14 | -0.12789 | -0.12594 | -84.7131 | 0 | 0 | -89.3109 | -89.3109 | -89.3109 | 1.0203 | 1.1 | 1.004 | 1.027 | 1.1 | 1.0149 | 33.6286 | -90 | 147.804 | 33.1268 | -90 | 147.9374
Line_2 | 0.40688 | 0.0024101 | 0.0024101 | 0.0073776 | 0.0073776 | 0.0073776 | 4.6982 | 0.027829 | 0.027829 | 0.085189 | 0.085189 | 0.085189 | 6.9733e-12 | -0.025927 | 0.027068 | -1.3925e-13 | 0.081281 | -0.081013 | -3.363e-12 | 0.041793 | 0.040114 | 4.6035e-14 | -0.12789 | -0.12594 | -84.7131 | 0 | 0 | -89.3109 | -89.3109 | -89.3109 | 1.0203 | 1.1 | 1.004 | 1.027 | 1.1 | 1.0149 | 33.6286 | -90 | 147.804 | 33.1268 | -90 | 147.9374
Line_4 | 0.19985 | 0.0024101 | 0.0024101 | 0.19985 | 0.0024101 | 0.0024101 | 2.3076 | 0.027829 | 0.027829 | 2.3076 | 0.027829 | 0.027829 | 3.4229e-12 | 0.025927 | -0.027068 | 3.4218e-12 | 0.025927 | -0.027068 | -1.6593e-12 | -0.041793 | -0.040114 | -1.6586e-12 | -0.041793 | -0.040114 | -81.8327 | 0 | 0 | 98.2437 | -88.1855 | -88.1855 | 1.0203 | 1.1 | 1.004 | 1.0203 | 1.1 | 1.004 | 33.6286 | -90 | 147.804 | 33.6286 | -90 | 147.804

## LG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mw | pf_q_b_from_mw | pf_q_c_from_mw | pf_q_a_to_mw | pf_q_b_to_mw | pf_q_c_to_mw | pf_ikss_a_from_deg | pf_ikss_b_from_deg | pf_ikss_c_from_deg | pf_ikss_a_to_deg | pf_ikss_b_to_deg | pf_ikss_c_to_deg | pf_vm_a_from_pu | pf_vm_b_from_bus_pu | pf_vm_c_from_bus_pu | pf_vm_a_to_bus_pu | pf_vm_b_to_bus_pu | pf_vm_c_to_bus_pu | pf_va_a_from_bus_deg | pf_va_b_from_bus_deg | pf_va_c_from_bus_deg | pf_va_a_to_bus_deg | pf_va_b_to_bus_deg | pf_va_c_to_bus_deg
Line_0 | 0.01558 | 0.01558 | 0.01558 | 0.49925 | 0.011449 | 0.011449 | 0.1799 | 0.1799 | 0.1799 | 5.7648 | 0.1322 | 0.1322 | 0.039826 | 0.14921 | -0.18664 | -1.2155 | -0.11112 | 0.13639 | 0.04032 | -0.26626 | -0.1978 | -1.22 | 0.1912 | 0.14451 | -74.7204 | 0 | 0 | 105.1743 | 100.6819 | 100.6819 | 1.0446 | 1.1 | 1.0546 | 1.036 | 1.1 | 1.0401 | 31.1576 | -90 | 147.9584 | 31.8128 | -90 | 147.8258
Line_1 | 0.3163 | 0.0018735 | 0.0018735 | 0.0057244 | 0.0057244 | 0.0057244 | 3.6523 | 0.021634 | 0.021634 | 0.066099 | 0.066099 | 0.066099 | -0.74542 | -0.017943 | 0.022535 | 0.012799 | 0.055558 | -0.068195 | -0.74639 | 0.031076 | 0.023302 | 0.015037 | -0.0956 | -0.072257 | -74.7204 | 0 | 0 | -79.3181 | -79.3181 | -79.3181 | 1.0301 | 1.1 | 1.0312 | 1.036 | 1.1 | 1.0401 | 32.2018 | -90 | 147.7006 | 31.8128 | -90 | 147.8258
Line_2 | 0.3163 | 0.0018735 | 0.0018735 | 0.0057244 | 0.0057244 | 0.0057244 | 3.6523 | 0.021634 | 0.021634 | 0.066099 | 0.066099 | 0.066099 | -0.74542 | -0.017943 | 0.022535 | 0.012799 | 0.055558 | -0.068195 | -0.74639 | 0.031076 | 0.023302 | 0.015037 | -0.0956 | -0.072257 | -74.7204 | 0 | 0 | -79.3181 | -79.3181 | -79.3181 | 1.0301 | 1.1 | 1.0312 | 1.036 | 1.1 | 1.0401 | 32.2018 | -90 | 147.7006 | 31.8128 | -90 | 147.8258
Line_4 | 0.15535 | 0.0018735 | 0.0018735 | 0.15535 | 0.0018735 | 0.0018735 | 1.7939 | 0.021634 | 0.021634 | 1.7939 | 0.021634 | 0.021634 | -0.36685 | 0.017943 | -0.022535 | -0.36685 | 0.017943 | -0.022535 | -0.36588 | -0.031076 | -0.023302 | -0.36588 | -0.031076 | -0.023302 | -72.7764 | 0 | 0 | 107.3 | -79.1292 | -79.1292 | 1.0301 | 1.1 | 1.0312 | 1.0301 | 1.1 | 1.0312 | 32.2018 | -90 | 147.7006 | 32.2018 | -90 | 147.7006

## LG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mw | pf_q_b_from_mw | pf_q_c_from_mw | pf_q_a_to_mw | pf_q_b_to_mw | pf_q_c_to_mw | pf_ikss_a_from_deg | pf_ikss_b_from_deg | pf_ikss_c_from_deg | pf_ikss_a_to_deg | pf_ikss_b_to_deg | pf_ikss_c_to_deg | pf_vm_a_from_pu | pf_vm_b_from_bus_pu | pf_vm_c_from_bus_pu | pf_vm_a_to_bus_pu | pf_vm_b_to_bus_pu | pf_vm_c_to_bus_pu | pf_va_a_from_bus_deg | pf_va_b_from_bus_deg | pf_va_c_from_bus_deg | pf_va_a_to_bus_deg | pf_va_b_to_bus_deg | pf_va_c_to_bus_deg
Line_0 | 0.01558 | 0.01558 | 0.01558 | 0.49925 | 0.011449 | 0.011449 | 0.1799 | 0.1799 | 0.1799 | 5.7648 | 0.1322 | 0.1322 | 0.039826 | 0.14921 | -0.18664 | -1.2155 | -0.11112 | 0.13639 | 0.04032 | -0.26626 | -0.1978 | -1.22 | 0.1912 | 0.14451 | -74.7204 | 0 | 0 | 105.1743 | 100.6819 | 100.6819 | 1.0446 | 1.1 | 1.0546 | 1.036 | 1.1 | 1.0401 | 31.1576 | -90 | 147.9584 | 31.8128 | -90 | 147.8258
Line_1 | 0.3163 | 0.0018735 | 0.0018735 | 0.0057244 | 0.0057244 | 0.0057244 | 3.6523 | 0.021634 | 0.021634 | 0.066099 | 0.066099 | 0.066099 | -0.74542 | -0.017943 | 0.022535 | 0.012799 | 0.055558 | -0.068195 | -0.74639 | 0.031076 | 0.023302 | 0.015037 | -0.0956 | -0.072257 | -74.7204 | 0 | 0 | -79.3181 | -79.3181 | -79.3181 | 1.0301 | 1.1 | 1.0312 | 1.036 | 1.1 | 1.0401 | 32.2018 | -90 | 147.7006 | 31.8128 | -90 | 147.8258
Line_2 | 0.3163 | 0.0018735 | 0.0018735 | 0.0057244 | 0.0057244 | 0.0057244 | 3.6523 | 0.021634 | 0.021634 | 0.066099 | 0.066099 | 0.066099 | -0.74542 | -0.017943 | 0.022535 | 0.012799 | 0.055558 | -0.068195 | -0.74639 | 0.031076 | 0.023302 | 0.015037 | -0.0956 | -0.072257 | -74.7204 | 0 | 0 | -79.3181 | -79.3181 | -79.3181 | 1.0301 | 1.1 | 1.0312 | 1.036 | 1.1 | 1.0401 | 32.2018 | -90 | 147.7006 | 31.8128 | -90 | 147.8258
Line_4 | 0.15535 | 0.0018735 | 0.0018735 | 0.15535 | 0.0018735 | 0.0018735 | 1.7939 | 0.021634 | 0.021634 | 1.7939 | 0.021634 | 0.021634 | -0.36685 | 0.017943 | -0.022535 | -0.36685 | 0.017943 | -0.022535 | -0.36588 | -0.031076 | -0.023302 | -0.36588 | -0.031076 | -0.023302 | -72.7764 | 0 | 0 | 107.3 | -79.1292 | -79.1292 | 1.0301 | 1.1 | 1.0312 | 1.0301 | 1.1 | 1.0312 | 32.2018 | -90 | 147.7006 | 32.2018 | -90 | 147.7006

## LG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mw | pf_q_b_from_mw | pf_q_c_from_mw | pf_q_a_to_mw | pf_q_b_to_mw | pf_q_c_to_mw | pf_ikss_a_from_deg | pf_ikss_b_from_deg | pf_ikss_c_from_deg | pf_ikss_a_to_deg | pf_ikss_b_to_deg | pf_ikss_c_to_deg | pf_vm_a_from_pu | pf_vm_b_from_bus_pu | pf_vm_c_from_bus_pu | pf_vm_a_to_bus_pu | pf_vm_b_to_bus_pu | pf_vm_c_to_bus_pu | pf_va_a_from_bus_deg | pf_va_b_from_bus_deg | pf_va_c_from_bus_deg | pf_va_a_to_bus_deg | pf_va_b_to_bus_deg | pf_va_c_to_bus_deg
Line_0 | 0.018181 | 0.018181 | 0.018181 | 0.57719 | 0.013334 | 0.013334 | 0.20993 | 0.20993 | 0.20993 | 6.6648 | 0.15396 | 0.15396 | 1.633e-13 | 0.18494 | -0.17867 | -5.4725e-12 | -0.13373 | 0.13289 | 1.3303e-13 | -0.28725 | -0.28978 | -2.991e-12 | 0.20982 | 0.20474 | -80.12 | 0 | 0 | 99.6778 | 91.0924 | 91.0924 | 0.93955 | 1 | 0.93624 | 0.93304 | 1 | 0.9153 | 32.3762 | -90 | 147.9449 | 33.6043 | -90 | 148.1056
Line_1 | 0.35991 | 0.0021629 | 0.0021629 | 0.0066668 | 0.0066668 | 0.0066668 | 4.1559 | 0.024975 | 0.024975 | 0.076981 | 0.076981 | 0.076981 | -3.35e-12 | -0.020741 | 0.022452 | 5.7344e-14 | 0.066866 | -0.066445 | -1.4176e-12 | 0.034297 | 0.031931 | 4.3596e-14 | -0.10491 | -0.10237 | -80.12 | 0 | 0 | -88.9076 | -88.9076 | -88.9076 | 0.92657 | 1 | 0.90238 | 0.93304 | 1 | 0.9153 | 34.298 | -90 | 148.0232 | 33.6043 | -90 | 148.1056
Line_2 | 0.35991 | 0.0021629 | 0.0021629 | 0.0066668 | 0.0066668 | 0.0066668 | 4.1559 | 0.024975 | 0.024975 | 0.076981 | 0.076981 | 0.076981 | -3.3499e-12 | -0.020741 | 0.022452 | 5.7344e-14 | 0.066866 | -0.066445 | -1.4171e-12 | 0.034297 | 0.031931 | 4.3596e-14 | -0.10491 | -0.10237 | -80.12 | 0 | 0 | -88.9076 | -88.9076 | -88.9076 | 0.92657 | 1 | 0.90238 | 0.93304 | 1 | 0.9153 | 34.298 | -90 | 148.0232 | 33.6043 | -90 | 148.1056
Line_4 | 0.17679 | 0.0021629 | 0.0021629 | 0.17679 | 0.0021629 | 0.0021629 | 2.0413 | 0.024975 | 0.024975 | 2.0413 | 0.024975 | 0.024975 | -1.6481e-12 | 0.020741 | -0.022452 | -1.6481e-12 | 0.020741 | -0.022452 | -6.8999e-13 | -0.034297 | -0.031931 | -6.8978e-13 | -0.034297 | -0.031931 | -74.7781 | 0 | 0 | 105.3687 | -86.8647 | -86.8647 | 0.92657 | 1 | 0.90238 | 0.92657 | 1 | 0.90238 | 34.298 | -90 | 148.0232 | 34.298 | -90 | 148.0232

## LG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mw | pf_q_b_from_mw | pf_q_c_from_mw | pf_q_a_to_mw | pf_q_b_to_mw | pf_q_c_to_mw | pf_ikss_a_from_deg | pf_ikss_b_from_deg | pf_ikss_c_from_deg | pf_ikss_a_to_deg | pf_ikss_b_to_deg | pf_ikss_c_to_deg | pf_vm_a_from_pu | pf_vm_b_from_bus_pu | pf_vm_c_from_bus_pu | pf_vm_a_to_bus_pu | pf_vm_b_to_bus_pu | pf_vm_c_to_bus_pu | pf_va_a_from_bus_deg | pf_va_b_from_bus_deg | pf_va_c_from_bus_deg | pf_va_a_to_bus_deg | pf_va_b_to_bus_deg | pf_va_c_to_bus_deg
Line_0 | 0.018181 | 0.018181 | 0.018181 | 0.57719 | 0.013334 | 0.013334 | 0.20993 | 0.20993 | 0.20993 | 6.6648 | 0.15396 | 0.15396 | 1.633e-13 | 0.18494 | -0.17867 | -5.4725e-12 | -0.13373 | 0.13289 | 1.3303e-13 | -0.28725 | -0.28978 | -2.991e-12 | 0.20982 | 0.20474 | -80.12 | 0 | 0 | 99.6778 | 91.0924 | 91.0924 | 0.93955 | 1 | 0.93624 | 0.93304 | 1 | 0.9153 | 32.3762 | -90 | 147.9449 | 33.6043 | -90 | 148.1056
Line_1 | 0.35991 | 0.0021629 | 0.0021629 | 0.0066668 | 0.0066668 | 0.0066668 | 4.1559 | 0.024975 | 0.024975 | 0.076981 | 0.076981 | 0.076981 | -3.35e-12 | -0.020741 | 0.022452 | 5.7344e-14 | 0.066866 | -0.066445 | -1.4176e-12 | 0.034297 | 0.031931 | 4.3596e-14 | -0.10491 | -0.10237 | -80.12 | 0 | 0 | -88.9076 | -88.9076 | -88.9076 | 0.92657 | 1 | 0.90238 | 0.93304 | 1 | 0.9153 | 34.298 | -90 | 148.0232 | 33.6043 | -90 | 148.1056
Line_2 | 0.35991 | 0.0021629 | 0.0021629 | 0.0066668 | 0.0066668 | 0.0066668 | 4.1559 | 0.024975 | 0.024975 | 0.076981 | 0.076981 | 0.076981 | -3.3499e-12 | -0.020741 | 0.022452 | 5.7344e-14 | 0.066866 | -0.066445 | -1.4171e-12 | 0.034297 | 0.031931 | 4.3596e-14 | -0.10491 | -0.10237 | -80.12 | 0 | 0 | -88.9076 | -88.9076 | -88.9076 | 0.92657 | 1 | 0.90238 | 0.93304 | 1 | 0.9153 | 34.298 | -90 | 148.0232 | 33.6043 | -90 | 148.1056
Line_4 | 0.17679 | 0.0021629 | 0.0021629 | 0.17679 | 0.0021629 | 0.0021629 | 2.0413 | 0.024975 | 0.024975 | 2.0413 | 0.024975 | 0.024975 | -1.6481e-12 | 0.020741 | -0.022452 | -1.6481e-12 | 0.020741 | -0.022452 | -6.8999e-13 | -0.034297 | -0.031931 | -6.8978e-13 | -0.034297 | -0.031931 | -74.7781 | 0 | 0 | 105.3687 | -86.8647 | -86.8647 | 0.92657 | 1 | 0.90238 | 0.92657 | 1 | 0.90238 | 34.298 | -90 | 148.0232 | 34.298 | -90 | 148.0232

## LG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mw | pf_q_b_from_mw | pf_q_c_from_mw | pf_q_a_to_mw | pf_q_b_to_mw | pf_q_c_to_mw | pf_ikss_a_from_deg | pf_ikss_b_from_deg | pf_ikss_c_from_deg | pf_ikss_a_to_deg | pf_ikss_b_to_deg | pf_ikss_c_to_deg | pf_vm_a_from_pu | pf_vm_b_from_bus_pu | pf_vm_c_from_bus_pu | pf_vm_a_to_bus_pu | pf_vm_b_to_bus_pu | pf_vm_c_to_bus_pu | pf_va_a_from_bus_deg | pf_va_b_from_bus_deg | pf_va_c_from_bus_deg | pf_va_a_to_bus_deg | pf_va_b_to_bus_deg | pf_va_c_to_bus_deg
Line_0 | 0.014122 | 0.014122 | 0.014122 | 0.44474 | 0.010274 | 0.010274 | 0.16307 | 0.16307 | 0.16307 | 5.1354 | 0.11863 | 0.11863 | 0.032526 | 0.12417 | -0.15291 | -0.96298 | -0.092133 | 0.11029 | 0.033306 | -0.21814 | -0.16333 | -0.9698 | 0.15346 | 0.11814 | -71.3133 | 0 | 0 | 108.4845 | 99.8991 | 99.8991 | 0.94752 | 1 | 0.95692 | 0.9414 | 1 | 0.93928 | 31.2145 | -90 | 147.8685 | 32.2249 | -90 | 147.981
Line_1 | 0.2778 | 0.0016694 | 0.0016694 | 0.0051369 | 0.0051369 | 0.0051369 | 3.2078 | 0.019277 | 0.019277 | 0.059316 | 0.059316 | 0.059316 | -0.57467 | -0.014583 | 0.018259 | 0.0093259 | 0.046066 | -0.055143 | -0.57612 | 0.024786 | 0.018775 | 0.012736 | -0.076732 | -0.05907 | -71.3133 | 0 | 0 | -80.1009 | -80.1009 | -80.1009 | 0.93615 | 1 | 0.92847 | 0.9414 | 1 | 0.93928 | 32.8028 | -90 | 147.9397 | 32.2249 | -90 | 147.981
Line_2 | 0.2778 | 0.0016694 | 0.0016694 | 0.0051369 | 0.0051369 | 0.0051369 | 3.2078 | 0.019277 | 0.019277 | 0.059316 | 0.059316 | 0.059316 | -0.57467 | -0.014583 | 0.018259 | 0.0093259 | 0.046066 | -0.055143 | -0.57612 | 0.024786 | 0.018775 | 0.012736 | -0.076732 | -0.05907 | -71.3133 | 0 | 0 | -80.1009 | -80.1009 | -80.1009 | 0.93615 | 1 | 0.92847 | 0.9414 | 1 | 0.93928 | 32.8028 | -90 | 147.9397 | 32.2249 | -90 | 147.981
Line_4 | 0.13645 | 0.0016694 | 0.0016694 | 0.13645 | 0.0016694 | 0.0016694 | 1.5756 | 0.019277 | 0.019277 | 1.5756 | 0.019277 | 0.019277 | -0.28335 | 0.014583 | -0.018259 | -0.28335 | 0.014583 | -0.018259 | -0.2819 | -0.024786 | -0.018775 | -0.2819 | -0.024786 | -0.018775 | -67.5404 | 0 | 0 | 112.6064 | -79.6269 | -79.6269 | 0.93615 | 1 | 0.92847 | 0.93615 | 1 | 0.92847 | 32.8028 | -90 | 147.9397 | 32.8028 | -90 | 147.9397

## LG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mw | pf_q_b_from_mw | pf_q_c_from_mw | pf_q_a_to_mw | pf_q_b_to_mw | pf_q_c_to_mw | pf_ikss_a_from_deg | pf_ikss_b_from_deg | pf_ikss_c_from_deg | pf_ikss_a_to_deg | pf_ikss_b_to_deg | pf_ikss_c_to_deg | pf_vm_a_from_pu | pf_vm_b_from_bus_pu | pf_vm_c_from_bus_pu | pf_vm_a_to_bus_pu | pf_vm_b_to_bus_pu | pf_vm_c_to_bus_pu | pf_va_a_from_bus_deg | pf_va_b_from_bus_deg | pf_va_c_from_bus_deg | pf_va_a_to_bus_deg | pf_va_b_to_bus_deg | pf_va_c_to_bus_deg
Line_0 | 0.014122 | 0.014122 | 0.014122 | 0.44474 | 0.010274 | 0.010274 | 0.16307 | 0.16307 | 0.16307 | 5.1354 | 0.11863 | 0.11863 | 0.032526 | 0.12417 | -0.15291 | -0.96298 | -0.092133 | 0.11029 | 0.033306 | -0.21814 | -0.16333 | -0.9698 | 0.15346 | 0.11814 | -71.3133 | 0 | 0 | 108.4845 | 99.8991 | 99.8991 | 0.94752 | 1 | 0.95692 | 0.9414 | 1 | 0.93928 | 31.2145 | -90 | 147.8685 | 32.2249 | -90 | 147.981
Line_1 | 0.2778 | 0.0016694 | 0.0016694 | 0.0051369 | 0.0051369 | 0.0051369 | 3.2078 | 0.019277 | 0.019277 | 0.059316 | 0.059316 | 0.059316 | -0.57467 | -0.014583 | 0.018259 | 0.0093259 | 0.046066 | -0.055143 | -0.57612 | 0.024786 | 0.018775 | 0.012736 | -0.076732 | -0.05907 | -71.3133 | 0 | 0 | -80.1009 | -80.1009 | -80.1009 | 0.93615 | 1 | 0.92847 | 0.9414 | 1 | 0.93928 | 32.8028 | -90 | 147.9397 | 32.2249 | -90 | 147.981
Line_2 | 0.2778 | 0.0016694 | 0.0016694 | 0.0051369 | 0.0051369 | 0.0051369 | 3.2078 | 0.019277 | 0.019277 | 0.059316 | 0.059316 | 0.059316 | -0.57467 | -0.014583 | 0.018259 | 0.0093259 | 0.046066 | -0.055143 | -0.57612 | 0.024786 | 0.018775 | 0.012736 | -0.076732 | -0.05907 | -71.3133 | 0 | 0 | -80.1009 | -80.1009 | -80.1009 | 0.93615 | 1 | 0.92847 | 0.9414 | 1 | 0.93928 | 32.8028 | -90 | 147.9397 | 32.2249 | -90 | 147.981
Line_4 | 0.13645 | 0.0016694 | 0.0016694 | 0.13645 | 0.0016694 | 0.0016694 | 1.5756 | 0.019277 | 0.019277 | 1.5756 | 0.019277 | 0.019277 | -0.28335 | 0.014583 | -0.018259 | -0.28335 | 0.014583 | -0.018259 | -0.2819 | -0.024786 | -0.018775 | -0.2819 | -0.024786 | -0.018775 | -67.5404 | 0 | 0 | 112.6064 | -79.6269 | -79.6269 | 0.93615 | 1 | 0.92847 | 0.93615 | 1 | 0.92847 | 32.8028 | -90 | 147.9397 | 32.8028 | -90 | 147.9397