## LLL_max_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 3.4587 | 3.4587 | 0 | 0 | 119.8128 | 119.8128 | 37.3233 | -18.6616 | 42.3476 | -21.1738 | -71.7883 | 108.2117 | 0.47113 | 0.23557 | -23.1798 | -23.1798
Line_1 | 3.4587 | 3.4587 | 6.7756 | 0 | 119.8128 | 119.8128 | -1e-07 | 18.6616 | -1e-07 | 21.1738 | 108.2117 | -71.7883 | 0 | 0.23557 | 0 | -23.1798
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23557 | 0.23557 | -23.1798 | -23.1798

## LLL_max_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 3.4587 | 3.4587 | 0 | 0 | 119.8128 | 119.8128 | 37.3233 | -18.6616 | 42.3476 | -21.1738 | -71.7883 | 108.2117 | 0.47113 | 0.23557 | -23.1798 | -23.1798
Line_1 | 3.4587 | 3.4587 | 6.7756 | 0 | 119.8128 | 119.8128 | -1e-07 | 18.6616 | -1e-07 | 21.1738 | 108.2117 | -71.7883 | 0 | 0.23557 | 0 | -23.1798
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23557 | 0.23557 | -23.1798 | -23.1798

## LLL_max_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 1.2119 | 1.2119 | 0 | 0 | 41.9813 | 41.9813 | 26.6127 | -24.3216 | 27.2296 | -24.63 | -54.0862 | 125.9138 | 0.90694 | 0.82453 | -8.4298 | -8.7252
Line_1 | 1.2119 | 1.2119 | 2.3741 | 0 | 41.9813 | 41.9813 | -22.0304 | 24.3216 | -22.0304 | 24.63 | 125.9138 | -54.0862 | 0.74213 | 0.82453 | -9.0862 | -8.7252
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.82453 | 0.82453 | -8.7252 | -8.7252

## LLL_max_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 1.2119 | 1.2119 | 0 | 0 | 41.9813 | 41.9813 | 26.6127 | -24.3216 | 27.2296 | -24.63 | -54.0862 | 125.9138 | 0.90694 | 0.82453 | -8.4298 | -8.7252
Line_1 | 1.2119 | 1.2119 | 2.3741 | 0 | 41.9813 | 41.9813 | -22.0304 | 24.3216 | -22.0304 | 24.63 | 125.9138 | -54.0862 | 0.74213 | 0.82453 | -9.0862 | -8.7252
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.82453 | 0.82453 | -8.7252 | -8.7252

## LLL_min_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 2.7686 | 2.7686 | 0 | 0 | 95.9057 | 95.9057 | 45.916 | -22.958 | 27.1338 | -13.5669 | -59.5744 | 120.4256 | 0.55611 | 0.27805 | -28.9937 | -28.9937
Line_1 | 2.7686 | 2.7686 | 4.6525 | 0 | 95.9057 | 95.9057 | -1e-07 | 22.958 | -1e-07 | 13.5669 | 120.4256 | -59.5744 | 0 | 0.27805 | 0 | -28.9937
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27805 | 0.27805 | -28.9937 | -28.9937

## LLL_min_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 2.7686 | 2.7686 | 0 | 0 | 95.9057 | 95.9057 | 45.916 | -22.958 | 27.1338 | -13.5669 | -59.5744 | 120.4256 | 0.55611 | 0.27805 | -28.9937 | -28.9937
Line_1 | 2.7686 | 2.7686 | 4.6525 | 0 | 95.9057 | 95.9057 | -1e-07 | 22.958 | -1e-07 | 13.5669 | 120.4256 | -59.5744 | 0 | 0.27805 | 0 | -28.9937
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27805 | 0.27805 | -28.9937 | -28.9937

## LLL_min_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 1.0349 | 1.0349 | 0 | 0 | 35.8516 | 35.8516 | 22.4832 | -19.2749 | 19.8585 | -17.9626 | -50.3977 | 129.6023 | 0.83671 | 0.7349 | -8.9447 | -7.416
Line_1 | 1.0349 | 1.0349 | 1.7392 | 0 | 35.8516 | 35.8516 | -16.0667 | 19.2749 | -16.0667 | 17.9626 | 129.6023 | -50.3977 | 0.63377 | 0.7349 | -5.3977 | -7.416
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7349 | 0.7349 | -7.416 | -7.416

## LLL_min_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 1.0349 | 1.0349 | 0 | 0 | 35.8516 | 35.8516 | 22.4832 | -19.2749 | 19.8585 | -17.9626 | -50.3977 | 129.6023 | 0.83671 | 0.7349 | -8.9447 | -7.416
Line_1 | 1.0349 | 1.0349 | 1.7392 | 0 | 35.8516 | 35.8516 | -16.0667 | 19.2749 | -16.0667 | 17.9626 | 129.6023 | -50.3977 | 0.63377 | 0.7349 | -5.3977 | -7.416
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7349 | 0.7349 | -7.416 | -7.416

## LL_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 2.9953 | 2.9953 | 0 | 2.9953 | 2.9953 | 0 | 34.587 | 34.587 | 0 | 34.587 | 34.587 | 2.0843e-14 | 27.4008 | -8.7391 | -2.0843e-14 | -22.7354 | 13.4045 | -1.0421e-14 | 4.6417 | 16.5321 | 5.2106e-15 | 0.65175 | -11.2386 | 0 | -161.7883 | 18.2117 | 0 | 18.2117 | -161.7883 | 1.1 | 0.80351 | 0.54066 | 1.1 | 0.65761 | 0.50575 | -6.143e-12 | -152.1736 | 136.0734 | -6.1638e-12 | -163.4303 | 158.2346
Line_1 | 0 | 2.9953 | 2.9953 | 0 | 2.9953 | 2.9953 | 0 | 34.587 | 34.587 | 0 | 34.587 | 34.587 | 1.0421e-14 | -18.0699 | 18.0699 | -1.5632e-14 | 22.7354 | -13.4045 | -1.0421e-14 | 5.9452 | -5.9452 | 1.0421e-14 | -0.65175 | 11.2386 | 0 | 18.2117 | -161.7883 | 0 | -161.7883 | 18.2117 | 1.1 | 0.55 | 0.55 | 1.1 | 0.65761 | 0.50575 | -6.1621e-12 | 180 | -180 | -6.1638e-12 | -163.4303 | 158.2346
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2106e-15 | 3.4052e-10 | 6.6439e-10 | -1.0421e-14 | -3.4053e-10 | -6.6441e-10 | -5.2106e-15 | -1.8234e-09 | 1.2624e-09 | 5.2106e-15 | 1.8234e-09 | -1.2624e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.65761 | 0.50575 | 1.1 | 0.65761 | 0.50575 | -6.1673e-12 | -163.4303 | 158.2346 | -6.1638e-12 | -163.4303 | 158.2346

## LL_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 2.9953 | 2.9953 | 0 | 2.9953 | 2.9953 | 0 | 34.587 | 34.587 | 0 | 34.587 | 34.587 | 2.0843e-14 | 27.4008 | -8.7391 | -2.0843e-14 | -22.7354 | 13.4045 | -1.0421e-14 | 4.6417 | 16.5321 | 5.2106e-15 | 0.65175 | -11.2386 | 0 | -161.7883 | 18.2117 | 0 | 18.2117 | -161.7883 | 1.1 | 0.80351 | 0.54066 | 1.1 | 0.65761 | 0.50575 | -6.143e-12 | -152.1736 | 136.0734 | -6.1638e-12 | -163.4303 | 158.2346
Line_1 | 0 | 2.9953 | 2.9953 | 0 | 2.9953 | 2.9953 | 0 | 34.587 | 34.587 | 0 | 34.587 | 34.587 | 1.0421e-14 | -18.0699 | 18.0699 | -1.5632e-14 | 22.7354 | -13.4045 | -1.0421e-14 | 5.9452 | -5.9452 | 1.0421e-14 | -0.65175 | 11.2386 | 0 | 18.2117 | -161.7883 | 0 | -161.7883 | 18.2117 | 1.1 | 0.55 | 0.55 | 1.1 | 0.65761 | 0.50575 | -6.1621e-12 | 180 | -180 | -6.1638e-12 | -163.4303 | 158.2346
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2106e-15 | 3.4052e-10 | 6.6439e-10 | -1.0421e-14 | -3.4053e-10 | -6.6441e-10 | -5.2106e-15 | -1.8234e-09 | 1.2624e-09 | 5.2106e-15 | 1.8234e-09 | -1.2624e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.65761 | 0.50575 | 1.1 | 0.65761 | 0.50575 | -6.1673e-12 | -163.4303 | 158.2346 | -6.1638e-12 | -163.4303 | 158.2346

## LL_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 1.5688 | 1.5688 | 0 | 1.5688 | 1.5688 | 0 | 18.1144 | 18.1144 | 0 | 18.1144 | 18.1144 | 1.3027e-14 | 17.2205 | 0.20321 | -1.3027e-14 | -15.9408 | 1.0765 | -2.6053e-15 | 3.8735 | 14.2393 | 2.6053e-15 | -2.4216 | -12.7873 | 0 | -148.6532 | 31.3468 | 0 | 31.3468 | -148.6532 | 1.1 | 0.97441 | 0.78616 | 1.1 | 0.89011 | 0.70842 | -3.0737e-12 | -135.9762 | 120.5292 | -3.0836e-12 | -140.0155 | 126.1589
Line_1 | 0 | 1.5688 | 1.5688 | 0 | 1.5688 | 1.5688 | 0 | 18.1144 | 18.1144 | 0 | 18.1144 | 18.1144 | 7.816e-15 | -14.6611 | 2.3562 | -5.2106e-15 | 15.9408 | -1.0765 | -5.2106e-15 | -0.96958 | -11.3353 | 5.2106e-15 | 2.4216 | 12.7873 | 0 | 31.3468 | -148.6532 | 0 | -148.6532 | 31.3468 | 1.1 | 0.81113 | 0.63914 | 1.1 | 0.89011 | 0.70842 | -3.083e-12 | -144.8696 | 133.0893 | -3.0836e-12 | -140.0155 | 126.1589
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6053e-15 | 4.682e-10 | 1.0007e-09 | -2.6053e-15 | -4.6819e-10 | -1.0007e-09 | -2.6053e-15 | -1.2288e-09 | 3.0654e-10 | 1.4021e-28 | 1.2288e-09 | -3.0654e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.89011 | 0.70842 | 1.1 | 0.89011 | 0.70842 | -3.0847e-12 | -140.0155 | 126.1589 | -3.0836e-12 | -140.0155 | 126.1589

## LL_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 1.5688 | 1.5688 | 0 | 1.5688 | 1.5688 | 0 | 18.1144 | 18.1144 | 0 | 18.1144 | 18.1144 | 1.3027e-14 | 17.2205 | 0.20321 | -1.3027e-14 | -15.9408 | 1.0765 | -2.6053e-15 | 3.8735 | 14.2393 | 2.6053e-15 | -2.4216 | -12.7873 | 0 | -148.6532 | 31.3468 | 0 | 31.3468 | -148.6532 | 1.1 | 0.97441 | 0.78616 | 1.1 | 0.89011 | 0.70842 | -3.0737e-12 | -135.9762 | 120.5292 | -3.0836e-12 | -140.0155 | 126.1589
Line_1 | 0 | 1.5688 | 1.5688 | 0 | 1.5688 | 1.5688 | 0 | 18.1144 | 18.1144 | 0 | 18.1144 | 18.1144 | 7.816e-15 | -14.6611 | 2.3562 | -5.2106e-15 | 15.9408 | -1.0765 | -5.2106e-15 | -0.96958 | -11.3353 | 5.2106e-15 | 2.4216 | 12.7873 | 0 | 31.3468 | -148.6532 | 0 | -148.6532 | 31.3468 | 1.1 | 0.81113 | 0.63914 | 1.1 | 0.89011 | 0.70842 | -3.083e-12 | -144.8696 | 133.0893 | -3.0836e-12 | -140.0155 | 126.1589
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6053e-15 | 4.682e-10 | 1.0007e-09 | -2.6053e-15 | -4.6819e-10 | -1.0007e-09 | -2.6053e-15 | -1.2288e-09 | 3.0654e-10 | 1.4021e-28 | 1.2288e-09 | -3.0654e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.89011 | 0.70842 | 1.1 | 0.89011 | 0.70842 | -3.0847e-12 | -140.0155 | 126.1589 | -3.0836e-12 | -140.0155 | 126.1589

## LL_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 2.3976 | 2.3976 | 0 | 2.3976 | 2.3976 | 0 | 27.6856 | 27.6856 | 0 | 27.6856 | 27.6856 | -2.3685e-15 | 23.4155 | -0.45749 | 8.2897e-15 | -17.676 | 6.197 | -1.6579e-14 | -0.22679 | 13.7937 | 1.1842e-14 | 3.6185 | -10.402 | 0 | -149.5744 | 30.4256 | 0 | 30.4256 | -149.5744 | 1 | 0.8458 | 0.4985 | 1 | 0.65169 | 0.43734 | -6.5545e-12 | -150.1294 | 122.3252 | -6.5266e-12 | -161.1438 | 151.2099
Line_1 | 0 | 2.3976 | 2.3976 | 0 | 2.3976 | 2.3976 | 0 | 27.6856 | 27.6856 | 0 | 27.6856 | 27.6856 | 3.5527e-15 | -11.9365 | 11.9365 | 4.737e-15 | 17.676 | -6.197 | -4.0448e-28 | 7.0103 | -7.0103 | -7.1054e-15 | -3.6185 | 10.402 | 0 | 30.4256 | -149.5744 | 0 | -149.5744 | 30.4256 | 1 | 0.5 | 0.5 | 1 | 0.65169 | 0.43734 | -6.5232e-12 | -180 | 180 | -6.5266e-12 | -161.1438 | 151.2099
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7063e-28 | 2.4222e-10 | 6.7019e-10 | 7.1054e-15 | -2.4222e-10 | -6.7019e-10 | 2.3685e-15 | -1.5722e-09 | 8.3093e-10 | -4.737e-15 | 1.5722e-09 | -8.3093e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.65169 | 0.43734 | 1 | 0.65169 | 0.43734 | -6.5468e-12 | -161.1438 | 151.2099 | -6.5266e-12 | -161.1438 | 151.2099

## LL_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 2.3976 | 2.3976 | 0 | 2.3976 | 2.3976 | 0 | 27.6856 | 27.6856 | 0 | 27.6856 | 27.6856 | -2.3685e-15 | 23.4155 | -0.45749 | 8.2897e-15 | -17.676 | 6.197 | -1.6579e-14 | -0.22679 | 13.7937 | 1.1842e-14 | 3.6185 | -10.402 | 0 | -149.5744 | 30.4256 | 0 | 30.4256 | -149.5744 | 1 | 0.8458 | 0.4985 | 1 | 0.65169 | 0.43734 | -6.5545e-12 | -150.1294 | 122.3252 | -6.5266e-12 | -161.1438 | 151.2099
Line_1 | 0 | 2.3976 | 2.3976 | 0 | 2.3976 | 2.3976 | 0 | 27.6856 | 27.6856 | 0 | 27.6856 | 27.6856 | 3.5527e-15 | -11.9365 | 11.9365 | 4.737e-15 | 17.676 | -6.197 | -4.0448e-28 | 7.0103 | -7.0103 | -7.1054e-15 | -3.6185 | 10.402 | 0 | 30.4256 | -149.5744 | 0 | -149.5744 | 30.4256 | 1 | 0.5 | 0.5 | 1 | 0.65169 | 0.43734 | -6.5232e-12 | -180 | 180 | -6.5266e-12 | -161.1438 | 151.2099
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7063e-28 | 2.4222e-10 | 6.7019e-10 | 7.1054e-15 | -2.4222e-10 | -6.7019e-10 | 2.3685e-15 | -1.5722e-09 | 8.3093e-10 | -4.737e-15 | 1.5722e-09 | -8.3093e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.65169 | 0.43734 | 1 | 0.65169 | 0.43734 | -6.5468e-12 | -161.1438 | 151.2099 | -6.5266e-12 | -161.1438 | 151.2099

## LL_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 1.3081 | 1.3081 | 0 | 1.3081 | 1.3081 | 0 | 15.105 | 15.105 | 0 | 15.105 | 15.105 | 2.9606e-15 | 13.7181 | 1.6719 | 2.9606e-15 | -12.0096 | 0.036546 | -1.1842e-14 | 1.7406 | 10.8539 | 7.1054e-15 | -0.73098 | -9.8443 | 0 | -142.8911 | 37.1089 | 0 | 37.1089 | -142.8911 | 1 | 0.91546 | 0.72704 | 1 | 0.79654 | 0.65173 | -4.0572e-12 | -135.6599 | 118.3519 | -4.0419e-12 | -139.408 | 127.3216
Line_1 | 0 | 1.3081 | 1.3081 | 0 | 1.3081 | 1.3081 | 0 | 15.105 | 15.105 | 0 | 15.105 | 15.105 | 2.3685e-15 | -10.3011 | 1.745 | 1.7764e-15 | 12.0096 | -0.036546 | -1.6708e-28 | 0.27863 | -8.8347 | -1.2531e-28 | 0.73098 | 9.8443 | 0 | 37.1089 | -142.8911 | 0 | -142.8911 | 37.1089 | 1 | 0.68221 | 0.59619 | 1 | 0.79654 | 0.65173 | -4.0417e-12 | -144.4405 | 138.2821 | -4.0419e-12 | -139.408 | 127.3216
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2826e-10 | 8.1276e-10 | 4.737e-15 | -4.2826e-10 | -8.1277e-10 | 0 | -9.7051e-10 | 3.0453e-10 | -4.737e-15 | 9.7051e-10 | -3.0453e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.79654 | 0.65173 | 1 | 0.79654 | 0.65173 | -4.0523e-12 | -139.408 | 127.3216 | -4.0419e-12 | -139.408 | 127.3216

## LL_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 1.3081 | 1.3081 | 0 | 1.3081 | 1.3081 | 0 | 15.105 | 15.105 | 0 | 15.105 | 15.105 | 2.9606e-15 | 13.7181 | 1.6719 | 2.9606e-15 | -12.0096 | 0.036546 | -1.1842e-14 | 1.7406 | 10.8539 | 7.1054e-15 | -0.73098 | -9.8443 | 0 | -142.8911 | 37.1089 | 0 | 37.1089 | -142.8911 | 1 | 0.91546 | 0.72704 | 1 | 0.79654 | 0.65173 | -4.0572e-12 | -135.6599 | 118.3519 | -4.0419e-12 | -139.408 | 127.3216
Line_1 | 0 | 1.3081 | 1.3081 | 0 | 1.3081 | 1.3081 | 0 | 15.105 | 15.105 | 0 | 15.105 | 15.105 | 2.3685e-15 | -10.3011 | 1.745 | 1.7764e-15 | 12.0096 | -0.036546 | -1.6708e-28 | 0.27863 | -8.8347 | -1.2531e-28 | 0.73098 | 9.8443 | 0 | 37.1089 | -142.8911 | 0 | -142.8911 | 37.1089 | 1 | 0.68221 | 0.59619 | 1 | 0.79654 | 0.65173 | -4.0417e-12 | -144.4405 | 138.2821 | -4.0419e-12 | -139.408 | 127.3216
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2826e-10 | 8.1276e-10 | 4.737e-15 | -4.2826e-10 | -8.1277e-10 | 0 | -9.7051e-10 | 3.0453e-10 | -4.737e-15 | 9.7051e-10 | -3.0453e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.79654 | 0.65173 | 1 | 0.79654 | 0.65173 | -4.0523e-12 | -139.408 | 127.3216 | -4.0419e-12 | -139.408 | 127.3216

## LG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.016772 | 0.016447 | 0.016447 | 0.022254 | 0.010965 | 0.010965 | 0.19366 | 0.18991 | 0.18991 | 0.25697 | 0.12661 | 0.12661 | 0.00073965 | 0.18139 | -0.18044 | -0.00094171 | -0.12076 | 0.12046 | 0.0005785 | -0.31445 | -0.31591 | -0.000563 | 0.20975 | 0.21072 | 89.7491 | -90.2308 | -90.2308 | -90.2462 | 89.7696 | 89.7696 |  | 0.0048487 | 1.9115 | 1.9157 | 0.0042697 | 1.9116 | 1.9171 | 127.779 | -150.2523 | 150.0357 | 120.6267 | -150.3006 | 150.0142
Line_1 | 0.033219 | 0 | 0 | 0.027738 | 0.0054805 | 0.0054805 | 0.38358 | 0 | 0 | 0.32029 | 0.063284 | 0.063284 | 1.2908e-13 | -6.7448e-09 | -6.7681e-09 | 0.0011737 | 0.060275 | -0.060296 | -2.7053e-14 | -3.884e-09 | 3.8705e-09 | 0.00070186 | -0.10489 | -0.10528 | -90.241 | 0 | 0 | 89.7479 | -90.1845 | -90.1845 |  | 0 | 1.9123 | 1.9156 | 0.0042697 | 1.9116 | 1.9171 | 0 | -150.2369 | 150.0633 | 120.6267 | -150.3006 | 150.0142
Line_2 | 0 | 0 | 0 | 0.005484 | 0.005484 | 0.005484 | 0 | 0 | 0 | 0.063324 | 0.063324 | 0.063324 | -1.0262e-11 | -6.7426e-09 | -6.7872e-09 | -0.00023199 | 0.060481 | -0.060166 | 1.8366e-11 | -3.893e-09 | 3.8673e-09 | -0.00013886 | -0.10486 | -0.10544 | 0 | 0 | 0 | -90.2762 | -90.2762 | -90.2762 |  | 0.0052041 | 1.9115 | 1.9178 | 0.0042697 | 1.9116 | 1.9171 | 118.9584 | -150.3286 | 149.9966 | 120.6267 | -150.3006 | 150.0142

## LG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.016772 | 0.016447 | 0.016447 | 0.022254 | 0.010965 | 0.010965 | 0.19366 | 0.18991 | 0.18991 | 0.25697 | 0.12661 | 0.12661 | 0.00073965 | 0.18139 | -0.18044 | -0.00094171 | -0.12076 | 0.12046 | 0.0005785 | -0.31445 | -0.31591 | -0.000563 | 0.20975 | 0.21072 | 89.7491 | -90.2308 | -90.2308 | -90.2462 | 89.7696 | 89.7696 |  | 0.0048487 | 1.9115 | 1.9157 | 0.0042697 | 1.9116 | 1.9171 | 127.779 | -150.2523 | 150.0357 | 120.6267 | -150.3006 | 150.0142
Line_1 | 0.033219 | 0 | 0 | 0.027738 | 0.0054805 | 0.0054805 | 0.38358 | 0 | 0 | 0.32029 | 0.063284 | 0.063284 | 1.2908e-13 | -6.7448e-09 | -6.7681e-09 | 0.0011737 | 0.060275 | -0.060296 | -2.7053e-14 | -3.884e-09 | 3.8705e-09 | 0.00070186 | -0.10489 | -0.10528 | -90.241 | 0 | 0 | 89.7479 | -90.1845 | -90.1845 |  | 0 | 1.9123 | 1.9156 | 0.0042697 | 1.9116 | 1.9171 | 0 | -150.2369 | 150.0633 | 120.6267 | -150.3006 | 150.0142
Line_2 | 0 | 0 | 0 | 0.005484 | 0.005484 | 0.005484 | 0 | 0 | 0 | 0.063324 | 0.063324 | 0.063324 | -1.0262e-11 | -6.7426e-09 | -6.7872e-09 | -0.00023199 | 0.060481 | -0.060166 | 1.8366e-11 | -3.893e-09 | 3.8673e-09 | -0.00013886 | -0.10486 | -0.10544 | 0 | 0 | 0 | -90.2762 | -90.2762 | -90.2762 |  | 0.0052041 | 1.9115 | 1.9178 | 0.0042697 | 1.9116 | 1.9171 | 118.9584 | -150.3286 | 149.9966 | 120.6267 | -150.3006 | 150.0142

## LG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.016992 | 0.016662 | 0.016662 | 0.022546 | 0.011108 | 0.011108 | 0.1962 | 0.1924 | 0.1924 | 0.26034 | 0.12827 | 0.12827 | 0.0036178 | 0.18515 | -0.18137 | -0.00476 | -0.12326 | 0.12109 | 0.0034534 | -0.31892 | -0.32527 | -0.004372 | 0.21273 | 0.21696 | 88.9868 | -90.9931 | -90.9931 | -91.0084 | 89.0074 | 89.0074 |  | 0.025492 | 1.9167 | 1.9356 | 0.024826 | 1.9168 | 1.9371 | 132.6549 | -150.8552 | 149.8635 | 131.5586 | -150.904 | 149.8415
Line_1 | 0.033654 | 0 | 0 | 0.028102 | 0.0055524 | 0.0055524 | 0.3886 | 0 | 0 | 0.32449 | 0.064113 | 0.064113 | -0.005663 | -6.8407e-09 | -6.9687e-09 | 0.0059324 | 0.061524 | -0.060611 | -0.005663 | -3.9646e-09 | 3.8906e-09 | 0.00545 | -0.10638 | -0.1084 | -91.0032 | 0 | 0 | 88.9856 | -90.9468 | -90.9468 |  | 0.020609 | 1.9174 | 1.9356 | 0.024826 | 1.9168 | 1.9371 | 133.9968 | -150.8397 | 149.8911 | 131.5586 | -150.904 | 149.8415
Line_2 | 0 | 0 | 0 | 0.0055559 | 0.0055559 | 0.0055559 | 0 | 0 | 0 | 0.064154 | 0.064154 | 0.064154 | -7.0213e-11 | -6.8384e-09 | -6.9881e-09 | -0.0011724 | 0.061734 | -0.060476 | 7.8538e-11 | -3.9736e-09 | 3.8871e-09 | -0.001078 | -0.10635 | -0.10856 | 0 | 0 | 0 | -91.0385 | -91.0385 | -91.0385 |  | 0.025722 | 1.9166 | 1.9378 | 0.024826 | 1.9168 | 1.9371 | 130.7973 | -150.9323 | 149.8236 | 131.5586 | -150.904 | 149.8415

## LG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.016992 | 0.016662 | 0.016662 | 0.022546 | 0.011108 | 0.011108 | 0.1962 | 0.1924 | 0.1924 | 0.26034 | 0.12827 | 0.12827 | 0.0036178 | 0.18515 | -0.18137 | -0.00476 | -0.12326 | 0.12109 | 0.0034534 | -0.31892 | -0.32527 | -0.004372 | 0.21273 | 0.21696 | 88.9868 | -90.9931 | -90.9931 | -91.0084 | 89.0074 | 89.0074 |  | 0.025492 | 1.9167 | 1.9356 | 0.024826 | 1.9168 | 1.9371 | 132.6549 | -150.8552 | 149.8635 | 131.5586 | -150.904 | 149.8415
Line_1 | 0.033654 | 0 | 0 | 0.028102 | 0.0055524 | 0.0055524 | 0.3886 | 0 | 0 | 0.32449 | 0.064113 | 0.064113 | -0.005663 | -6.8407e-09 | -6.9687e-09 | 0.0059324 | 0.061524 | -0.060611 | -0.005663 | -3.9646e-09 | 3.8906e-09 | 0.00545 | -0.10638 | -0.1084 | -91.0032 | 0 | 0 | 88.9856 | -90.9468 | -90.9468 |  | 0.020609 | 1.9174 | 1.9356 | 0.024826 | 1.9168 | 1.9371 | 133.9968 | -150.8397 | 149.8911 | 131.5586 | -150.904 | 149.8415
Line_2 | 0 | 0 | 0 | 0.0055559 | 0.0055559 | 0.0055559 | 0 | 0 | 0 | 0.064154 | 0.064154 | 0.064154 | -7.0213e-11 | -6.8384e-09 | -6.9881e-09 | -0.0011724 | 0.061734 | -0.060476 | 7.8538e-11 | -3.9736e-09 | 3.8871e-09 | -0.001078 | -0.10635 | -0.10856 | 0 | 0 | 0 | -91.0385 | -91.0385 | -91.0385 |  | 0.025722 | 1.9166 | 1.9378 | 0.024826 | 1.9168 | 1.9371 | 130.7973 | -150.9323 | 149.8236 | 131.5586 | -150.904 | 149.8415

## LG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.01525 | 0.014954 | 0.014954 | 0.020234 | 0.0099694 | 0.0099694 | 0.17609 | 0.17268 | 0.17268 | 0.23365 | 0.11512 | 0.11512 | 0.0011741 | 0.1503 | -0.14878 | -0.0014948 | -0.099924 | 0.099458 | 0.00047752 | -0.25943 | -0.2617 | -0.00046454 | 0.17305 | 0.17456 | 89.5273 | -90.4341 | -90.4341 | -90.4636 | 89.5667 | 89.5667 |  | 0.0071978 | 1.7363 | 1.7433 | 0.0066994 | 1.7359 | 1.7452 | 111.6603 | -150.3493 | 149.9471 | 106.8002 | -150.4297 | 149.8935
Line_1 | 0.030204 | 0 | 0 | 0.025221 | 0.0049831 | 0.0049831 | 0.34876 | 0 | 0 | 0.29122 | 0.05754 | 0.05754 | -8.8402e-14 | -5.5685e-09 | -5.604e-09 | 0.001863 | 0.049813 | -0.049847 | -6.6837e-14 | -3.2155e-09 | 3.1949e-09 | 0.00057938 | -0.086574 | -0.087175 | -90.4536 | 0 | 0 | 89.525 | -90.3452 | -90.3452 |  | 0 | 1.7374 | 1.743 | 0.0066994 | 1.7359 | 1.7452 | 0 | -150.3143 | 149.9945 | 106.8002 | -150.4297 | 149.8935
Line_2 | 0 | 0 | 0 | 0.0049863 | 0.0049863 | 0.0049863 | 0 | 0 | 0 | 0.057576 | 0.057576 | 0.057576 | -8.4587e-12 | -5.5585e-09 | -5.6278e-09 | -0.00036824 | 0.050111 | -0.04961 | 2.9144e-11 | -3.2274e-09 | 3.1874e-09 | -0.00011484 | -0.086475 | -0.087383 | 0 | 0 | 0 | -90.5213 | -90.5213 | -90.5213 |  | 0.0082578 | 1.7354 | 1.7462 | 0.0066994 | 1.7359 | 1.7452 | 105.7298 | -150.4787 | 149.8549 | 106.8002 | -150.4297 | 149.8935

## LG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.01525 | 0.014954 | 0.014954 | 0.020234 | 0.0099694 | 0.0099694 | 0.17609 | 0.17268 | 0.17268 | 0.23365 | 0.11512 | 0.11512 | 0.0011741 | 0.1503 | -0.14878 | -0.0014948 | -0.099924 | 0.099458 | 0.00047752 | -0.25943 | -0.2617 | -0.00046454 | 0.17305 | 0.17456 | 89.5273 | -90.4341 | -90.4341 | -90.4636 | 89.5667 | 89.5667 |  | 0.0071978 | 1.7363 | 1.7433 | 0.0066994 | 1.7359 | 1.7452 | 111.6603 | -150.3493 | 149.9471 | 106.8002 | -150.4297 | 149.8935
Line_1 | 0.030204 | 0 | 0 | 0.025221 | 0.0049831 | 0.0049831 | 0.34876 | 0 | 0 | 0.29122 | 0.05754 | 0.05754 | -8.8402e-14 | -5.5685e-09 | -5.604e-09 | 0.001863 | 0.049813 | -0.049847 | -6.6837e-14 | -3.2155e-09 | 3.1949e-09 | 0.00057938 | -0.086574 | -0.087175 | -90.4536 | 0 | 0 | 89.525 | -90.3452 | -90.3452 |  | 0 | 1.7374 | 1.743 | 0.0066994 | 1.7359 | 1.7452 | 0 | -150.3143 | 149.9945 | 106.8002 | -150.4297 | 149.8935
Line_2 | 0 | 0 | 0 | 0.0049863 | 0.0049863 | 0.0049863 | 0 | 0 | 0 | 0.057576 | 0.057576 | 0.057576 | -8.4587e-12 | -5.5585e-09 | -5.6278e-09 | -0.00036824 | 0.050111 | -0.04961 | 2.9144e-11 | -3.2274e-09 | 3.1874e-09 | -0.00011484 | -0.086475 | -0.087383 | 0 | 0 | 0 | -90.5213 | -90.5213 | -90.5213 |  | 0.0082578 | 1.7354 | 1.7462 | 0.0066994 | 1.7359 | 1.7452 | 105.7298 | -150.4787 | 149.8549 | 106.8002 | -150.4297 | 149.8935

## LG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.015449 | 0.015149 | 0.015149 | 0.020499 | 0.0101 | 0.0101 | 0.17839 | 0.17493 | 0.17493 | 0.2367 | 0.11662 | 0.11662 | 0.0035676 | 0.1534 | -0.14952 | -0.0046696 | -0.10199 | 0.099961 | 0.0028544 | -0.26308 | -0.26942 | -0.0036134 | 0.17549 | 0.17971 | 88.7622 | -91.1993 | -91.1993 | -91.2288 | 88.8016 | 88.8016 |  | 0.025613 | 1.7409 | 1.7615 | 0.024945 | 1.7404 | 1.7634 | 127.4246 | -150.9537 | 149.7717 | 126.5043 | -151.035 | 149.7174
Line_1 | 0.030598 | 0 | 0 | 0.02555 | 0.0050482 | 0.0050482 | 0.35332 | 0 | 0 | 0.29503 | 0.058291 | 0.058291 | -0.0046812 | -5.6469e-09 | -5.7696e-09 | 0.0058194 | 0.050842 | -0.050103 | -0.0046812 | -3.2819e-09 | 3.211e-09 | 0.004505 | -0.087794 | -0.08975 | -91.2187 | 0 | 0 | 88.7598 | -91.1103 | -91.1103 |  | 0.018737 | 1.742 | 1.7611 | 0.024945 | 1.7404 | 1.7634 | 133.7813 | -150.9185 | 149.8194 | 126.5043 | -151.035 | 149.7174
Line_2 | 0 | 0 | 0 | 0.0050514 | 0.0050514 | 0.0050514 | 0 | 0 | 0 | 0.058328 | 0.058328 | 0.058328 | -5.8009e-11 | -5.6367e-09 | -5.7938e-09 | -0.0011498 | 0.051144 | -0.049858 | 7.9237e-11 | -3.2938e-09 | 3.2032e-09 | -0.00089159 | -0.087693 | -0.089961 | 0 | 0 | 0 | -91.2864 | -91.2864 | -91.2864 |  | 0.026377 | 1.7399 | 1.7644 | 0.024945 | 1.7404 | 1.7634 | 124.9879 | -151.0845 | 149.6784 | 126.5043 | -151.035 | 149.7174

## LG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.015449 | 0.015149 | 0.015149 | 0.020499 | 0.0101 | 0.0101 | 0.17839 | 0.17493 | 0.17493 | 0.2367 | 0.11662 | 0.11662 | 0.0035676 | 0.1534 | -0.14952 | -0.0046696 | -0.10199 | 0.099961 | 0.0028544 | -0.26308 | -0.26942 | -0.0036134 | 0.17549 | 0.17971 | 88.7622 | -91.1993 | -91.1993 | -91.2288 | 88.8016 | 88.8016 |  | 0.025613 | 1.7409 | 1.7615 | 0.024945 | 1.7404 | 1.7634 | 127.4246 | -150.9537 | 149.7717 | 126.5043 | -151.035 | 149.7174
Line_1 | 0.030598 | 0 | 0 | 0.02555 | 0.0050482 | 0.0050482 | 0.35332 | 0 | 0 | 0.29503 | 0.058291 | 0.058291 | -0.0046812 | -5.6469e-09 | -5.7696e-09 | 0.0058194 | 0.050842 | -0.050103 | -0.0046812 | -3.2819e-09 | 3.211e-09 | 0.004505 | -0.087794 | -0.08975 | -91.2187 | 0 | 0 | 88.7598 | -91.1103 | -91.1103 |  | 0.018737 | 1.742 | 1.7611 | 0.024945 | 1.7404 | 1.7634 | 133.7813 | -150.9185 | 149.8194 | 126.5043 | -151.035 | 149.7174
Line_2 | 0 | 0 | 0 | 0.0050514 | 0.0050514 | 0.0050514 | 0 | 0 | 0 | 0.058328 | 0.058328 | 0.058328 | -5.8009e-11 | -5.6367e-09 | -5.7938e-09 | -0.0011498 | 0.051144 | -0.049858 | 7.9237e-11 | -3.2938e-09 | 3.2032e-09 | -0.00089159 | -0.087693 | -0.089961 | 0 | 0 | 0 | -91.2864 | -91.2864 | -91.2864 |  | 0.026377 | 1.7399 | 1.7644 | 0.024945 | 1.7404 | 1.7634 | 124.9879 | -151.0845 | 149.6784 | 126.5043 | -151.035 | 149.7174

## LLG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.0081861 | 2.9953 | 2.9953 | 0.0054574 | 2.9962 | 2.9944 | 0.094525 | 34.5873 | 34.5867 | 0.063017 | 34.5972 | 34.5768 | 0.00027569 | 9.3227 | 9.3389 | -0.0001409 | -4.6654 | -4.6655 | -0.15618 | 10.6317 | 10.5421 | 0.10415 | -5.3458 | -5.2411 | 89.8559 | -161.7868 | 18.2103 | -90.1437 | 18.2627 | -161.8393 |  | 1.6523 | 0.40883 | 0.4072 | 1.6527 | 0.20508 | 0.20293 | -0.042997 | -113.0336 | 66.6735 | -0.066167 | -112.8494 | 66.4863
Line_1 | 0 | 2.9979 | 2.9927 | 0.0027278 | 2.9971 | 2.9936 | 0 | 34.6172 | 34.557 | 0.031498 | 34.6072 | 34.5668 | -3.3476e-09 | 5.7977e-11 | 5.9221e-11 | 2.8749e-05 | 4.6714 | 4.6596 | -3.3159e-12 | -3.223e-11 | 2.5247e-11 | -0.052059 | 5.3433 | 5.2436 | 0 | 18.3617 | -161.9385 | 89.9022 | -161.6878 | 18.1111 |  | 1.6525 | 0 | 0 | 1.6527 | 0.20508 | 0.20293 | -0.028724 | 0 | 0 | -0.066167 | -112.8494 | 66.4863
Line_2 | 0 | 0 | 0 | 0.0027296 | 0.0027296 | 0.0027296 | 0 | 0 | 0 | 0.031518 | 0.031518 | 0.031518 | -3.3511e-09 | 6.672e-10 | 3.3432e-10 | 0.00011215 | -0.005965 | 0.0058735 | -9.4781e-12 | 1.0444e-10 | -6.578e-10 | -0.052092 | 0.0024903 | -0.0025325 | 0 | 0 | 0 | 89.8105 | 89.8105 | 89.8105 |  | 1.6529 | 0.20542 | 0.2026 | 1.6527 | 0.20508 | 0.20293 | -0.081324 | -112.7578 | 66.3923 | -0.066167 | -112.8494 | 66.4863

## LLG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.0081861 | 2.9953 | 2.9953 | 0.0054574 | 2.9962 | 2.9944 | 0.094525 | 34.5873 | 34.5867 | 0.063017 | 34.5972 | 34.5768 | 0.00027569 | 9.3227 | 9.3389 | -0.0001409 | -4.6654 | -4.6655 | -0.15618 | 10.6317 | 10.5421 | 0.10415 | -5.3458 | -5.2411 | 89.8559 | -161.7868 | 18.2103 | -90.1437 | 18.2627 | -161.8393 |  | 1.6523 | 0.40883 | 0.4072 | 1.6527 | 0.20508 | 0.20293 | -0.042997 | -113.0336 | 66.6735 | -0.066167 | -112.8494 | 66.4863
Line_1 | 0 | 2.9979 | 2.9927 | 0.0027278 | 2.9971 | 2.9936 | 0 | 34.6172 | 34.557 | 0.031498 | 34.6072 | 34.5668 | -3.3476e-09 | 5.7977e-11 | 5.9221e-11 | 2.8749e-05 | 4.6714 | 4.6596 | -3.3159e-12 | -3.223e-11 | 2.5247e-11 | -0.052059 | 5.3433 | 5.2436 | 0 | 18.3617 | -161.9385 | 89.9022 | -161.6878 | 18.1111 |  | 1.6525 | 0 | 0 | 1.6527 | 0.20508 | 0.20293 | -0.028724 | 0 | 0 | -0.066167 | -112.8494 | 66.4863
Line_2 | 0 | 0 | 0 | 0.0027296 | 0.0027296 | 0.0027296 | 0 | 0 | 0 | 0.031518 | 0.031518 | 0.031518 | -3.3511e-09 | 6.672e-10 | 3.3432e-10 | 0.00011215 | -0.005965 | 0.0058735 | -9.4781e-12 | 1.0444e-10 | -6.578e-10 | -0.052092 | 0.0024903 | -0.0025325 | 0 | 0 | 0 | 89.8105 | 89.8105 | 89.8105 |  | 1.6529 | 0.20542 | 0.2026 | 1.6527 | 0.20508 | 0.20293 | -0.081324 | -112.7578 | 66.3923 | -0.066167 | -112.8494 | 66.4863

## LLG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.0082394 | 1.0496 | 1.0495 | 0.0054929 | 1.0512 | 1.0479 | 0.095141 | 12.1195 | 12.1184 | 0.063427 | 12.1384 | 12.0996 | 0.000965 | 6.6468 | 6.6596 | -0.00059989 | -6.0984 | -6.0627 | -0.15754 | 6.8844 | 6.7304 | 0.10505 | -6.2345 | -6.0808 | 89.4795 | -144.0826 | 35.9103 | -90.52 | 36.0378 | -144.2105 |  | 1.6559 | 0.78959 | 0.78131 | 1.6563 | 0.71848 | 0.70967 | -0.16953 | -98.0768 | 81.2136 | -0.19286 | -98.3301 | 80.8749
Line_1 | 0 | 1.0545 | 1.0446 | 0.0027456 | 1.0529 | 1.0462 | 0 | 12.1763 | 12.0621 | 0.031703 | 12.1573 | 12.0808 | -3.3767e-09 | -5.5598 | -5.4561 | 0.00025781 | 6.121 | 6.0404 | -1.8105e-11 | -5.5598 | -5.4561 | -0.052511 | 6.2314 | 6.0842 | 0 | 36.2775 | -144.4533 | 89.5258 | -143.8422 | 35.6683 |  | 1.6561 | 0.64575 | 0.63969 | 1.6563 | 0.71848 | 0.70967 | -0.15522 | -98.7225 | 80.5467 | -0.19286 | -98.3301 | 80.8749
Line_2 | 0 | 0 | 0 | 0.0027473 | 0.0027473 | 0.0027473 | 0 | 0 | 0 | 0.031724 | 0.031724 | 0.031724 | -3.3801e-09 | 7.9932e-10 | 3.7409e-10 | 0.00034208 | -0.022584 | 0.022263 | -2.4242e-11 | 1.0715e-09 | -1.8059e-09 | -0.052543 | 0.0030792 | -0.0033507 | 0 | 0 | 0 | 89.4341 | 89.4341 | 89.4341 |  | 1.6565 | 0.71889 | 0.70927 | 1.6563 | 0.71848 | 0.70967 | -0.20811 | -98.3116 | 80.8557 | -0.19286 | -98.3301 | 80.8749

## LLG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.0082394 | 1.0496 | 1.0495 | 0.0054929 | 1.0512 | 1.0479 | 0.095141 | 12.1195 | 12.1184 | 0.063427 | 12.1384 | 12.0996 | 0.000965 | 6.6468 | 6.6596 | -0.00059989 | -6.0984 | -6.0627 | -0.15754 | 6.8844 | 6.7304 | 0.10505 | -6.2345 | -6.0808 | 89.4795 | -144.0826 | 35.9103 | -90.52 | 36.0378 | -144.2105 |  | 1.6559 | 0.78959 | 0.78131 | 1.6563 | 0.71848 | 0.70967 | -0.16953 | -98.0768 | 81.2136 | -0.19286 | -98.3301 | 80.8749
Line_1 | 0 | 1.0545 | 1.0446 | 0.0027456 | 1.0529 | 1.0462 | 0 | 12.1763 | 12.0621 | 0.031703 | 12.1573 | 12.0808 | -3.3767e-09 | -5.5598 | -5.4561 | 0.00025781 | 6.121 | 6.0404 | -1.8105e-11 | -5.5598 | -5.4561 | -0.052511 | 6.2314 | 6.0842 | 0 | 36.2775 | -144.4533 | 89.5258 | -143.8422 | 35.6683 |  | 1.6561 | 0.64575 | 0.63969 | 1.6563 | 0.71848 | 0.70967 | -0.15522 | -98.7225 | 80.5467 | -0.19286 | -98.3301 | 80.8749
Line_2 | 0 | 0 | 0 | 0.0027473 | 0.0027473 | 0.0027473 | 0 | 0 | 0 | 0.031724 | 0.031724 | 0.031724 | -3.3801e-09 | 7.9932e-10 | 3.7409e-10 | 0.00034208 | -0.022584 | 0.022263 | -2.4242e-11 | 1.0715e-09 | -1.8059e-09 | -0.052543 | 0.0030792 | -0.0033507 | 0 | 0 | 0 | 89.4341 | 89.4341 | 89.4341 |  | 1.6565 | 0.71889 | 0.70927 | 1.6563 | 0.71848 | 0.70967 | -0.20811 | -98.3116 | 80.8557 | -0.19286 | -98.3301 | 80.8749

## LLG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.0074422 | 2.3977 | 2.3976 | 0.0049614 | 2.399 | 2.3963 | 0.085935 | 27.6861 | 27.6851 | 0.05729 | 27.7007 | 27.6705 | 0.00043747 | 11.4941 | 11.4639 | -0.00022359 | -5.7672 | -5.7119 | -0.12909 | 6.8395 | 6.7274 | 0.08608 | -3.4572 | -3.3263 | 89.7255 | -149.573 | 30.4241 | -90.2736 | 30.478 | -149.6269 |  | 1.5021 | 0.4831 | 0.48011 | 1.5025 | 0.24274 | 0.23888 | -0.080291 | -118.8183 | 60.8299 | -0.12478 | -118.5812 | 60.5872
Line_1 | 0 | 2.4015 | 2.3938 | 0.0024799 | 2.4002 | 2.3951 | 0 | 27.73 | 27.6414 | 0.028636 | 27.7154 | 27.6559 | -2.7671e-09 | -1.3569e-10 | 1.2414e-11 | 4.5619e-05 | 5.7734 | 5.7059 | -5.0889e-12 | -9.743e-11 | -1.5493e-10 | -0.043027 | 3.4539 | 3.3296 | 0 | 30.5797 | -149.7291 | 89.8145 | -149.4711 | 30.3221 |  | 1.5023 | 0 | 0 | 1.5025 | 0.24274 | 0.23888 | -0.052888 | 0 | 0 | -0.12478 | -118.5812 | 60.5872
Line_2 | 0 | 0 | 0 | 0.0024815 | 0.0024815 | 0.0024815 | 0 | 0 | 0 | 0.028654 | 0.028654 | 0.028654 | -2.7699e-09 | 6.748e-10 | 2.3479e-10 | 0.00017797 | -0.0061288 | 0.0059836 | -1.4813e-11 | 2.3921e-11 | -7.5309e-10 | -0.043054 | 0.0032889 | -0.0033238 | 0 | 0 | 0 | 89.6384 | 89.6384 | 89.6384 |  | 1.5027 | 0.24334 | 0.23829 | 1.5025 | 0.24274 | 0.23888 | -0.15388 | -118.4636 | 60.4651 | -0.12478 | -118.5812 | 60.5872

## LLG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.0074422 | 2.3977 | 2.3976 | 0.0049614 | 2.399 | 2.3963 | 0.085935 | 27.6861 | 27.6851 | 0.05729 | 27.7007 | 27.6705 | 0.00043747 | 11.4941 | 11.4639 | -0.00022359 | -5.7672 | -5.7119 | -0.12909 | 6.8395 | 6.7274 | 0.08608 | -3.4572 | -3.3263 | 89.7255 | -149.573 | 30.4241 | -90.2736 | 30.478 | -149.6269 |  | 1.5021 | 0.4831 | 0.48011 | 1.5025 | 0.24274 | 0.23888 | -0.080291 | -118.8183 | 60.8299 | -0.12478 | -118.5812 | 60.5872
Line_1 | 0 | 2.4015 | 2.3938 | 0.0024799 | 2.4002 | 2.3951 | 0 | 27.73 | 27.6414 | 0.028636 | 27.7154 | 27.6559 | -2.7671e-09 | -1.3569e-10 | 1.2414e-11 | 4.5619e-05 | 5.7734 | 5.7059 | -5.0889e-12 | -9.743e-11 | -1.5493e-10 | -0.043027 | 3.4539 | 3.3296 | 0 | 30.5797 | -149.7291 | 89.8145 | -149.4711 | 30.3221 |  | 1.5023 | 0 | 0 | 1.5025 | 0.24274 | 0.23888 | -0.052888 | 0 | 0 | -0.12478 | -118.5812 | 60.5872
Line_2 | 0 | 0 | 0 | 0.0024815 | 0.0024815 | 0.0024815 | 0 | 0 | 0 | 0.028654 | 0.028654 | 0.028654 | -2.7699e-09 | 6.748e-10 | 2.3479e-10 | 0.00017797 | -0.0061288 | 0.0059836 | -1.4813e-11 | 2.3921e-11 | -7.5309e-10 | -0.043054 | 0.0032889 | -0.0033238 | 0 | 0 | 0 | 89.6384 | 89.6384 | 89.6384 |  | 1.5027 | 0.24334 | 0.23829 | 1.5025 | 0.24274 | 0.23888 | -0.15388 | -118.4636 | 60.4651 | -0.12478 | -118.5812 | 60.5872

## LLG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.0074905 | 0.89634 | 0.89624 | 0.0049937 | 0.89796 | 0.89463 | 0.086493 | 10.35 | 10.3489 | 0.057662 | 10.3687 | 10.3303 | 0.00101 | 5.6264 | 5.6151 | -0.00060439 | -4.846 | -4.7918 | -0.1302 | 5.0323 | 4.897 | 0.086825 | -4.5606 | -4.421 | 89.3483 | -140.3941 | 39.5988 | -90.6509 | 39.7274 | -140.5232 |  | 1.5054 | 0.72933 | 0.71993 | 1.5058 | 0.64179 | 0.63113 | -0.2073 | -98.5847 | 80.6905 | -0.25205 | -97.0106 | 82.1716
Line_1 | 0 | 0.9012 | 0.89142 | 0.0024961 | 0.89958 | 0.89302 | 0 | 10.4062 | 10.2932 | 0.028822 | 10.3874 | 10.3117 | -2.7911e-09 | -4.0608 | -3.9731 | 0.00023539 | 4.8644 | 4.7738 | -1.7319e-11 | -4.0608 | -3.9731 | -0.043399 | 4.5585 | 4.4232 | 0 | 39.9693 | -140.7686 | 89.4372 | -140.1515 | 39.3544 |  | 1.5056 | 0.55187 | 0.54588 | 1.5058 | 0.64179 | 0.63113 | -0.17981 | -95.0307 | 84.2314 | -0.25205 | -97.0106 | 82.1716
Line_2 | 0 | 0 | 0 | 0.0024976 | 0.0024976 | 0.0024976 | 0 | 0 | 0 | 0.02884 | 0.02884 | 0.02884 | -2.7938e-09 | 6.5471e-10 | 3.6802e-10 | 0.000369 | -0.018398 | 0.018063 | -2.7117e-11 | 9.2096e-10 | -1.4183e-09 | -0.043426 | 0.002022 | -0.0022464 | 0 | 0 | 0 | 89.2611 | 89.2611 | 89.2611 |  | 1.5059 | 0.64253 | 0.63038 | 1.5058 | 0.64179 | 0.63113 | -0.2813 | -96.9891 | 82.1487 | -0.25205 | -97.0106 | 82.1716

## LLG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.0074905 | 0.89634 | 0.89624 | 0.0049937 | 0.89796 | 0.89463 | 0.086493 | 10.35 | 10.3489 | 0.057662 | 10.3687 | 10.3303 | 0.00101 | 5.6264 | 5.6151 | -0.00060439 | -4.846 | -4.7918 | -0.1302 | 5.0323 | 4.897 | 0.086825 | -4.5606 | -4.421 | 89.3483 | -140.3941 | 39.5988 | -90.6509 | 39.7274 | -140.5232 |  | 1.5054 | 0.72933 | 0.71993 | 1.5058 | 0.64179 | 0.63113 | -0.2073 | -98.5847 | 80.6905 | -0.25205 | -97.0106 | 82.1716
Line_1 | 0 | 0.9012 | 0.89142 | 0.0024961 | 0.89958 | 0.89302 | 0 | 10.4062 | 10.2932 | 0.028822 | 10.3874 | 10.3117 | -2.7911e-09 | -4.0608 | -3.9731 | 0.00023539 | 4.8644 | 4.7738 | -1.7319e-11 | -4.0608 | -3.9731 | -0.043399 | 4.5585 | 4.4232 | 0 | 39.9693 | -140.7686 | 89.4372 | -140.1515 | 39.3544 |  | 1.5056 | 0.55187 | 0.54588 | 1.5058 | 0.64179 | 0.63113 | -0.17981 | -95.0307 | 84.2314 | -0.25205 | -97.0106 | 82.1716
Line_2 | 0 | 0 | 0 | 0.0024976 | 0.0024976 | 0.0024976 | 0 | 0 | 0 | 0.02884 | 0.02884 | 0.02884 | -2.7938e-09 | 6.5471e-10 | 3.6802e-10 | 0.000369 | -0.018398 | 0.018063 | -2.7117e-11 | 9.2096e-10 | -1.4183e-09 | -0.043426 | 0.002022 | -0.0022464 | 0 | 0 | 0 | 89.2611 | 89.2611 | 89.2611 |  | 1.5059 | 0.64253 | 0.63038 | 1.5058 | 0.64179 | 0.63113 | -0.2813 | -96.9891 | 82.1487 | -0.25205 | -97.0106 | 82.1716