## LLL_max_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 4.283 | 4.283 | 0 | 9.2778 | 148.3662 | 148.3662 | 28.6163 | -1e-07 | 32.4685 | -1e-07 | -77.7798 | 102.2202 | 0.29171 | 0 | -29.1714 | 0
Line_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.602e-19 | 0 | -1.2513e-19 | 0 | 0 | 0 | 0 | 0 | 0
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.602e-19 | 0 | -1.2513e-19 | 0 | 0 | 0 | 0 | 0 | 0
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## LLL_max_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 4.283 | 4.283 | 0 | 9.2778 | 148.3662 | 148.3662 | 28.6163 | -1e-07 | 32.4685 | -1e-07 | -77.7798 | 102.2202 | 0.29171 | 0 | -29.1714 | 0
Line_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.602e-19 | 0 | -1.2513e-19 | 0 | 0 | 0 | 0 | 0 | 0
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.602e-19 | 0 | -1.2513e-19 | 0 | 0 | 0 | 0 | 0 | 0
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## LLL_max_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 1.3097 | 1.3097 | 0 | 2.8371 | 45.3689 | 45.3689 | 28.405 | -25.7292 | 28.7652 | -25.7292 | -54.5297 | 125.4703 | 0.89106 | 0.80202 | -9.1687 | -9.5297
Line_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.495e-09 | 0 | 1.6066e-09 | 0 | 0 | 0.80202 | 0.80202 | -9.5297 | -9.5297
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.495e-09 | 0 | 1.6066e-09 | 0 | 0 | 0.80202 | 0.80202 | -9.5297 | -9.5297
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80202 | 0.80202 | -9.5297 | -9.5297

## LLL_max_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 1.3097 | 1.3097 | 0 | 2.8371 | 45.3689 | 45.3689 | 28.405 | -25.7292 | 28.7652 | -25.7292 | -54.5297 | 125.4703 | 0.89106 | 0.80202 | -9.1687 | -9.5297
Line_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.495e-09 | 0 | 1.6066e-09 | 0 | 0 | 0.80202 | 0.80202 | -9.5297 | -9.5297
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.495e-09 | 0 | 1.6066e-09 | 0 | 0 | 0.80202 | 0.80202 | -9.5297 | -9.5297
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80202 | 0.80202 | -9.5297 | -9.5297

## LLL_min_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 3.6016 | 3.6016 | 0 | 6.8381 | 124.7634 | 124.7634 | 38.8525 | -1e-07 | 22.9597 | -1e-07 | -69.6723 | 110.3277 | 0.36172 | 0 | -39.0915 | 0
Line_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7305e-20 | 0 | 6.3226e-20 | 0 | 0 | 0 | 0 | 0 | 0
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7305e-20 | 0 | 6.3226e-20 | 0 | 0 | 0 | 0 | 0 | 0
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## LLL_min_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 3.6016 | 3.6016 | 0 | 6.8381 | 124.7634 | 124.7634 | 38.8525 | -1e-07 | 22.9597 | -1e-07 | -69.6723 | 110.3277 | 0.36172 | 0 | -39.0915 | 0
Line_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7305e-20 | 0 | 6.3226e-20 | 0 | 0 | 0 | 0 | 0 | 0
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7305e-20 | 0 | 6.3226e-20 | 0 | 0 | 0 | 0 | 0 | 0
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## LLL_min_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 1.1462 | 1.1462 | 0 | 2.1763 | 39.7072 | 39.7072 | 23.6436 | -19.7082 | 22.0338 | -19.7082 | -52.6343 | 127.3657 | 0.81393 | 0.70193 | -9.6527 | -7.6343
Line_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.233e-09 | 0 | 1.0258e-09 | 0 | 0 | 0.70193 | 0.70193 | -7.6343 | -7.6343
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.233e-09 | 0 | 1.0258e-09 | 0 | 0 | 0.70193 | 0.70193 | -7.6343 | -7.6343
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.70193 | 0.70193 | -7.6343 | -7.6343

## LLL_min_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 1.1462 | 1.1462 | 0 | 2.1763 | 39.7072 | 39.7072 | 23.6436 | -19.7082 | 22.0338 | -19.7082 | -52.6343 | 127.3657 | 0.81393 | 0.70193 | -9.6527 | -7.6343
Line_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.233e-09 | 0 | 1.0258e-09 | 0 | 0 | 0.70193 | 0.70193 | -7.6343 | -7.6343
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.233e-09 | 0 | 1.0258e-09 | 0 | 0 | 0.70193 | 0.70193 | -7.6343 | -7.6343
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.70193 | 0.70193 | -7.6343 | -7.6343

## LL_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 3.7092 | 3.7092 | 0 | 3.7092 | 3.7092 | 0 | 42.8296 | 42.8296 | 0 | 42.8296 | 42.8296 | -5.2106e-14 | 30.1766 | -15.8685 | 4.6896e-14 | -23.0225 | 23.0225 | -2.0843e-14 | 3.131 | 13.1032 | 1.0421e-14 | 4.9861 | -4.9861 | 0 | -167.7798 | 12.2202 | 0 | 12.2202 | -167.7798 | 1.1 | 0.70836 | 0.48049 | 1.1 | 0.55 | 0.55 | -3.1871e-12 | -161.8563 | 152.6723 | -3.1941e-12 | 180 | -180
Line_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.2106e-15 | -1.3027e-14 | 2.6053e-14 | -5.8095e-28 | 1.8237e-14 | -2.6053e-14 | 5.2106e-15 | -1.9211e-09 | 1.9211e-09 | -1.0421e-14 | 1.9211e-09 | -1.9211e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.55 | 0.55 | 1.1 | 0.55 | 0.55 | -3.1875e-12 | -180 | 180 | -3.1941e-12 | 180 | -180
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.6053e-15 | 1.5632e-14 | -1.0421e-14 | 7.816e-15 | -2.6053e-14 | 0 | -1.9211e-09 | 1.9211e-09 | -1.0421e-14 | 1.9211e-09 | -1.9211e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.55 | 0.55 | 1.1 | 0.55 | 0.55 | -3.19e-12 | -180 | 180 | -3.1941e-12 | 180 | -180
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.2106e-15 | -5.2106e-15 | 0 | -2.9011e-28 | 7.816e-15 | -5.2106e-15 | 2.8988e-28 | 7.816e-15 | 0 | -5.2106e-15 | -7.816e-15 | -5.2106e-15 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.55 | 0.55 | 1.1 | 0.55 | 0.55 | -3.1875e-12 | -180 | 180 | -3.19e-12 | -180 | 180

## LL_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 3.7092 | 3.7092 | 0 | 3.7092 | 3.7092 | 0 | 42.8296 | 42.8296 | 0 | 42.8296 | 42.8296 | -5.2106e-14 | 30.1766 | -15.8685 | 4.6896e-14 | -23.0225 | 23.0225 | -2.0843e-14 | 3.131 | 13.1032 | 1.0421e-14 | 4.9861 | -4.9861 | 0 | -167.7798 | 12.2202 | 0 | 12.2202 | -167.7798 | 1.1 | 0.70836 | 0.48049 | 1.1 | 0.55 | 0.55 | -3.1871e-12 | -161.8563 | 152.6723 | -3.1941e-12 | 180 | -180
Line_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.2106e-15 | -1.3027e-14 | 2.6053e-14 | -5.8095e-28 | 1.8237e-14 | -2.6053e-14 | 5.2106e-15 | -1.9211e-09 | 1.9211e-09 | -1.0421e-14 | 1.9211e-09 | -1.9211e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.55 | 0.55 | 1.1 | 0.55 | 0.55 | -3.1875e-12 | -180 | 180 | -3.1941e-12 | 180 | -180
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.6053e-15 | 1.5632e-14 | -1.0421e-14 | 7.816e-15 | -2.6053e-14 | 0 | -1.9211e-09 | 1.9211e-09 | -1.0421e-14 | 1.9211e-09 | -1.9211e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.55 | 0.55 | 1.1 | 0.55 | 0.55 | -3.19e-12 | -180 | 180 | -3.1941e-12 | 180 | -180
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.2106e-15 | -5.2106e-15 | 0 | -2.9011e-28 | 7.816e-15 | -5.2106e-15 | 2.8988e-28 | 7.816e-15 | 0 | -5.2106e-15 | -7.816e-15 | -5.2106e-15 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.55 | 0.55 | 1.1 | 0.55 | 0.55 | -3.1875e-12 | -180 | 180 | -3.19e-12 | -180 | 180

## LL_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 1.7631 | 1.7631 | 0 | 1.7631 | 1.7631 | 0 | 20.3584 | 20.3584 | 0 | 20.3584 | 20.3584 | -1.8237e-14 | 19.0761 | -0.30087 | 1.3027e-14 | -17.4596 | 1.9173 | -1.0421e-14 | 3.9919 | 15.2185 | 2.6053e-15 | -2.1579 | -13.3845 | 0 | -149.913 | 30.087 | 0 | 30.087 | -149.913 | 1.1 | 0.95731 | 0.74767 | 1.1 | 0.86414 | 0.66415 | 5.6213e-13 | -138.0936 | 121.2196 | 5.5491e-13 | -142.8673 | 128.239
Line_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.816e-15 | 4.7339e-10 | 1.0338e-09 | -1.0421e-14 | -4.7339e-10 | -1.0338e-09 | 5.2106e-15 | -1.3544e-09 | 3.8386e-10 | -1.0421e-14 | 1.3544e-09 | -3.8387e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.86414 | 0.66415 | 1.1 | 0.86414 | 0.66415 | 5.5409e-13 | -142.8673 | 128.239 | 5.5491e-13 | -142.8673 | 128.239
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2106e-15 | 4.7339e-10 | 1.0338e-09 | -7.816e-15 | -4.7339e-10 | -1.0338e-09 | 5.2106e-15 | -1.3544e-09 | 3.8387e-10 | -1.0421e-14 | 1.3544e-09 | -3.8387e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.86414 | 0.66415 | 1.1 | 0.86414 | 0.66415 | 5.5294e-13 | -142.8673 | 128.239 | 5.5491e-13 | -142.8673 | 128.239
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6053e-15 | -1.6786e-15 | 0 | -7.816e-15 | 7.9238e-16 | -4.9421e-15 | 2.5195e-29 | 8.9979e-15 | 0 | -7.5429e-29 | 5.7344e-15 | -3.8945e-15 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.86414 | 0.66415 | 1.1 | 0.86414 | 0.66415 | 5.5409e-13 | -142.8673 | 128.239 | 5.5294e-13 | -142.8673 | 128.239

## LL_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 1.7631 | 1.7631 | 0 | 1.7631 | 1.7631 | 0 | 20.3584 | 20.3584 | 0 | 20.3584 | 20.3584 | -1.8237e-14 | 19.0761 | -0.30087 | 1.3027e-14 | -17.4596 | 1.9173 | -1.0421e-14 | 3.9919 | 15.2185 | 2.6053e-15 | -2.1579 | -13.3845 | 0 | -149.913 | 30.087 | 0 | 30.087 | -149.913 | 1.1 | 0.95731 | 0.74767 | 1.1 | 0.86414 | 0.66415 | 5.6213e-13 | -138.0936 | 121.2196 | 5.5491e-13 | -142.8673 | 128.239
Line_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.816e-15 | 4.7339e-10 | 1.0338e-09 | -1.0421e-14 | -4.7339e-10 | -1.0338e-09 | 5.2106e-15 | -1.3544e-09 | 3.8386e-10 | -1.0421e-14 | 1.3544e-09 | -3.8387e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.86414 | 0.66415 | 1.1 | 0.86414 | 0.66415 | 5.5409e-13 | -142.8673 | 128.239 | 5.5491e-13 | -142.8673 | 128.239
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2106e-15 | 4.7339e-10 | 1.0338e-09 | -7.816e-15 | -4.7339e-10 | -1.0338e-09 | 5.2106e-15 | -1.3544e-09 | 3.8387e-10 | -1.0421e-14 | 1.3544e-09 | -3.8387e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.86414 | 0.66415 | 1.1 | 0.86414 | 0.66415 | 5.5294e-13 | -142.8673 | 128.239 | 5.5491e-13 | -142.8673 | 128.239
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6053e-15 | -1.6786e-15 | 0 | -7.816e-15 | 7.9238e-16 | -4.9421e-15 | 2.5195e-29 | 8.9979e-15 | 0 | -7.5429e-29 | 5.7344e-15 | -3.8945e-15 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.86414 | 0.66415 | 1.1 | 0.86414 | 0.66415 | 5.5409e-13 | -142.8673 | 128.239 | 5.5294e-13 | -142.8673 | 128.239

## LL_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 3.1191 | 3.1191 | 0 | 3.1191 | 3.1191 | 0 | 36.0161 | 36.0161 | 0 | 36.0161 | 36.0161 | 4.737e-15 | 26.5997 | -7.1734 | -9.4739e-15 | -16.8865 | 16.8865 | 1.4211e-14 | -0.51586 | 11.9957 | -1.4211e-14 | 6.2558 | -6.2558 | 0 | -159.6723 | 20.3277 | 0 | 20.3277 | -159.6723 | 1 | 0.73869 | 0.38808 | 1 | 0.5 | 0.5 | 6.2667e-12 | -160.7833 | 141.207 | 6.2826e-12 | -180 | 180
Line_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.6579e-14 | -7.1053e-15 | 9.0108e-20 | 1.1842e-14 | 8.2897e-15 | 2.3685e-15 | -1.8144e-27 | -1.5877e-09 | 1.5877e-09 | -4.737e-15 | 1.5877e-09 | -1.5877e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 6.2703e-12 | -180 | 180 | 6.2826e-12 | -180 | 180
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.4211e-14 | -7.1053e-15 | 4.737e-15 | 9.4739e-15 | 8.2897e-15 | 2.3685e-15 | -4.737e-15 | -1.5877e-09 | 1.5877e-09 | 9.4739e-15 | 1.5877e-09 | -1.5877e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 6.2778e-12 | -180 | 180 | 6.2826e-12 | -180 | 180
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.737e-15 | 1.1842e-15 | -9.4739e-15 | 1.038e-27 | 1.1842e-15 | 9.4739e-15 | 9.4739e-15 | 4.737e-15 | 5.3768e-25 | -9.4739e-15 | -4.737e-15 | -5.3768e-25 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 6.2703e-12 | -180 | 180 | 6.2778e-12 | -180 | 180

## LL_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 3.1191 | 3.1191 | 0 | 3.1191 | 3.1191 | 0 | 36.0161 | 36.0161 | 0 | 36.0161 | 36.0161 | 4.737e-15 | 26.5997 | -7.1734 | -9.4739e-15 | -16.8865 | 16.8865 | 1.4211e-14 | -0.51586 | 11.9957 | -1.4211e-14 | 6.2558 | -6.2558 | 0 | -159.6723 | 20.3277 | 0 | 20.3277 | -159.6723 | 1 | 0.73869 | 0.38808 | 1 | 0.5 | 0.5 | 6.2667e-12 | -160.7833 | 141.207 | 6.2826e-12 | -180 | 180
Line_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.6579e-14 | -7.1053e-15 | 9.0108e-20 | 1.1842e-14 | 8.2897e-15 | 2.3685e-15 | -1.8144e-27 | -1.5877e-09 | 1.5877e-09 | -4.737e-15 | 1.5877e-09 | -1.5877e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 6.2703e-12 | -180 | 180 | 6.2826e-12 | -180 | 180
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.4211e-14 | -7.1053e-15 | 4.737e-15 | 9.4739e-15 | 8.2897e-15 | 2.3685e-15 | -4.737e-15 | -1.5877e-09 | 1.5877e-09 | 9.4739e-15 | 1.5877e-09 | -1.5877e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 6.2778e-12 | -180 | 180 | 6.2826e-12 | -180 | 180
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.737e-15 | 1.1842e-15 | -9.4739e-15 | 1.038e-27 | 1.1842e-15 | 9.4739e-15 | 9.4739e-15 | 4.737e-15 | 5.3768e-25 | -9.4739e-15 | -4.737e-15 | -5.3768e-25 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 6.2703e-12 | -180 | 180 | 6.2778e-12 | -180 | 180

## LL_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 1.5183 | 1.5183 | 0 | 1.5183 | 1.5183 | 0 | 17.5318 | 17.5318 | 0 | 17.5318 | 17.5318 | 1.1842e-15 | 15.3932 | 0.73601 | -2.9606e-15 | -13.0917 | 1.5655 | 7.1054e-15 | 2.3135 | 11.9328 | -1.1842e-14 | -0.95344 | -10.5727 | 0 | -146.7238 | 33.2762 | 0 | 33.2762 | -146.7238 | 1 | 0.88788 | 0.68193 | 1 | 0.74872 | 0.60963 | 2.3167e-12 | -138.1765 | 119.7467 | 2.3269e-12 | -142.5584 | 131.6989
Line_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.2897e-15 | 4.798e-10 | 8.2615e-10 | 5.3291e-15 | -4.7979e-10 | -8.2616e-10 | -3.3554e-28 | -1.0532e-09 | 4.5325e-10 | -2.3685e-15 | 1.0532e-09 | -4.5325e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.74872 | 0.60963 | 1 | 0.74872 | 0.60963 | 2.3192e-12 | -142.5584 | 131.6989 | 2.3269e-12 | -142.5584 | 131.6989
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.0658e-14 | 4.7979e-10 | 8.2616e-10 | 8.8818e-15 | -4.7978e-10 | -8.2616e-10 | 2.3685e-15 | -1.0532e-09 | 4.5326e-10 | -4.737e-15 | 1.0532e-09 | -4.5326e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.74872 | 0.60963 | 1 | 0.74872 | 0.60963 | 2.3242e-12 | -142.5584 | 131.6989 | 2.3269e-12 | -142.5584 | 131.6989
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3685e-15 | 7.4582e-15 | -2.3517e-16 | -4.737e-15 | -2.112e-15 | -1.6759e-15 | -2.3685e-15 | -9.8963e-16 | -4.0772e-15 | 2.3685e-15 | -1.6171e-15 | -2.4601e-15 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.74872 | 0.60963 | 1 | 0.74872 | 0.60963 | 2.3192e-12 | -142.5584 | 131.6989 | 2.3242e-12 | -142.5584 | 131.6989

## LL_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 1.5183 | 1.5183 | 0 | 1.5183 | 1.5183 | 0 | 17.5318 | 17.5318 | 0 | 17.5318 | 17.5318 | 1.1842e-15 | 15.3932 | 0.73601 | -2.9606e-15 | -13.0917 | 1.5655 | 7.1054e-15 | 2.3135 | 11.9328 | -1.1842e-14 | -0.95344 | -10.5727 | 0 | -146.7238 | 33.2762 | 0 | 33.2762 | -146.7238 | 1 | 0.88788 | 0.68193 | 1 | 0.74872 | 0.60963 | 2.3167e-12 | -138.1765 | 119.7467 | 2.3269e-12 | -142.5584 | 131.6989
Line_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.2897e-15 | 4.798e-10 | 8.2615e-10 | 5.3291e-15 | -4.7979e-10 | -8.2616e-10 | -3.3554e-28 | -1.0532e-09 | 4.5325e-10 | -2.3685e-15 | 1.0532e-09 | -4.5325e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.74872 | 0.60963 | 1 | 0.74872 | 0.60963 | 2.3192e-12 | -142.5584 | 131.6989 | 2.3269e-12 | -142.5584 | 131.6989
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.0658e-14 | 4.7979e-10 | 8.2616e-10 | 8.8818e-15 | -4.7978e-10 | -8.2616e-10 | 2.3685e-15 | -1.0532e-09 | 4.5326e-10 | -4.737e-15 | 1.0532e-09 | -4.5326e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.74872 | 0.60963 | 1 | 0.74872 | 0.60963 | 2.3242e-12 | -142.5584 | 131.6989 | 2.3269e-12 | -142.5584 | 131.6989
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3685e-15 | 7.4582e-15 | -2.3517e-16 | -4.737e-15 | -2.112e-15 | -1.6759e-15 | -2.3685e-15 | -9.8963e-16 | -4.0772e-15 | 2.3685e-15 | -1.6171e-15 | -2.4601e-15 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.74872 | 0.60963 | 1 | 0.74872 | 0.60963 | 2.3192e-12 | -142.5584 | 131.6989 | 2.3242e-12 | -142.5584 | 131.6989

## LG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.02744 | 0.021949 | 0.021949 | 0.032924 | 0.016464 | 0.016464 | 0.31684 | 0.25344 | 0.25344 | 0.38018 | 0.19011 | 0.19011 | 0.00019163 | 0.24214 | -0.24074 | 1.0965e-13 | -0.18144 | 0.18077 | 0.00042187 | -0.42046 | -0.42159 | -2.2854e-13 | 0.31555 | 0.31653 | 89.8148 | -90.1335 | -90.1335 | -90.1662 | 89.8457 | 89.8457 |  | 0.0014624 | 1.9144 | 1.9155 | 0 | 1.9146 | 1.9173 | 155.3851 | -150.1961 | 150.1391 | 0 | -150.2559 | 150.1147
Line_1 | 0.0027446 | 0.0027446 | 0.0027446 | 0.0082321 | 0.0082321 | 0.0082321 | 0.031692 | 0.031692 | 0.031692 | 0.095056 | 0.095056 | 0.095056 | 5.5667e-05 | -0.030218 | 0.030163 | 2.7404e-14 | 0.090719 | -0.090385 | 2.2146e-05 | 0.052609 | 0.052804 | -5.7146e-14 | -0.15778 | -0.15826 | 89.8154 | 89.8154 | 89.8154 | -90.1543 | -90.1543 | -90.1543 |  | 0.0018904 | 1.9144 | 1.9188 | 0 | 1.9146 | 1.9173 | 111.5098 | -150.3119 | 150.0795 | 0 | -150.2559 | 150.1147
Line_2 | 0.0027446 | 0.0027446 | 0.0027446 | 0.0082321 | 0.0082321 | 0.0082321 | 0.031692 | 0.031692 | 0.031692 | 0.095056 | 0.095056 | 0.095056 | 5.5667e-05 | -0.030218 | 0.030163 | 2.7404e-14 | 0.090719 | -0.090385 | 2.2146e-05 | 0.052609 | 0.052804 | -5.7146e-14 | -0.15778 | -0.15826 | 89.8154 | 89.8154 | 89.8154 | -90.1543 | -90.1543 | -90.1543 |  | 0.0018904 | 1.9144 | 1.9188 | 0 | 1.9146 | 1.9173 | 111.5098 | -150.3119 | 150.0795 | 0 | -150.2559 | 150.1147
Line_3 | 0.0027446 | 0.0027446 | 0.0027446 | 0.0027446 | 0.0027446 | 0.0027446 | 0.031692 | 0.031692 | 0.031692 | 0.031692 | 0.031692 | 0.031692 | -5.5667e-05 | 0.030218 | -0.030163 | -5.5667e-05 | 0.030218 | -0.030163 | -2.2146e-05 | -0.052609 | -0.052804 | -2.2146e-05 | -0.052609 | -0.052804 | -90.1846 | -90.1846 | -90.1846 | -90.1846 | -90.1846 | -90.1846 |  | 0.0018904 | 1.9144 | 1.9188 | 0.0018904 | 1.9144 | 1.9188 | 111.5098 | -150.3119 | 150.0795 | 111.5098 | -150.3119 | 150.0795

## LG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.02744 | 0.021949 | 0.021949 | 0.032924 | 0.016464 | 0.016464 | 0.31684 | 0.25344 | 0.25344 | 0.38018 | 0.19011 | 0.19011 | 0.00019163 | 0.24214 | -0.24074 | 1.0965e-13 | -0.18144 | 0.18077 | 0.00042187 | -0.42046 | -0.42159 | -2.2854e-13 | 0.31555 | 0.31653 | 89.8148 | -90.1335 | -90.1335 | -90.1662 | 89.8457 | 89.8457 |  | 0.0014624 | 1.9144 | 1.9155 | 0 | 1.9146 | 1.9173 | 155.3851 | -150.1961 | 150.1391 | 0 | -150.2559 | 150.1147
Line_1 | 0.0027446 | 0.0027446 | 0.0027446 | 0.0082321 | 0.0082321 | 0.0082321 | 0.031692 | 0.031692 | 0.031692 | 0.095056 | 0.095056 | 0.095056 | 5.5667e-05 | -0.030218 | 0.030163 | 2.7404e-14 | 0.090719 | -0.090385 | 2.2146e-05 | 0.052609 | 0.052804 | -5.7146e-14 | -0.15778 | -0.15826 | 89.8154 | 89.8154 | 89.8154 | -90.1543 | -90.1543 | -90.1543 |  | 0.0018904 | 1.9144 | 1.9188 | 0 | 1.9146 | 1.9173 | 111.5098 | -150.3119 | 150.0795 | 0 | -150.2559 | 150.1147
Line_2 | 0.0027446 | 0.0027446 | 0.0027446 | 0.0082321 | 0.0082321 | 0.0082321 | 0.031692 | 0.031692 | 0.031692 | 0.095056 | 0.095056 | 0.095056 | 5.5667e-05 | -0.030218 | 0.030163 | 2.7404e-14 | 0.090719 | -0.090385 | 2.2146e-05 | 0.052609 | 0.052804 | -5.7146e-14 | -0.15778 | -0.15826 | 89.8154 | 89.8154 | 89.8154 | -90.1543 | -90.1543 | -90.1543 |  | 0.0018904 | 1.9144 | 1.9188 | 0 | 1.9146 | 1.9173 | 111.5098 | -150.3119 | 150.0795 | 0 | -150.2559 | 150.1147
Line_3 | 0.0027446 | 0.0027446 | 0.0027446 | 0.0027446 | 0.0027446 | 0.0027446 | 0.031692 | 0.031692 | 0.031692 | 0.031692 | 0.031692 | 0.031692 | -5.5667e-05 | 0.030218 | -0.030163 | -5.5667e-05 | 0.030218 | -0.030163 | -2.2146e-05 | -0.052609 | -0.052804 | -2.2146e-05 | -0.052609 | -0.052804 | -90.1846 | -90.1846 | -90.1846 | -90.1846 | -90.1846 | -90.1846 |  | 0.0018904 | 1.9144 | 1.9188 | 0.0018904 | 1.9144 | 1.9188 | 111.5098 | -150.3119 | 150.0795 | 111.5098 | -150.3119 | 150.0795

## LG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.027977 | 0.022378 | 0.022378 | 0.033569 | 0.016786 | 0.016786 | 0.32305 | 0.2584 | 0.2584 | 0.38762 | 0.19383 | 0.19383 | 0.0072402 | 0.24965 | -0.24255 | -0.0084512 | -0.18706 | 0.18214 | 0.0074852 | -0.42938 | -0.44031 | -0.0084523 | 0.32225 | 0.33058 | 88.6758 | -91.2725 | -91.2725 | -91.3052 | 88.7067 | 88.7067 |  | 0.032236 | 1.9221 | 1.9454 | 0.030836 | 1.9223 | 1.9473 | 134.6289 | -151.0977 | 149.8786 | 133.6988 | -151.1585 | 149.8533
Line_1 | 0.0027983 | 0.0027983 | 0.0027983 | 0.0083931 | 0.0083931 | 0.0083931 | 0.032312 | 0.032312 | 0.032312 | 0.096916 | 0.096916 | 0.096916 | 0.00076213 | -0.031154 | 0.030392 | -0.0021135 | 0.093531 | -0.091071 | 0.00072784 | 0.053726 | 0.055148 | -0.0021129 | -0.16112 | -0.16529 | 88.6764 | 88.6764 | 88.6764 | -91.2933 | -91.2933 | -91.2933 |  | 0.032615 | 1.922 | 1.9487 | 0.030836 | 1.9223 | 1.9473 | 132.3578 | -151.2153 | 149.8172 | 133.6988 | -151.1585 | 149.8533
Line_2 | 0.0027983 | 0.0027983 | 0.0027983 | 0.0083931 | 0.0083931 | 0.0083931 | 0.032312 | 0.032312 | 0.032312 | 0.096916 | 0.096916 | 0.096916 | 0.00076213 | -0.031154 | 0.030392 | -0.0021135 | 0.093531 | -0.091071 | 0.00072784 | 0.053726 | 0.055148 | -0.0021129 | -0.16112 | -0.16529 | 88.6764 | 88.6764 | 88.6764 | -91.2933 | -91.2933 | -91.2933 |  | 0.032615 | 1.922 | 1.9487 | 0.030836 | 1.9223 | 1.9473 | 132.3578 | -151.2153 | 149.8172 | 133.6988 | -151.1585 | 149.8533
Line_3 | 0.0027983 | 0.0027983 | 0.0027983 | 0.0027983 | 0.0027983 | 0.0027983 | 0.032312 | 0.032312 | 0.032312 | 0.032312 | 0.032312 | 0.032312 | -0.00076213 | 0.031154 | -0.030392 | -0.00076213 | 0.031154 | -0.030392 | -0.00072784 | -0.053726 | -0.055148 | -0.00072784 | -0.053726 | -0.055148 | -91.3236 | -91.3236 | -91.3236 | -91.3236 | -91.3236 | -91.3236 |  | 0.032615 | 1.922 | 1.9487 | 0.032615 | 1.922 | 1.9487 | 132.3578 | -151.2153 | 149.8172 | 132.3578 | -151.2153 | 149.8172

## LG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.027977 | 0.022378 | 0.022378 | 0.033569 | 0.016786 | 0.016786 | 0.32305 | 0.2584 | 0.2584 | 0.38762 | 0.19383 | 0.19383 | 0.0072402 | 0.24965 | -0.24255 | -0.0084512 | -0.18706 | 0.18214 | 0.0074852 | -0.42938 | -0.44031 | -0.0084523 | 0.32225 | 0.33058 | 88.6758 | -91.2725 | -91.2725 | -91.3052 | 88.7067 | 88.7067 |  | 0.032236 | 1.9221 | 1.9454 | 0.030836 | 1.9223 | 1.9473 | 134.6289 | -151.0977 | 149.8786 | 133.6988 | -151.1585 | 149.8533
Line_1 | 0.0027983 | 0.0027983 | 0.0027983 | 0.0083931 | 0.0083931 | 0.0083931 | 0.032312 | 0.032312 | 0.032312 | 0.096916 | 0.096916 | 0.096916 | 0.00076213 | -0.031154 | 0.030392 | -0.0021135 | 0.093531 | -0.091071 | 0.00072784 | 0.053726 | 0.055148 | -0.0021129 | -0.16112 | -0.16529 | 88.6764 | 88.6764 | 88.6764 | -91.2933 | -91.2933 | -91.2933 |  | 0.032615 | 1.922 | 1.9487 | 0.030836 | 1.9223 | 1.9473 | 132.3578 | -151.2153 | 149.8172 | 133.6988 | -151.1585 | 149.8533
Line_2 | 0.0027983 | 0.0027983 | 0.0027983 | 0.0083931 | 0.0083931 | 0.0083931 | 0.032312 | 0.032312 | 0.032312 | 0.096916 | 0.096916 | 0.096916 | 0.00076213 | -0.031154 | 0.030392 | -0.0021135 | 0.093531 | -0.091071 | 0.00072784 | 0.053726 | 0.055148 | -0.0021129 | -0.16112 | -0.16529 | 88.6764 | 88.6764 | 88.6764 | -91.2933 | -91.2933 | -91.2933 |  | 0.032615 | 1.922 | 1.9487 | 0.030836 | 1.9223 | 1.9473 | 132.3578 | -151.2153 | 149.8172 | 133.6988 | -151.1585 | 149.8533
Line_3 | 0.0027983 | 0.0027983 | 0.0027983 | 0.0027983 | 0.0027983 | 0.0027983 | 0.032312 | 0.032312 | 0.032312 | 0.032312 | 0.032312 | 0.032312 | -0.00076213 | 0.031154 | -0.030392 | -0.00076213 | 0.031154 | -0.030392 | -0.00072784 | -0.053726 | -0.055148 | -0.00072784 | -0.053726 | -0.055148 | -91.3236 | -91.3236 | -91.3236 | -91.3236 | -91.3236 | -91.3236 |  | 0.032615 | 1.922 | 1.9487 | 0.032615 | 1.922 | 1.9487 | 132.3578 | -151.2153 | 149.8172 | 132.3578 | -151.2153 | 149.8172

## LG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.024952 | 0.019959 | 0.019959 | 0.02994 | 0.014971 | 0.014971 | 0.28812 | 0.23047 | 0.23047 | 0.34572 | 0.17287 | 0.17287 | 0.00030428 | 0.2007 | -0.19847 | 1.204e-14 | -0.15024 | 0.14918 | 0.00034779 | -0.34729 | -0.34899 | -2.7878e-14 | 0.26059 | 0.26207 | 89.6584 | -90.2428 | -90.2428 | -90.3051 | 89.7172 | 89.7172 |  | 0.0016039 | 1.7405 | 1.742 | 0 | 1.74 | 1.7444 | 138.4758 | -150.2189 | 150.1298 | 0 | -150.3174 | 150.0667
Line_1 | 0.0024958 | 0.0024958 | 0.0024958 | 0.0074857 | 0.0074857 | 0.0074857 | 0.028819 | 0.028819 | 0.028819 | 0.086437 | 0.086437 | 0.086437 | 8.8379e-05 | -0.025001 | 0.024913 | 3.0077e-15 | 0.075121 | -0.074591 | 1.8313e-05 | 0.043434 | 0.043731 | -6.9715e-15 | -0.1303 | -0.13103 | 89.6592 | 89.6592 | 89.6592 | -90.2828 | -90.2828 | -90.2828 |  | 0.0031319 | 1.739 | 1.7464 | 0 | 1.74 | 1.7444 | 101.3655 | -150.4154 | 149.9895 | 0 | -150.3174 | 150.0667
Line_2 | 0.0024958 | 0.0024958 | 0.0024958 | 0.0074857 | 0.0074857 | 0.0074857 | 0.028819 | 0.028819 | 0.028819 | 0.086437 | 0.086437 | 0.086437 | 8.8379e-05 | -0.025001 | 0.024913 | 3.0077e-15 | 0.075121 | -0.074591 | 1.8313e-05 | 0.043434 | 0.043731 | -6.9715e-15 | -0.1303 | -0.13103 | 89.6592 | 89.6592 | 89.6592 | -90.2828 | -90.2828 | -90.2828 |  | 0.0031319 | 1.739 | 1.7464 | 0 | 1.74 | 1.7444 | 101.3655 | -150.4154 | 149.9895 | 0 | -150.3174 | 150.0667
Line_3 | 0.0024958 | 0.0024958 | 0.0024958 | 0.0024958 | 0.0024958 | 0.0024958 | 0.028819 | 0.028819 | 0.028819 | 0.028819 | 0.028819 | 0.028819 | -8.8379e-05 | 0.025001 | -0.024913 | -8.8379e-05 | 0.025001 | -0.024913 | -1.8313e-05 | -0.043434 | -0.043731 | -1.8313e-05 | -0.043434 | -0.043731 | -90.3408 | -90.3408 | -90.3408 | -90.3408 | -90.3408 | -90.3408 |  | 0.0031319 | 1.739 | 1.7464 | 0.0031319 | 1.739 | 1.7464 | 101.3655 | -150.4154 | 149.9895 | 101.3655 | -150.4154 | 149.9895

## LG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.024952 | 0.019959 | 0.019959 | 0.02994 | 0.014971 | 0.014971 | 0.28812 | 0.23047 | 0.23047 | 0.34572 | 0.17287 | 0.17287 | 0.00030428 | 0.2007 | -0.19847 | 1.204e-14 | -0.15024 | 0.14918 | 0.00034779 | -0.34729 | -0.34899 | -2.7878e-14 | 0.26059 | 0.26207 | 89.6584 | -90.2428 | -90.2428 | -90.3051 | 89.7172 | 89.7172 |  | 0.0016039 | 1.7405 | 1.742 | 0 | 1.74 | 1.7444 | 138.4758 | -150.2189 | 150.1298 | 0 | -150.3174 | 150.0667
Line_1 | 0.0024958 | 0.0024958 | 0.0024958 | 0.0074857 | 0.0074857 | 0.0074857 | 0.028819 | 0.028819 | 0.028819 | 0.086437 | 0.086437 | 0.086437 | 8.8379e-05 | -0.025001 | 0.024913 | 3.0077e-15 | 0.075121 | -0.074591 | 1.8313e-05 | 0.043434 | 0.043731 | -6.9715e-15 | -0.1303 | -0.13103 | 89.6592 | 89.6592 | 89.6592 | -90.2828 | -90.2828 | -90.2828 |  | 0.0031319 | 1.739 | 1.7464 | 0 | 1.74 | 1.7444 | 101.3655 | -150.4154 | 149.9895 | 0 | -150.3174 | 150.0667
Line_2 | 0.0024958 | 0.0024958 | 0.0024958 | 0.0074857 | 0.0074857 | 0.0074857 | 0.028819 | 0.028819 | 0.028819 | 0.086437 | 0.086437 | 0.086437 | 8.8379e-05 | -0.025001 | 0.024913 | 3.0077e-15 | 0.075121 | -0.074591 | 1.8313e-05 | 0.043434 | 0.043731 | -6.9715e-15 | -0.1303 | -0.13103 | 89.6592 | 89.6592 | 89.6592 | -90.2828 | -90.2828 | -90.2828 |  | 0.0031319 | 1.739 | 1.7464 | 0 | 1.74 | 1.7444 | 101.3655 | -150.4154 | 149.9895 | 0 | -150.3174 | 150.0667
Line_3 | 0.0024958 | 0.0024958 | 0.0024958 | 0.0024958 | 0.0024958 | 0.0024958 | 0.028819 | 0.028819 | 0.028819 | 0.028819 | 0.028819 | 0.028819 | -8.8379e-05 | 0.025001 | -0.024913 | -8.8379e-05 | 0.025001 | -0.024913 | -1.8313e-05 | -0.043434 | -0.043731 | -1.8313e-05 | -0.043434 | -0.043731 | -90.3408 | -90.3408 | -90.3408 | -90.3408 | -90.3408 | -90.3408 |  | 0.0031319 | 1.739 | 1.7464 | 0.0031319 | 1.739 | 1.7464 | 101.3655 | -150.4154 | 149.9895 | 101.3655 | -150.4154 | 149.9895

## LG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.025439 | 0.020349 | 0.020349 | 0.030524 | 0.015264 | 0.015264 | 0.29375 | 0.23497 | 0.23497 | 0.35247 | 0.17625 | 0.17625 | 0.0061359 | 0.20692 | -0.19994 | -0.0069874 | -0.15489 | 0.15029 | 0.0061901 | -0.35462 | -0.36446 | -0.0069892 | 0.26609 | 0.27368 | 88.5165 | -91.3848 | -91.3848 | -91.4471 | 88.5753 | 88.5753 |  | 0.029671 | 1.7474 | 1.7692 | 0.028039 | 1.7469 | 1.7715 | 133.7682 | -151.1217 | 149.8667 | 133.5604 | -151.2217 | 149.8022
Line_1 | 0.0025445 | 0.0025445 | 0.0025445 | 0.0076319 | 0.0076319 | 0.0076319 | 0.029381 | 0.029381 | 0.029381 | 0.088125 | 0.088125 | 0.088125 | 0.00067396 | -0.025773 | 0.025099 | -0.0017477 | 0.077444 | -0.075146 | 0.00060201 | 0.044351 | 0.045668 | -0.0017468 | -0.13305 | -0.13684 | 88.5172 | 88.5172 | 88.5172 | -91.4247 | -91.4247 | -91.4247 |  | 0.030757 | 1.7459 | 1.7736 | 0.028039 | 1.7469 | 1.7715 | 130.2897 | -151.321 | 149.7237 | 133.5604 | -151.2217 | 149.8022
Line_2 | 0.0025445 | 0.0025445 | 0.0025445 | 0.0076319 | 0.0076319 | 0.0076319 | 0.029381 | 0.029381 | 0.029381 | 0.088125 | 0.088125 | 0.088125 | 0.00067396 | -0.025773 | 0.025099 | -0.0017477 | 0.077444 | -0.075146 | 0.00060201 | 0.044351 | 0.045668 | -0.0017468 | -0.13305 | -0.13684 | 88.5172 | 88.5172 | 88.5172 | -91.4247 | -91.4247 | -91.4247 |  | 0.030757 | 1.7459 | 1.7736 | 0.028039 | 1.7469 | 1.7715 | 130.2897 | -151.321 | 149.7237 | 133.5604 | -151.2217 | 149.8022
Line_3 | 0.0025445 | 0.0025445 | 0.0025445 | 0.0025445 | 0.0025445 | 0.0025445 | 0.029381 | 0.029381 | 0.029381 | 0.029381 | 0.029381 | 0.029381 | -0.00067396 | 0.025773 | -0.025099 | -0.00067396 | 0.025773 | -0.025099 | -0.00060201 | -0.044351 | -0.045668 | -0.00060201 | -0.044351 | -0.045668 | -91.4828 | -91.4828 | -91.4828 | -91.4828 | -91.4828 | -91.4828 |  | 0.030757 | 1.7459 | 1.7736 | 0.030757 | 1.7459 | 1.7736 | 130.2897 | -151.321 | 149.7237 | 130.2897 | -151.321 | 149.7237

## LG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.025439 | 0.020349 | 0.020349 | 0.030524 | 0.015264 | 0.015264 | 0.29375 | 0.23497 | 0.23497 | 0.35247 | 0.17625 | 0.17625 | 0.0061359 | 0.20692 | -0.19994 | -0.0069874 | -0.15489 | 0.15029 | 0.0061901 | -0.35462 | -0.36446 | -0.0069892 | 0.26609 | 0.27368 | 88.5165 | -91.3848 | -91.3848 | -91.4471 | 88.5753 | 88.5753 |  | 0.029671 | 1.7474 | 1.7692 | 0.028039 | 1.7469 | 1.7715 | 133.7682 | -151.1217 | 149.8667 | 133.5604 | -151.2217 | 149.8022
Line_1 | 0.0025445 | 0.0025445 | 0.0025445 | 0.0076319 | 0.0076319 | 0.0076319 | 0.029381 | 0.029381 | 0.029381 | 0.088125 | 0.088125 | 0.088125 | 0.00067396 | -0.025773 | 0.025099 | -0.0017477 | 0.077444 | -0.075146 | 0.00060201 | 0.044351 | 0.045668 | -0.0017468 | -0.13305 | -0.13684 | 88.5172 | 88.5172 | 88.5172 | -91.4247 | -91.4247 | -91.4247 |  | 0.030757 | 1.7459 | 1.7736 | 0.028039 | 1.7469 | 1.7715 | 130.2897 | -151.321 | 149.7237 | 133.5604 | -151.2217 | 149.8022
Line_2 | 0.0025445 | 0.0025445 | 0.0025445 | 0.0076319 | 0.0076319 | 0.0076319 | 0.029381 | 0.029381 | 0.029381 | 0.088125 | 0.088125 | 0.088125 | 0.00067396 | -0.025773 | 0.025099 | -0.0017477 | 0.077444 | -0.075146 | 0.00060201 | 0.044351 | 0.045668 | -0.0017468 | -0.13305 | -0.13684 | 88.5172 | 88.5172 | 88.5172 | -91.4247 | -91.4247 | -91.4247 |  | 0.030757 | 1.7459 | 1.7736 | 0.028039 | 1.7469 | 1.7715 | 130.2897 | -151.321 | 149.7237 | 133.5604 | -151.2217 | 149.8022
Line_3 | 0.0025445 | 0.0025445 | 0.0025445 | 0.0025445 | 0.0025445 | 0.0025445 | 0.029381 | 0.029381 | 0.029381 | 0.029381 | 0.029381 | 0.029381 | -0.00067396 | 0.025773 | -0.025099 | -0.00067396 | 0.025773 | -0.025099 | -0.00060201 | -0.044351 | -0.045668 | -0.00060201 | -0.044351 | -0.045668 | -91.4828 | -91.4828 | -91.4828 | -91.4828 | -91.4828 | -91.4828 |  | 0.030757 | 1.7459 | 1.7736 | 0.030757 | 1.7459 | 1.7736 | 130.2897 | -151.321 | 149.7237 | 130.2897 | -151.321 | 149.7237

## LLG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.010913 | 3.7095 | 3.7089 | 0.0081859 | 3.71 | 3.7083 | 0.12601 | 42.8331 | 42.8262 | 0.094523 | 42.8397 | 42.8196 | 0.00024599 | 7.1538 | 7.1543 | -0.00016515 | 7.7694e-11 | 4.5805e-11 | -0.20823 | 8.105 | 8.1293 | 0.15625 | -3.1001e-11 | 3.5396e-11 | 89.9369 | -167.7593 | 12.1996 | -90.0839 | 12.2819 | -167.8416 |  | 1.6525 | 0.25239 | 0.25286 | 1.6531 | 0 | 0 | 0.0046253 | -119.1923 | 60.8495 | -0.023306 | 0 | 0
Line_1 | 0.0013646 | 0.0013646 | 0.0013646 | 0.004093 | 0.004093 | 0.004093 | 0.015757 | 0.015757 | 0.015757 | 0.047262 | 0.047262 | 0.047262 | -2.7526e-05 | 1.3761e-05 | 1.3761e-05 | 8.2572e-05 | -1.5052e-14 | -4.89e-14 | 0.026053 | 5.4748e-06 | 5.4748e-06 | -0.078127 | -9.1049e-14 | 4.1123e-14 | -90.1141 | -90.1141 | -90.1141 | 89.9161 | 89.9161 | 89.9161 |  | 1.6534 | 0.00093992 | 0.00093992 | 1.6531 | 0 | 0 | -0.053588 | -68.4197 | -68.4197 | -0.023306 | 0 | 0
Line_2 | 0.0013646 | 0.0013646 | 0.0013646 | 0.004093 | 0.004093 | 0.004093 | 0.015757 | 0.015757 | 0.015757 | 0.047262 | 0.047262 | 0.047262 | -2.7526e-05 | 1.3761e-05 | 1.3761e-05 | 8.2572e-05 | -1.5052e-14 | -4.89e-14 | 0.026053 | 5.4748e-06 | 5.4748e-06 | -0.078127 | -9.1049e-14 | 4.1123e-14 | -90.1141 | -90.1141 | -90.1141 | 89.9161 | 89.9161 | 89.9161 |  | 1.6534 | 0.00093992 | 0.00093992 | 1.6531 | 0 | 0 | -0.053588 | -68.4197 | -68.4197 | -0.023306 | 0 | 0
Line_3 | 0.0013646 | 0.0013646 | 0.0013646 | 0.0013646 | 0.0013646 | 0.0013646 | 0.015757 | 0.015757 | 0.015757 | 0.015757 | 0.015757 | 0.015757 | 2.7523e-05 | -1.3761e-05 | -1.3761e-05 | 2.7523e-05 | -1.3761e-05 | -1.3761e-05 | -0.026053 | -5.4748e-06 | -5.4748e-06 | -0.026053 | -5.4748e-06 | -5.4748e-06 | 89.8859 | 89.8859 | 89.8859 | 89.8859 | 89.8859 | 89.8859 |  | 1.6534 | 0.00093992 | 0.00093992 | 1.6534 | 0.00093992 | 0.00093992 | -0.053588 | -68.4197 | -68.4197 | -0.053588 | -68.4197 | -68.4197

## LLG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.010913 | 3.7095 | 3.7089 | 0.0081859 | 3.71 | 3.7083 | 0.12601 | 42.8331 | 42.8262 | 0.094523 | 42.8397 | 42.8196 | 0.00024599 | 7.1538 | 7.1543 | -0.00016515 | 7.7694e-11 | 4.5805e-11 | -0.20823 | 8.105 | 8.1293 | 0.15625 | -3.1001e-11 | 3.5396e-11 | 89.9369 | -167.7593 | 12.1996 | -90.0839 | 12.2819 | -167.8416 |  | 1.6525 | 0.25239 | 0.25286 | 1.6531 | 0 | 0 | 0.0046253 | -119.1923 | 60.8495 | -0.023306 | 0 | 0
Line_1 | 0.0013646 | 0.0013646 | 0.0013646 | 0.004093 | 0.004093 | 0.004093 | 0.015757 | 0.015757 | 0.015757 | 0.047262 | 0.047262 | 0.047262 | -2.7526e-05 | 1.3761e-05 | 1.3761e-05 | 8.2572e-05 | -1.5052e-14 | -4.89e-14 | 0.026053 | 5.4748e-06 | 5.4748e-06 | -0.078127 | -9.1049e-14 | 4.1123e-14 | -90.1141 | -90.1141 | -90.1141 | 89.9161 | 89.9161 | 89.9161 |  | 1.6534 | 0.00093992 | 0.00093992 | 1.6531 | 0 | 0 | -0.053588 | -68.4197 | -68.4197 | -0.023306 | 0 | 0
Line_2 | 0.0013646 | 0.0013646 | 0.0013646 | 0.004093 | 0.004093 | 0.004093 | 0.015757 | 0.015757 | 0.015757 | 0.047262 | 0.047262 | 0.047262 | -2.7526e-05 | 1.3761e-05 | 1.3761e-05 | 8.2572e-05 | -1.5052e-14 | -4.89e-14 | 0.026053 | 5.4748e-06 | 5.4748e-06 | -0.078127 | -9.1049e-14 | 4.1123e-14 | -90.1141 | -90.1141 | -90.1141 | 89.9161 | 89.9161 | 89.9161 |  | 1.6534 | 0.00093992 | 0.00093992 | 1.6531 | 0 | 0 | -0.053588 | -68.4197 | -68.4197 | -0.023306 | 0 | 0
Line_3 | 0.0013646 | 0.0013646 | 0.0013646 | 0.0013646 | 0.0013646 | 0.0013646 | 0.015757 | 0.015757 | 0.015757 | 0.015757 | 0.015757 | 0.015757 | 2.7523e-05 | -1.3761e-05 | -1.3761e-05 | 2.7523e-05 | -1.3761e-05 | -1.3761e-05 | -0.026053 | -5.4748e-06 | -5.4748e-06 | -0.026053 | -5.4748e-06 | -5.4748e-06 | 89.8859 | 89.8859 | 89.8859 | 89.8859 | 89.8859 | 89.8859 |  | 1.6534 | 0.00093992 | 0.00093992 | 1.6534 | 0.00093992 | 0.00093992 | -0.053588 | -68.4197 | -68.4197 | -0.053588 | -68.4197 | -68.4197

## LLG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.011019 | 1.135 | 1.1334 | 0.0082653 | 1.1367 | 1.1318 | 0.12723 | 13.1063 | 13.0874 | 0.09544 | 13.1251 | 13.0688 | 0.0016175 | 7.0958 | 7.1069 | -0.0011932 | -6.4499 | -6.4151 | -0.21093 | 7.2854 | 7.0973 | 0.15827 | -6.5257 | -6.3394 | 89.3768 | -144.4736 | 35.4142 | -90.644 | 35.6385 | -144.6986 |  | 1.6578 | 0.77596 | 0.76745 | 1.6584 | 0.69907 | 0.69012 | -0.18382 | -98.7182 | 80.3759 | -0.21206 | -99.0271 | 79.9612
Line_1 | 0.0013778 | 0.0013778 | 0.0013778 | 0.0041327 | 0.0041327 | 0.0041327 | 0.01591 | 0.01591 | 0.01591 | 0.04772 | 0.04772 | 0.04772 | -0.00019881 | 0.011018 | -0.010819 | 0.00059658 | -0.033003 | 0.032491 | 0.02639 | -0.0016101 | 0.0017922 | -0.079137 | 0.0048635 | -0.0053758 | -90.6742 | -90.6742 | -90.6742 | 89.356 | 89.356 | 89.356 |  | 1.6588 | 0.69989 | 0.68931 | 1.6584 | 0.69907 | 0.69012 | -0.24262 | -98.9882 | 79.9205 | -0.21206 | -99.0271 | 79.9612
Line_2 | 0.0013778 | 0.0013778 | 0.0013778 | 0.0041327 | 0.0041327 | 0.0041327 | 0.01591 | 0.01591 | 0.01591 | 0.04772 | 0.04772 | 0.04772 | -0.00019881 | 0.011018 | -0.010819 | 0.00059658 | -0.033003 | 0.032491 | 0.02639 | -0.0016101 | 0.0017922 | -0.079137 | 0.0048635 | -0.0053758 | -90.6742 | -90.6742 | -90.6742 | 89.356 | 89.356 | 89.356 |  | 1.6588 | 0.69989 | 0.68931 | 1.6584 | 0.69907 | 0.69012 | -0.24262 | -98.9882 | 79.9205 | -0.21206 | -99.0271 | 79.9612
Line_3 | 0.0013778 | 0.0013778 | 0.0013778 | 0.0013778 | 0.0013778 | 0.0013778 | 0.01591 | 0.01591 | 0.01591 | 0.01591 | 0.01591 | 0.01591 | 0.0001988 | -0.011018 | 0.010819 | 0.0001988 | -0.011018 | 0.010819 | -0.02639 | 0.0016101 | -0.0017922 | -0.02639 | 0.0016101 | -0.0017922 | 89.3258 | 89.3258 | 89.3258 | 89.3258 | 89.3258 | 89.3258 |  | 1.6588 | 0.69989 | 0.68931 | 1.6588 | 0.69989 | 0.68931 | -0.24262 | -98.9882 | 79.9205 | -0.24262 | -98.9882 | 79.9205

## LLG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.011019 | 1.135 | 1.1334 | 0.0082653 | 1.1367 | 1.1318 | 0.12723 | 13.1063 | 13.0874 | 0.09544 | 13.1251 | 13.0688 | 0.0016175 | 7.0958 | 7.1069 | -0.0011932 | -6.4499 | -6.4151 | -0.21093 | 7.2854 | 7.0973 | 0.15827 | -6.5257 | -6.3394 | 89.3768 | -144.4736 | 35.4142 | -90.644 | 35.6385 | -144.6986 |  | 1.6578 | 0.77596 | 0.76745 | 1.6584 | 0.69907 | 0.69012 | -0.18382 | -98.7182 | 80.3759 | -0.21206 | -99.0271 | 79.9612
Line_1 | 0.0013778 | 0.0013778 | 0.0013778 | 0.0041327 | 0.0041327 | 0.0041327 | 0.01591 | 0.01591 | 0.01591 | 0.04772 | 0.04772 | 0.04772 | -0.00019881 | 0.011018 | -0.010819 | 0.00059658 | -0.033003 | 0.032491 | 0.02639 | -0.0016101 | 0.0017922 | -0.079137 | 0.0048635 | -0.0053758 | -90.6742 | -90.6742 | -90.6742 | 89.356 | 89.356 | 89.356 |  | 1.6588 | 0.69989 | 0.68931 | 1.6584 | 0.69907 | 0.69012 | -0.24262 | -98.9882 | 79.9205 | -0.21206 | -99.0271 | 79.9612
Line_2 | 0.0013778 | 0.0013778 | 0.0013778 | 0.0041327 | 0.0041327 | 0.0041327 | 0.01591 | 0.01591 | 0.01591 | 0.04772 | 0.04772 | 0.04772 | -0.00019881 | 0.011018 | -0.010819 | 0.00059658 | -0.033003 | 0.032491 | 0.02639 | -0.0016101 | 0.0017922 | -0.079137 | 0.0048635 | -0.0053758 | -90.6742 | -90.6742 | -90.6742 | 89.356 | 89.356 | 89.356 |  | 1.6588 | 0.69989 | 0.68931 | 1.6584 | 0.69907 | 0.69012 | -0.24262 | -98.9882 | 79.9205 | -0.21206 | -99.0271 | 79.9612
Line_3 | 0.0013778 | 0.0013778 | 0.0013778 | 0.0013778 | 0.0013778 | 0.0013778 | 0.01591 | 0.01591 | 0.01591 | 0.01591 | 0.01591 | 0.01591 | 0.0001988 | -0.011018 | 0.010819 | 0.0001988 | -0.011018 | 0.010819 | -0.02639 | 0.0016101 | -0.0017922 | -0.02639 | 0.0016101 | -0.0017922 | 89.3258 | 89.3258 | 89.3258 | 89.3258 | 89.3258 | 89.3258 |  | 1.6588 | 0.69989 | 0.68931 | 1.6588 | 0.69989 | 0.68931 | -0.24262 | -98.9882 | 79.9205 | -0.24262 | -98.9882 | 79.9205

## LLG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.0099216 | 3.1195 | 3.1186 | 0.0074423 | 3.1204 | 3.1178 | 0.11456 | 36.0212 | 36.011 | 0.085936 | 36.0312 | 36.0011 | 0.00039037 | 9.7101 | 9.7161 | -0.00026208 | -1.322e-10 | 4.6152e-11 | -0.17212 | 5.7227 | 5.7572 | 0.12915 | -1.3386e-10 | -1.7998e-10 | 89.8823 | -159.651 | 20.3064 | -90.1576 | 20.3917 | -159.7363 |  | 1.5024 | 0.3129 | 0.31362 | 1.5029 | 0 | 0 | 0.012245 | -129.138 | 50.9548 | -0.04138 | 0 | 0
Line_1 | 0.0012406 | 0.0012406 | 0.0012406 | 0.0037211 | 0.0037211 | 0.0037211 | 0.014326 | 0.014326 | 0.014326 | 0.042968 | 0.042968 | 0.042968 | -4.3681e-05 | 2.1839e-05 | 2.1839e-05 | 0.00013104 | -2.0481e-13 | 1.8209e-13 | 0.021534 | 4.5252e-06 | 4.5252e-06 | -0.064576 | 9.1591e-14 | 1.2657e-13 | -90.2157 | -90.2157 | -90.2157 | 89.8424 | 89.8424 | 89.8424 |  | 1.5032 | 0.0015569 | 0.0015569 | 1.5029 | 0 | 0 | -0.099523 | -78.5094 | -78.5094 | -0.04138 | 0 | 0
Line_2 | 0.0012406 | 0.0012406 | 0.0012406 | 0.0037211 | 0.0037211 | 0.0037211 | 0.014326 | 0.014326 | 0.014326 | 0.042968 | 0.042968 | 0.042968 | -4.3681e-05 | 2.1839e-05 | 2.1839e-05 | 0.00013104 | -2.0481e-13 | 1.8209e-13 | 0.021534 | 4.5252e-06 | 4.5252e-06 | -0.064576 | 9.1591e-14 | 1.2657e-13 | -90.2157 | -90.2157 | -90.2157 | 89.8424 | 89.8424 | 89.8424 |  | 1.5032 | 0.0015569 | 0.0015569 | 1.5029 | 0 | 0 | -0.099523 | -78.5094 | -78.5094 | -0.04138 | 0 | 0
Line_3 | 0.0012406 | 0.0012406 | 0.0012406 | 0.0012406 | 0.0012406 | 0.0012406 | 0.014326 | 0.014326 | 0.014326 | 0.014326 | 0.014326 | 0.014326 | 4.3678e-05 | -2.1839e-05 | -2.1839e-05 | 4.3678e-05 | -2.1839e-05 | -2.1839e-05 | -0.021534 | -4.5252e-06 | -4.5252e-06 | -0.021534 | -4.5252e-06 | -4.5252e-06 | 89.7843 | 89.7843 | 89.7843 | 89.7843 | 89.7843 | 89.7843 |  | 1.5032 | 0.0015569 | 0.0015569 | 1.5032 | 0.0015569 | 0.0015569 | -0.099523 | -78.5094 | -78.5094 | -0.099523 | -78.5094 | -78.5094

## LLG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.0099216 | 3.1195 | 3.1186 | 0.0074423 | 3.1204 | 3.1178 | 0.11456 | 36.0212 | 36.011 | 0.085936 | 36.0312 | 36.0011 | 0.00039037 | 9.7101 | 9.7161 | -0.00026208 | -1.322e-10 | 4.6152e-11 | -0.17212 | 5.7227 | 5.7572 | 0.12915 | -1.3386e-10 | -1.7998e-10 | 89.8823 | -159.651 | 20.3064 | -90.1576 | 20.3917 | -159.7363 |  | 1.5024 | 0.3129 | 0.31362 | 1.5029 | 0 | 0 | 0.012245 | -129.138 | 50.9548 | -0.04138 | 0 | 0
Line_1 | 0.0012406 | 0.0012406 | 0.0012406 | 0.0037211 | 0.0037211 | 0.0037211 | 0.014326 | 0.014326 | 0.014326 | 0.042968 | 0.042968 | 0.042968 | -4.3681e-05 | 2.1839e-05 | 2.1839e-05 | 0.00013104 | -2.0481e-13 | 1.8209e-13 | 0.021534 | 4.5252e-06 | 4.5252e-06 | -0.064576 | 9.1591e-14 | 1.2657e-13 | -90.2157 | -90.2157 | -90.2157 | 89.8424 | 89.8424 | 89.8424 |  | 1.5032 | 0.0015569 | 0.0015569 | 1.5029 | 0 | 0 | -0.099523 | -78.5094 | -78.5094 | -0.04138 | 0 | 0
Line_2 | 0.0012406 | 0.0012406 | 0.0012406 | 0.0037211 | 0.0037211 | 0.0037211 | 0.014326 | 0.014326 | 0.014326 | 0.042968 | 0.042968 | 0.042968 | -4.3681e-05 | 2.1839e-05 | 2.1839e-05 | 0.00013104 | -2.0481e-13 | 1.8209e-13 | 0.021534 | 4.5252e-06 | 4.5252e-06 | -0.064576 | 9.1591e-14 | 1.2657e-13 | -90.2157 | -90.2157 | -90.2157 | 89.8424 | 89.8424 | 89.8424 |  | 1.5032 | 0.0015569 | 0.0015569 | 1.5029 | 0 | 0 | -0.099523 | -78.5094 | -78.5094 | -0.04138 | 0 | 0
Line_3 | 0.0012406 | 0.0012406 | 0.0012406 | 0.0012406 | 0.0012406 | 0.0012406 | 0.014326 | 0.014326 | 0.014326 | 0.014326 | 0.014326 | 0.014326 | 4.3678e-05 | -2.1839e-05 | -2.1839e-05 | 4.3678e-05 | -2.1839e-05 | -2.1839e-05 | -0.021534 | -4.5252e-06 | -4.5252e-06 | -0.021534 | -4.5252e-06 | -4.5252e-06 | 89.7843 | 89.7843 | 89.7843 | 89.7843 | 89.7843 | 89.7843 |  | 1.5032 | 0.0015569 | 0.0015569 | 1.5032 | 0.0015569 | 0.0015569 | -0.099523 | -78.5094 | -78.5094 | -0.099523 | -78.5094 | -78.5094

## LLG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.010018 | 0.99346 | 0.9919 | 0.0075143 | 0.995 | 0.99036 | 0.11567 | 11.4715 | 11.4535 | 0.086768 | 11.4893 | 11.4357 | 0.0015281 | 5.9081 | 5.9138 | -0.0011143 | -4.9439 | -4.9106 | -0.17434 | 5.5818 | 5.4353 | 0.13082 | -5.0027 | -4.8519 | 89.3214 | -142.5778 | 37.309 | -90.7186 | 37.5358 | -142.8053 |  | 1.5072 | 0.70853 | 0.70128 | 1.5078 | 0.61217 | 0.60366 | -0.17645 | -99.2049 | 79.8948 | -0.23055 | -97.126 | 81.8501
Line_1 | 0.0012526 | 0.0012526 | 0.0012526 | 0.0037572 | 0.0037572 | 0.0037572 | 0.014464 | 0.014464 | 0.014464 | 0.043384 | 0.043384 | 0.043384 | -0.00018561 | 0.0088226 | -0.008637 | 0.00055716 | -0.026393 | 0.025969 | 0.021812 | -0.00097462 | 0.0011251 | -0.06541 | 0.0029639 | -0.0033872 | -90.7767 | -90.7767 | -90.7767 | 89.2814 | 89.2814 | 89.2814 |  | 1.5081 | 0.61367 | 0.60217 | 1.5078 | 0.61217 | 0.60366 | -0.28915 | -97.0805 | 81.8012 | -0.23055 | -97.126 | 81.8501
Line_2 | 0.0012526 | 0.0012526 | 0.0012526 | 0.0037572 | 0.0037572 | 0.0037572 | 0.014464 | 0.014464 | 0.014464 | 0.043384 | 0.043384 | 0.043384 | -0.00018561 | 0.0088226 | -0.008637 | 0.00055716 | -0.026393 | 0.025969 | 0.021812 | -0.00097462 | 0.0011251 | -0.06541 | 0.0029639 | -0.0033872 | -90.7767 | -90.7767 | -90.7767 | 89.2814 | 89.2814 | 89.2814 |  | 1.5081 | 0.61367 | 0.60217 | 1.5078 | 0.61217 | 0.60366 | -0.28915 | -97.0805 | 81.8012 | -0.23055 | -97.126 | 81.8501
Line_3 | 0.0012526 | 0.0012526 | 0.0012526 | 0.0012526 | 0.0012526 | 0.0012526 | 0.014464 | 0.014464 | 0.014464 | 0.014464 | 0.014464 | 0.014464 | 0.0001856 | -0.0088226 | 0.008637 | 0.0001856 | -0.0088226 | 0.008637 | -0.021812 | 0.00097462 | -0.0011251 | -0.021812 | 0.00097462 | -0.0011251 | 89.2233 | 89.2233 | 89.2233 | 89.2233 | 89.2233 | 89.2233 |  | 1.5081 | 0.61367 | 0.60217 | 1.5081 | 0.61367 | 0.60217 | -0.28915 | -97.0805 | 81.8012 | -0.28915 | -97.0805 | 81.8012

## LLG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.010018 | 0.99346 | 0.9919 | 0.0075143 | 0.995 | 0.99036 | 0.11567 | 11.4715 | 11.4535 | 0.086768 | 11.4893 | 11.4357 | 0.0015281 | 5.9081 | 5.9138 | -0.0011143 | -4.9439 | -4.9106 | -0.17434 | 5.5818 | 5.4353 | 0.13082 | -5.0027 | -4.8519 | 89.3214 | -142.5778 | 37.309 | -90.7186 | 37.5358 | -142.8053 |  | 1.5072 | 0.70853 | 0.70128 | 1.5078 | 0.61217 | 0.60366 | -0.17645 | -99.2049 | 79.8948 | -0.23055 | -97.126 | 81.8501
Line_1 | 0.0012526 | 0.0012526 | 0.0012526 | 0.0037572 | 0.0037572 | 0.0037572 | 0.014464 | 0.014464 | 0.014464 | 0.043384 | 0.043384 | 0.043384 | -0.00018561 | 0.0088226 | -0.008637 | 0.00055716 | -0.026393 | 0.025969 | 0.021812 | -0.00097462 | 0.0011251 | -0.06541 | 0.0029639 | -0.0033872 | -90.7767 | -90.7767 | -90.7767 | 89.2814 | 89.2814 | 89.2814 |  | 1.5081 | 0.61367 | 0.60217 | 1.5078 | 0.61217 | 0.60366 | -0.28915 | -97.0805 | 81.8012 | -0.23055 | -97.126 | 81.8501
Line_2 | 0.0012526 | 0.0012526 | 0.0012526 | 0.0037572 | 0.0037572 | 0.0037572 | 0.014464 | 0.014464 | 0.014464 | 0.043384 | 0.043384 | 0.043384 | -0.00018561 | 0.0088226 | -0.008637 | 0.00055716 | -0.026393 | 0.025969 | 0.021812 | -0.00097462 | 0.0011251 | -0.06541 | 0.0029639 | -0.0033872 | -90.7767 | -90.7767 | -90.7767 | 89.2814 | 89.2814 | 89.2814 |  | 1.5081 | 0.61367 | 0.60217 | 1.5078 | 0.61217 | 0.60366 | -0.28915 | -97.0805 | 81.8012 | -0.23055 | -97.126 | 81.8501
Line_3 | 0.0012526 | 0.0012526 | 0.0012526 | 0.0012526 | 0.0012526 | 0.0012526 | 0.014464 | 0.014464 | 0.014464 | 0.014464 | 0.014464 | 0.014464 | 0.0001856 | -0.0088226 | 0.008637 | 0.0001856 | -0.0088226 | 0.008637 | -0.021812 | 0.00097462 | -0.0011251 | -0.021812 | 0.00097462 | -0.0011251 | 89.2233 | 89.2233 | 89.2233 | 89.2233 | 89.2233 | 89.2233 |  | 1.5081 | 0.61367 | 0.60217 | 1.5081 | 0.61367 | 0.60217 | -0.28915 | -97.0805 | 81.8012 | -0.28915 | -97.0805 | 81.8012