## LLL_max
name | pf_ikss_ka | pf_skss_mw | pf_rk_ohm | pf_xk_ohm | pf_vm_pu | pf_va_degree
Bus_0 | 5.2486 | 1000.0001 | 1.3244 | 13.2439 | 0 | 84.2894
Bus_1 | 5.4963 | 190.3978 | 0.10773 | 2.3084 | 0 | 87.328
Bus_2 | 4.283 | 148.3662 | 0.62773 | 2.8984 | 0 | 77.7798
Bus_3 | 3.4587 | 119.8128 | 1.1477 | 3.4884 | 0 | 71.7883
Bus_4 | 3.4587 | 119.8128 | 1.1477 | 3.4884 | 0 | 71.7883

## LLL_max_branch
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_vm_pu
Line_0 | 0 | 4.283 | 0 | 9.2778 | 0 | 148.3662 | 6.297e-19 | -1e-07 | -4.9284e-19 | -1e-07
Line_1 | 3.4587 | 0 | 6.7756 | 0 | 119.8128 | 0 | -1e-07 | 1.6014e-19 | -1e-07 | -1.2512e-19
Line_2 | 3.4587 | 0 | 6.7756 | 0 | 119.8128 | 0 | -1e-07 | 1.6014e-19 | -1e-07 | -1.2512e-19

## LLL_max_fault
name | pf_ikss_ka | pf_skss_mw | pf_rk_ohm | pf_xk_ohm | pf_vm_pu | pf_va_degree
Bus_0 | 3.618 | 689.314 | 1.3244 | 13.2439 | 0.40283 | 45
Bus_1 | 1.4245 | 49.3473 | 0.10773 | 2.3084 | 0.87234 | 45
Bus_2 | 1.3097 | 45.3689 | 0.62773 | 2.8984 | 0.80202 | 45
Bus_3 | 1.2119 | 41.9813 | 1.1477 | 3.4884 | 0.74213 | 45
Bus_4 | 1.2119 | 41.9813 | 1.1477 | 3.4884 | 0.74213 | 45

## LLL_max_fault_branch
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_vm_pu
Line_0 | 0 | 1.3097 | 0 | 2.8371 | 0 | 45.3689 | -6.0676e-09 | -25.7292 | 5.5265e-09 | -25.7292
Line_1 | 1.2119 | 0 | 2.3741 | 0 | 41.9813 | 0 | -22.0304 | -2.495e-09 | -22.0304 | 1.6066e-09
Line_2 | 1.2119 | 0 | 2.3741 | 0 | 41.9813 | 0 | -22.0304 | -2.495e-09 | -22.0304 | 1.6066e-09

## LLL_min
name | pf_ikss_ka | pf_skss_mw | pf_rk_ohm | pf_xk_ohm | pf_vm_pu | pf_va_degree
Bus_0 | 4.1989 | 800 | 1.505 | 15.0499 | 0 | 84.2894
Bus_1 | 4.7732 | 165.3474 | 0.11535 | 2.4164 | 0 | 87.2669
Bus_2 | 3.6016 | 124.7634 | 1.1138 | 3.0064 | 0 | 69.6723
Bus_3 | 2.7686 | 95.9057 | 2.1122 | 3.5964 | 0 | 59.5744
Bus_4 | 2.7686 | 95.9057 | 2.1122 | 3.5964 | 0 | 59.5744

## LLL_min_branch
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_vm_pu
Line_0 | 0 | 3.6016 | 0 | 6.8381 | 0 | 124.7634 | 7.2789e-20 | -1e-07 | 2.6702e-19 | -1e-07
Line_1 | 2.7686 | 0 | 4.6525 | 0 | 95.9057 | 0 | -1e-07 | 1.7283e-20 | -1e-07 | 6.3218e-20
Line_2 | 2.7686 | 0 | 4.6525 | 0 | 95.9057 | 0 | -1e-07 | 1.7283e-20 | -1e-07 | 6.3218e-20

## LLL_min_fault
name | pf_ikss_ka | pf_skss_mw | pf_rk_ohm | pf_xk_ohm | pf_vm_pu | pf_va_degree
Bus_0 | 3.0129 | 574.037 | 1.505 | 15.0499 | 0.33546 | 45
Bus_1 | 1.2817 | 44.3979 | 0.11535 | 2.4164 | 0.78485 | 45
Bus_2 | 1.1462 | 39.7072 | 1.1138 | 3.0064 | 0.70193 | 45
Bus_3 | 1.0349 | 35.8516 | 2.1122 | 3.5964 | 0.63377 | 45
Bus_4 | 1.0349 | 35.8516 | 2.1122 | 3.5964 | 0.63377 | 45

## LLL_min_fault_branch
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_vm_pu
Line_0 | 0 | 1.1462 | 0 | 2.1763 | 0 | 39.7072 | -5.1465e-09 | -19.7082 | 4.6774e-09 | -19.7082
Line_1 | 1.0349 | 0 | 1.7392 | 0 | 35.8516 | 0 | -16.0667 | -2.233e-09 | -16.0667 | 1.0258e-09
Line_2 | 1.0349 | 0 | 1.7392 | 0 | 35.8516 | 0 | -16.0667 | -2.233e-09 | -16.0667 | 1.0258e-09

## LL_max
name | pf_ikss_a_ka | pf_ikss_b_ka | pf_ikss_c_ka | pf_skss_a_mw | pf_skss_b_mw | pf_skss_c_mw | pf_rk0_ohm | pf_xk0_ohm | pf_rk1_ohm | pf_xk1_ohm | pf_rk2_ohm | pf_xk2_ohm | pf_vm_a_pu | pf_vm_b_pu | pf_vm_c_pu | pf_va_a_degree | pf_va_b_degree | pf_va_c_degree
Bus_0 | 0 | 4.5455 | 4.5455 | 0 | 288.6752 | 288.6752 | 1.3244 | 13.2439 | 1.3244 | 13.2439 | 1.3244 | 13.2439 | 0.95263 | 0 | 0.95263 | -8.6929e-11 | 0 | -180
Bus_1 | 0 | 4.7599 | 4.7599 | 0 | 54.9631 | 54.9631 | 0.01229 | 51.6946 | 0.10773 | 2.3084 | 0.10773 | 2.3084 | 0.95263 | 0 | 0.95263 | -4.0142e-12 | 0 | -180
Bus_2 | 0 | 3.7092 | 3.7092 | 0 | 42.8296 | 42.8296 | 4.1304 | 53.3128 | 0.62773 | 2.8984 | 0.62773 | 2.8984 | 0.95263 | 0 | 0.95263 | -1.2485e-11 | 0 | -180
Bus_3 | 0 | 2.9953 | 2.9953 | 0 | 34.587 | 34.587 | 7.9148 | 54.8073 | 1.1477 | 3.4884 | 1.1477 | 3.4884 | 0.95263 | 0 | 0.95263 | -1.4671e-11 | 0 | -180
Bus_4 | 0 | 2.9953 | 2.9953 | 0 | 34.587 | 34.587 | 7.9148 | 54.8073 | 1.1477 | 3.4884 | 1.1477 | 3.4884 | 0.95263 | 0 | 0.95263 | -1.4657e-11 | 0 | -180

## LL_max_branch
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mw | pf_q_b_from_mw | pf_q_c_from_mw | pf_q_a_to_mw | pf_q_b_to_mw | pf_q_c_to_mw
Line_0 | 0 | 0 | 0 | 0 | 3.7092 | 3.7092 | 0 | 0 | 0 | 0 | 42.8296 | 42.8296 | -6.7738e-14 | 5.2106e-15 | -2.0843e-14 | 4.1685e-14 | -23.0225 | 23.0225 | 2.0843e-14 | 5.7634e-09 | -5.7634e-09 | -1.0421e-14 | 4.9861 | -4.9861
Line_1 | 0 | 2.9953 | 2.9953 | 0 | 0 | 0 | 0 | 34.587 | 34.587 | 0 | 0 | 0 | -1.0421e-14 | -18.0699 | 18.0699 | 5.2106e-15 | 1.3027e-14 | -5.2106e-15 | -1.0421e-14 | 5.9452 | -5.9452 | -5.2106e-15 | 1.9211e-09 | -1.9211e-09
Line_2 | 0 | 2.9953 | 2.9953 | 0 | 0 | 0 | 0 | 34.587 | 34.587 | 0 | 0 | 0 | -5.2106e-15 | -18.0699 | 18.0699 | 0 | 1.3027e-14 | -5.2106e-15 | -5.2106e-15 | 5.9452 | -5.9452 | 0 | 1.9211e-09 | -1.9211e-09

## LL_max_fault
name | pf_ikss_a_ka | pf_ikss_b_ka | pf_ikss_c_ka | pf_skss_a_mw | pf_skss_b_mw | pf_skss_c_mw | pf_rk0_ohm | pf_xk0_ohm | pf_rk1_ohm | pf_xk1_ohm | pf_rk2_ohm | pf_xk2_ohm | pf_vm_a_pu | pf_vm_b_pu | pf_vm_c_pu | pf_va_a_degree | pf_va_b_degree | pf_va_c_degree
Bus_0 | 0 | 3.7342 | 3.7342 | 0 | 237.1508 | 237.1508 | 1.3244 | 13.2439 | 1.3244 | 13.2439 | 1.3244 | 13.2439 | 1.0202 | 0.24004 | 0.89607 | 5.7662 | -121.3466 | 173.4316
Bus_1 | 0 | 2.011 | 2.011 | 0 | 23.2205 | 23.2205 | 0.01229 | 51.6946 | 0.10773 | 2.3084 | 0.10773 | 2.3084 | 1.1075 | 0.71098 | 0.91717 | 17.922 | -106.528 | 158.1868
Bus_2 | 0 | 1.7631 | 1.7631 | 0 | 20.3584 | 20.3584 | 4.1304 | 53.3128 | 0.62773 | 2.8984 | 0.62773 | 2.8984 | 1.0759 | 0.62335 | 0.92294 | 16.2567 | -104.913 | 160.9544
Bus_3 | 0 | 1.5688 | 1.5688 | 0 | 18.1144 | 18.1144 | 7.9148 | 54.8073 | 1.1477 | 3.4884 | 1.1477 | 3.4884 | 1.0531 | 0.55464 | 0.92719 | 14.8259 | -103.6532 | 163.1035
Bus_4 | 0 | 1.5688 | 1.5688 | 0 | 18.1144 | 18.1144 | 7.9148 | 54.8073 | 1.1477 | 3.4884 | 1.1477 | 3.4884 | 1.0531 | 0.55464 | 0.92719 | 14.8259 | -103.6532 | 163.1035

## LL_max_fault_branch
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mw | pf_q_b_from_mw | pf_q_c_from_mw | pf_q_a_to_mw | pf_q_b_to_mw | pf_q_c_to_mw
Line_0 | 0 | 0 | 0 | 0 | 1.7631 | 1.7631 | 0 | 0 | 0 | 0 | 20.3584 | 20.3584 | -1.8237e-14 | -9.5548e-10 | -3.0749e-09 | 1.3027e-14 | -17.4596 | 1.9173 | -9.5322e-29 | 4.0277e-09 | -3.5664e-10 | 7.816e-15 | -2.1579 | -13.3845
Line_1 | 0 | 1.5688 | 1.5688 | 0 | 0 | 0 | 0 | 18.1144 | 18.1144 | 0 | 0 | 0 | -7.816e-15 | -14.6611 | 2.3562 | 5.2106e-15 | -4.7339e-10 | -1.0337e-09 | -2.6053e-15 | -0.96958 | -11.3353 | 2.6053e-15 | 1.3544e-09 | -3.8387e-10
Line_2 | 0 | 1.5688 | 1.5688 | 0 | 0 | 0 | 0 | 18.1144 | 18.1144 | 0 | 0 | 0 | -5.2106e-15 | -14.6611 | 2.3562 | -1.286e-29 | -4.7338e-10 | -1.0337e-09 | 5.2106e-15 | -0.96958 | -11.3353 | 2.6053e-15 | 1.3544e-09 | -3.8386e-10

## LL_min
name | pf_ikss_a_ka | pf_ikss_b_ka | pf_ikss_c_ka | pf_skss_a_mw | pf_skss_b_mw | pf_skss_c_mw | pf_rk0_ohm | pf_xk0_ohm | pf_rk1_ohm | pf_xk1_ohm | pf_rk2_ohm | pf_xk2_ohm | pf_vm_a_pu | pf_vm_b_pu | pf_vm_c_pu | pf_va_a_degree | pf_va_b_degree | pf_va_c_degree
Bus_0 | 0 | 3.6364 | 3.6364 | 0 | 230.9401 | 230.9401 | 1.505 | 15.0499 | 1.505 | 15.0499 | 1.505 | 15.0499 | 0.86603 | 0 | 0.86603 | 1.7201e-10 | 0 | 180
Bus_1 | 0 | 4.1337 | 4.1337 | 0 | 47.7317 | 47.7317 | 0.023608 | 51.7082 | 0.11535 | 2.4164 | 0.11535 | 2.4164 | 0.86603 | 0 | 0.86603 | 3.075e-11 | 0 | 180
Bus_2 | 0 | 3.1191 | 3.1191 | 0 | 36.0161 | 36.0161 | 7.9301 | 53.2797 | 1.1138 | 3.0064 | 1.1138 | 3.0064 | 0.86603 | 0 | 0.86603 | 1.7233e-10 | 0 | 180
Bus_3 | 0 | 2.3976 | 2.3976 | 0 | 27.6856 | 27.6856 | 15.1961 | 54.7485 | 2.1122 | 3.5964 | 2.1122 | 3.5964 | 0.86603 | 0 | 0.86603 | 1.9334e-10 | 0 | 180
Bus_4 | 0 | 2.3976 | 2.3976 | 0 | 27.6856 | 27.6856 | 15.1961 | 54.7485 | 2.1122 | 3.5964 | 2.1122 | 3.5964 | 0.86603 | 0 | 0.86603 | 1.9335e-10 | 0 | 180

## LL_min_branch
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mw | pf_q_b_from_mw | pf_q_c_from_mw | pf_q_a_to_mw | pf_q_b_to_mw | pf_q_c_to_mw
Line_0 | 0 | 0 | 0 | 0 | 3.1191 | 3.1191 | 0 | 0 | 0 | 0 | 36.0161 | 36.0161 | -1.1842e-14 | 4.7369e-15 | 1.1842e-14 | 2.3685e-15 | -16.8865 | 16.8865 | -4.737e-15 | 4.7631e-09 | -4.7631e-09 | 4.737e-15 | 6.2558 | -6.2558
Line_1 | 0 | 2.3976 | 2.3976 | 0 | 0 | 0 | 0 | 27.6856 | 27.6856 | 0 | 0 | 0 | 2.3685e-15 | -11.9365 | 11.9365 | -1.6579e-14 | 7.1054e-15 | 2.3685e-15 | 2.3685e-15 | 7.0103 | -7.0103 | 9.4739e-15 | 1.5877e-09 | -1.5877e-09
Line_2 | 0 | 2.3976 | 2.3976 | 0 | 0 | 0 | 0 | 27.6856 | 27.6856 | 0 | 0 | 0 | -4.737e-15 | -11.9365 | 11.9365 | 1.5313e-28 | 7.1054e-15 | 7.1054e-15 | 7.1054e-15 | 7.0103 | -7.0103 | -1.4211e-14 | 1.5877e-09 | -1.5877e-09

## LL_min_fault
name | pf_ikss_a_ka | pf_ikss_b_ka | pf_ikss_c_ka | pf_skss_a_mw | pf_skss_b_mw | pf_skss_c_mw | pf_rk0_ohm | pf_xk0_ohm | pf_rk1_ohm | pf_xk1_ohm | pf_rk2_ohm | pf_xk2_ohm | pf_vm_a_pu | pf_vm_b_pu | pf_vm_c_pu | pf_va_a_degree | pf_va_b_degree | pf_va_c_degree
Bus_0 | 0 | 3.0554 | 3.0554 | 0 | 194.0418 | 194.0418 | 1.505 | 15.0499 | 1.505 | 15.0499 | 1.505 | 15.0499 | 0.92203 | 0.19641 | 0.81801 | 5.174 | -122.1449 | 174.1659
Bus_1 | 0 | 1.7957 | 1.7957 | 0 | 20.7353 | 20.7353 | 0.023608 | 51.7082 | 0.11535 | 2.4164 | 0.11535 | 2.4164 | 1.0057 | 0.63489 | 0.83074 | 17.5701 | -106.9886 | 158.5648
Bus_2 | 0 | 1.5183 | 1.5183 | 0 | 17.5318 | 17.5318 | 7.9301 | 53.2797 | 1.1138 | 3.0064 | 1.1138 | 3.0064 | 0.95734 | 0.5368 | 0.85298 | 15.9329 | -101.7238 | 162.0554
Bus_3 | 0 | 1.3081 | 1.3081 | 0 | 15.105 | 15.105 | 15.1961 | 54.7485 | 2.1122 | 3.5964 | 2.1122 | 3.5964 | 0.92653 | 0.4625 | 0.86515 | 14.3131 | -97.8911 | 164.6473
Bus_4 | 0 | 1.3081 | 1.3081 | 0 | 15.105 | 15.105 | 15.1961 | 54.7485 | 2.1122 | 3.5964 | 2.1122 | 3.5964 | 0.92653 | 0.4625 | 0.86515 | 14.3131 | -97.8911 | 164.6473

## LL_min_fault_branch
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mw | pf_q_b_from_mw | pf_q_c_from_mw | pf_q_a_to_mw | pf_q_b_to_mw | pf_q_c_to_mw
Line_0 | 0 | 0 | 0 | 0 | 1.5183 | 1.5183 | 0 | 0 | 0 | 0 | 17.5318 | 17.5318 | -2.6645e-15 | -8.0026e-10 | -2.5674e-09 | 5.3291e-15 | -13.0917 | 1.5655 | -2.3685e-15 | 3.4014e-09 | -3.4064e-10 | 2.3685e-15 | -0.95344 | -10.5727
Line_1 | 0 | 1.3081 | 1.3081 | 0 | 0 | 0 | 0 | 15.105 | 15.105 | 0 | 0 | 0 | -5.9212e-16 | -10.3011 | 1.745 | -3.5527e-15 | -4.798e-10 | -8.2616e-10 | -2.2446e-30 | 0.27863 | -8.8347 | -1.6995e-29 | 1.0532e-09 | -4.5326e-10
Line_2 | 0 | 1.3081 | 1.3081 | 0 | 0 | 0 | 0 | 15.105 | 15.105 | 0 | 0 | 0 | -3.5527e-15 | -10.3011 | 1.745 | 5.9212e-16 | -4.798e-10 | -8.2616e-10 | 4.737e-15 | 0.27863 | -8.8347 | 2.8325e-30 | 1.0532e-09 | -4.5326e-10

## LLG_max
name | pf_ikss_a_ka | pf_ikss_b_ka | pf_ikss_c_ka | pf_skss_a_mw | pf_skss_b_mw | pf_skss_c_mw | pf_rk0_ohm | pf_xk0_ohm | pf_rk1_ohm | pf_xk1_ohm | pf_rk2_ohm | pf_xk2_ohm | pf_vm_a_pu | pf_vm_b_pu | pf_vm_c_pu | pf_va_a_degree | pf_va_b_degree | pf_va_c_degree
Bus_0 | 0 | 5.2486 | 5.2486 | 0 | 333.3334 | 333.3334 | 1.3244 | 13.2439 | 1.3244 | 13.2439 | 1.3244 | 13.2439 | 0.63509 | 0 | 0.63509 | -4.8774e-09 | 0 | 180
Bus_1 | 0 | 4.7552 | 4.7715 | 0 | 54.9081 | 55.0968 | 0.01229 | 51.6946 | 0.10773 | 2.3084 | 0.10773 | 2.3084 | 0.93182 | 0 | 0.93182 | 0.058101 | 0 | -179.9419
Bus_2 | 0 | 3.6903 | 3.736 | 0 | 42.6118 | 43.1394 | 4.1304 | 53.3128 | 0.62773 | 2.8984 | 0.62773 | 2.8984 | 0.92715 | 0 | 0.92715 | 0.2096 | 0 | -179.7904
Bus_3 | 0 | 2.9719 | 3.0278 | 0 | 34.3161 | 34.9617 | 7.9148 | 54.8073 | 1.1477 | 3.4884 | 1.1477 | 3.4884 | 0.92249 | 0 | 0.92249 | 0.31929 | 0 | -179.6807
Bus_4 | 0 | 2.9719 | 3.0278 | 0 | 34.3161 | 34.9617 | 7.9148 | 54.8073 | 1.1477 | 3.4884 | 1.1477 | 3.4884 | 0.92249 | 0 | 0.92249 | 0.31929 | 0 | -179.6807

## LLG_max_branch
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mw | pf_q_b_from_mw | pf_q_c_from_mw | pf_q_a_to_mw | pf_q_b_to_mw | pf_q_c_to_mw
Line_0 | 0.0080002 | 0.0080002 | 0.0080002 | 0.0053 | 3.6894 | 3.7373 | 0.092378 | 0.092378 | 0.092378 | 0.0612 | 42.6018 | 43.155 | 0.00053243 | -4.8412e-14 | -4.2192e-14 | -3.8944e-05 | 7.8029e-11 | 8.2548e-11 | -0.14909 | -8.2972e-14 | 7.9684e-14 | 0.098279 | -4.8019e-11 | 3.3593e-11
Line_1 | 0 | 2.9719 | 3.0278 | 0.00265 | 0.00265 | 0.00265 | 0 | 34.3161 | 34.9617 | 0.0306 | 0.0306 | 0.0306 | -2.9165e-09 | 6.7408e-11 | 7.8364e-11 | 1.9471e-05 | -2.4999e-14 | -3.7936e-14 | 3.5896e-11 | -4.9295e-11 | 2.3969e-11 | -0.049139 | -6.0876e-14 | 5.0539e-14
Line_2 | 0 | 2.9719 | 3.0278 | 0.00265 | 0.00265 | 0.00265 | 0 | 34.3161 | 34.9617 | 0.0306 | 0.0306 | 0.0306 | -2.9165e-09 | 6.7423e-11 | 7.832e-11 | 1.9471e-05 | -2.4999e-14 | -3.7936e-14 | 3.5911e-11 | -4.9311e-11 | 2.3899e-11 | -0.049139 | -6.0876e-14 | 5.0539e-14

## LLG_max_fault
name | pf_ikss_a_ka | pf_ikss_b_ka | pf_ikss_c_ka | pf_skss_a_mw | pf_skss_b_mw | pf_skss_c_mw | pf_rk0_ohm | pf_xk0_ohm | pf_rk1_ohm | pf_xk1_ohm | pf_rk2_ohm | pf_xk2_ohm | pf_vm_a_pu | pf_vm_b_pu | pf_vm_c_pu | pf_va_a_degree | pf_va_b_degree | pf_va_c_degree
Bus_0 | 0 | 3.618 | 3.618 | 0 | 229.7713 | 229.7713 | 1.3244 | 13.2439 | 1.3244 | 13.2439 | 1.3244 | 13.2439 | 0.83784 | 0.40283 | 0.69184 | 8.9575 | -115.8808 | 160.4095
Bus_1 | 0 | 1.1689 | 1.3141 | 0 | 13.4969 | 15.1735 | 0.01229 | 51.6946 | 0.10773 | 2.3084 | 0.10773 | 2.3084 | 1.0976 | 0.87234 | 0.96053 | 22.9542 | -100.051 | 153.3464
Bus_2 | 0 | 1.0803 | 1.2046 | 0 | 12.4744 | 13.9092 | 4.1304 | 53.3128 | 0.62773 | 2.8984 | 0.62773 | 2.8984 | 1.0725 | 0.80202 | 0.94995 | 21.6678 | -99.5297 | 155.4334
Bus_3 | 0 | 1.0047 | 1.1114 | 0 | 11.601 | 12.8339 | 7.9148 | 54.8073 | 1.1477 | 3.4884 | 1.1477 | 3.4884 | 1.0514 | 0.74213 | 0.94105 | 20.5075 | -99.0862 | 157.2132
Bus_4 | 0 | 1.0047 | 1.1114 | 0 | 11.601 | 12.8339 | 7.9148 | 54.8073 | 1.1477 | 3.4884 | 1.1477 | 3.4884 | 1.0514 | 0.74213 | 0.94105 | 20.5075 | -99.0862 | 157.2132

## LLG_max_fault_branch
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mw | pf_q_b_from_mw | pf_q_c_from_mw | pf_q_a_to_mw | pf_q_b_to_mw | pf_q_c_to_mw
Line_0 | 0.0069515 | 0.0069515 | 0.0069515 | 0.0045932 | 1.0786 | 1.2072 | 0.080269 | 0.080269 | 0.080269 | 0.053038 | 12.4548 | 13.9401 | -0.010444 | -0.052575 | 0.063421 | 0.0063159 | -5.8032 | -7.2935 | -0.1235 | 0.023173 | -0.012244 | 0.081229 | -5.8492 | -7.2485
Line_1 | 0 | 1.0047 | 1.1114 | 0.0022966 | 0.0022966 | 0.0022966 | 0 | 11.601 | 12.8339 | 0.026519 | 0.026519 | 0.026519 | -2.4101e-09 | -5.0469 | -6.1765 | -0.003158 | -0.016125 | 0.019297 | 1.97e-10 | -5.0469 | -6.1765 | -0.040614 | 0.0069115 | -0.0032031
Line_2 | 0 | 1.0047 | 1.1114 | 0.0022966 | 0.0022966 | 0.0022966 | 0 | 11.601 | 12.8339 | 0.026519 | 0.026519 | 0.026519 | -2.4101e-09 | -5.0469 | -6.1765 | -0.003158 | -0.016125 | 0.019297 | 1.9703e-10 | -5.0469 | -6.1765 | -0.040614 | 0.0069115 | -0.0032031

## LLG_min
name | pf_ikss_a_ka | pf_ikss_b_ka | pf_ikss_c_ka | pf_skss_a_mw | pf_skss_b_mw | pf_skss_c_mw | pf_rk0_ohm | pf_xk0_ohm | pf_rk1_ohm | pf_xk1_ohm | pf_rk2_ohm | pf_xk2_ohm | pf_vm_a_pu | pf_vm_b_pu | pf_vm_c_pu | pf_va_a_degree | pf_va_b_degree | pf_va_c_degree
Bus_0 | 0 | 4.1989 | 4.1989 | 0 | 266.6667 | 266.6667 | 1.505 | 15.0499 | 1.505 | 15.0499 | 1.505 | 15.0499 | 0.57735 | 0 | 0.57735 | -5.8129e-09 | 0 | 180
Bus_1 | 0 | 4.1294 | 4.1445 | 0 | 47.6819 | 47.8561 | 0.023608 | 51.7082 | 0.11535 | 2.4164 | 0.11535 | 2.4164 | 0.84625 | 0 | 0.84625 | 0.061852 | 0 | -179.9381
Bus_2 | 0 | 3.0917 | 3.154 | 0 | 35.6996 | 36.4193 | 7.9301 | 53.2797 | 1.1138 | 3.0064 | 1.1138 | 3.0064 | 0.8415 | 0 | 0.8415 | 0.34056 | 0 | -179.6594
Bus_3 | 0 | 2.3654 | 2.4384 | 0 | 27.3129 | 28.1562 | 15.1961 | 54.7485 | 2.1122 | 3.5964 | 2.1122 | 3.5964 | 0.83633 | 0 | 0.83633 | 0.52263 | 0 | -179.4774
Bus_4 | 0 | 2.3654 | 2.4384 | 0 | 27.3129 | 28.1562 | 15.1961 | 54.7485 | 2.1122 | 3.5964 | 2.1122 | 3.5964 | 0.83633 | 0 | 0.83633 | 0.52263 | 0 | -179.4774

## LLG_min_branch
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mw | pf_q_b_from_mw | pf_q_c_from_mw | pf_q_a_to_mw | pf_q_b_to_mw | pf_q_c_to_mw
Line_0 | 0.0072653 | 0.0072653 | 0.0072653 | 0.0048104 | 3.0903 | 3.1559 | 0.083893 | 0.083893 | 0.083893 | 0.055546 | 35.6832 | 36.4409 | 0.00084308 | -7.9513e-14 | 8.5002e-14 | -6.1589e-05 | -1.3521e-10 | 2.9691e-11 | -0.12296 | 4.9679e-14 | 4.1655e-14 | 0.08096 | -1.3613e-10 | -1.9404e-10
Line_1 | 0 | 2.3654 | 2.4384 | 0.0024052 | 0.0024052 | 0.0024052 | 0 | 27.3129 | 28.1562 | 0.027773 | 0.027773 | 0.027773 | -2.3827e-09 | -1.3268e-10 | -4.9288e-12 | 3.0794e-05 | -1.3222e-13 | 1.2744e-13 | 4.8436e-11 | -9.5779e-11 | -1.6903e-10 | -0.04048 | 6.9415e-14 | 7.8377e-14
Line_2 | 0 | 2.3654 | 2.4384 | 0.0024052 | 0.0024052 | 0.0024052 | 0 | 27.3129 | 28.1562 | 0.027773 | 0.027773 | 0.027773 | -2.3827e-09 | -1.3267e-10 | -4.9206e-12 | 3.0794e-05 | -1.3222e-13 | 1.2744e-13 | 4.8423e-11 | -9.5735e-11 | -1.6911e-10 | -0.04048 | 6.9415e-14 | 7.8377e-14

## LLG_min_fault
name | pf_ikss_a_ka | pf_ikss_b_ka | pf_ikss_c_ka | pf_skss_a_mw | pf_skss_b_mw | pf_skss_c_mw | pf_rk0_ohm | pf_xk0_ohm | pf_rk1_ohm | pf_xk1_ohm | pf_rk2_ohm | pf_xk2_ohm | pf_vm_a_pu | pf_vm_b_pu | pf_vm_c_pu | pf_va_a_degree | pf_va_b_degree | pf_va_c_degree
Bus_0 | 0 | 3.0129 | 3.0129 | 0 | 191.3457 | 191.3457 | 1.505 | 15.0499 | 1.505 | 15.0499 | 1.505 | 15.0499 | 0.7473 | 0.33546 | 0.61843 | 8.1092 | -117.0249 | 161.7746
Bus_1 | 0 | 1.052 | 1.1823 | 0 | 12.1475 | 13.6515 | 0.023608 | 51.7082 | 0.11535 | 2.4164 | 0.11535 | 2.4164 | 0.99694 | 0.78485 | 0.86907 | 22.6952 | -100.4046 | 153.5353
Bus_2 | 0 | 0.94826 | 1.0526 | 0 | 10.9496 | 12.154 | 7.9301 | 53.2797 | 1.1138 | 3.0064 | 1.1138 | 3.0064 | 0.95747 | 0.70193 | 0.86956 | 21.4466 | -97.6343 | 156.58
Bus_3 | 0 | 0.86282 | 0.9457 | 0 | 9.963 | 10.92 | 15.1961 | 54.7485 | 2.1122 | 3.5964 | 2.1122 | 3.5964 | 0.92684 | 0.63377 | 0.86777 | 20.2048 | -95.3977 | 159.009
Bus_4 | 0 | 0.86282 | 0.9457 | 0 | 9.963 | 10.92 | 15.1961 | 54.7485 | 2.1122 | 3.5964 | 2.1122 | 3.5964 | 0.92684 | 0.63377 | 0.86777 | 20.2048 | -95.3977 | 159.009

## LLG_min_fault_branch
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mw | pf_q_b_from_mw | pf_q_c_from_mw | pf_q_a_to_mw | pf_q_b_to_mw | pf_q_c_to_mw
Line_0 | 0.0063139 | 0.0063139 | 0.0063139 | 0.0041472 | 0.94659 | 1.0551 | 0.072907 | 0.072907 | 0.072907 | 0.047888 | 10.9302 | 12.1837 | -0.0082775 | -0.042897 | 0.051812 | 0.0046518 | -4.4701 | -5.5701 | -0.10191 | 0.019125 | -0.01008 | 0.066525 | -4.506 | -5.5359
Line_1 | 0 | 0.86282 | 0.9457 | 0.0020736 | 0.0020736 | 0.0020736 | 0 | 9.963 | 10.92 | 0.023944 | 0.023944 | 0.023944 | -1.957e-09 | -3.7223 | -4.4718 | -0.0023259 | -0.012977 | 0.015326 | 1.4811e-10 | -3.7223 | -4.4718 | -0.033262 | 0.0049907 | -0.0018155
Line_2 | 0 | 0.86282 | 0.9457 | 0.0020736 | 0.0020736 | 0.0020736 | 0 | 9.963 | 10.92 | 0.023944 | 0.023944 | 0.023944 | -1.9569e-09 | -3.7223 | -4.4718 | -0.0023259 | -0.012977 | 0.015326 | 1.4812e-10 | -3.7223 | -4.4718 | -0.033262 | 0.0049907 | -0.0018155

## LG_max
name | pf_ikss_a_ka | pf_ikss_b_ka | pf_ikss_c_ka | pf_skss_a_mw | pf_skss_b_mw | pf_skss_c_mw | pf_rk0_ohm | pf_xk0_ohm | pf_rk1_ohm | pf_xk1_ohm | pf_rk2_ohm | pf_xk2_ohm | pf_vm_a_pu | pf_vm_b_pu | pf_vm_c_pu | pf_va_a_degree | pf_va_b_degree | pf_va_c_degree
Bus_0 | 5.2486 | 0 | 0 | 333.3334 | 0 | 0 | 1.3244 | 13.2439 | 1.3244 | 13.2439 | 1.3244 | 13.2439 | 0.63509 | 1.1 | 0.63509 | 60 | -90 | 120
Bus_1 | 0.67668 | 0 | 0 | 7.8136 | 0 | 0 | 0.01229 | 51.6946 | 0.10773 | 2.3084 | 0.10773 | 2.3084 | 1.0349 | 1.1 | 1.0313 | 32.3228 | -90 | 147.9898
Bus_2 | 0.64199 | 0 | 0 | 7.4131 | 0 | 0 | 4.1304 | 53.3128 | 0.62773 | 2.8984 | 0.62773 | 2.8984 | 1.0256 | 1.1 | 1.013 | 33.2033 | -90 | 147.897
Bus_3 | 0.60849 | 0 | 0 | 7.0263 | 0 | 0 | 7.9148 | 54.8073 | 1.1477 | 3.4884 | 1.1477 | 3.4884 | 1.0154 | 1.1 | 0.99663 | 33.9561 | -90 | 147.6794
Bus_4 | 0.60849 | 0 | 0 | 7.0263 | 0 | 0 | 7.9148 | 54.8073 | 1.1477 | 3.4884 | 1.1477 | 3.4884 | 1.0154 | 1.1 | 0.99663 | 33.9561 | -90 | 147.6794

## LG_max_branch
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mw | pf_q_b_from_mw | pf_q_c_from_mw | pf_q_a_to_mw | pf_q_b_to_mw | pf_q_c_to_mw
Line_0 | 0.015016 | 0.015016 | 0.015016 | 0.65177 | 0.0098121 | 0.0098121 | 0.17339 | 0.17339 | 0.17339 | 7.526 | 0.1133 | 0.1133 | -3.1147e-13 | 0.16612 | -0.16424 | 1.2354e-11 | -0.10799 | 0.10786 | 9.0936e-14 | -0.26268 | -0.2626 | -4.836e-12 | 0.16984 | 0.167
Line_1 | 0.60849 | 0 | 0 | 0.004906 | 0.004906 | 0.004906 | 7.0263 | 0 | 0 | 0.05665 | 0.05665 | 0.05665 | 1.0461e-11 | -4.9678e-09 | -4.7603e-09 | -9.5506e-14 | 0.053995 | -0.053928 | -5.0004e-12 | -3.1144e-09 | 3.2342e-09 | 2.9183e-14 | -0.084919 | -0.0835
Line_2 | 0.60849 | 0 | 0 | 0.004906 | 0.004906 | 0.004906 | 7.0263 | 0 | 0 | 0.05665 | 0.05665 | 0.05665 | 1.0459e-11 | -4.9678e-09 | -4.7603e-09 | -9.5506e-14 | 0.053995 | -0.053928 | -5.0065e-12 | -3.1143e-09 | 3.2342e-09 | 2.9183e-14 | -0.084919 | -0.0835

## LG_max_fault
name | pf_ikss_a_ka | pf_ikss_b_ka | pf_ikss_c_ka | pf_skss_a_mw | pf_skss_b_mw | pf_skss_c_mw | pf_rk0_ohm | pf_xk0_ohm | pf_rk1_ohm | pf_xk1_ohm | pf_rk2_ohm | pf_xk2_ohm | pf_vm_a_pu | pf_vm_b_pu | pf_vm_c_pu | pf_va_a_degree | pf_va_b_degree | pf_va_c_degree
Bus_0 | 3.618 | 0 | 0 | 229.7713 | 0 | 0 | 1.3244 | 13.2439 | 1.3244 | 13.2439 | 1.3244 | 13.2439 | 0.69184 | 1.1 | 0.83784 | 40.4095 | -90 | 128.9575
Bus_1 | 0.52257 | 0 | 0 | 6.0341 | 0 | 0 | 0.01229 | 51.6946 | 0.10773 | 2.3084 | 0.10773 | 2.3084 | 1.0437 | 1.1 | 1.054 | 31.1673 | -90 | 147.917
Bus_2 | 0.49576 | 0 | 0 | 5.7245 | 0 | 0 | 4.1304 | 53.3128 | 0.62773 | 2.8984 | 0.62773 | 2.8984 | 1.0349 | 1.1 | 1.0392 | 31.8378 | -90 | 147.7826
Bus_3 | 0.4715 | 0 | 0 | 5.4444 | 0 | 0 | 7.9148 | 54.8073 | 1.1477 | 3.4884 | 1.1477 | 3.4884 | 1.026 | 1.1 | 1.0259 | 32.4208 | -90 | 147.5843
Bus_4 | 0.4715 | 0 | 0 | 5.4444 | 0 | 0 | 7.9148 | 54.8073 | 1.1477 | 3.4884 | 1.1477 | 3.4884 | 1.026 | 1.1 | 1.0259 | 32.4208 | -90 | 147.5843

## LG_max_fault_branch
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mw | pf_q_b_from_mw | pf_q_c_from_mw | pf_q_a_to_mw | pf_q_b_to_mw | pf_q_c_to_mw
Line_0 | 0.011596 | 0.011596 | 0.011596 | 0.50331 | 0.0075771 | 0.0075771 | 0.1339 | 0.1339 | 0.1339 | 5.8117 | 0.087492 | 0.087492 | 0.030184 | 0.11032 | -0.13938 | -1.2461 | -0.073243 | 0.09043 | 0.030415 | -0.198 | -0.14567 | -1.2491 | 0.12632 | 0.094724
Line_1 | 0.4715 | 0 | 0 | 0.0037885 | 0.0037885 | 0.0037885 | 5.4444 | 0 | 0 | 0.043746 | 0.043746 | 0.043746 | -1.1116 | -3.6718e-09 | -2.761e-09 | 0.0086335 | 0.036621 | -0.045215 | -1.1116 | -2.1555e-09 | 2.6814e-09 | 0.010092 | -0.063162 | -0.047362
Line_2 | 0.4715 | 0 | 0 | 0.0037885 | 0.0037885 | 0.0037885 | 5.4444 | 0 | 0 | 0.043746 | 0.043746 | 0.043746 | -1.1116 | -3.6718e-09 | -2.761e-09 | 0.0086335 | 0.036621 | -0.045215 | -1.1116 | -2.1555e-09 | 2.6814e-09 | 0.010092 | -0.063162 | -0.047362

## LG_min
name | pf_ikss_a_ka | pf_ikss_b_ka | pf_ikss_c_ka | pf_skss_a_mw | pf_skss_b_mw | pf_skss_c_mw | pf_rk0_ohm | pf_xk0_ohm | pf_rk1_ohm | pf_xk1_ohm | pf_rk2_ohm | pf_xk2_ohm | pf_vm_a_pu | pf_vm_b_pu | pf_vm_c_pu | pf_va_a_degree | pf_va_b_degree | pf_va_c_degree
Bus_0 | 4.1989 | 0 | 0 | 266.6667 | 0 | 0 | 1.505 | 15.0499 | 1.505 | 15.0499 | 1.505 | 15.0499 | 0.57735 | 1 | 0.57735 | 60 | -90 | 120
Bus_1 | 0.61266 | 0 | 0 | 7.0744 | 0 | 0 | 0.023608 | 51.7082 | 0.11535 | 2.4164 | 0.11535 | 2.4164 | 0.93833 | 1 | 0.93491 | 32.4304 | -90 | 147.9007
Bus_2 | 0.57585 | 0 | 0 | 6.6493 | 0 | 0 | 7.9301 | 53.2797 | 1.1138 | 3.0064 | 1.1138 | 3.0064 | 0.93186 | 1 | 0.91344 | 33.6967 | -90 | 148.077
Bus_3 | 0.53364 | 0 | 0 | 6.162 | 0 | 0 | 15.1961 | 54.7485 | 2.1122 | 3.5964 | 2.1122 | 3.5964 | 0.92177 | 1 | 0.89416 | 34.7245 | -90 | 147.9168
Bus_4 | 0.53364 | 0 | 0 | 6.162 | 0 | 0 | 15.1961 | 54.7485 | 2.1122 | 3.5964 | 2.1122 | 3.5964 | 0.92177 | 1 | 0.89416 | 34.7245 | -90 | 147.9168

## LG_min_branch
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mw | pf_q_b_from_mw | pf_q_c_from_mw | pf_q_a_to_mw | pf_q_b_to_mw | pf_q_c_to_mw
Line_0 | 0.013599 | 0.013599 | 0.013599 | 0.58462 | 0.008866 | 0.008866 | 0.15703 | 0.15703 | 0.15703 | 6.7506 | 0.10238 | 0.10238 | 1.2322e-13 | 0.13747 | -0.13451 | -5.5861e-12 | -0.088745 | 0.088536 | 1.0282e-13 | -0.21502 | -0.21578 | -3.1878e-12 | 0.13938 | 0.13563
Line_1 | 0.53364 | 0 | 0 | 0.004433 | 0.004433 | 0.004433 | 6.162 | 0 | 0 | 0.051188 | 0.051188 | 0.051188 | -4.9218e-12 | -4.0526e-09 | -3.7769e-09 | 3.8383e-14 | 0.044373 | -0.044268 | -1.9406e-12 | -2.4995e-09 | 2.6587e-09 | 3.0088e-14 | -0.069692 | -0.067817
Line_2 | 0.53364 | 0 | 0 | 0.004433 | 0.004433 | 0.004433 | 6.162 | 0 | 0 | 0.051188 | 0.051188 | 0.051188 | -4.9245e-12 | -4.0526e-09 | -3.7769e-09 | 3.8383e-14 | 0.044373 | -0.044268 | -1.9397e-12 | -2.4995e-09 | 2.6587e-09 | 3.0088e-14 | -0.069692 | -0.067817

## LG_min_fault
name | pf_ikss_a_ka | pf_ikss_b_ka | pf_ikss_c_ka | pf_skss_a_mw | pf_skss_b_mw | pf_skss_c_mw | pf_rk0_ohm | pf_xk0_ohm | pf_rk1_ohm | pf_xk1_ohm | pf_rk2_ohm | pf_xk2_ohm | pf_vm_a_pu | pf_vm_b_pu | pf_vm_c_pu | pf_va_a_degree | pf_va_b_degree | pf_va_c_degree
Bus_0 | 3.0129 | 0 | 0 | 191.3457 | 0 | 0 | 1.505 | 15.0499 | 1.505 | 15.0499 | 1.505 | 15.0499 | 0.61843 | 1 | 0.7473 | 41.7746 | -90 | 128.1092
Bus_1 | 0.47357 | 0 | 0 | 5.4683 | 0 | 0 | 0.023608 | 51.7082 | 0.11535 | 2.4164 | 0.11535 | 2.4164 | 0.94663 | 1 | 0.95636 | 31.2254 | -90 | 147.8257
Bus_2 | 0.44164 | 0 | 0 | 5.0997 | 0 | 0 | 7.9301 | 53.2797 | 1.1138 | 3.0064 | 1.1138 | 3.0064 | 0.94045 | 1 | 0.93832 | 32.262 | -90 | 147.9448
Bus_3 | 0.41098 | 0 | 0 | 4.7455 | 0 | 0 | 15.1961 | 54.7485 | 2.1122 | 3.5964 | 2.1122 | 3.5964 | 0.93233 | 1 | 0.92215 | 33.1214 | -90 | 147.8611
Bus_4 | 0.41098 | 0 | 0 | 4.7455 | 0 | 0 | 15.1961 | 54.7485 | 2.1122 | 3.5964 | 2.1122 | 3.5964 | 0.93233 | 1 | 0.92215 | 33.1214 | -90 | 147.8611

## LG_min_fault_branch
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mw | pf_q_b_from_mw | pf_q_c_from_mw | pf_q_a_to_mw | pf_q_b_to_mw | pf_q_c_to_mw
Line_0 | 0.010512 | 0.010512 | 0.010512 | 0.44837 | 0.0067997 | 0.0067997 | 0.12138 | 0.12138 | 0.12138 | 5.1773 | 0.078517 | 0.078517 | 0.024707 | 0.091491 | -0.11443 | -0.98788 | -0.060671 | 0.073176 | 0.025071 | -0.1624 | -0.12006 | -0.99232 | 0.10146 | 0.077379
Line_1 | 0.41098 | 0 | 0 | 0.0033999 | 0.0033999 | 0.0033999 | 4.7455 | 0 | 0 | 0.039258 | 0.039258 | 0.039258 | -0.84451 | -2.9075e-09 | -2.2335e-09 | 0.0063141 | 0.030335 | -0.036588 | -0.84451 | -1.7658e-09 | 2.1549e-09 | 0.0085359 | -0.050729 | -0.03869
Line_2 | 0.41098 | 0 | 0 | 0.0033999 | 0.0033999 | 0.0033999 | 4.7455 | 0 | 0 | 0.039258 | 0.039258 | 0.039258 | -0.84451 | -2.9075e-09 | -2.2335e-09 | 0.0063141 | 0.030335 | -0.036588 | -0.84451 | -1.7658e-09 | 2.1549e-09 | 0.0085359 | -0.050729 | -0.03869