## LLL_max
name | pf_ikss_ka | pf_skss_mw | pf_rk_ohm | pf_xk_ohm | pf_vm_pu | pf_va_degree
Bus_0 | 5.2486 | 1000.0001 | 1.3244 | 13.2439 | 0 | 84.2894
Bus_1 | 5.4963 | 190.3978 | 0.10773 | 2.3084 | 0 | 87.328
Bus_2 | 4.283 | 148.3662 | 0.62773 | 2.8984 | 0 | 77.7798
Bus_3 | 3.6999 | 128.1693 | 0.9744 | 3.2918 | 0 | 73.5107
Bus_4 | 3.6999 | 128.1693 | 0.9744 | 3.2918 | 0 | 73.5107

## LLL_max_branch
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_vm_pu
Line_0 | 0 | 4.283 | 0 | 9.2778 | 0 | 148.3662 | 6.2984e-19 | -1e-07 | -4.9301e-19 | -1e-07
Line_1 | 2.4666 | 0 | 4.9647 | 0 | 85.4462 | 0 | -1e-07 | 1.602e-19 | -1e-07 | -1.2518e-19
Line_2 | 2.4666 | 0 | 4.9647 | 0 | 85.4462 | 0 | -1e-07 | 1.602e-19 | -1e-07 | -1.2518e-19
Line_4 | 1.2333 | 1.2333 | 2.4824 | 2.4824 | 42.7231 | 42.7231 | -1e-07 | -1e-07 | -1e-07 | -1e-07

## LLL_max_fault
name | pf_ikss_ka | pf_skss_mw | pf_rk_ohm | pf_xk_ohm | pf_vm_pu | pf_va_degree
Bus_0 | 3.618 | 689.314 | 1.3244 | 13.2439 | 0.40283 | 45
Bus_1 | 1.4245 | 49.3473 | 0.10773 | 2.3084 | 0.87234 | 45
Bus_2 | 1.3097 | 45.3689 | 0.62773 | 2.8984 | 0.80202 | 45
Bus_3 | 1.2428 | 43.0531 | 0.9744 | 3.2918 | 0.76108 | 45
Bus_4 | 1.2428 | 43.0531 | 0.9744 | 3.2918 | 0.76108 | 45

## LLL_max_fault_branch
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_vm_pu
Line_0 | 0 | 1.3097 | 0 | 2.8371 | 0 | 45.3689 | -6.0676e-09 | -25.7292 | 5.5265e-09 | -25.7292
Line_1 | 0.82856 | 0 | 1.6677 | 0 | 28.7021 | 0 | -15.4464 | -2.495e-09 | -15.4464 | 1.6066e-09
Line_2 | 0.82856 | 0 | 1.6677 | 0 | 28.7021 | 0 | -15.4464 | -2.495e-09 | -15.4464 | 1.6066e-09
Line_4 | 0.41428 | 0.41428 | 0.83384 | 0.83384 | 14.351 | 14.351 | -7.7232 | -7.7232 | -7.7232 | -7.7232

## LLL_min
name | pf_ikss_ka | pf_skss_mw | pf_rk_ohm | pf_xk_ohm | pf_vm_pu | pf_va_degree
Bus_0 | 4.1989 | 800 | 1.505 | 15.0499 | 0 | 84.2894
Bus_1 | 4.7732 | 165.3474 | 0.11535 | 2.4164 | 0 | 87.2669
Bus_2 | 3.6016 | 124.7634 | 1.1138 | 3.0064 | 0 | 69.6723
Bus_3 | 3.0092 | 104.2421 | 1.7794 | 3.3997 | 0 | 62.3733
Bus_4 | 3.0092 | 104.2421 | 1.7794 | 3.3997 | 0 | 62.3733

## LLL_min_branch
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_vm_pu
Line_0 | 0 | 3.6016 | 0 | 6.8381 | 0 | 124.7634 | 7.2813e-20 | -1e-07 | 2.6704e-19 | -1e-07
Line_1 | 2.0061 | 0 | 3.4722 | 0 | 69.4947 | 0 | -1e-07 | 1.7288e-20 | -1e-07 | 6.3228e-20
Line_2 | 2.0061 | 0 | 3.4722 | 0 | 69.4947 | 0 | -1e-07 | 1.7288e-20 | -1e-07 | 6.3228e-20
Line_4 | 1.0031 | 1.0031 | 1.7361 | 1.7361 | 34.7474 | 34.7474 | -1e-07 | -1e-07 | -1e-07 | -1e-07

## LLL_min_fault
name | pf_ikss_ka | pf_skss_mw | pf_rk_ohm | pf_xk_ohm | pf_vm_pu | pf_va_degree
Bus_0 | 3.0129 | 574.037 | 1.505 | 15.0499 | 0.33546 | 45
Bus_1 | 1.2817 | 44.3979 | 0.11535 | 2.4164 | 0.78485 | 45
Bus_2 | 1.1462 | 39.7072 | 1.1138 | 3.0064 | 0.70193 | 45
Bus_3 | 1.0697 | 37.0569 | 1.7794 | 3.3997 | 0.65508 | 45
Bus_4 | 1.0697 | 37.0569 | 1.7794 | 3.3997 | 0.65508 | 45

## LLL_min_fault_branch
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_vm_pu
Line_0 | 0 | 1.1462 | 0 | 2.1763 | 0 | 39.7072 | -5.1465e-09 | -19.7082 | 4.6775e-09 | -19.7082
Line_1 | 0.71316 | 0 | 1.2343 | 0 | 24.7046 | 0 | -11.4434 | -2.233e-09 | -11.4434 | 1.0258e-09
Line_2 | 0.71316 | 0 | 1.2343 | 0 | 24.7046 | 0 | -11.4434 | -2.233e-09 | -11.4434 | 1.0258e-09
Line_4 | 0.35658 | 0.35658 | 0.61717 | 0.61717 | 12.3523 | 12.3523 | -5.7217 | -5.7217 | -5.7217 | -5.7217

## LL_max
name | pf_ikss_a_ka | pf_ikss_b_ka | pf_ikss_c_ka | pf_skss_a_mw | pf_skss_b_mw | pf_skss_c_mw | pf_rk0_ohm | pf_xk0_ohm | pf_rk1_ohm | pf_xk1_ohm | pf_rk2_ohm | pf_xk2_ohm | pf_vm_a_pu | pf_vm_b_pu | pf_vm_c_pu | pf_va_a_degree | pf_va_b_degree | pf_va_c_degree
Bus_0 | 0 | 4.5455 | 4.5455 | 0 | 288.6752 | 288.6752 | 1.3244 | 13.2439 | 1.3244 | 13.2439 | 1.3244 | 13.2439 | 0.95263 | 0 | 0.95263 | -8.6942e-11 | 0 | -180
Bus_1 | 0 | 4.7599 | 4.7599 | 0 | 54.9631 | 54.9631 | 2.133e-06 | 0.46831 | 0.10773 | 2.3084 | 0.10773 | 2.3084 | 0.95263 | 0 | 0.95263 | -4.0638e-12 | 0 | -180
Bus_2 | 0 | 3.7092 | 3.7092 | 0 | 42.8296 | 42.8296 | 3.7165 | 1.9229 | 0.62773 | 2.8984 | 0.62773 | 2.8984 | 0.95263 | 0 | 0.95263 | -1.2526e-11 | 0 | -180
Bus_3 | 0 | 3.2042 | 3.2042 | 0 | 36.9993 | 36.9993 | 6.1931 | 2.8908 | 0.9744 | 3.2918 | 0.9744 | 3.2918 | 0.95263 | 0 | 0.95263 | -1.4344e-11 | 0 | -180
Bus_4 | 0 | 3.2042 | 3.2042 | 0 | 36.9993 | 36.9993 | 6.1931 | 2.8908 | 0.9744 | 3.2918 | 0.9744 | 3.2918 | 0.95263 | 0 | 0.95263 | -1.4346e-11 | 0 | -180

## LL_max_branch
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mw | pf_q_b_from_mw | pf_q_c_from_mw | pf_q_a_to_mw | pf_q_b_to_mw | pf_q_c_to_mw
Line_0 | 0 | 0 | 0 | 0 | 3.7092 | 3.7092 | 0 | 0 | 0 | 0 | 42.8296 | 42.8296 | -9.3792e-14 | 6.2528e-14 | -4.1685e-14 | 8.337e-14 | -23.0225 | 23.0225 | -4.6896e-14 | 5.7634e-09 | -5.7634e-09 | 4.6896e-14 | 4.9861 | -4.9861
Line_1 | 0 | 2.1362 | 2.1362 | 0 | 0 | 0 | 0 | 24.6662 | 24.6662 | 0 | 0 | 0 | 1.5632e-14 | -13.0085 | 13.0085 | -1.0421e-14 | 3.1264e-14 | -2.6053e-14 | 5.2106e-15 | 3.8506 | -3.8506 | -5.2106e-15 | 1.9211e-09 | -1.9211e-09
Line_2 | 0 | 2.1362 | 2.1362 | 0 | 0 | 0 | 0 | 24.6662 | 24.6662 | 0 | 0 | 0 | -5.2106e-15 | -13.0085 | 13.0085 | -1.0421e-14 | 3.1264e-14 | -2.6053e-14 | -5.1818e-29 | 3.8506 | -3.8506 | -1.1813e-28 | 1.9211e-09 | -1.9211e-09
Line_4 | 0 | 1.0681 | 1.0681 | 0 | 1.0681 | 1.0681 | 0 | 12.3331 | 12.3331 | 0 | 12.3331 | 12.3331 | 2.0843e-14 | -6.5042 | 6.5042 | -2.6053e-14 | -6.5042 | 6.5042 | -1.0421e-14 | 1.9253 | -1.9253 | -2.5909e-28 | 1.9253 | -1.9253

## LL_max_fault
name | pf_ikss_a_ka | pf_ikss_b_ka | pf_ikss_c_ka | pf_skss_a_mw | pf_skss_b_mw | pf_skss_c_mw | pf_rk0_ohm | pf_xk0_ohm | pf_rk1_ohm | pf_xk1_ohm | pf_rk2_ohm | pf_xk2_ohm | pf_vm_a_pu | pf_vm_b_pu | pf_vm_c_pu | pf_va_a_degree | pf_va_b_degree | pf_va_c_degree
Bus_0 | 0 | 3.7342 | 3.7342 | 0 | 237.1508 | 237.1508 | 1.3244 | 13.2439 | 1.3244 | 13.2439 | 1.3244 | 13.2439 | 1.0202 | 0.24004 | 0.89607 | 5.7662 | -121.3466 | 173.4316
Bus_1 | 0 | 2.011 | 2.011 | 0 | 23.2205 | 23.2205 | 2.133e-06 | 0.46831 | 0.10773 | 2.3084 | 0.10773 | 2.3084 | 1.1075 | 0.71098 | 0.91717 | 17.922 | -106.528 | 158.1868
Bus_2 | 0 | 1.7631 | 1.7631 | 0 | 20.3584 | 20.3584 | 3.7165 | 1.9229 | 0.62773 | 2.8984 | 0.62773 | 2.8984 | 1.0759 | 0.62335 | 0.92294 | 16.2567 | -104.913 | 160.9544
Bus_3 | 0 | 1.6287 | 1.6287 | 0 | 18.8063 | 18.8063 | 6.1931 | 2.8908 | 0.9744 | 3.2918 | 0.9744 | 3.2918 | 1.0599 | 0.57582 | 0.92591 | 15.2786 | -104.0411 | 162.4427
Bus_4 | 0 | 1.6287 | 1.6287 | 0 | 18.8063 | 18.8063 | 6.1931 | 2.8908 | 0.9744 | 3.2918 | 0.9744 | 3.2918 | 1.0599 | 0.57582 | 0.92591 | 15.2786 | -104.0411 | 162.4427

## LL_max_fault_branch
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mw | pf_q_b_from_mw | pf_q_c_from_mw | pf_q_a_to_mw | pf_q_b_to_mw | pf_q_c_to_mw
Line_0 | 0 | 0 | 0 | 0 | 1.7631 | 1.7631 | 0 | 0 | 0 | 0 | 20.3584 | 20.3584 | -2.9961e-14 | -9.5544e-10 | -3.075e-09 | 3.3869e-14 | -17.4596 | 1.9173 | -2.3448e-14 | 4.0277e-09 | -3.5663e-10 | 2.3448e-14 | -2.1579 | -13.3845
Line_1 | 0 | 1.0858 | 1.0858 | 0 | 0 | 0 | 0 | 12.5375 | 12.5375 | 0 | 0 | 0 | 5.2106e-15 | -10.3342 | 1.4923 | -2.6053e-15 | -4.7336e-10 | -1.0337e-09 | 2.6053e-15 | -0.87368 | -7.9682 | -5.2106e-15 | 1.3544e-09 | -3.8387e-10
Line_2 | 0 | 1.0858 | 1.0858 | 0 | 0 | 0 | 0 | 12.5375 | 12.5375 | 0 | 0 | 0 | -1.1797e-29 | -10.3342 | 1.4923 | 2.4945e-29 | -4.7336e-10 | -1.0338e-09 | 2.6053e-15 | -0.87368 | -7.9682 | -5.2106e-15 | 1.3544e-09 | -3.8387e-10
Line_4 | 0 | 0.54289 | 0.54289 | 0 | 0.54289 | 0.54289 | 0 | 6.2688 | 6.2688 | 0 | 6.2688 | 6.2688 | -1.1747e-29 | -5.1671 | 0.74615 | -5.2106e-15 | -5.1671 | 0.74615 | 2.6053e-15 | -0.43684 | -3.9841 | 2.6053e-15 | -0.43684 | -3.9841

## LL_min
name | pf_ikss_a_ka | pf_ikss_b_ka | pf_ikss_c_ka | pf_skss_a_mw | pf_skss_b_mw | pf_skss_c_mw | pf_rk0_ohm | pf_xk0_ohm | pf_rk1_ohm | pf_xk1_ohm | pf_rk2_ohm | pf_xk2_ohm | pf_vm_a_pu | pf_vm_b_pu | pf_vm_c_pu | pf_va_a_degree | pf_va_b_degree | pf_va_c_degree
Bus_0 | 0 | 3.6364 | 3.6364 | 0 | 230.9401 | 230.9401 | 1.505 | 15.0499 | 1.505 | 15.0499 | 1.505 | 15.0499 | 0.86603 | 0 | 0.86603 | 1.72e-10 | 0 | 180
Bus_1 | 0 | 4.1337 | 4.1337 | 0 | 47.7317 | 47.7317 | 4.309e-06 | 0.4804 | 0.11535 | 2.4164 | 0.11535 | 2.4164 | 0.86603 | 0 | 0.86603 | 3.0763e-11 | 0 | 180
Bus_2 | 0 | 3.1191 | 3.1191 | 0 | 36.0161 | 36.0161 | 7.1352 | 1.8795 | 1.1138 | 3.0064 | 1.1138 | 3.0064 | 0.86603 | 0 | 0.86603 | 1.7232e-10 | 0 | 180
Bus_3 | 0 | 2.6061 | 2.6061 | 0 | 30.0921 | 30.0921 | 11.89 | 2.8069 | 1.7794 | 3.3997 | 1.7794 | 3.3997 | 0.86603 | 0 | 0.86603 | 1.9237e-10 | 0 | 180
Bus_4 | 0 | 2.6061 | 2.6061 | 0 | 30.0921 | 30.0921 | 11.89 | 2.8069 | 1.7794 | 3.3997 | 1.7794 | 3.3997 | 0.86603 | 0 | 0.86603 | 1.9237e-10 | 0 | 180

## LL_min_branch
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mw | pf_q_b_from_mw | pf_q_c_from_mw | pf_q_a_to_mw | pf_q_b_to_mw | pf_q_c_to_mw
Line_0 | 0 | 0 | 0 | 0 | 3.1191 | 3.1191 | 0 | 0 | 0 | 0 | 36.0161 | 36.0161 | -9.4739e-15 | 2.1316e-14 | -1.1842e-14 | 4.737e-15 | -16.8865 | 16.8865 | -1.8948e-14 | 4.7631e-09 | -4.7631e-09 | 1.4211e-14 | 6.2558 | -6.2558
Line_1 | 0 | 1.7374 | 1.7374 | 0 | 0 | 0 | 0 | 20.0614 | 20.0614 | 0 | 0 | 0 | -3.5527e-15 | -8.8871 | 8.8871 | 2.3685e-15 | 4.7369e-15 | 2.3685e-15 | 7.1054e-15 | 4.6513 | -4.6513 | -1.8948e-14 | 1.5877e-09 | -1.5877e-09
Line_2 | 0 | 1.7374 | 1.7374 | 0 | 0 | 0 | 0 | 20.0614 | 20.0614 | 0 | 0 | 0 | -3.5527e-15 | -8.8871 | 8.8871 | -4.737e-15 | 4.7369e-15 | 7.1054e-15 | 9.4739e-15 | 4.6513 | -4.6513 | -9.4739e-15 | 1.5877e-09 | -1.5877e-09
Line_4 | 0 | 0.86868 | 0.86868 | 0 | 0.86868 | 0.86868 | 0 | 10.0307 | 10.0307 | 0 | 10.0307 | 10.0307 | -9.4739e-15 | -4.4435 | 4.4435 | 5.8453e-29 | -4.4435 | 4.4435 | 9.4739e-15 | 2.3257 | -2.3257 | -9.4739e-15 | 2.3257 | -2.3257

## LL_min_fault
name | pf_ikss_a_ka | pf_ikss_b_ka | pf_ikss_c_ka | pf_skss_a_mw | pf_skss_b_mw | pf_skss_c_mw | pf_rk0_ohm | pf_xk0_ohm | pf_rk1_ohm | pf_xk1_ohm | pf_rk2_ohm | pf_xk2_ohm | pf_vm_a_pu | pf_vm_b_pu | pf_vm_c_pu | pf_va_a_degree | pf_va_b_degree | pf_va_c_degree
Bus_0 | 0 | 3.0554 | 3.0554 | 0 | 194.0418 | 194.0418 | 1.505 | 15.0499 | 1.505 | 15.0499 | 1.505 | 15.0499 | 0.92203 | 0.19641 | 0.81801 | 5.174 | -122.1449 | 174.1659
Bus_1 | 0 | 1.7957 | 1.7957 | 0 | 20.7353 | 20.7353 | 4.309e-06 | 0.4804 | 0.11535 | 2.4164 | 0.11535 | 2.4164 | 1.0057 | 0.63489 | 0.83074 | 17.5701 | -106.9886 | 158.5648
Bus_2 | 0 | 1.5183 | 1.5183 | 0 | 17.5318 | 17.5318 | 7.1352 | 1.8795 | 1.1138 | 3.0064 | 1.1138 | 3.0064 | 0.95734 | 0.5368 | 0.85298 | 15.9329 | -101.7238 | 162.0554
Bus_3 | 0 | 1.3721 | 1.3721 | 0 | 15.8432 | 15.8432 | 11.89 | 2.8069 | 1.7794 | 3.3997 | 1.7794 | 3.3997 | 0.93535 | 0.4851 | 0.86185 | 14.8381 | -99.0449 | 163.8635
Bus_4 | 0 | 1.3721 | 1.3721 | 0 | 15.8432 | 15.8432 | 11.89 | 2.8069 | 1.7794 | 3.3997 | 1.7794 | 3.3997 | 0.93535 | 0.4851 | 0.86185 | 14.8381 | -99.0449 | 163.8635

## LL_min_fault_branch
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mw | pf_q_b_from_mw | pf_q_c_from_mw | pf_q_a_to_mw | pf_q_b_to_mw | pf_q_c_to_mw
Line_0 | 0 | 0 | 0 | 0 | 1.5183 | 1.5183 | 0 | 0 | 0 | 0 | 17.5318 | 17.5318 | -2.3685e-15 | -8.0023e-10 | -2.5674e-09 | 3.5527e-15 | -13.0917 | 1.5655 | -9.4739e-15 | 3.4014e-09 | -3.4064e-10 | 9.4739e-15 | -0.95344 | -10.5727
Line_1 | 0 | 0.9147 | 0.9147 | 0 | 0 | 0 | 0 | 10.5621 | 10.5621 | 0 | 0 | 0 | -6.8089e-30 | -7.4125 | 1.1373 | -2.9606e-15 | -4.7979e-10 | -8.2616e-10 | 2.3685e-15 | -0.036791 | -6.2383 | -4.737e-15 | 1.0532e-09 | -4.5325e-10
Line_2 | 0 | 0.9147 | 0.9147 | 0 | 0 | 0 | 0 | 10.5621 | 10.5621 | 0 | 0 | 0 | -2.9606e-15 | -7.4125 | 1.1373 | -1.7764e-15 | -4.798e-10 | -8.2616e-10 | 4.737e-15 | -0.036791 | -6.2383 | -6.2967e-30 | 1.0532e-09 | -4.5326e-10
Line_4 | 0 | 0.45735 | 0.45735 | 0 | 0.45735 | 0.45735 | 0 | 5.2811 | 5.2811 | 0 | 5.2811 | 5.2811 | 5.9212e-16 | -3.7062 | 0.56866 | 0 | -3.7062 | 0.56866 | 1.7022e-30 | -0.018396 | -3.1192 | 0 | -0.018396 | -3.1192

## LLG_max
name | pf_ikss_a_ka | pf_ikss_b_ka | pf_ikss_c_ka | pf_skss_a_mw | pf_skss_b_mw | pf_skss_c_mw | pf_rk0_ohm | pf_xk0_ohm | pf_rk1_ohm | pf_xk1_ohm | pf_rk2_ohm | pf_xk2_ohm | pf_vm_a_pu | pf_vm_b_pu | pf_vm_c_pu | pf_va_a_degree | pf_va_b_degree | pf_va_c_degree
Bus_0 | 0 | 5.2486 | 5.2486 | 0 | 333.3334 | 333.3334 | 1.3244 | 13.2439 | 1.3244 | 13.2439 | 1.3244 | 13.2439 | 0.63509 | 0 | 0.63509 | -4.8774e-09 | 0 | 180
Bus_1 | 0 | 7.506 | 7.6054 | 0 | 86.6716 | 87.8196 | 2.133e-06 | 0.46831 | 0.10773 | 2.3084 | 0.10773 | 2.3084 | 0.2748 | 0 | 0.2748 | 1.9013 | 0 | -178.0987
Bus_2 | 0 | 5.0297 | 2.9649 | 0 | 58.0778 | 34.2354 | 3.7165 | 1.9229 | 0.62773 | 2.8984 | 0.62773 | 2.8984 | 0.75856 | 0 | 0.75856 | -12.5615 | 0 | 167.4385
Bus_3 | 0 | 4.0559 | 2.6206 | 0 | 46.8334 | 30.2597 | 6.1931 | 2.8908 | 0.9744 | 3.2918 | 0.9744 | 3.2918 | 0.80628 | 0 | 0.80628 | -9.1588 | 0 | 170.8412
Bus_4 | 0 | 4.0559 | 2.6206 | 0 | 46.8334 | 30.2597 | 6.1931 | 2.8908 | 0.9744 | 3.2918 | 0.9744 | 3.2918 | 0.80628 | 0 | 0.80628 | -9.1588 | 0 | 170.8412

## LLG_max_branch
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mw | pf_q_b_from_mw | pf_q_c_from_mw | pf_q_a_to_mw | pf_q_b_to_mw | pf_q_c_to_mw
Line_0 | 0.0031483 | 0.0031483 | 0.0031483 | 0.0065062 | 5.0287 | 2.9701 | 0.036354 | 0.036354 | 0.036354 | 0.075127 | 58.0669 | 34.296 | 9.7924e-05 | -4.7049e-13 | -1.2738e-13 | -0.00010432 | 2.3472e-10 | 1.5534e-10 | -0.017303 | -4.2102e-13 | 6.1729e-13 | 0.098707 | -1.5134e-10 | -5.2102e-11
Line_1 | 0.0010034 | 2.7037 | 1.7478 | 0.0032531 | 0.0032531 | 0.0032531 | 0.011586 | 31.2198 | 20.1814 | 0.037563 | 0.037564 | 0.037563 | 0.00014073 | 9.2871e-11 | 7.1866e-11 | 5.216e-05 | -7.5139e-14 | -1.0354e-13 | 0.01618 | -6.5338e-11 | -1.0982e-11 | -0.049353 | -1.643e-13 | 1.4657e-13
Line_2 | 0.0010034 | 2.7037 | 1.7478 | 0.0032531 | 0.0032531 | 0.0032531 | 0.011586 | 31.2198 | 20.1814 | 0.037563 | 0.037564 | 0.037563 | 0.00014073 | 9.2868e-11 | 7.1867e-11 | 5.216e-05 | -7.5139e-14 | -1.0354e-13 | 0.01618 | -6.5338e-11 | -1.098e-11 | -0.049353 | -1.643e-13 | 1.4657e-13
Line_4 | 0.0010034 | 1.3522 | 0.87281 | 0.0010034 | 1.3522 | 0.87281 | 0.011586 | 15.6136 | 10.0783 | 0.011586 | 15.6136 | 10.0783 | -0.00014073 | 4.6411e-11 | 3.5895e-11 | -0.00014073 | 4.6409e-11 | 3.5896e-11 | -0.01618 | -3.2727e-11 | -5.4407e-12 | -0.01618 | -3.2727e-11 | -5.4398e-12

## LLG_max_fault
name | pf_ikss_a_ka | pf_ikss_b_ka | pf_ikss_c_ka | pf_skss_a_mw | pf_skss_b_mw | pf_skss_c_mw | pf_rk0_ohm | pf_xk0_ohm | pf_rk1_ohm | pf_xk1_ohm | pf_rk2_ohm | pf_xk2_ohm | pf_vm_a_pu | pf_vm_b_pu | pf_vm_c_pu | pf_va_a_degree | pf_va_b_degree | pf_va_c_degree
Bus_0 | 0 | 3.618 | 3.618 | 0 | 229.7713 | 229.7713 | 1.3244 | 13.2439 | 1.3244 | 13.2439 | 1.3244 | 13.2439 | 0.83784 | 0.40283 | 0.69184 | 8.9575 | -115.8808 | 160.4095
Bus_1 | 0 | 1.5267 | 1.4167 | 0 | 17.6284 | 16.3587 | 2.133e-06 | 0.46831 | 0.10773 | 2.3084 | 0.10773 | 2.3084 | 1.025 | 0.87234 | 0.93763 | 21.3765 | -100.051 | 148.8263
Bus_2 | 0 | 1.3831 | 1.1759 | 0 | 15.9706 | 13.5777 | 3.7165 | 1.9229 | 0.62773 | 2.8984 | 0.62773 | 2.8984 | 1.0065 | 0.80202 | 0.92704 | 20.0477 | -99.5297 | 151.2487
Bus_3 | 0 | 1.2983 | 1.0751 | 0 | 14.9918 | 12.4146 | 6.1931 | 2.8908 | 0.9744 | 3.2918 | 0.9744 | 3.2918 | 0.99548 | 0.76108 | 0.92127 | 19.2072 | -99.2264 | 152.6164
Bus_4 | 0 | 1.2983 | 1.0751 | 0 | 14.9918 | 12.4146 | 6.1931 | 2.8908 | 0.9744 | 3.2918 | 0.9744 | 3.2918 | 0.99548 | 0.76108 | 0.92127 | 19.2072 | -99.2264 | 152.6164

## LLG_max_fault_branch
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mw | pf_q_b_from_mw | pf_q_c_from_mw | pf_q_a_to_mw | pf_q_b_to_mw | pf_q_c_to_mw
Line_0 | 0.00043153 | 0.00043153 | 0.00043153 | 0.0021574 | 1.3821 | 1.178 | 0.0049829 | 0.0049829 | 0.0049829 | 0.024911 | 15.9596 | 13.6023 | -0.0034493 | -0.00072659 | 0.0041777 | -0.0055884 | -9.5447 | -6.9276 | -0.0038155 | 0.0046014 | -0.001111 | 0.028325 | -9.5715 | -6.9239
Line_1 | 0.00043562 | 0.86535 | 0.71719 | 0.0010787 | 0.0010787 | 0.0010787 | 0.0050301 | 9.9922 | 8.2813 | 0.012456 | 0.012456 | 0.012456 | -0.0010256 | -5.6151 | -3.8559 | 0.0027942 | -0.0099901 | 0.0072017 | 0.0060242 | -5.62 | -3.8549 | -0.014162 | 0.00339 | 0.0053458
Line_2 | 0.00043562 | 0.86535 | 0.71719 | 0.0010787 | 0.0010787 | 0.0010787 | 0.0050301 | 9.9922 | 8.2813 | 0.012456 | 0.012456 | 0.012456 | -0.0010256 | -5.6151 | -3.8559 | 0.0027942 | -0.0099901 | 0.0072017 | 0.0060242 | -5.62 | -3.8549 | -0.014162 | 0.00339 | 0.0053458
Line_4 | 0.00043562 | 0.43298 | 0.35795 | 0.00043562 | 0.43298 | 0.35795 | 0.0050301 | 4.9996 | 4.1333 | 0.0050301 | 4.9996 | 4.1333 | 0.0010256 | -2.8133 | -1.9238 | 0.0010256 | -2.8133 | -1.9238 | -0.0060242 | -2.8083 | -1.9247 | -0.0060242 | -2.8083 | -1.9247

## LLG_min
name | pf_ikss_a_ka | pf_ikss_b_ka | pf_ikss_c_ka | pf_skss_a_mw | pf_skss_b_mw | pf_skss_c_mw | pf_rk0_ohm | pf_xk0_ohm | pf_rk1_ohm | pf_xk1_ohm | pf_rk2_ohm | pf_xk2_ohm | pf_vm_a_pu | pf_vm_b_pu | pf_vm_c_pu | pf_va_a_degree | pf_va_b_degree | pf_va_c_degree
Bus_0 | 0 | 4.1989 | 4.1989 | 0 | 266.6667 | 266.6667 | 1.505 | 15.0499 | 1.505 | 15.0499 | 1.505 | 15.0499 | 0.57735 | 0 | 0.57735 | -5.8129e-09 | 0 | 180
Bus_1 | 0 | 6.5411 | 6.6283 | 0 | 75.5298 | 76.5371 | 4.309e-06 | 0.4804 | 0.11535 | 2.4164 | 0.11535 | 2.4164 | 0.24624 | 0 | 0.24624 | 1.9559 | 0 | -178.0441
Bus_2 | 0 | 3.9256 | 2.4842 | 0 | 45.3291 | 28.6851 | 7.1352 | 1.8795 | 1.1138 | 3.0064 | 1.1138 | 3.0064 | 0.76045 | 0 | 0.76045 | -8.981 | 0 | 171.019
Bus_3 | 0 | 3.0772 | 2.2205 | 0 | 35.533 | 25.6396 | 11.89 | 2.8069 | 1.7794 | 3.3997 | 1.7794 | 3.3997 | 0.78076 | 0 | 0.78076 | -6.1425 | 0 | 173.8575
Bus_4 | 0 | 3.0772 | 2.2205 | 0 | 35.533 | 25.6396 | 11.89 | 2.8069 | 1.7794 | 3.3997 | 1.7794 | 3.3997 | 0.78076 | 0 | 0.78076 | -6.1425 | 0 | 173.8575

## LLG_min_branch
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mw | pf_q_b_from_mw | pf_q_c_from_mw | pf_q_a_to_mw | pf_q_b_to_mw | pf_q_c_to_mw
Line_0 | 0.0028209 | 0.0028209 | 0.0028209 | 0.0065223 | 3.9235 | 2.4889 | 0.032573 | 0.032573 | 0.032573 | 0.075313 | 45.3048 | 28.7395 | 0.00015094 | -8.4152e-14 | 2.8755e-13 | -0.00020129 | -1.6969e-10 | -2.579e-11 | -0.013891 | 2.815e-13 | -6.8382e-14 | 0.099197 | -1.9371e-10 | -1.6144e-10
Line_1 | 0.00096864 | 2.0511 | 1.481 | 0.0032612 | 0.0032612 | 0.0032612 | 0.011185 | 23.684 | 17.1011 | 0.037657 | 0.037657 | 0.037657 | 6.549e-05 | -1.0595e-10 | -1.6122e-11 | 0.00010064 | -1.9789e-13 | 1.7058e-13 | 0.015125 | -9.6707e-11 | -1.0236e-10 | -0.049599 | 8.1582e-14 | 1.2958e-13
Line_2 | 0.00096864 | 2.0511 | 1.481 | 0.0032612 | 0.0032612 | 0.0032612 | 0.011185 | 23.684 | 17.1011 | 0.037657 | 0.037657 | 0.037657 | 6.549e-05 | -1.0596e-10 | -1.6112e-11 | 0.00010064 | -1.9789e-13 | 1.7058e-13 | 0.015125 | -9.6727e-11 | -1.0235e-10 | -0.049599 | 8.1582e-14 | 1.2958e-13
Line_4 | 0.00096864 | 1.0262 | 0.73946 | 0.00096864 | 1.0262 | 0.73946 | 0.011185 | 11.849 | 8.5385 | 0.011185 | 11.849 | 8.5385 | -6.5492e-05 | -5.3071e-11 | -7.9797e-12 | -6.5492e-05 | -5.3075e-11 | -7.9745e-12 | -0.015125 | -4.8314e-11 | -5.1118e-11 | -0.015125 | -4.8324e-11 | -5.1112e-11

## LLG_min_fault
name | pf_ikss_a_ka | pf_ikss_b_ka | pf_ikss_c_ka | pf_skss_a_mw | pf_skss_b_mw | pf_skss_c_mw | pf_rk0_ohm | pf_xk0_ohm | pf_rk1_ohm | pf_xk1_ohm | pf_rk2_ohm | pf_xk2_ohm | pf_vm_a_pu | pf_vm_b_pu | pf_vm_c_pu | pf_va_a_degree | pf_va_b_degree | pf_va_c_degree
Bus_0 | 0 | 3.0129 | 3.0129 | 0 | 191.3457 | 191.3457 | 1.505 | 15.0499 | 1.505 | 15.0499 | 1.505 | 15.0499 | 0.7473 | 0.33546 | 0.61843 | 8.1092 | -117.0249 | 161.7746
Bus_1 | 0 | 1.3778 | 1.2749 | 0 | 15.9091 | 14.7216 | 4.309e-06 | 0.4804 | 0.11535 | 2.4164 | 0.11535 | 2.4164 | 0.92823 | 0.78485 | 0.84697 | 21.0464 | -100.4046 | 148.8124
Bus_2 | 0 | 1.2122 | 0.96482 | 0 | 13.9974 | 11.1408 | 7.1352 | 1.8795 | 1.1138 | 3.0064 | 1.1138 | 3.0064 | 0.90453 | 0.70193 | 0.85207 | 19.7902 | -97.6343 | 152.8016
Bus_3 | 0 | 1.1097 | 0.86904 | 0 | 12.8132 | 10.0348 | 11.89 | 2.8069 | 1.7794 | 3.3997 | 1.7794 | 3.3997 | 0.88899 | 0.65508 | 0.85236 | 18.9434 | -96.0933 | 154.81
Bus_4 | 0 | 1.1097 | 0.86904 | 0 | 12.8132 | 10.0348 | 11.89 | 2.8069 | 1.7794 | 3.3997 | 1.7794 | 3.3997 | 0.88899 | 0.65508 | 0.85236 | 18.9434 | -96.0933 | 154.81

## LLG_min_fault_branch
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mw | pf_q_b_from_mw | pf_q_c_from_mw | pf_q_a_to_mw | pf_q_b_to_mw | pf_q_c_to_mw
Line_0 | 0.0004006 | 0.0004006 | 0.0004006 | 0.0029328 | 1.2105 | 0.96775 | 0.0046257 | 0.0046257 | 0.0046257 | 0.033865 | 13.9771 | 11.1746 | -0.0028811 | -0.00061158 | 0.0034957 | -0.0097551 | -7.3224 | -4.6696 | -0.0032277 | 0.0038545 | -0.00090699 | 0.036642 | -7.3508 | -4.6675
Line_1 | 0.00055695 | 0.73943 | 0.57991 | 0.0014664 | 0.0014664 | 0.0014664 | 0.0064312 | 8.5382 | 6.6962 | 0.016932 | 0.016932 | 0.016932 | -0.0014893 | -4.1001 | -2.5203 | 0.0048776 | -0.012444 | 0.0075867 | 0.0074692 | -4.105 | -2.5194 | -0.018321 | 0.0017713 | 0.0065212
Line_2 | 0.00055695 | 0.73943 | 0.57991 | 0.0014664 | 0.0014664 | 0.0014664 | 0.0064312 | 8.5382 | 6.6962 | 0.016932 | 0.016932 | 0.016932 | -0.0014893 | -4.1001 | -2.5203 | 0.0048776 | -0.012444 | 0.0075867 | 0.0074692 | -4.105 | -2.5194 | -0.018321 | 0.0017713 | 0.0065212
Line_4 | 0.00055695 | 0.37023 | 0.28913 | 0.00055695 | 0.37023 | 0.28913 | 0.0064312 | 4.275 | 3.3386 | 0.0064312 | 4.275 | 3.3386 | 0.0014893 | -2.0566 | -1.2559 | 0.0014893 | -2.0566 | -1.2559 | -0.0074692 | -2.0517 | -1.2568 | -0.0074692 | -2.0517 | -1.2568

## LG_max
name | pf_ikss_a_ka | pf_ikss_b_ka | pf_ikss_c_ka | pf_skss_a_mw | pf_skss_b_mw | pf_skss_c_mw | pf_rk0_ohm | pf_xk0_ohm | pf_rk1_ohm | pf_xk1_ohm | pf_rk2_ohm | pf_xk2_ohm | pf_vm_a_pu | pf_vm_b_pu | pf_vm_c_pu | pf_va_a_degree | pf_va_b_degree | pf_va_c_degree
Bus_0 | 5.2486 | 0 | 0 | 333.3334 | 0 | 0 | 1.3244 | 13.2439 | 1.3244 | 13.2439 | 1.3244 | 13.2439 | 0.63509 | 1.1 | 0.63509 | 60 | -90 | 120
Bus_1 | 7.4866 | 0 | 0 | 86.4483 | 0 | 0 | 2.133e-06 | 0.46831 | 0.10773 | 2.3084 | 0.10773 | 2.3084 | 0.56059 | 1.1 | 0.55326 | 81.0128 | -90 | 99.1072
Bus_2 | 4.1498 | 0 | 0 | 47.918 | 0 | 0 | 3.7165 | 1.9229 | 0.62773 | 2.8984 | 0.62773 | 2.8984 | 0.5032 | 1.1 | 0.85364 | 41.566 | -90 | 116.1703
Bus_3 | 3.0503 | 0 | 0 | 35.222 | 0 | 0 | 6.1931 | 2.8908 | 0.9744 | 3.2918 | 0.9744 | 3.2918 | 0.58154 | 1.1 | 0.90005 | 35.2335 | -90 | 121.8536
Bus_4 | 3.0503 | 0 | 0 | 35.222 | 0 | 0 | 6.1931 | 2.8908 | 0.9744 | 3.2918 | 0.9744 | 3.2918 | 0.58154 | 1.1 | 0.90005 | 35.2335 | -90 | 121.8536

## LG_max_branch
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mw | pf_q_b_from_mw | pf_q_c_from_mw | pf_q_a_to_mw | pf_q_b_to_mw | pf_q_c_to_mw
Line_0 | 0.0020084 | 0.0020084 | 0.0020084 | 4.1532 | 0.0074469 | 0.0074469 | 0.023191 | 0.023191 | 0.023191 | 47.9575 | 0.085989 | 0.085989 | -4.7143e-13 | 0.022097 | -0.022057 | 3.0921e-10 | -0.071067 | 0.07093 | 1.6603e-13 | -0.0043309 | -0.0027105 | -3.6806e-10 | 0.023799 | 0.10552
Line_1 | 2.0341 | 0.0012972 | 0.0012972 | 0.0037234 | 0.0037234 | 0.0037234 | 23.4878 | 0.014979 | 0.014979 | 0.042995 | 0.042995 | 0.042995 | 8.2803e-11 | -0.012938 | 0.013173 | -4.2051e-13 | 0.035533 | -0.035465 | -1.3199e-10 | 0.007762 | 0.019281 | -9.4343e-14 | -0.011899 | -0.052758
Line_2 | 2.0341 | 0.0012972 | 0.0012972 | 0.0037234 | 0.0037234 | 0.0037234 | 23.4878 | 0.014979 | 0.014979 | 0.042995 | 0.042995 | 0.042995 | 8.2805e-11 | -0.012938 | 0.013173 | -4.2051e-13 | 0.035533 | -0.035465 | -1.3197e-10 | 0.007762 | 0.019281 | -9.4343e-14 | -0.011899 | -0.052758
Line_4 | 1.0162 | 0.0012972 | 0.0012972 | 1.0162 | 0.0012972 | 0.0012972 | 11.7342 | 0.014979 | 0.014979 | 11.7342 | 0.014979 | 0.014979 | 4.1254e-11 | 0.012938 | -0.013173 | 4.1254e-11 | 0.012938 | -0.013173 | -6.601e-11 | -0.007762 | -0.019281 | -6.6004e-11 | -0.007762 | -0.019281

## LG_max_fault
name | pf_ikss_a_ka | pf_ikss_b_ka | pf_ikss_c_ka | pf_skss_a_mw | pf_skss_b_mw | pf_skss_c_mw | pf_rk0_ohm | pf_xk0_ohm | pf_rk1_ohm | pf_xk1_ohm | pf_rk2_ohm | pf_xk2_ohm | pf_vm_a_pu | pf_vm_b_pu | pf_vm_c_pu | pf_va_a_degree | pf_va_b_degree | pf_va_c_degree
Bus_0 | 3.618 | 0 | 0 | 229.7713 | 0 | 0 | 1.3244 | 13.2439 | 1.3244 | 13.2439 | 1.3244 | 13.2439 | 0.69184 | 1.1 | 0.83784 | 40.4095 | -90 | 128.9575
Bus_1 | 1.5122 | 0 | 0 | 17.4619 | 0 | 0 | 2.133e-06 | 0.46831 | 0.10773 | 2.3084 | 0.10773 | 2.3084 | 0.9259 | 1.1 | 1.0368 | 29.1566 | -90 | 141.252
Bus_2 | 1.2597 | 0 | 0 | 14.5454 | 0 | 0 | 3.7165 | 1.9229 | 0.62773 | 2.8984 | 0.62773 | 2.8984 | 0.91324 | 1.1 | 1.0168 | 30.1847 | -90 | 140.931
Bus_3 | 1.1313 | 0 | 0 | 13.063 | 0 | 0 | 6.1931 | 2.8908 | 0.9744 | 3.2918 | 0.9744 | 3.2918 | 0.90616 | 1.1 | 1.0072 | 30.6623 | -90 | 140.7048
Bus_4 | 1.1313 | 0 | 0 | 13.063 | 0 | 0 | 6.1931 | 2.8908 | 0.9744 | 3.2918 | 0.9744 | 3.2918 | 0.90616 | 1.1 | 1.0072 | 30.6623 | -90 | 140.7048

## LG_max_fault_branch
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mw | pf_q_b_from_mw | pf_q_c_from_mw | pf_q_a_to_mw | pf_q_b_to_mw | pf_q_c_to_mw
Line_0 | 0.00040568 | 0.00040568 | 0.00040568 | 1.2607 | 0.0022605 | 0.0022605 | 0.0046844 | 0.0046844 | 0.0046844 | 14.5574 | 0.026102 | 0.026102 | 0.00305 | 0.0020481 | -0.0050964 | -7.9277 | -0.026221 | 0.020086 | 0.0030847 | -0.0043604 | 0.00098841 | -7.953 | 0.0064811 | 0.024615
Line_1 | 0.7544 | 0.00048111 | 0.00048111 | 0.0011302 | 0.0011302 | 0.0011302 | 8.711 | 0.0055553 | 0.0055553 | 0.013051 | 0.013051 | 0.013051 | -4.2647 | -0.0055634 | 0.0043124 | -0.0030613 | 0.01311 | -0.010043 | -4.2697 | 0.0017703 | 0.0055777 | 0.0095906 | -0.0032405 | -0.012308
Line_2 | 0.7544 | 0.00048111 | 0.00048111 | 0.0011302 | 0.0011302 | 0.0011302 | 8.711 | 0.0055553 | 0.0055553 | 0.013051 | 0.013051 | 0.013051 | -4.2647 | -0.0055634 | 0.0043124 | -0.0030613 | 0.01311 | -0.010043 | -4.2697 | 0.0017703 | 0.0055777 | 0.0095906 | -0.0032405 | -0.012308
Line_4 | 0.37689 | 0.00048111 | 0.00048111 | 0.37689 | 0.00048111 | 0.00048111 | 4.3519 | 0.0055553 | 0.0055553 | 4.3519 | 0.0055553 | 0.0055553 | -2.1343 | 0.0055634 | -0.0043124 | -2.1343 | 0.0055634 | -0.0043124 | -2.1294 | -0.0017703 | -0.0055777 | -2.1294 | -0.0017703 | -0.0055777

## LG_min
name | pf_ikss_a_ka | pf_ikss_b_ka | pf_ikss_c_ka | pf_skss_a_mw | pf_skss_b_mw | pf_skss_c_mw | pf_rk0_ohm | pf_xk0_ohm | pf_rk1_ohm | pf_xk1_ohm | pf_rk2_ohm | pf_xk2_ohm | pf_vm_a_pu | pf_vm_b_pu | pf_vm_c_pu | pf_va_a_degree | pf_va_b_degree | pf_va_c_degree
Bus_0 | 4.1989 | 0 | 0 | 266.6667 | 0 | 0 | 1.505 | 15.0499 | 1.505 | 15.0499 | 1.505 | 15.0499 | 0.57735 | 1 | 0.57735 | 60 | -90 | 120
Bus_1 | 6.5137 | 0 | 0 | 75.2134 | 0 | 0 | 4.309e-06 | 0.4804 | 0.11535 | 2.4164 | 0.11535 | 2.4164 | 0.50942 | 1 | 0.50272 | 81.1749 | -90 | 98.9437
Bus_2 | 2.8289 | 0 | 0 | 32.6655 | 0 | 0 | 7.1352 | 1.8795 | 1.1138 | 3.0064 | 1.1138 | 3.0064 | 0.54654 | 1 | 0.86366 | 30.3792 | -90 | 123.0883
Bus_3 | 1.9042 | 0 | 0 | 21.9879 | 0 | 0 | 11.89 | 2.8069 | 1.7794 | 3.3997 | 1.7794 | 3.3997 | 0.63468 | 1 | 0.87958 | 29.7127 | -90 | 128.8071
Bus_4 | 1.9042 | 0 | 0 | 21.9879 | 0 | 0 | 11.89 | 2.8069 | 1.7794 | 3.3997 | 1.7794 | 3.3997 | 0.63468 | 1 | 0.87958 | 29.7127 | -90 | 128.8071

## LG_min_branch
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mw | pf_q_b_from_mw | pf_q_c_from_mw | pf_q_a_to_mw | pf_q_b_to_mw | pf_q_c_to_mw
Line_0 | 0.0017924 | 0.0017924 | 0.0017924 | 2.8312 | 0.0089515 | 0.0089515 | 0.020697 | 0.020697 | 0.020697 | 32.6918 | 0.10336 | 0.10336 | 1.6703e-13 | 0.017945 | -0.017884 | -9.7469e-11 | -0.080992 | 0.080613 | 1.447e-13 | -0.0033869 | -0.0022214 | 1.259e-11 | 0.054903 | 0.13194
Line_1 | 1.2698 | 0.0014431 | 0.0014431 | 0.0044758 | 0.0044758 | 0.0044758 | 14.6625 | 0.016663 | 0.016663 | 0.051682 | 0.051682 | 0.051682 | -2.3441e-11 | -0.013625 | 0.01377 | 5.8644e-14 | 0.040496 | -0.040307 | 6.7207e-12 | 0.012244 | 0.021327 | 1.4387e-13 | -0.027452 | -0.065972
Line_2 | 1.2698 | 0.0014431 | 0.0014431 | 0.0044758 | 0.0044758 | 0.0044758 | 14.6625 | 0.016663 | 0.016663 | 0.051682 | 0.051682 | 0.051682 | -2.3436e-11 | -0.013625 | 0.01377 | 5.8644e-14 | 0.040496 | -0.040307 | 6.726e-12 | 0.012244 | 0.021327 | 1.4387e-13 | -0.027452 | -0.065972
Line_4 | 0.6344 | 0.0014431 | 0.0014431 | 0.6344 | 0.0014431 | 0.0014431 | 7.3254 | 0.016663 | 0.016663 | 7.3254 | 0.016663 | 0.016663 | -1.17e-11 | 0.013625 | -0.01377 | -1.1698e-11 | 0.013625 | -0.01377 | 3.3965e-12 | -0.012244 | -0.021327 | 3.3991e-12 | -0.012244 | -0.021327

## LG_min_fault
name | pf_ikss_a_ka | pf_ikss_b_ka | pf_ikss_c_ka | pf_skss_a_mw | pf_skss_b_mw | pf_skss_c_mw | pf_rk0_ohm | pf_xk0_ohm | pf_rk1_ohm | pf_xk1_ohm | pf_rk2_ohm | pf_xk2_ohm | pf_vm_a_pu | pf_vm_b_pu | pf_vm_c_pu | pf_va_a_degree | pf_va_b_degree | pf_va_c_degree
Bus_0 | 3.0129 | 0 | 0 | 191.3457 | 0 | 0 | 1.505 | 15.0499 | 1.505 | 15.0499 | 1.505 | 15.0499 | 0.61843 | 1 | 0.7473 | 41.7746 | -90 | 128.1092
Bus_1 | 1.3644 | 0 | 0 | 15.7549 | 0 | 0 | 4.309e-06 | 0.4804 | 0.11535 | 2.4164 | 0.11535 | 2.4164 | 0.83548 | 1 | 0.93979 | 29.185 | -90 | 140.9086
Bus_2 | 1.0362 | 0 | 0 | 11.9651 | 0 | 0 | 7.1352 | 1.8795 | 1.1138 | 3.0064 | 1.1138 | 3.0064 | 0.83427 | 1 | 0.9187 | 30.7055 | -90 | 141.3329
Bus_3 | 0.88487 | 0 | 0 | 10.2175 | 0 | 0 | 11.89 | 2.8069 | 1.7794 | 3.3997 | 1.7794 | 3.3997 | 0.83157 | 1 | 0.90913 | 31.3383 | -90 | 141.3744
Bus_4 | 0.88487 | 0 | 0 | 10.2175 | 0 | 0 | 11.89 | 2.8069 | 1.7794 | 3.3997 | 1.7794 | 3.3997 | 0.83157 | 1 | 0.90913 | 31.3383 | -90 | 141.3744

## LG_min_fault_branch
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mw | pf_q_b_from_mw | pf_q_c_from_mw | pf_q_a_to_mw | pf_q_b_to_mw | pf_q_c_to_mw
Line_0 | 0.00037545 | 0.00037545 | 0.00037545 | 1.037 | 0.0032789 | 0.0032789 | 0.0043353 | 0.0043353 | 0.0043353 | 11.9748 | 0.037861 | 0.037861 | 0.0025333 | 0.0017629 | -0.0042935 | -5.3565 | -0.034891 | 0.022698 | 0.002589 | -0.003637 | 0.00080194 | -5.3894 | 0.0072158 | 0.038584
Line_1 | 0.59007 | 0.00067058 | 0.00067058 | 0.0016394 | 0.0016394 | 0.0016394 | 6.8135 | 0.0077432 | 0.0077432 | 0.018931 | 0.018931 | 0.018931 | -2.6078 | -0.0071365 | 0.0049775 | -0.0060712 | 0.017445 | -0.011349 | -2.6135 | 0.0025362 | 0.0082914 | 0.010365 | -0.0036079 | -0.019292
Line_2 | 0.59007 | 0.00067058 | 0.00067058 | 0.0016394 | 0.0016394 | 0.0016394 | 6.8135 | 0.0077432 | 0.0077432 | 0.018931 | 0.018931 | 0.018931 | -2.6078 | -0.0071365 | 0.0049775 | -0.0060712 | 0.017445 | -0.011349 | -2.6135 | 0.0025362 | 0.0082914 | 0.010365 | -0.0036079 | -0.019292
Line_4 | 0.2948 | 0.00067058 | 0.00067058 | 0.2948 | 0.00067058 | 0.00067058 | 3.404 | 0.0077432 | 0.0077432 | 3.404 | 0.0077432 | 0.0077432 | -1.3072 | 0.0071365 | -0.0049775 | -1.3072 | 0.0071365 | -0.0049775 | -1.3014 | -0.0025362 | -0.0082914 | -1.3014 | -0.0025362 | -0.0082914