## LLL_max_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0 | 2.5104 | 0 | 5.5724 | 0 | 86.9625 | -1.9117e-19 | -1e-07 | -1.6603e-21 | -1e-07 | -79.0878 | 100.9122 | 0 | 0 | 84.2894 | 79.0878
Line_1 | 0 | 2.2085 | 0 | 4.5643 | 0 | 76.5048 | -5.4633e-20 | -1e-07 | -3.9589e-22 | -1e-07 | -75.1106 | 104.8894 | 0 | 0 | 79.0878 | 75.1106
Line_2 | 0 | 2.2085 | 0 | 4.5643 | 0 | 76.5048 | -5.4632e-20 | -1e-07 | -3.9588e-22 | -1e-07 | -75.1106 | 104.8894 | 0 | 0 | 79.0878 | 75.1106

## LLL_max_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0 | 2.5104 | 0 | 5.5724 | 0 | 86.9625 | -1.9117e-19 | -1e-07 | -1.6603e-21 | -1e-07 | -79.0878 | 100.9122 | 0 | 0 | 84.2894 | 79.0878
Line_1 | 0 | 2.2085 | 0 | 4.5643 | 0 | 76.5048 | -5.4633e-20 | -1e-07 | -3.9589e-22 | -1e-07 | -75.1106 | 104.8894 | 0 | 0 | 79.0878 | 75.1106
Line_2 | 0 | 2.2085 | 0 | 4.5643 | 0 | 76.5048 | -5.4632e-20 | -1e-07 | -3.9588e-22 | -1e-07 | -75.1106 | 104.8894 | 0 | 0 | 79.0878 | 75.1106

## LLL_max_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0 | 1.0938 | 0 | 2.4279 | 0 | 37.8888 | -8.1816e-09 | -17.9446 | 6.694e-09 | -17.9446 | -59.1339 | 120.8661 | 0.7175 | 0.66979 | 45 | 45
Line_1 | 0 | 1.0254 | 0 | 2.1192 | 0 | 35.5212 | -2.9243e-09 | -15.772 | 1.979e-09 | -15.772 | -58.4694 | 121.5306 | 0.66979 | 0.62793 | 45 | 45
Line_2 | 0 | 1.0254 | 0 | 2.1192 | 0 | 35.5212 | -2.9243e-09 | -15.772 | 1.979e-09 | -15.772 | -58.4694 | 121.5306 | 0.66979 | 0.62793 | 45 | 45

## LLL_max_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0 | 1.0938 | 0 | 2.4279 | 0 | 37.8888 | -8.1816e-09 | -17.9446 | 6.694e-09 | -17.9446 | -59.1339 | 120.8661 | 0.7175 | 0.66979 | 45 | 45
Line_1 | 0 | 1.0254 | 0 | 2.1192 | 0 | 35.5212 | -2.9243e-09 | -15.772 | 1.979e-09 | -15.772 | -58.4694 | 121.5306 | 0.66979 | 0.62793 | 45 | 45
Line_2 | 0 | 1.0254 | 0 | 2.1192 | 0 | 35.5212 | -2.9243e-09 | -15.772 | 1.979e-09 | -15.772 | -58.4694 | 121.5306 | 0.66979 | 0.62793 | 45 | 45

## LLL_min_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0 | 2.0037 | 0 | 4.1302 | 0 | 69.4115 | 8.7469e-20 | -1e-07 | -1.3401e-19 | -1e-07 | -74.9546 | 105.0454 | 0 | 0 | 84.2894 | 74.9546
Line_1 | 0 | 1.7386 | 0 | 3.2224 | 0 | 60.2284 | 2.4608e-20 | -1e-07 | -3.7514e-20 | -1e-07 | -67.9403 | 112.0597 | 0 | 0 | 74.9546 | 67.9403
Line_2 | 0 | 1.7386 | 0 | 3.2224 | 0 | 60.2284 | 2.4608e-20 | -1e-07 | -3.7514e-20 | -1e-07 | -67.9403 | 112.0597 | 0 | 0 | 74.9546 | 67.9403

## LLL_min_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0 | 2.0037 | 0 | 4.1302 | 0 | 69.4115 | 8.7469e-20 | -1e-07 | -1.3401e-19 | -1e-07 | -74.9546 | 105.0454 | 0 | 0 | 84.2894 | 74.9546
Line_1 | 0 | 1.7386 | 0 | 3.2224 | 0 | 60.2284 | 2.4608e-20 | -1e-07 | -3.7514e-20 | -1e-07 | -67.9403 | 112.0597 | 0 | 0 | 74.9546 | 67.9403
Line_2 | 0 | 1.7386 | 0 | 3.2224 | 0 | 60.2284 | 2.4608e-20 | -1e-07 | -3.7514e-20 | -1e-07 | -67.9403 | 112.0597 | 0 | 0 | 74.9546 | 67.9403

## LLL_min_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0 | 0.93103 | 0 | 1.9191 | 0 | 32.2518 | -6.9607e-09 | -13.0022 | 5.6951e-09 | -13.0022 | -58.4151 | 121.5849 | 0.62083 | 0.57014 | 45 | 45
Line_1 | 0 | 0.85923 | 0 | 1.5925 | 0 | 29.7644 | -2.5248e-09 | -11.074 | 1.455e-09 | -11.074 | -56.1059 | 123.8941 | 0.57014 | 0.52617 | 45 | 45
Line_2 | 0 | 0.85923 | 0 | 1.5925 | 0 | 29.7644 | -2.5248e-09 | -11.074 | 1.455e-09 | -11.074 | -56.1059 | 123.8941 | 0.57014 | 0.52617 | 45 | 45

## LLL_min_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0 | 0.93103 | 0 | 1.9191 | 0 | 32.2518 | -6.9607e-09 | -13.0022 | 5.6951e-09 | -13.0022 | -58.4151 | 121.5849 | 0.62083 | 0.57014 | 45 | 45
Line_1 | 0 | 0.85923 | 0 | 1.5925 | 0 | 29.7644 | -2.5248e-09 | -11.074 | 1.455e-09 | -11.074 | -56.1059 | 123.8941 | 0.57014 | 0.52617 | 45 | 45
Line_2 | 0 | 0.85923 | 0 | 1.5925 | 0 | 29.7644 | -2.5248e-09 | -11.074 | 1.455e-09 | -11.074 | -56.1059 | 123.8941 | 0.57014 | 0.52617 | 45 | 45

## LL_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 0 | 0 | 0 | 2.1741 | 2.1741 | 0 | 0 | 0 | 0 | 25.1039 | 25.1039 | -2.0843e-14 | -5.2106e-15 | 4.6896e-14 | 1.0421e-14 | -13.5575 | 13.5575 | 5.2106e-15 | 5.7634e-09 | -5.7634e-09 | -1.0421e-14 | 2.6138 | -2.6138 | 0 | -169.0878 | 10.9122 | 0 | 10.9122 | -169.0878 | 0.95263 | 0 | 0.95263 | 0.95263 | 0 | 0.95263 | -6.29e-13 | 0 | 180 | -4.8524e-13 | 0 | 180
Line_1 | 0 | 0 | 0 | 0 | 1.9126 | 1.9126 | 0 | 0 | 0 | 0 | 22.085 | 22.085 | -1.0421e-14 | 1.8237e-14 | -1.1828e-22 | 1.0421e-14 | -11.7389 | 11.7389 | -1.19e-28 | 1.9211e-09 | -1.9212e-09 | -1.0421e-14 | 3.1212 | -3.1212 | 0 | -165.1106 | 14.8894 | 0 | 14.8894 | -165.1106 | 0.95263 | 0 | 0.95263 | 0.95263 | 0 | 0.95263 | -4.8524e-13 | 0 | 180 | -3.6437e-13 | 0 | 180
Line_2 | 0 | 0 | 0 | 0 | 1.9126 | 1.9126 | 0 | 0 | 0 | 0 | 22.085 | 22.085 | -1.0421e-14 | 2.3448e-14 | -1.1828e-22 | -5.2106e-15 | -11.7389 | 11.7389 | -1.19e-28 | 1.9211e-09 | -1.9211e-09 | -5.2024e-29 | 3.1212 | -3.1212 | 0 | -165.1106 | 14.8894 | 0 | 14.8894 | -165.1106 | 0.95263 | 0 | 0.95263 | 0.95263 | 0 | 0.95263 | -4.8524e-13 | 0 | 180 | -3.5884e-13 | 0 | 180

## LL_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 0 | 0 | 0 | 2.1741 | 2.1741 | 0 | 0 | 0 | 0 | 25.1039 | 25.1039 | -2.0843e-14 | -5.2106e-15 | 4.6896e-14 | 1.0421e-14 | -13.5575 | 13.5575 | 5.2106e-15 | 5.7634e-09 | -5.7634e-09 | -1.0421e-14 | 2.6138 | -2.6138 | 0 | -169.0878 | 10.9122 | 0 | 10.9122 | -169.0878 | 0.95263 | 0 | 0.95263 | 0.95263 | 0 | 0.95263 | -6.29e-13 | 0 | 180 | -4.8524e-13 | 0 | 180
Line_1 | 0 | 0 | 0 | 0 | 1.9126 | 1.9126 | 0 | 0 | 0 | 0 | 22.085 | 22.085 | -1.0421e-14 | 1.8237e-14 | -1.1828e-22 | 1.0421e-14 | -11.7389 | 11.7389 | -1.19e-28 | 1.9211e-09 | -1.9212e-09 | -1.0421e-14 | 3.1212 | -3.1212 | 0 | -165.1106 | 14.8894 | 0 | 14.8894 | -165.1106 | 0.95263 | 0 | 0.95263 | 0.95263 | 0 | 0.95263 | -4.8524e-13 | 0 | 180 | -3.6437e-13 | 0 | 180
Line_2 | 0 | 0 | 0 | 0 | 1.9126 | 1.9126 | 0 | 0 | 0 | 0 | 22.085 | 22.085 | -1.0421e-14 | 2.3448e-14 | -1.1828e-22 | -5.2106e-15 | -11.7389 | 11.7389 | -1.19e-28 | 1.9211e-09 | -1.9211e-09 | -5.2024e-29 | 3.1212 | -3.1212 | 0 | -165.1106 | 14.8894 | 0 | 14.8894 | -165.1106 | 0.95263 | 0 | 0.95263 | 0.95263 | 0 | 0.95263 | -4.8524e-13 | 0 | 180 | -3.5884e-13 | 0 | 180

## LL_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 0 | 0 | 0 | 1.3366 | 1.3366 | 0 | 0 | 0 | 0 | 15.4338 | 15.4338 | -7.816e-15 | -1.1336e-09 | -3.1634e-09 | 1.3027e-14 | -12.1692 | 3.2367 | -7.816e-15 | 4.993e-09 | -1.4772e-09 | -2.6053e-15 | -0.89974 | -8.0328 | 0 | -155.1555 | 24.8445 | 0 | 24.8445 | -155.1555 | 1.0769 | 0.51998 | 0.88914 | 1.0576 | 0.47256 | 0.89901 | 12.9473 | -111.8716 | 164.2548 | 12.1069 | -110.1555 | 165.716
Line_1 | 0 | 0 | 0 | 0 | 1.2241 | 1.2241 | 0 | 0 | 0 | 0 | 14.1342 | 14.1342 | 1.696e-29 | -4.4345e-10 | -1.0122e-09 | 7.816e-15 | -10.7166 | 3.225 | -2.6053e-15 | 1.6389e-09 | -6.538e-10 | 4.6824e-29 | -0.30477 | -7.1868 | 0 | -153.7273 | 26.2727 | 0 | 26.2727 | -153.7273 | 1.0576 | 0.47256 | 0.89901 | 1.0424 | 0.43277 | 0.90662 | 12.1069 | -110.1555 | 165.716 | 11.3374 | -108.7273 | 166.9361
Line_2 | 0 | 0 | 0 | 0 | 1.2241 | 1.2241 | 0 | 0 | 0 | 0 | 14.1342 | 14.1342 | -7.816e-15 | -4.4347e-10 | -1.0122e-09 | 2.6053e-15 | -10.7166 | 3.225 | 5.2106e-15 | 1.6389e-09 | -6.538e-10 | -2.6053e-15 | -0.30477 | -7.1868 | 0 | -153.7273 | 26.2727 | 0 | 26.2727 | -153.7273 | 1.0576 | 0.47256 | 0.89901 | 1.0424 | 0.43277 | 0.90662 | 12.1069 | -110.1555 | 165.716 | 11.3374 | -108.7273 | 166.9361

## LL_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 0 | 0 | 0 | 1.3366 | 1.3366 | 0 | 0 | 0 | 0 | 15.4338 | 15.4338 | -7.816e-15 | -1.1336e-09 | -3.1634e-09 | 1.3027e-14 | -12.1692 | 3.2367 | -7.816e-15 | 4.993e-09 | -1.4772e-09 | -2.6053e-15 | -0.89974 | -8.0328 | 0 | -155.1555 | 24.8445 | 0 | 24.8445 | -155.1555 | 1.0769 | 0.51998 | 0.88914 | 1.0576 | 0.47256 | 0.89901 | 12.9473 | -111.8716 | 164.2548 | 12.1069 | -110.1555 | 165.716
Line_1 | 0 | 0 | 0 | 0 | 1.2241 | 1.2241 | 0 | 0 | 0 | 0 | 14.1342 | 14.1342 | 1.696e-29 | -4.4345e-10 | -1.0122e-09 | 7.816e-15 | -10.7166 | 3.225 | -2.6053e-15 | 1.6389e-09 | -6.538e-10 | 4.6824e-29 | -0.30477 | -7.1868 | 0 | -153.7273 | 26.2727 | 0 | 26.2727 | -153.7273 | 1.0576 | 0.47256 | 0.89901 | 1.0424 | 0.43277 | 0.90662 | 12.1069 | -110.1555 | 165.716 | 11.3374 | -108.7273 | 166.9361
Line_2 | 0 | 0 | 0 | 0 | 1.2241 | 1.2241 | 0 | 0 | 0 | 0 | 14.1342 | 14.1342 | -7.816e-15 | -4.4347e-10 | -1.0122e-09 | 2.6053e-15 | -10.7166 | 3.225 | 5.2106e-15 | 1.6389e-09 | -6.538e-10 | -2.6053e-15 | -0.30477 | -7.1868 | 0 | -153.7273 | 26.2727 | 0 | 26.2727 | -153.7273 | 1.0576 | 0.47256 | 0.89901 | 1.0424 | 0.43277 | 0.90662 | 12.1069 | -110.1555 | 165.716 | 11.3374 | -108.7273 | 166.9361

## LL_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 0 | 0 | 0 | 1.7353 | 1.7353 | 0 | 0 | 0 | 0 | 20.0374 | 20.0374 | 2.3685e-15 | 2.3685e-15 | 1.1842e-14 | 2.3685e-15 | -9.6753 | 9.6753 | 1.4211e-14 | 4.7631e-09 | -4.7631e-09 | -1.4211e-14 | 2.6007 | -2.6007 | 0 | -164.9546 | 15.0454 | 0 | 15.0454 | -164.9546 | 0.86603 | 0 | 0.86603 | 0.86603 | 0 | 0.86603 | 7.4054e-12 | 0 | 180 | 1.7807e-11 | 0 | 180
Line_1 | 0 | 0 | 0 | 0 | 1.5057 | 1.5057 | 0 | 0 | 0 | 0 | 17.3865 | 17.3865 | 8.8366e-29 | 8.2897e-15 | 7.1054e-15 | 0 | -8.0568 | 8.0568 | -9.4739e-15 | 1.5877e-09 | -1.5877e-09 | 0 | 3.2649 | -3.2649 | 0 | -157.9403 | 22.0597 | 0 | 22.0597 | -157.9403 | 0.86603 | 0 | 0.86603 | 0.86603 | 0 | 0.86603 | 1.7807e-11 | 0 | 180 | 2.2636e-11 | 0 | 180
Line_2 | 0 | 0 | 0 | 0 | 1.5057 | 1.5057 | 0 | 0 | 0 | 0 | 17.3865 | 17.3865 | 2.3685e-15 | 3.5527e-15 | -1.6104e-21 | -3.5943e-29 | -8.0568 | 8.0568 | -9.4739e-15 | 1.5877e-09 | -1.5877e-09 | 4.737e-15 | 3.2649 | -3.2649 | 0 | -157.9403 | 22.0597 | 0 | 22.0597 | -157.9403 | 0.86603 | 0 | 0.86603 | 0.86603 | 0 | 0.86603 | 1.7807e-11 | 0 | 180 | 2.2639e-11 | 0 | 180

## LL_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 0 | 0 | 0 | 1.7353 | 1.7353 | 0 | 0 | 0 | 0 | 20.0374 | 20.0374 | 2.3685e-15 | 2.3685e-15 | 1.1842e-14 | 2.3685e-15 | -9.6753 | 9.6753 | 1.4211e-14 | 4.7631e-09 | -4.7631e-09 | -1.4211e-14 | 2.6007 | -2.6007 | 0 | -164.9546 | 15.0454 | 0 | 15.0454 | -164.9546 | 0.86603 | 0 | 0.86603 | 0.86603 | 0 | 0.86603 | 7.4054e-12 | 0 | 180 | 1.7807e-11 | 0 | 180
Line_1 | 0 | 0 | 0 | 0 | 1.5057 | 1.5057 | 0 | 0 | 0 | 0 | 17.3865 | 17.3865 | 8.8366e-29 | 8.2897e-15 | 7.1054e-15 | 0 | -8.0568 | 8.0568 | -9.4739e-15 | 1.5877e-09 | -1.5877e-09 | 0 | 3.2649 | -3.2649 | 0 | -157.9403 | 22.0597 | 0 | 22.0597 | -157.9403 | 0.86603 | 0 | 0.86603 | 0.86603 | 0 | 0.86603 | 1.7807e-11 | 0 | 180 | 2.2636e-11 | 0 | 180
Line_2 | 0 | 0 | 0 | 0 | 1.5057 | 1.5057 | 0 | 0 | 0 | 0 | 17.3865 | 17.3865 | 2.3685e-15 | 3.5527e-15 | -1.6104e-21 | -3.5943e-29 | -8.0568 | 8.0568 | -9.4739e-15 | 1.5877e-09 | -1.5877e-09 | 4.737e-15 | 3.2649 | -3.2649 | 0 | -157.9403 | 22.0597 | 0 | 22.0597 | -157.9403 | 0.86603 | 0 | 0.86603 | 0.86603 | 0 | 0.86603 | 1.7807e-11 | 0 | 180 | 2.2639e-11 | 0 | 180

## LL_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 0 | 0 | 0 | 1.111 | 1.111 | 0 | 0 | 0 | 0 | 12.8289 | 12.8289 | -8.6297e-29 | -9.1816e-10 | -2.5622e-09 | 2.3685e-15 | -8.8335 | 2.6618 | 1.1842e-14 | 4.2643e-09 | -1.4167e-09 | -4.737e-15 | -0.23817 | -5.9336 | 0 | -153.6438 | 26.3562 | 0 | 26.3562 | -153.6438 | 0.97347 | 0.43899 | 0.80543 | 0.94727 | 0.3928 | 0.82451 | 11.9655 | -113.1494 | 165.4884 | 11.3296 | -108.6438 | 166.9558
Line_1 | 0 | 0 | 0 | 0 | 1.0007 | 1.0007 | 0 | 0 | 0 | 0 | 11.5554 | 11.5554 | -2.3685e-15 | -3.9984e-10 | -7.9858e-10 | -1.1842e-15 | -7.5079 | 2.5007 | 7.1054e-15 | 1.3421e-09 | -6.5146e-10 | 7.1054e-15 | 0.38403 | -5.3913 | 0 | -150.0137 | 29.9863 | 0 | 29.9863 | -150.0137 | 0.94727 | 0.3928 | 0.82451 | 0.92772 | 0.35381 | 0.83781 | 11.3296 | -108.6438 | 166.9558 | 10.6132 | -105.0137 | 168.2323
Line_2 | 0 | 0 | 0 | 0 | 1.0007 | 1.0007 | 0 | 0 | 0 | 0 | 11.5554 | 11.5554 | 3.5527e-15 | -3.9984e-10 | -7.9859e-10 | 2.3685e-15 | -7.5079 | 2.5007 | -4.737e-15 | 1.3421e-09 | -6.5147e-10 | -4.737e-15 | 0.38403 | -5.3913 | 0 | -150.0137 | 29.9863 | 0 | 29.9863 | -150.0137 | 0.94727 | 0.3928 | 0.82451 | 0.92772 | 0.35381 | 0.83781 | 11.3296 | -108.6438 | 166.9558 | 10.6132 | -105.0137 | 168.2323

## LL_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 0 | 0 | 0 | 1.111 | 1.111 | 0 | 0 | 0 | 0 | 12.8289 | 12.8289 | -8.6297e-29 | -9.1816e-10 | -2.5622e-09 | 2.3685e-15 | -8.8335 | 2.6618 | 1.1842e-14 | 4.2643e-09 | -1.4167e-09 | -4.737e-15 | -0.23817 | -5.9336 | 0 | -153.6438 | 26.3562 | 0 | 26.3562 | -153.6438 | 0.97347 | 0.43899 | 0.80543 | 0.94727 | 0.3928 | 0.82451 | 11.9655 | -113.1494 | 165.4884 | 11.3296 | -108.6438 | 166.9558
Line_1 | 0 | 0 | 0 | 0 | 1.0007 | 1.0007 | 0 | 0 | 0 | 0 | 11.5554 | 11.5554 | -2.3685e-15 | -3.9984e-10 | -7.9858e-10 | -1.1842e-15 | -7.5079 | 2.5007 | 7.1054e-15 | 1.3421e-09 | -6.5146e-10 | 7.1054e-15 | 0.38403 | -5.3913 | 0 | -150.0137 | 29.9863 | 0 | 29.9863 | -150.0137 | 0.94727 | 0.3928 | 0.82451 | 0.92772 | 0.35381 | 0.83781 | 11.3296 | -108.6438 | 166.9558 | 10.6132 | -105.0137 | 168.2323
Line_2 | 0 | 0 | 0 | 0 | 1.0007 | 1.0007 | 0 | 0 | 0 | 0 | 11.5554 | 11.5554 | 3.5527e-15 | -3.9984e-10 | -7.9859e-10 | 2.3685e-15 | -7.5079 | 2.5007 | -4.737e-15 | 1.3421e-09 | -6.5147e-10 | -4.737e-15 | 0.38403 | -5.3913 | 0 | -150.0137 | 29.9863 | 0 | 29.9863 | -150.0137 | 0.94727 | 0.3928 | 0.82451 | 0.92772 | 0.35381 | 0.83781 | 11.3296 | -108.6438 | 166.9558 | 10.6132 | -105.0137 | 168.2323

## LLG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.0054628 | 0.0054628 | 0.0054628 | 0.0041034 | 2.66 | 2.0912 | 0.063079 | 0.063079 | 0.063079 | 0.047381 | 30.7155 | 24.1467 | 0.00024825 | 2.1221e-13 | 8.158e-15 | -2.334e-05 | -4.3204e-11 | -4.3341e-11 | -0.069517 | 1.2753e-13 | -2.4897e-13 | 0.058909 | 5.3632e-11 | 3.3665e-11 | 0 | 170.0913 | 37.8304 | -96.3362 | -9.9969 | -142.089 | 0.63628 | 0 | 0.63628 | 0.71781 | 0 | 0.71781 | -0.011174 | 0 | 179.9888 | -6.3135 | 0 | 173.6865
Line_1 | 0.0020517 | 0.0020517 | 0.0020517 | 0 | 2.3141 | 1.7284 | 0.023691 | 0.023691 | 0.023691 | 0 | 26.7212 | 19.958 | 1.167e-05 | 4.341e-14 | 6.0101e-15 | -1.1986e-09 | -1.5456e-11 | -2.0209e-11 | -0.029454 | 3.0614e-14 | -5.3506e-14 | -6.2175e-10 | 3.0573e-11 | 1.6684e-11 | 0 | 178.6783 | 36.8385 | 0 | -1.3217 | -143.1615 | 0.71781 | 0 | 0.71781 | 0.77199 | 0 | 0.77199 | -6.3135 | 0 | 173.6865 | -6.62 | 0 | 173.38
Line_2 | 0.0020517 | 0.0020517 | 0.0020517 | 0 | 2.3141 | 1.7284 | 0.023691 | 0.023691 | 0.023691 | 0 | 26.7212 | 19.958 | 1.167e-05 | 4.341e-14 | 6.0101e-15 | -1.1986e-09 | -1.5448e-11 | -2.0212e-11 | -0.029454 | 3.0614e-14 | -5.3506e-14 | -6.2175e-10 | 3.057e-11 | 1.6681e-11 | 0 | 178.6783 | 36.8385 | 0 | -1.3217 | -143.1615 | 0.71781 | 0 | 0.71781 | 0.77199 | 0 | 0.77199 | -6.3135 | 0 | 173.6865 | -6.62 | 0 | 173.38

## LLG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.0054628 | 0.0054628 | 0.0054628 | 0.0041034 | 2.66 | 2.0912 | 0.063079 | 0.063079 | 0.063079 | 0.047381 | 30.7155 | 24.1467 | 0.00024825 | 2.1221e-13 | 8.158e-15 | -2.334e-05 | -4.3204e-11 | -4.3341e-11 | -0.069517 | 1.2753e-13 | -2.4897e-13 | 0.058909 | 5.3632e-11 | 3.3665e-11 | 0 | 170.0913 | 37.8304 | -96.3362 | -9.9969 | -142.089 | 0.63628 | 0 | 0.63628 | 0.71781 | 0 | 0.71781 | -0.011174 | 0 | 179.9888 | -6.3135 | 0 | 173.6865
Line_1 | 0.0020517 | 0.0020517 | 0.0020517 | 0 | 2.3141 | 1.7284 | 0.023691 | 0.023691 | 0.023691 | 0 | 26.7212 | 19.958 | 1.167e-05 | 4.341e-14 | 6.0101e-15 | -1.1986e-09 | -1.5456e-11 | -2.0209e-11 | -0.029454 | 3.0614e-14 | -5.3506e-14 | -6.2175e-10 | 3.0573e-11 | 1.6684e-11 | 0 | 178.6783 | 36.8385 | 0 | -1.3217 | -143.1615 | 0.71781 | 0 | 0.71781 | 0.77199 | 0 | 0.77199 | -6.3135 | 0 | 173.6865 | -6.62 | 0 | 173.38
Line_2 | 0.0020517 | 0.0020517 | 0.0020517 | 0 | 2.3141 | 1.7284 | 0.023691 | 0.023691 | 0.023691 | 0 | 26.7212 | 19.958 | 1.167e-05 | 4.341e-14 | 6.0101e-15 | -1.1986e-09 | -1.5448e-11 | -2.0212e-11 | -0.029454 | 3.0614e-14 | -5.3506e-14 | -6.2175e-10 | 3.057e-11 | 1.6681e-11 | 0 | 178.6783 | 36.8385 | 0 | -1.3217 | -143.1615 | 0.71781 | 0 | 0.71781 | 0.77199 | 0 | 0.77199 | -6.3135 | 0 | 173.6865 | -6.62 | 0 | 173.38

## LLG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.0022224 | 0.0022224 | 0.0022224 | 0.0019648 | 1.1084 | 1.0117 | 0.025662 | 0.025662 | 0.025662 | 0.022687 | 12.7984 | 11.6819 | -0.011542 | -0.0065964 | 0.018179 | 0.0021778 | -6.1323 | -5.1146 | -0.025783 | 0.017179 | -0.0029009 | 0.026571 | -6.154 | -5.1037 | 0 | -174.4216 | 58.8229 | -88.015 | 5.477 | -121.1162 | 0.97296 | 0.7175 | 0.8439 | 0.96532 | 0.66979 | 0.85183 | 17.5633 | -104.8932 | 151.7221 | 16.2908 | -104.1339 | 153.6019
Line_1 | 0.00098239 | 0.00098239 | 0.00098239 | 0 | 1.0403 | 0.90167 | 0.011344 | 0.011344 | 0.011344 | 0 | 12.0127 | 10.4116 | -0.0010889 | -0.0057755 | 0.006867 | -6.1043e-10 | -5.4115 | -4.065 | -0.013285 | 0.0050929 | 0.0014394 | -3.2801e-10 | -5.4115 | -4.065 | 0 | -170.5778 | 57.2677 | 0 | 9.4222 | -122.7323 | 0.96532 | 0.66979 | 0.85183 | 0.95792 | 0.62793 | 0.85648 | 16.2908 | -104.1339 | 153.6019 | 15.2646 | -103.4694 | 155.2584
Line_2 | 0.00098239 | 0.00098239 | 0.00098239 | 0 | 1.0403 | 0.90167 | 0.011344 | 0.011344 | 0.011344 | 0 | 12.0127 | 10.4116 | -0.0010889 | -0.0057755 | 0.006867 | -6.1043e-10 | -5.4115 | -4.065 | -0.013285 | 0.0050929 | 0.0014394 | -3.2801e-10 | -5.4115 | -4.065 | 0 | -170.5778 | 57.2677 | 0 | 9.4222 | -122.7323 | 0.96532 | 0.66979 | 0.85183 | 0.95792 | 0.62793 | 0.85648 | 16.2908 | -104.1339 | 153.6019 | 15.2646 | -103.4694 | 155.2584

## LLG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.0022224 | 0.0022224 | 0.0022224 | 0.0019648 | 1.1084 | 1.0117 | 0.025662 | 0.025662 | 0.025662 | 0.022687 | 12.7984 | 11.6819 | -0.011542 | -0.0065964 | 0.018179 | 0.0021778 | -6.1323 | -5.1146 | -0.025783 | 0.017179 | -0.0029009 | 0.026571 | -6.154 | -5.1037 | 0 | -174.4216 | 58.8229 | -88.015 | 5.477 | -121.1162 | 0.97296 | 0.7175 | 0.8439 | 0.96532 | 0.66979 | 0.85183 | 17.5633 | -104.8932 | 151.7221 | 16.2908 | -104.1339 | 153.6019
Line_1 | 0.00098239 | 0.00098239 | 0.00098239 | 0 | 1.0403 | 0.90167 | 0.011344 | 0.011344 | 0.011344 | 0 | 12.0127 | 10.4116 | -0.0010889 | -0.0057755 | 0.006867 | -6.1043e-10 | -5.4115 | -4.065 | -0.013285 | 0.0050929 | 0.0014394 | -3.2801e-10 | -5.4115 | -4.065 | 0 | -170.5778 | 57.2677 | 0 | 9.4222 | -122.7323 | 0.96532 | 0.66979 | 0.85183 | 0.95792 | 0.62793 | 0.85648 | 16.2908 | -104.1339 | 153.6019 | 15.2646 | -103.4694 | 155.2584
Line_2 | 0.00098239 | 0.00098239 | 0.00098239 | 0 | 1.0403 | 0.90167 | 0.011344 | 0.011344 | 0.011344 | 0 | 12.0127 | 10.4116 | -0.0010889 | -0.0057755 | 0.006867 | -6.1043e-10 | -5.4115 | -4.065 | -0.013285 | 0.0050929 | 0.0014394 | -3.2801e-10 | -5.4115 | -4.065 | 0 | -170.5778 | 57.2677 | 0 | 9.4222 | -122.7323 | 0.96532 | 0.66979 | 0.85183 | 0.95792 | 0.62793 | 0.85648 | 16.2908 | -104.1339 | 153.6019 | 15.2646 | -103.4694 | 155.2584

## LLG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.0049673 | 0.0049673 | 0.0049673 | 0.0039731 | 2.1444 | 1.5463 | 0.057358 | 0.057358 | 0.057358 | 0.045877 | 24.7611 | 17.8556 | 0.00039409 | -1.493e-13 | 1.2375e-13 | -4.2012e-05 | -2.5473e-11 | -1.0135e-11 | -0.057479 | 5.3132e-14 | 1.0175e-13 | 0.055228 | -3.2914e-11 | -2.8769e-11 | 0 | 178.39 | 38.516 | -97.6554 | -1.7156 | -141.3821 | 0.57859 | 0 | 0.57859 | 0.69502 | 0 | 0.69502 | -0.013103 | 0 | 179.9869 | -7.6118 | 0 | 172.3882
Line_1 | 0.0019866 | 0.0019866 | 0.0019866 | 0 | 1.7914 | 1.3122 | 0.022939 | 0.022939 | 0.022939 | 0 | 20.6851 | 15.1525 | 2.1005e-05 | -3.277e-14 | 3.4956e-14 | -1.4272e-09 | -2.6133e-11 | -1.2611e-11 | -0.027614 | 2.0316e-14 | 1.7709e-14 | -5.2069e-10 | -1.1398e-11 | -1.7205e-11 | 0 | -169.8819 | 38.4671 | 0 | 10.1181 | -141.5329 | 0.69502 | 0 | 0.69502 | 0.74745 | 0 | 0.74745 | -7.6118 | 0 | 172.3882 | -6.2976 | 0 | 173.7024
Line_2 | 0.0019866 | 0.0019866 | 0.0019866 | 0 | 1.7914 | 1.3122 | 0.022939 | 0.022939 | 0.022939 | 0 | 20.6851 | 15.1525 | 2.1005e-05 | -3.277e-14 | 3.4956e-14 | -1.4272e-09 | -2.6115e-11 | -1.2622e-11 | -0.027614 | 2.0316e-14 | 1.7709e-14 | -5.207e-10 | -1.1385e-11 | -1.7205e-11 | 0 | -169.8819 | 38.4671 | 0 | 10.1181 | -141.5329 | 0.69502 | 0 | 0.69502 | 0.74745 | 0 | 0.74745 | -7.6118 | 0 | 172.3882 | -6.2976 | 0 | 173.7024

## LLG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.0049673 | 0.0049673 | 0.0049673 | 0.0039731 | 2.1444 | 1.5463 | 0.057358 | 0.057358 | 0.057358 | 0.045877 | 24.7611 | 17.8556 | 0.00039409 | -1.493e-13 | 1.2375e-13 | -4.2012e-05 | -2.5473e-11 | -1.0135e-11 | -0.057479 | 5.3132e-14 | 1.0175e-13 | 0.055228 | -3.2914e-11 | -2.8769e-11 | 0 | 178.39 | 38.516 | -97.6554 | -1.7156 | -141.3821 | 0.57859 | 0 | 0.57859 | 0.69502 | 0 | 0.69502 | -0.013103 | 0 | 179.9869 | -7.6118 | 0 | 172.3882
Line_1 | 0.0019866 | 0.0019866 | 0.0019866 | 0 | 1.7914 | 1.3122 | 0.022939 | 0.022939 | 0.022939 | 0 | 20.6851 | 15.1525 | 2.1005e-05 | -3.277e-14 | 3.4956e-14 | -1.4272e-09 | -2.6133e-11 | -1.2611e-11 | -0.027614 | 2.0316e-14 | 1.7709e-14 | -5.2069e-10 | -1.1398e-11 | -1.7205e-11 | 0 | -169.8819 | 38.4671 | 0 | 10.1181 | -141.5329 | 0.69502 | 0 | 0.69502 | 0.74745 | 0 | 0.74745 | -7.6118 | 0 | 172.3882 | -6.2976 | 0 | 173.7024
Line_2 | 0.0019866 | 0.0019866 | 0.0019866 | 0 | 1.7914 | 1.3122 | 0.022939 | 0.022939 | 0.022939 | 0 | 20.6851 | 15.1525 | 2.1005e-05 | -3.277e-14 | 3.4956e-14 | -1.4272e-09 | -2.6115e-11 | -1.2622e-11 | -0.027614 | 2.0316e-14 | 1.7709e-14 | -5.207e-10 | -1.1385e-11 | -1.7205e-11 | 0 | -169.8819 | 38.4671 | 0 | 10.1181 | -141.5329 | 0.69502 | 0 | 0.69502 | 0.74745 | 0 | 0.74745 | -7.6118 | 0 | 172.3882 | -6.2976 | 0 | 173.7024

## LLG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.002186 | 0.002186 | 0.002186 | 0.0021499 | 0.95704 | 0.81697 | 0.025242 | 0.025242 | 0.025242 | 0.024824 | 11.051 | 9.4335 | -0.0097374 | -0.005666 | 0.01548 | -0.0010383 | -4.5725 | -3.333 | -0.023313 | 0.014599 | -0.002418 | 0.027522 | -4.5923 | -3.3255 | 0 | -170.9236 | 58.3157 | -96.5121 | 8.9524 | -121.6201 | 0.87213 | 0.62083 | 0.74906 | 0.86718 | 0.57014 | 0.77804 | 16.5558 | -106.14 | 152.3303 | 15.0772 | -103.4151 | 154.9844
Line_1 | 0.0010749 | 0.0010749 | 0.0010749 | 0 | 0.87798 | 0.70992 | 0.012412 | 0.012412 | 0.012412 | 0 | 10.138 | 8.1974 | 0.00051914 | -0.0063406 | 0.0058276 | -8.179e-10 | -3.8542 | -2.5199 | -0.013761 | 0.0035744 | 0.0021013 | -3.826e-10 | -3.8542 | -2.5199 | 0 | -164.3656 | 56.6931 | 0 | 15.6344 | -123.3069 | 0.86718 | 0.57014 | 0.77804 | 0.85952 | 0.52617 | 0.79344 | 15.0772 | -103.4151 | 154.9844 | 14.1612 | -101.1059 | 157.3128
Line_2 | 0.0010749 | 0.0010749 | 0.0010749 | 0 | 0.87798 | 0.70992 | 0.012412 | 0.012412 | 0.012412 | 0 | 10.138 | 8.1974 | 0.00051914 | -0.0063406 | 0.0058276 | -8.179e-10 | -3.8542 | -2.5199 | -0.013761 | 0.0035744 | 0.0021013 | -3.826e-10 | -3.8542 | -2.5199 | 0 | -164.3656 | 56.6931 | 0 | 15.6344 | -123.3069 | 0.86718 | 0.57014 | 0.77804 | 0.85952 | 0.52617 | 0.79344 | 15.0772 | -103.4151 | 154.9844 | 14.1612 | -101.1059 | 157.3128

## LLG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.002186 | 0.002186 | 0.002186 | 0.0021499 | 0.95704 | 0.81697 | 0.025242 | 0.025242 | 0.025242 | 0.024824 | 11.051 | 9.4335 | -0.0097374 | -0.005666 | 0.01548 | -0.0010383 | -4.5725 | -3.333 | -0.023313 | 0.014599 | -0.002418 | 0.027522 | -4.5923 | -3.3255 | 0 | -170.9236 | 58.3157 | -96.5121 | 8.9524 | -121.6201 | 0.87213 | 0.62083 | 0.74906 | 0.86718 | 0.57014 | 0.77804 | 16.5558 | -106.14 | 152.3303 | 15.0772 | -103.4151 | 154.9844
Line_1 | 0.0010749 | 0.0010749 | 0.0010749 | 0 | 0.87798 | 0.70992 | 0.012412 | 0.012412 | 0.012412 | 0 | 10.138 | 8.1974 | 0.00051914 | -0.0063406 | 0.0058276 | -8.179e-10 | -3.8542 | -2.5199 | -0.013761 | 0.0035744 | 0.0021013 | -3.826e-10 | -3.8542 | -2.5199 | 0 | -164.3656 | 56.6931 | 0 | 15.6344 | -123.3069 | 0.86718 | 0.57014 | 0.77804 | 0.85952 | 0.52617 | 0.79344 | 15.0772 | -103.4151 | 154.9844 | 14.1612 | -101.1059 | 157.3128
Line_2 | 0.0010749 | 0.0010749 | 0.0010749 | 0 | 0.87798 | 0.70992 | 0.012412 | 0.012412 | 0.012412 | 0 | 10.138 | 8.1974 | 0.00051914 | -0.0063406 | 0.0058276 | -8.179e-10 | -3.8542 | -2.5199 | -0.013761 | 0.0035744 | 0.0021013 | -3.826e-10 | -3.8542 | -2.5199 | 0 | -164.3656 | 56.6931 | 0 | 15.6344 | -123.3069 | 0.86718 | 0.57014 | 0.77804 | 0.85952 | 0.52617 | 0.79344 | 15.0772 | -103.4151 | 154.9844 | 14.1612 | -101.1059 | 157.3128

## LG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.0054731 | 0.0054731 | 0.0054731 | 2.2527 | 0.0046346 | 0.0046346 | 0.063198 | 0.063198 | 0.063198 | 26.0121 | 0.053516 | 0.053516 | 1.1594e-13 | 0.060328 | -0.060079 | -6.2764e-12 | -0.049393 | 0.049363 | -2.4248e-13 | -0.034651 | -0.035128 | 8.1161e-11 | 0.024891 | 0.050259 | -68.8931 | 0 | 0 | 111.0385 | 75.5938 | 75.5938 | 0.63558 | 1.1 | 0.63579 | 0.59671 | 1.1 | 0.76 | 59.9009 | -90 | 120.0879 | 48.8481 | -90 | 121.109
Line_1 | 0.0023173 | 0.0023173 | 0.0023173 | 1.7802 | 0 | 0 | 0.026758 | 0.026758 | 0.026758 | 20.5555 | 0 | 0 | 5.3676e-14 | 0.024696 | -0.024682 | 3.9665e-12 | -9.3951e-11 | -1.7564e-09 | -6.4272e-14 | -0.012446 | -0.02513 | 4.7101e-11 | -1.3388e-09 | 3.7893e-10 | -59.5413 | 0 | 0 | 120.4587 | 0 | 0 | 0.59671 | 1.1 | 0.76 | 0.61756 | 1.1 | 0.82684 | 48.8481 | -90 | 121.109 | 41.9216 | -90 | 123.7614
Line_2 | 0.0023173 | 0.0023173 | 0.0023173 | 1.7802 | 0 | 0 | 0.026758 | 0.026758 | 0.026758 | 20.5555 | 0 | 0 | 5.3676e-14 | 0.024696 | -0.024682 | 3.9796e-12 | -9.394e-11 | -1.7565e-09 | -6.4272e-14 | -0.012446 | -0.02513 | 4.712e-11 | -1.3388e-09 | 3.7894e-10 | -59.5413 | 0 | 0 | 120.4587 | 0 | 0 | 0.59671 | 1.1 | 0.76 | 0.61756 | 1.1 | 0.82684 | 48.8481 | -90 | 121.109 | 41.9216 | -90 | 123.7614

## LG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.0054731 | 0.0054731 | 0.0054731 | 2.2527 | 0.0046346 | 0.0046346 | 0.063198 | 0.063198 | 0.063198 | 26.0121 | 0.053516 | 0.053516 | 1.1594e-13 | 0.060328 | -0.060079 | -6.2764e-12 | -0.049393 | 0.049363 | -2.4248e-13 | -0.034651 | -0.035128 | 8.1161e-11 | 0.024891 | 0.050259 | -68.8931 | 0 | 0 | 111.0385 | 75.5938 | 75.5938 | 0.63558 | 1.1 | 0.63579 | 0.59671 | 1.1 | 0.76 | 59.9009 | -90 | 120.0879 | 48.8481 | -90 | 121.109
Line_1 | 0.0023173 | 0.0023173 | 0.0023173 | 1.7802 | 0 | 0 | 0.026758 | 0.026758 | 0.026758 | 20.5555 | 0 | 0 | 5.3676e-14 | 0.024696 | -0.024682 | 3.9665e-12 | -9.3951e-11 | -1.7564e-09 | -6.4272e-14 | -0.012446 | -0.02513 | 4.7101e-11 | -1.3388e-09 | 3.7893e-10 | -59.5413 | 0 | 0 | 120.4587 | 0 | 0 | 0.59671 | 1.1 | 0.76 | 0.61756 | 1.1 | 0.82684 | 48.8481 | -90 | 121.109 | 41.9216 | -90 | 123.7614
Line_2 | 0.0023173 | 0.0023173 | 0.0023173 | 1.7802 | 0 | 0 | 0.026758 | 0.026758 | 0.026758 | 20.5555 | 0 | 0 | 5.3676e-14 | 0.024696 | -0.024682 | 3.9796e-12 | -9.394e-11 | -1.7565e-09 | -6.4272e-14 | -0.012446 | -0.02513 | 4.712e-11 | -1.3388e-09 | 3.7894e-10 | -59.5413 | 0 | 0 | 120.4587 | 0 | 0 | 0.59671 | 1.1 | 0.76 | 0.61756 | 1.1 | 0.82684 | 48.8481 | -90 | 121.109 | 41.9216 | -90 | 123.7614

## LG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.002224 | 0.002224 | 0.002224 | 1.0222 | 0.002103 | 0.002103 | 0.02568 | 0.02568 | 0.02568 | 11.8031 | 0.024283 | 0.024283 | 0.0116 | 0.016544 | -0.028103 | -5.2093 | -0.021881 | 0.024376 | 0.014299 | -0.022917 | -0.0029038 | -5.2217 | 0.014775 | 0.015666 | -55.5903 | 0 | 0 | 124.3412 | 88.8965 | 88.8965 | 0.84403 | 1.1 | 0.97279 | 0.84401 | 1.1 | 0.96891 | 31.7119 | -90 | 137.5699 | 31.9851 | -90 | 137.6329
Line_1 | 0.0010515 | 0.0010515 | 0.0010515 | 0.90134 | 0 | 0 | 0.012142 | 0.012142 | 0.012142 | 10.4078 | 0 | 0 | 0.0012506 | 0.010941 | -0.012188 | -4.0621 | -2.7002e-11 | -7.525e-10 | 0.0074836 | -0.0073873 | -0.0078328 | -4.0621 | -6.9387e-10 | 2.7499e-10 | -52.3036 | 0 | 0 | 127.6964 | 0 | 0 | 0.84401 | 1.1 | 0.96891 | 0.84347 | 1.1 | 0.96565 | 31.9851 | -90 | 137.6329 | 32.2051 | -90 | 137.6538
Line_2 | 0.0010515 | 0.0010515 | 0.0010515 | 0.90134 | 0 | 0 | 0.012142 | 0.012142 | 0.012142 | 10.4078 | 0 | 0 | 0.0012506 | 0.010941 | -0.012188 | -4.0621 | -2.6996e-11 | -7.525e-10 | 0.0074836 | -0.0073873 | -0.0078328 | -4.0621 | -6.9386e-10 | 2.75e-10 | -52.3036 | 0 | 0 | 127.6964 | 0 | 0 | 0.84401 | 1.1 | 0.96891 | 0.84347 | 1.1 | 0.96565 | 31.9851 | -90 | 137.6329 | 32.2051 | -90 | 137.6538

## LG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.002224 | 0.002224 | 0.002224 | 1.0222 | 0.002103 | 0.002103 | 0.02568 | 0.02568 | 0.02568 | 11.8031 | 0.024283 | 0.024283 | 0.0116 | 0.016544 | -0.028103 | -5.2093 | -0.021881 | 0.024376 | 0.014299 | -0.022917 | -0.0029038 | -5.2217 | 0.014775 | 0.015666 | -55.5903 | 0 | 0 | 124.3412 | 88.8965 | 88.8965 | 0.84403 | 1.1 | 0.97279 | 0.84401 | 1.1 | 0.96891 | 31.7119 | -90 | 137.5699 | 31.9851 | -90 | 137.6329
Line_1 | 0.0010515 | 0.0010515 | 0.0010515 | 0.90134 | 0 | 0 | 0.012142 | 0.012142 | 0.012142 | 10.4078 | 0 | 0 | 0.0012506 | 0.010941 | -0.012188 | -4.0621 | -2.7002e-11 | -7.525e-10 | 0.0074836 | -0.0073873 | -0.0078328 | -4.0621 | -6.9387e-10 | 2.7499e-10 | -52.3036 | 0 | 0 | 127.6964 | 0 | 0 | 0.84401 | 1.1 | 0.96891 | 0.84347 | 1.1 | 0.96565 | 31.9851 | -90 | 137.6329 | 32.2051 | -90 | 137.6538
Line_2 | 0.0010515 | 0.0010515 | 0.0010515 | 0.90134 | 0 | 0 | 0.012142 | 0.012142 | 0.012142 | 10.4078 | 0 | 0 | 0.0012506 | 0.010941 | -0.012188 | -4.0621 | -2.6996e-11 | -7.525e-10 | 0.0074836 | -0.0073873 | -0.0078328 | -4.0621 | -6.9386e-10 | 2.75e-10 | -52.3036 | 0 | 0 | 127.6964 | 0 | 0 | 0.84401 | 1.1 | 0.96891 | 0.84347 | 1.1 | 0.96565 | 31.9851 | -90 | 137.6329 | 32.2051 | -90 | 137.6538

## LG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.004978 | 0.004978 | 0.004978 | 1.6879 | 0.0048311 | 0.0048311 | 0.057481 | 0.057481 | 0.057481 | 19.4907 | 0.055785 | 0.055785 | -7.5556e-14 | 0.049976 | -0.04958 | 3.8373e-11 | -0.045755 | 0.045693 | -2.2558e-13 | -0.028499 | -0.029227 | 3.2942e-11 | 0.025231 | 0.056426 | -58.671 | 0 | 0 | 121.2031 | 71.1644 | 71.1644 | 0.57785 | 1 | 0.57808 | 0.54077 | 1 | 0.75145 | 59.8872 | -90 | 120.0996 | 42.2904 | -90 | 122.1644
Line_1 | 0.0024156 | 0.0024156 | 0.0024156 | 1.2249 | 0 | 0 | 0.027892 | 0.027892 | 0.027892 | 14.1439 | 0 | 0 | 8.6343e-16 | 0.022878 | -0.022846 | 1.9687e-11 | -4.967e-10 | -2.2022e-09 | -7.2368e-14 | -0.012616 | -0.028213 | 1.0434e-11 | -1.5995e-09 | 6.1486e-10 | -45.5335 | 0 | 0 | 134.4665 | 0 | 0 | 0.54077 | 1 | 0.75145 | 0.59923 | 1 | 0.81803 | 42.2904 | -90 | 122.1644 | 35.146 | -90 | 126.797
Line_2 | 0.0024156 | 0.0024156 | 0.0024156 | 1.2249 | 0 | 0 | 0.027892 | 0.027892 | 0.027892 | 14.1439 | 0 | 0 | 8.6343e-16 | 0.022878 | -0.022846 | 1.9695e-11 | -4.9669e-10 | -2.2022e-09 | -7.2368e-14 | -0.012616 | -0.028213 | 1.0439e-11 | -1.5995e-09 | 6.1486e-10 | -45.5335 | 0 | 0 | 134.4665 | 0 | 0 | 0.54077 | 1 | 0.75145 | 0.59923 | 1 | 0.81803 | 42.2904 | -90 | 122.1644 | 35.146 | -90 | 126.797

## LG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.004978 | 0.004978 | 0.004978 | 1.6879 | 0.0048311 | 0.0048311 | 0.057481 | 0.057481 | 0.057481 | 19.4907 | 0.055785 | 0.055785 | -7.5556e-14 | 0.049976 | -0.04958 | 3.8373e-11 | -0.045755 | 0.045693 | -2.2558e-13 | -0.028499 | -0.029227 | 3.2942e-11 | 0.025231 | 0.056426 | -58.671 | 0 | 0 | 121.2031 | 71.1644 | 71.1644 | 0.57785 | 1 | 0.57808 | 0.54077 | 1 | 0.75145 | 59.8872 | -90 | 120.0996 | 42.2904 | -90 | 122.1644
Line_1 | 0.0024156 | 0.0024156 | 0.0024156 | 1.2249 | 0 | 0 | 0.027892 | 0.027892 | 0.027892 | 14.1439 | 0 | 0 | 8.6343e-16 | 0.022878 | -0.022846 | 1.9687e-11 | -4.967e-10 | -2.2022e-09 | -7.2368e-14 | -0.012616 | -0.028213 | 1.0434e-11 | -1.5995e-09 | 6.1486e-10 | -45.5335 | 0 | 0 | 134.4665 | 0 | 0 | 0.54077 | 1 | 0.75145 | 0.59923 | 1 | 0.81803 | 42.2904 | -90 | 122.1644 | 35.146 | -90 | 126.797
Line_2 | 0.0024156 | 0.0024156 | 0.0024156 | 1.2249 | 0 | 0 | 0.027892 | 0.027892 | 0.027892 | 14.1439 | 0 | 0 | 8.6343e-16 | 0.022878 | -0.022846 | 1.9695e-11 | -4.9669e-10 | -2.2022e-09 | -7.2368e-14 | -0.012616 | -0.028213 | 1.0439e-11 | -1.5995e-09 | 6.1486e-10 | -45.5335 | 0 | 0 | 134.4665 | 0 | 0 | 0.54077 | 1 | 0.75145 | 0.59923 | 1 | 0.81803 | 42.2904 | -90 | 122.1644 | 35.146 | -90 | 126.797

## LG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.002188 | 0.002188 | 0.002188 | 0.83673 | 0.0023948 | 0.0023948 | 0.025265 | 0.025265 | 0.025265 | 9.6617 | 0.027653 | 0.027653 | 0.0098315 | 0.015307 | -0.025062 | -3.4865 | -0.024078 | 0.02279 | 0.012203 | -0.020122 | -0.0032335 | -3.5018 | 0.01214 | 0.022011 | -51.7282 | 0 | 0 | 128.1459 | 78.1073 | 78.1073 | 0.74921 | 1 | 0.87194 | 0.76156 | 1 | 0.87737 | 32.3158 | -90 | 136.5651 | 32.1359 | -90 | 137.3084
Line_1 | 0.0011974 | 0.0011974 | 0.0011974 | 0.69991 | 0 | 0 | 0.013827 | 0.013827 | 0.013827 | 8.0819 | 0 | 0 | -0.00063656 | 0.012039 | -0.011395 | -2.4494 | -1.1353e-10 | -1.083e-09 | 0.0070428 | -0.0060701 | -0.011005 | -2.4494 | -9.1446e-10 | 3.5473e-10 | -45.3048 | 0 | 0 | 134.6952 | 0 | 0 | 0.76156 | 1 | 0.87737 | 0.77007 | 1 | 0.87859 | 32.1359 | -90 | 137.3084 | 32.2172 | -90 | 137.8629
Line_2 | 0.0011974 | 0.0011974 | 0.0011974 | 0.69991 | 0 | 0 | 0.013827 | 0.013827 | 0.013827 | 8.0819 | 0 | 0 | -0.00063656 | 0.012039 | -0.011395 | -2.4494 | -1.1353e-10 | -1.083e-09 | 0.0070428 | -0.0060701 | -0.011005 | -2.4494 | -9.1446e-10 | 3.5474e-10 | -45.3048 | 0 | 0 | 134.6952 | 0 | 0 | 0.76156 | 1 | 0.87737 | 0.77007 | 1 | 0.87859 | 32.1359 | -90 | 137.3084 | 32.2172 | -90 | 137.8629

## LG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.002188 | 0.002188 | 0.002188 | 0.83673 | 0.0023948 | 0.0023948 | 0.025265 | 0.025265 | 0.025265 | 9.6617 | 0.027653 | 0.027653 | 0.0098315 | 0.015307 | -0.025062 | -3.4865 | -0.024078 | 0.02279 | 0.012203 | -0.020122 | -0.0032335 | -3.5018 | 0.01214 | 0.022011 | -51.7282 | 0 | 0 | 128.1459 | 78.1073 | 78.1073 | 0.74921 | 1 | 0.87194 | 0.76156 | 1 | 0.87737 | 32.3158 | -90 | 136.5651 | 32.1359 | -90 | 137.3084
Line_1 | 0.0011974 | 0.0011974 | 0.0011974 | 0.69991 | 0 | 0 | 0.013827 | 0.013827 | 0.013827 | 8.0819 | 0 | 0 | -0.00063656 | 0.012039 | -0.011395 | -2.4494 | -1.1353e-10 | -1.083e-09 | 0.0070428 | -0.0060701 | -0.011005 | -2.4494 | -9.1446e-10 | 3.5473e-10 | -45.3048 | 0 | 0 | 134.6952 | 0 | 0 | 0.76156 | 1 | 0.87737 | 0.77007 | 1 | 0.87859 | 32.1359 | -90 | 137.3084 | 32.2172 | -90 | 137.8629
Line_2 | 0.0011974 | 0.0011974 | 0.0011974 | 0.69991 | 0 | 0 | 0.013827 | 0.013827 | 0.013827 | 8.0819 | 0 | 0 | -0.00063656 | 0.012039 | -0.011395 | -2.4494 | -1.1353e-10 | -1.083e-09 | 0.0070428 | -0.0060701 | -0.011005 | -2.4494 | -9.1446e-10 | 3.5474e-10 | -45.3048 | 0 | 0 | 134.6952 | 0 | 0 | 0.76156 | 1 | 0.87737 | 0.77007 | 1 | 0.87859 | 32.1359 | -90 | 137.3084 | 32.2172 | -90 | 137.8629