## LLL_max_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 1.7394 | 1.7394 | 4.0301 | 0 | 60.2556 | 60.2556 | -1e-07 | 4.72 | -1e-07 | 5.3553 | 107.5423 | -72.4577 | 0 | 0.11847 | 0 | -23.8492
Line_1 | 0.86972 | 0.86972 | 0 | 0 | 30.1278 | 30.1278 | 3.54 | -2.36 | 4.0165 | -2.6777 | -72.4577 | 107.5423 | 0.1777 | 0.11847 | -23.8492 | -23.8492
Line_2 | 0.86972 | 0.86972 | 0 | 0 | 30.1278 | 30.1278 | 3.54 | -2.36 | 4.0165 | -2.6777 | -72.4577 | 107.5423 | 0.1777 | 0.11847 | -23.8492 | -23.8492

## LLL_max_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 1.7394 | 1.7394 | 4.0301 | 0 | 60.2556 | 60.2556 | -1e-07 | 4.72 | -1e-07 | 5.3553 | 107.5423 | -72.4577 | 0 | 0.11847 | 0 | -23.8492
Line_1 | 0.86972 | 0.86972 | 0 | 0 | 30.1278 | 30.1278 | 3.54 | -2.36 | 4.0165 | -2.6777 | -72.4577 | 107.5423 | 0.1777 | 0.11847 | -23.8492 | -23.8492
Line_2 | 0.86972 | 0.86972 | 0 | 0 | 30.1278 | 30.1278 | 3.54 | -2.36 | 4.0165 | -2.6777 | -72.4577 | 107.5423 | 0.1777 | 0.11847 | -23.8492 | -23.8492

## LLL_max_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.51746 | 0.51746 | 1.048 | 0 | 17.9254 | 17.9254 | -10.4881 | 10.9059 | -13.3195 | 13.7934 | 120.4894 | -59.5106 | 0.94576 | 0.98095 | -7.7285 | -7.8425
Line_1 | 0.25873 | 0.25873 | 0 | 0 | 8.9627 | 8.9627 | 5.5574 | -5.4529 | 7.0152 | -6.8967 | -59.5106 | 120.4894 | 0.99855 | 0.98095 | -7.8965 | -7.8425
Line_2 | 0.25873 | 0.25873 | 0 | 0 | 8.9627 | 8.9627 | 5.5574 | -5.4529 | 7.0152 | -6.8967 | -59.5106 | 120.4894 | 0.99855 | 0.98095 | -7.8965 | -7.8425

## LLL_max_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.51746 | 0.51746 | 1.048 | 0 | 17.9254 | 17.9254 | -10.4881 | 10.9059 | -13.3195 | 13.7934 | 120.4894 | -59.5106 | 0.94576 | 0.98095 | -7.7285 | -7.8425
Line_1 | 0.25873 | 0.25873 | 0 | 0 | 8.9627 | 8.9627 | 5.5574 | -5.4529 | 7.0152 | -6.8967 | -59.5106 | 120.4894 | 0.99855 | 0.98095 | -7.8965 | -7.8425
Line_2 | 0.25873 | 0.25873 | 0 | 0 | 8.9627 | 8.9627 | 5.5574 | -5.4529 | 7.0152 | -6.8967 | -59.5106 | 120.4894 | 0.99855 | 0.98095 | -7.8965 | -7.8425

## LLL_min_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 1.3783 | 1.3783 | 3.412 | 0 | 47.7473 | 47.7473 | -1e-07 | 5.6904 | -1e-07 | 3.3627 | 114.7975 | -65.2025 | 0 | 0.13843 | 0 | -34.6217
Line_1 | 0.68917 | 0.68917 | 0 | 0 | 23.8737 | 23.8737 | 4.2678 | -2.8452 | 2.522 | -1.6814 | -65.2025 | 114.7975 | 0.20765 | 0.13843 | -34.6217 | -34.6217
Line_2 | 0.68917 | 0.68917 | 0 | 0 | 23.8737 | 23.8737 | 4.2678 | -2.8452 | 2.522 | -1.6814 | -65.2025 | 114.7975 | 0.20765 | 0.13843 | -34.6217 | -34.6217

## LLL_min_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 1.3783 | 1.3783 | 3.412 | 0 | 47.7473 | 47.7473 | -1e-07 | 5.6904 | -1e-07 | 3.3627 | 114.7975 | -65.2025 | 0 | 0.13843 | 0 | -34.6217
Line_1 | 0.68917 | 0.68917 | 0 | 0 | 23.8737 | 23.8737 | 4.2678 | -2.8452 | 2.522 | -1.6814 | -65.2025 | 114.7975 | 0.20765 | 0.13843 | -34.6217 | -34.6217
Line_2 | 0.68917 | 0.68917 | 0 | 0 | 23.8737 | 23.8737 | 4.2678 | -2.8452 | 2.522 | -1.6814 | -65.2025 | 114.7975 | 0.20765 | 0.13843 | -34.6217 | -34.6217

## LLL_min_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.30266 | 0.30266 | 0.74922 | 0 | 10.4846 | 10.4846 | -7.5715 | 7.8458 | -3.9965 | 4.1586 | 144.5132 | -35.4868 | 0.81658 | 0.84694 | -7.6601 | -7.5613
Line_1 | 0.15133 | 0.15133 | 0 | 0 | 5.2423 | 5.2423 | 3.9915 | -3.9229 | 2.1199 | -2.0793 | -35.4868 | 144.5132 | 0.86212 | 0.84694 | -7.5145 | -7.5613
Line_2 | 0.15133 | 0.15133 | 0 | 0 | 5.2423 | 5.2423 | 3.9915 | -3.9229 | 2.1199 | -2.0793 | -35.4868 | 144.5132 | 0.86212 | 0.84694 | -7.5145 | -7.5613

## LLL_min_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.30266 | 0.30266 | 0.74922 | 0 | 10.4846 | 10.4846 | -7.5715 | 7.8458 | -3.9965 | 4.1586 | 144.5132 | -35.4868 | 0.81658 | 0.84694 | -7.6601 | -7.5613
Line_1 | 0.15133 | 0.15133 | 0 | 0 | 5.2423 | 5.2423 | 3.9915 | -3.9229 | 2.1199 | -2.0793 | -35.4868 | 144.5132 | 0.86212 | 0.84694 | -7.5145 | -7.5613
Line_2 | 0.15133 | 0.15133 | 0 | 0 | 5.2423 | 5.2423 | 3.9915 | -3.9229 | 2.1199 | -2.0793 | -35.4868 | 144.5132 | 0.86212 | 0.84694 | -7.5145 | -7.5613

## LL_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.32048 | 1.5098 | 1.3931 | 0.32048 | 1.5098 | 1.3931 | 3.7006 | 17.4334 | 16.0862 | 3.7006 | 17.4334 | 16.0862 | -2.2014 | -10.0544 | 8.9537 | 2.2548 | 11.2397 | -7.9445 | -3.6682 | 0.67371 | -2.5078 | 3.7288 | 0.67115 | 3.6529 | 122.5535 | 5.4174 | -162.7693 | -57.4465 | -174.5826 | 17.2307 | 1.1561 | 0.57803 | 0.57803 | 1.1775 | 0.64587 | 0.54357 | 1.5839 | -178.4161 | -178.4161 | 1.3918 | -171.1654 | 172.538
Line_1 | 0.16024 | 0.75489 | 0.69655 | 0.16024 | 0.75489 | 0.69655 | 1.8503 | 8.7167 | 8.0431 | 1.8503 | 8.7167 | 8.0431 | 1.1408 | 5.9162 | -3.72 | -1.1274 | -5.6199 | 3.9723 | 1.8795 | 0.67179 | 2.1127 | -1.8644 | -0.33558 | -1.8264 | -57.4465 | -174.5826 | 17.2307 | 122.5535 | 5.4174 | -162.7693 | 1.1883 | 0.68308 | 0.53189 | 1.1775 | 0.64587 | 0.54357 | 1.2983 | -168.1044 | 167.6371 | 1.3918 | -171.1654 | 172.538
Line_2 | 0.16024 | 0.75489 | 0.69655 | 0.16024 | 0.75489 | 0.69655 | 1.8503 | 8.7167 | 8.0431 | 1.8503 | 8.7167 | 8.0431 | 1.1408 | 5.9162 | -3.72 | -1.1274 | -5.6199 | 3.9723 | 1.8795 | 0.67179 | 2.1127 | -1.8644 | -0.33558 | -1.8264 | -57.4465 | -174.5826 | 17.2307 | 122.5535 | 5.4174 | -162.7693 | 1.1883 | 0.68308 | 0.53189 | 1.1775 | 0.64587 | 0.54357 | 1.2983 | -168.1044 | 167.6371 | 1.3918 | -171.1654 | 172.538

## LL_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.32048 | 1.5098 | 1.3931 | 0.32048 | 1.5098 | 1.3931 | 3.7006 | 17.4334 | 16.0862 | 3.7006 | 17.4334 | 16.0862 | -2.2014 | -10.0544 | 8.9537 | 2.2548 | 11.2397 | -7.9445 | -3.6682 | 0.67371 | -2.5078 | 3.7288 | 0.67115 | 3.6529 | 122.5535 | 5.4174 | -162.7693 | -57.4465 | -174.5826 | 17.2307 | 1.1561 | 0.57803 | 0.57803 | 1.1775 | 0.64587 | 0.54357 | 1.5839 | -178.4161 | -178.4161 | 1.3918 | -171.1654 | 172.538
Line_1 | 0.16024 | 0.75489 | 0.69655 | 0.16024 | 0.75489 | 0.69655 | 1.8503 | 8.7167 | 8.0431 | 1.8503 | 8.7167 | 8.0431 | 1.1408 | 5.9162 | -3.72 | -1.1274 | -5.6199 | 3.9723 | 1.8795 | 0.67179 | 2.1127 | -1.8644 | -0.33558 | -1.8264 | -57.4465 | -174.5826 | 17.2307 | 122.5535 | 5.4174 | -162.7693 | 1.1883 | 0.68308 | 0.53189 | 1.1775 | 0.64587 | 0.54357 | 1.2983 | -168.1044 | 167.6371 | 1.3918 | -171.1654 | 172.538
Line_2 | 0.16024 | 0.75489 | 0.69655 | 0.16024 | 0.75489 | 0.69655 | 1.8503 | 8.7167 | 8.0431 | 1.8503 | 8.7167 | 8.0431 | 1.1408 | 5.9162 | -3.72 | -1.1274 | -5.6199 | 3.9723 | 1.8795 | 0.67179 | 2.1127 | -1.8644 | -0.33558 | -1.8264 | -57.4465 | -174.5826 | 17.2307 | 122.5535 | 5.4174 | -162.7693 | 1.1883 | 0.68308 | 0.53189 | 1.1775 | 0.64587 | 0.54357 | 1.2983 | -168.1044 | 167.6371 | 1.3918 | -171.1654 | 172.538

## LL_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.23496 | 0.62005 | 0.6638 | 0.23496 | 0.62005 | 0.6638 | 2.7131 | 7.1597 | 7.6649 | 2.7131 | 7.1597 | 7.6649 | -0.87371 | -6.4592 | -0.64541 | 0.90242 | 6.6591 | 0.87454 | -2.9829 | -3.0836 | -5.9544 | 3.0155 | 3.3104 | 6.2144 | 106.904 | 17.0933 | -142.1771 | -73.096 | -162.9067 | 37.8229 | 1.1456 | 0.99969 | 0.78139 | 1.1602 | 1.0387 | 0.81874 | 0.57818 | -137.3873 | 121.6367 | 0.24336 | -136.4737 | 119.8124
Line_1 | 0.11748 | 0.31003 | 0.3319 | 0.11748 | 0.31003 | 0.3319 | 1.3565 | 3.5799 | 3.8325 | 1.3565 | 3.5799 | 3.8325 | 0.45839 | 3.3796 | 0.49455 | -0.45121 | -3.3296 | -0.43727 | 1.5159 | 1.7119 | 3.1722 | -1.5077 | -1.6552 | -3.1072 | -73.096 | -162.9067 | 37.8229 | 106.904 | 17.0933 | -142.1771 | 1.1674 | 1.0583 | 0.83771 | 1.1602 | 1.0387 | 0.81874 | 0.079071 | -136.0422 | 118.9617 | 0.24336 | -136.4737 | 119.8124
Line_2 | 0.11748 | 0.31003 | 0.3319 | 0.11748 | 0.31003 | 0.3319 | 1.3565 | 3.5799 | 3.8325 | 1.3565 | 3.5799 | 3.8325 | 0.45839 | 3.3796 | 0.49455 | -0.45121 | -3.3296 | -0.43727 | 1.5159 | 1.7119 | 3.1722 | -1.5077 | -1.6552 | -3.1072 | -73.096 | -162.9067 | 37.8229 | 106.904 | 17.0933 | -142.1771 | 1.1674 | 1.0583 | 0.83771 | 1.1602 | 1.0387 | 0.81874 | 0.079071 | -136.0422 | 118.9617 | 0.24336 | -136.4737 | 119.8124

## LL_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.23496 | 0.62005 | 0.6638 | 0.23496 | 0.62005 | 0.6638 | 2.7131 | 7.1597 | 7.6649 | 2.7131 | 7.1597 | 7.6649 | -0.87371 | -6.4592 | -0.64541 | 0.90242 | 6.6591 | 0.87454 | -2.9829 | -3.0836 | -5.9544 | 3.0155 | 3.3104 | 6.2144 | 106.904 | 17.0933 | -142.1771 | -73.096 | -162.9067 | 37.8229 | 1.1456 | 0.99969 | 0.78139 | 1.1602 | 1.0387 | 0.81874 | 0.57818 | -137.3873 | 121.6367 | 0.24336 | -136.4737 | 119.8124
Line_1 | 0.11748 | 0.31003 | 0.3319 | 0.11748 | 0.31003 | 0.3319 | 1.3565 | 3.5799 | 3.8325 | 1.3565 | 3.5799 | 3.8325 | 0.45839 | 3.3796 | 0.49455 | -0.45121 | -3.3296 | -0.43727 | 1.5159 | 1.7119 | 3.1722 | -1.5077 | -1.6552 | -3.1072 | -73.096 | -162.9067 | 37.8229 | 106.904 | 17.0933 | -142.1771 | 1.1674 | 1.0583 | 0.83771 | 1.1602 | 1.0387 | 0.81874 | 0.079071 | -136.0422 | 118.9617 | 0.24336 | -136.4737 | 119.8124
Line_2 | 0.11748 | 0.31003 | 0.3319 | 0.11748 | 0.31003 | 0.3319 | 1.3565 | 3.5799 | 3.8325 | 1.3565 | 3.5799 | 3.8325 | 0.45839 | 3.3796 | 0.49455 | -0.45121 | -3.3296 | -0.43727 | 1.5159 | 1.7119 | 3.1722 | -1.5077 | -1.6552 | -3.1072 | -73.096 | -162.9067 | 37.8229 | 106.904 | 17.0933 | -142.1771 | 1.1674 | 1.0583 | 0.83771 | 1.1602 | 1.0387 | 0.81874 | 0.079071 | -136.0422 | 118.9617 | 0.24336 | -136.4737 | 119.8124

## LL_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.14393 | 1.2145 | 1.0782 | 0.14393 | 1.2145 | 1.0782 | 1.662 | 14.0243 | 12.4494 | 1.662 | 14.0243 | 12.4494 | -1.664 | -6.8035 | 5.9715 | 1.6847 | 8.2762 | -4.811 | -0.085413 | 1.7696 | -1.8123 | 0.097635 | -0.89926 | 2.4981 | 178.781 | 16.2989 | -161.3982 | -1.219 | -163.7011 | 18.6018 | 1.0025 | 0.50126 | 0.50126 | 1.0154 | 0.59361 | 0.43543 | 1.7195 | -178.2805 | -178.2805 | 2.0979 | -169.9023 | 171.1612
Line_1 | 0.071965 | 0.60727 | 0.53908 | 0.071965 | 0.60727 | 0.53908 | 0.83098 | 7.0121 | 6.2247 | 0.83098 | 7.0121 | 6.2247 | 0.8475 | 4.5063 | -2.1153 | -0.84233 | -4.1381 | 2.4055 | 0.051873 | -0.23205 | 1.4205 | -0.048818 | 0.44963 | -1.2491 | -1.219 | -163.7011 | 18.6018 | 178.781 | 16.2989 | -161.3982 | 1.0218 | 0.6435 | 0.40934 | 1.0154 | 0.59361 | 0.43543 | 2.2836 | -166.649 | 164.7195 | 2.0979 | -169.9023 | 171.1612
Line_2 | 0.071965 | 0.60727 | 0.53908 | 0.071965 | 0.60727 | 0.53908 | 0.83098 | 7.0121 | 6.2247 | 0.83098 | 7.0121 | 6.2247 | 0.8475 | 4.5063 | -2.1153 | -0.84233 | -4.1381 | 2.4055 | 0.051873 | -0.23205 | 1.4205 | -0.048818 | 0.44963 | -1.2491 | -1.219 | -163.7011 | 18.6018 | 178.781 | 16.2989 | -161.3982 | 1.0218 | 0.6435 | 0.40934 | 1.0154 | 0.59361 | 0.43543 | 2.2836 | -166.649 | 164.7195 | 2.0979 | -169.9023 | 171.1612

## LL_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.14393 | 1.2145 | 1.0782 | 0.14393 | 1.2145 | 1.0782 | 1.662 | 14.0243 | 12.4494 | 1.662 | 14.0243 | 12.4494 | -1.664 | -6.8035 | 5.9715 | 1.6847 | 8.2762 | -4.811 | -0.085413 | 1.7696 | -1.8123 | 0.097635 | -0.89926 | 2.4981 | 178.781 | 16.2989 | -161.3982 | -1.219 | -163.7011 | 18.6018 | 1.0025 | 0.50126 | 0.50126 | 1.0154 | 0.59361 | 0.43543 | 1.7195 | -178.2805 | -178.2805 | 2.0979 | -169.9023 | 171.1612
Line_1 | 0.071965 | 0.60727 | 0.53908 | 0.071965 | 0.60727 | 0.53908 | 0.83098 | 7.0121 | 6.2247 | 0.83098 | 7.0121 | 6.2247 | 0.8475 | 4.5063 | -2.1153 | -0.84233 | -4.1381 | 2.4055 | 0.051873 | -0.23205 | 1.4205 | -0.048818 | 0.44963 | -1.2491 | -1.219 | -163.7011 | 18.6018 | 178.781 | 16.2989 | -161.3982 | 1.0218 | 0.6435 | 0.40934 | 1.0154 | 0.59361 | 0.43543 | 2.2836 | -166.649 | 164.7195 | 2.0979 | -169.9023 | 171.1612
Line_2 | 0.071965 | 0.60727 | 0.53908 | 0.071965 | 0.60727 | 0.53908 | 0.83098 | 7.0121 | 6.2247 | 0.83098 | 7.0121 | 6.2247 | 0.8475 | 4.5063 | -2.1153 | -0.84233 | -4.1381 | 2.4055 | 0.051873 | -0.23205 | 1.4205 | -0.048818 | 0.44963 | -1.2491 | -1.219 | -163.7011 | 18.6018 | 178.781 | 16.2989 | -161.3982 | 1.0218 | 0.6435 | 0.40934 | 1.0154 | 0.59361 | 0.43543 | 2.2836 | -166.649 | 164.7195 | 2.0979 | -169.9023 | 171.1612

## LL_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.053172 | 0.44869 | 0.3983 | 0.053172 | 0.44869 | 0.3983 | 0.61398 | 5.181 | 4.5992 | 0.61398 | 5.181 | 4.5992 | -0.55942 | -4.4702 | -0.65138 | 0.56224 | 4.6712 | 0.80977 | 0.2469 | -0.04336 | -3.0398 | -0.24523 | 0.16214 | 3.1334 | -155.5905 | 41.9274 | -135.7696 | 24.4095 | -138.0726 | 44.2304 | 0.99594 | 0.86284 | 0.67595 | 0.99906 | 0.90214 | 0.70368 | 0.59555 | -137.5168 | 122.1359 | 0.84456 | -136.0846 | 119.7405
Line_1 | 0.026586 | 0.22434 | 0.19915 | 0.026586 | 0.22434 | 0.19915 | 0.30699 | 2.5905 | 2.2996 | 0.30699 | 2.5905 | 2.2996 | 0.28183 | 2.3858 | 0.44448 | -0.28112 | -2.3356 | -0.40488 | -0.1222 | 0.11076 | 1.5901 | 0.12261 | -0.081069 | -1.5667 | 24.4095 | -138.0726 | 44.2304 | -155.5905 | 41.9274 | -135.7696 | 1.0006 | 0.92199 | 0.71798 | 0.99906 | 0.90214 | 0.70368 | 0.96848 | -135.4145 | 118.6132 | 0.84456 | -136.0846 | 119.7405
Line_2 | 0.026586 | 0.22434 | 0.19915 | 0.026586 | 0.22434 | 0.19915 | 0.30699 | 2.5905 | 2.2996 | 0.30699 | 2.5905 | 2.2996 | 0.28183 | 2.3858 | 0.44448 | -0.28112 | -2.3356 | -0.40488 | -0.1222 | 0.11076 | 1.5901 | 0.12261 | -0.081069 | -1.5667 | 24.4095 | -138.0726 | 44.2304 | -155.5905 | 41.9274 | -135.7696 | 1.0006 | 0.92199 | 0.71798 | 0.99906 | 0.90214 | 0.70368 | 0.96848 | -135.4145 | 118.6132 | 0.84456 | -136.0846 | 119.7405

## LL_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.053172 | 0.44869 | 0.3983 | 0.053172 | 0.44869 | 0.3983 | 0.61398 | 5.181 | 4.5992 | 0.61398 | 5.181 | 4.5992 | -0.55942 | -4.4702 | -0.65138 | 0.56224 | 4.6712 | 0.80977 | 0.2469 | -0.04336 | -3.0398 | -0.24523 | 0.16214 | 3.1334 | -155.5905 | 41.9274 | -135.7696 | 24.4095 | -138.0726 | 44.2304 | 0.99594 | 0.86284 | 0.67595 | 0.99906 | 0.90214 | 0.70368 | 0.59555 | -137.5168 | 122.1359 | 0.84456 | -136.0846 | 119.7405
Line_1 | 0.026586 | 0.22434 | 0.19915 | 0.026586 | 0.22434 | 0.19915 | 0.30699 | 2.5905 | 2.2996 | 0.30699 | 2.5905 | 2.2996 | 0.28183 | 2.3858 | 0.44448 | -0.28112 | -2.3356 | -0.40488 | -0.1222 | 0.11076 | 1.5901 | 0.12261 | -0.081069 | -1.5667 | 24.4095 | -138.0726 | 44.2304 | -155.5905 | 41.9274 | -135.7696 | 1.0006 | 0.92199 | 0.71798 | 0.99906 | 0.90214 | 0.70368 | 0.96848 | -135.4145 | 118.6132 | 0.84456 | -136.0846 | 119.7405
Line_2 | 0.026586 | 0.22434 | 0.19915 | 0.026586 | 0.22434 | 0.19915 | 0.30699 | 2.5905 | 2.2996 | 0.30699 | 2.5905 | 2.2996 | 0.28183 | 2.3858 | 0.44448 | -0.28112 | -2.3356 | -0.40488 | -0.1222 | 0.11076 | 1.5901 | 0.12261 | -0.081069 | -1.5667 | 24.4095 | -138.0726 | 44.2304 | -155.5905 | 41.9274 | -135.7696 | 1.0006 | 0.92199 | 0.71798 | 0.99906 | 0.90214 | 0.70368 | 0.96848 | -135.4145 | 118.6132 | 0.84456 | -136.0846 | 119.7405

## LG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.6562 | 0.55268 | 0.7825 | 1.6567 | 0.55221 | 0.78205 | 19.124 | 6.3818 | 9.0355 | 19.1297 | 6.3764 | 9.0303 | 2.7002e-10 | 5.1873 | -8.1652 | 2.0754 | -5.2848 | 8.3523 | -1.7664e-10 | -3.9423 | -4.1654 | 2.249 | 3.971 | 4.1182 | 103.7072 | -61.8515 | -105.0495 | -76.2939 | 118.1643 | 74.935 |  | 0 | 1.0209 | 1.0145 | 0.15997 | 1.0367 | 1.0312 | 0 | -99.0861 | 101.9781 | -28.9951 | -98.7567 | 101.1811
Line_1 | 0.82867 | 0.27576 | 0.39079 | 0.82834 | 0.2761 | 0.39103 | 9.5686 | 3.1842 | 4.5124 | 9.5648 | 3.1882 | 4.5152 | 1.5582 | -2.6653 | 4.2203 | -1.0377 | 2.6424 | -4.1762 | 1.6877 | 1.9904 | 2.0484 | -1.1245 | -1.9855 | -2.0591 | -76.2866 | 118.1603 | 74.8982 | 103.7061 | -61.8357 | -105.065 |  | 0.24006 | 1.0447 | 1.0396 | 0.15997 | 1.0367 | 1.0312 | -29.002 | -98.5913 | 100.7892 | -28.9951 | -98.7567 | 101.1811
Line_2 | 0.82867 | 0.27576 | 0.39079 | 0.82834 | 0.2761 | 0.39103 | 9.5686 | 3.1842 | 4.5124 | 9.5648 | 3.1882 | 4.5152 | 1.5582 | -2.6653 | 4.2203 | -1.0377 | 2.6424 | -4.1762 | 1.6877 | 1.9904 | 2.0484 | -1.1245 | -1.9855 | -2.0591 | -76.2866 | 118.1603 | 74.8982 | 103.7061 | -61.8357 | -105.065 |  | 0.24006 | 1.0447 | 1.0396 | 0.15997 | 1.0367 | 1.0312 | -29.002 | -98.5913 | 100.7892 | -28.9951 | -98.7567 | 101.1811

## LG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.6562 | 0.55268 | 0.7825 | 1.6567 | 0.55221 | 0.78205 | 19.124 | 6.3818 | 9.0355 | 19.1297 | 6.3764 | 9.0303 | 2.7002e-10 | 5.1873 | -8.1652 | 2.0754 | -5.2848 | 8.3523 | -1.7664e-10 | -3.9423 | -4.1654 | 2.249 | 3.971 | 4.1182 | 103.7072 | -61.8515 | -105.0495 | -76.2939 | 118.1643 | 74.935 |  | 0 | 1.0209 | 1.0145 | 0.15997 | 1.0367 | 1.0312 | 0 | -99.0861 | 101.9781 | -28.9951 | -98.7567 | 101.1811
Line_1 | 0.82867 | 0.27576 | 0.39079 | 0.82834 | 0.2761 | 0.39103 | 9.5686 | 3.1842 | 4.5124 | 9.5648 | 3.1882 | 4.5152 | 1.5582 | -2.6653 | 4.2203 | -1.0377 | 2.6424 | -4.1762 | 1.6877 | 1.9904 | 2.0484 | -1.1245 | -1.9855 | -2.0591 | -76.2866 | 118.1603 | 74.8982 | 103.7061 | -61.8357 | -105.065 |  | 0.24006 | 1.0447 | 1.0396 | 0.15997 | 1.0367 | 1.0312 | -29.002 | -98.5913 | 100.7892 | -28.9951 | -98.7567 | 101.1811
Line_2 | 0.82867 | 0.27576 | 0.39079 | 0.82834 | 0.2761 | 0.39103 | 9.5686 | 3.1842 | 4.5124 | 9.5648 | 3.1882 | 4.5152 | 1.5582 | -2.6653 | 4.2203 | -1.0377 | 2.6424 | -4.1762 | 1.6877 | 1.9904 | 2.0484 | -1.1245 | -1.9855 | -2.0591 | -76.2866 | 118.1603 | 74.8982 | 103.7061 | -61.8357 | -105.065 |  | 0.24006 | 1.0447 | 1.0396 | 0.15997 | 1.0367 | 1.0312 | -29.002 | -98.5913 | 100.7892 | -28.9951 | -98.7567 | 101.1811

## LG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.44258 | 0.30305 | 0.26157 | 0.44266 | 0.30297 | 0.26155 | 5.1105 | 3.4993 | 3.0203 | 5.1114 | 3.4983 | 3.0201 | -2.7321 | 0.23126 | -1.7232 | 2.8514 | -0.20647 | 1.7718 | -4.2808 | -3.7961 | -3.0311 | 4.4345 | 3.8336 | 3.0521 | 116.2006 | -31.7769 | -123.4379 | -63.796 | 148.2269 | 56.5442 |  | 0.99371 | 1.0868 | 1.1544 | 1.0314 | 1.0974 | 1.1685 | -6.3456 | -118.2908 | 116.9441 | -6.5369 | -118.6904 | 116.4088
Line_1 | 0.22138 | 0.15142 | 0.13078 | 0.22133 | 0.15148 | 0.13077 | 2.5562 | 1.7485 | 1.5102 | 2.5557 | 1.7492 | 1.51 | 1.456 | -0.0972 | 0.8977 | -1.4257 | 0.10323 | -0.88589 | 2.2557 | 1.9257 | 1.5317 | -2.2172 | -1.9168 | -1.5261 | -63.7863 | 148.224 | 56.5187 | 116.204 | -31.7731 | -123.4558 |  | 1.0503 | 1.1027 | 1.1756 | 1.0314 | 1.0974 | 1.1685 | -6.6275 | -118.8864 | 116.1454 | -6.5369 | -118.6904 | 116.4088
Line_2 | 0.22138 | 0.15142 | 0.13078 | 0.22133 | 0.15148 | 0.13077 | 2.5562 | 1.7485 | 1.5102 | 2.5557 | 1.7492 | 1.51 | 1.456 | -0.0972 | 0.8977 | -1.4257 | 0.10323 | -0.88589 | 2.2557 | 1.9257 | 1.5317 | -2.2172 | -1.9168 | -1.5261 | -63.7863 | 148.224 | 56.5187 | 116.204 | -31.7731 | -123.4558 |  | 1.0503 | 1.1027 | 1.1756 | 1.0314 | 1.0974 | 1.1685 | -6.6275 | -118.8864 | 116.1454 | -6.5369 | -118.6904 | 116.4088

## LG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.44258 | 0.30305 | 0.26157 | 0.44266 | 0.30297 | 0.26155 | 5.1105 | 3.4993 | 3.0203 | 5.1114 | 3.4983 | 3.0201 | -2.7321 | 0.23126 | -1.7232 | 2.8514 | -0.20647 | 1.7718 | -4.2808 | -3.7961 | -3.0311 | 4.4345 | 3.8336 | 3.0521 | 116.2006 | -31.7769 | -123.4379 | -63.796 | 148.2269 | 56.5442 |  | 0.99371 | 1.0868 | 1.1544 | 1.0314 | 1.0974 | 1.1685 | -6.3456 | -118.2908 | 116.9441 | -6.5369 | -118.6904 | 116.4088
Line_1 | 0.22138 | 0.15142 | 0.13078 | 0.22133 | 0.15148 | 0.13077 | 2.5562 | 1.7485 | 1.5102 | 2.5557 | 1.7492 | 1.51 | 1.456 | -0.0972 | 0.8977 | -1.4257 | 0.10323 | -0.88589 | 2.2557 | 1.9257 | 1.5317 | -2.2172 | -1.9168 | -1.5261 | -63.7863 | 148.224 | 56.5187 | 116.204 | -31.7731 | -123.4558 |  | 1.0503 | 1.1027 | 1.1756 | 1.0314 | 1.0974 | 1.1685 | -6.6275 | -118.8864 | 116.1454 | -6.5369 | -118.6904 | 116.4088
Line_2 | 0.22138 | 0.15142 | 0.13078 | 0.22133 | 0.15148 | 0.13077 | 2.5562 | 1.7485 | 1.5102 | 2.5557 | 1.7492 | 1.51 | 1.456 | -0.0972 | 0.8977 | -1.4257 | 0.10323 | -0.88589 | 2.2557 | 1.9257 | 1.5317 | -2.2172 | -1.9168 | -1.5261 | -63.7863 | 148.224 | 56.5187 | 116.204 | -31.7731 | -123.4558 |  | 1.0503 | 1.1027 | 1.1756 | 1.0314 | 1.0974 | 1.1685 | -6.6275 | -118.8864 | 116.1454 | -6.5369 | -118.6904 | 116.4088

## LG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.2511 | 0.41506 | 0.63317 | 1.2515 | 0.41467 | 0.63278 | 14.4467 | 4.7927 | 7.3112 | 14.4512 | 4.7882 | 7.3067 | -1.0956e-10 | 3.988 | -6.3897 | 2.0607 | -3.9438 | 6.6135 | -2.957e-11 | -1.5055 | -0.6054 | 1.5419 | 1.378 | 0.47942 | 110.3569 | -78.4706 | -83.0577 | -69.6461 | 101.5299 | 96.9398 |  | 0 | 0.8894 | 0.87786 | 0.1781 | 0.87248 | 0.9075 | 0 | -99.1525 | 102.3547 | -32.8417 | -97.7302 | 101.086
Line_1 | 0.62595 | 0.20715 | 0.31622 | 0.62575 | 0.20733 | 0.31639 | 7.2278 | 2.392 | 3.6513 | 7.2256 | 2.3941 | 3.6533 | 1.547 | -1.9607 | 3.3614 | -1.0304 | 1.9719 | -3.3067 | 1.1569 | 0.6558 | 0.20914 | -0.77093 | -0.68901 | -0.23971 | -69.6393 | 101.5014 | 96.9185 | 110.3539 | -78.4701 | -83.0602 |  | 0.26726 | 0.86432 | 0.92237 | 0.1781 | 0.87248 | 0.9075 | -32.8503 | -96.9926 | 100.4788 | -32.8417 | -97.7302 | 101.086
Line_2 | 0.62595 | 0.20715 | 0.31622 | 0.62575 | 0.20733 | 0.31639 | 7.2278 | 2.392 | 3.6513 | 7.2256 | 2.3941 | 3.6533 | 1.547 | -1.9607 | 3.3614 | -1.0304 | 1.9719 | -3.3067 | 1.1569 | 0.6558 | 0.20914 | -0.77093 | -0.68901 | -0.23971 | -69.6393 | 101.5014 | 96.9185 | 110.3539 | -78.4701 | -83.0602 |  | 0.26726 | 0.86432 | 0.92237 | 0.1781 | 0.87248 | 0.9075 | -32.8503 | -96.9926 | 100.4788 | -32.8417 | -97.7302 | 101.086

## LG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.2511 | 0.41506 | 0.63317 | 1.2515 | 0.41467 | 0.63278 | 14.4467 | 4.7927 | 7.3112 | 14.4512 | 4.7882 | 7.3067 | -1.0956e-10 | 3.988 | -6.3897 | 2.0607 | -3.9438 | 6.6135 | -2.957e-11 | -1.5055 | -0.6054 | 1.5419 | 1.378 | 0.47942 | 110.3569 | -78.4706 | -83.0577 | -69.6461 | 101.5299 | 96.9398 |  | 0 | 0.8894 | 0.87786 | 0.1781 | 0.87248 | 0.9075 | 0 | -99.1525 | 102.3547 | -32.8417 | -97.7302 | 101.086
Line_1 | 0.62595 | 0.20715 | 0.31622 | 0.62575 | 0.20733 | 0.31639 | 7.2278 | 2.392 | 3.6513 | 7.2256 | 2.3941 | 3.6533 | 1.547 | -1.9607 | 3.3614 | -1.0304 | 1.9719 | -3.3067 | 1.1569 | 0.6558 | 0.20914 | -0.77093 | -0.68901 | -0.23971 | -69.6393 | 101.5014 | 96.9185 | 110.3539 | -78.4701 | -83.0602 |  | 0.26726 | 0.86432 | 0.92237 | 0.1781 | 0.87248 | 0.9075 | -32.8503 | -96.9926 | 100.4788 | -32.8417 | -97.7302 | 101.086
Line_2 | 0.62595 | 0.20715 | 0.31622 | 0.62575 | 0.20733 | 0.31639 | 7.2278 | 2.392 | 3.6513 | 7.2256 | 2.3941 | 3.6533 | 1.547 | -1.9607 | 3.3614 | -1.0304 | 1.9719 | -3.3067 | 1.1569 | 0.6558 | 0.20914 | -0.77093 | -0.68901 | -0.23971 | -69.6393 | 101.5014 | 96.9185 | 110.3539 | -78.4701 | -83.0602 |  | 0.26726 | 0.86432 | 0.92237 | 0.1781 | 0.87248 | 0.9075 | -32.8503 | -96.9926 | 100.4788 | -32.8417 | -97.7302 | 101.086

## LG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.21705 | 0.072006 | 0.10984 | 0.21711 | 0.071937 | 0.10978 | 2.5062 | 0.83145 | 1.2684 | 2.507 | 0.83066 | 1.2676 | -1.8649 | 0.231 | -1.2384 | 1.9275 | -0.22956 | 1.2445 | -1.0811 | -0.75178 | 0.29135 | 1.1279 | 0.74727 | -0.29491 | 143.5588 | -45.2686 | -49.8558 | -36.4441 | 134.7319 | 130.1417 |  | 0.8601 | 0.9459 | 1.003 | 0.8908 | 0.9411 | 1.009 | -6.3412 | -118.1881 | 116.9051 | -6.1093 | -118.1915 | 116.8102
Line_1 | 0.10859 | 0.035937 | 0.054858 | 0.10856 | 0.035968 | 0.054888 | 1.2539 | 0.41496 | 0.63344 | 1.2535 | 0.41533 | 0.63379 | 0.97964 | -0.11457 | 0.62365 | -0.96374 | 0.11478 | -0.62224 | 0.57562 | 0.3723 | -0.14809 | -0.56395 | -0.37363 | 0.14745 | -36.4373 | 134.7034 | 130.1205 | 143.5559 | -45.2681 | -49.8583 |  | 0.90617 | 0.9387 | 1.0119 | 0.8908 | 0.9411 | 1.009 | -5.9995 | -118.1919 | 116.7623 | -6.1093 | -118.1915 | 116.8102
Line_2 | 0.10859 | 0.035937 | 0.054858 | 0.10856 | 0.035968 | 0.054888 | 1.2539 | 0.41496 | 0.63344 | 1.2535 | 0.41533 | 0.63379 | 0.97964 | -0.11457 | 0.62365 | -0.96374 | 0.11478 | -0.62224 | 0.57562 | 0.3723 | -0.14809 | -0.56395 | -0.37363 | 0.14745 | -36.4373 | 134.7034 | 130.1205 | 143.5559 | -45.2681 | -49.8583 |  | 0.90617 | 0.9387 | 1.0119 | 0.8908 | 0.9411 | 1.009 | -5.9995 | -118.1919 | 116.7623 | -6.1093 | -118.1915 | 116.8102

## LG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.21705 | 0.072006 | 0.10984 | 0.21711 | 0.071937 | 0.10978 | 2.5062 | 0.83145 | 1.2684 | 2.507 | 0.83066 | 1.2676 | -1.8649 | 0.231 | -1.2384 | 1.9275 | -0.22956 | 1.2445 | -1.0811 | -0.75178 | 0.29135 | 1.1279 | 0.74727 | -0.29491 | 143.5588 | -45.2686 | -49.8558 | -36.4441 | 134.7319 | 130.1417 |  | 0.8601 | 0.9459 | 1.003 | 0.8908 | 0.9411 | 1.009 | -6.3412 | -118.1881 | 116.9051 | -6.1093 | -118.1915 | 116.8102
Line_1 | 0.10859 | 0.035937 | 0.054858 | 0.10856 | 0.035968 | 0.054888 | 1.2539 | 0.41496 | 0.63344 | 1.2535 | 0.41533 | 0.63379 | 0.97964 | -0.11457 | 0.62365 | -0.96374 | 0.11478 | -0.62224 | 0.57562 | 0.3723 | -0.14809 | -0.56395 | -0.37363 | 0.14745 | -36.4373 | 134.7034 | 130.1205 | 143.5559 | -45.2681 | -49.8583 |  | 0.90617 | 0.9387 | 1.0119 | 0.8908 | 0.9411 | 1.009 | -5.9995 | -118.1919 | 116.7623 | -6.1093 | -118.1915 | 116.8102
Line_2 | 0.10859 | 0.035937 | 0.054858 | 0.10856 | 0.035968 | 0.054888 | 1.2539 | 0.41496 | 0.63344 | 1.2535 | 0.41533 | 0.63379 | 0.97964 | -0.11457 | 0.62365 | -0.96374 | 0.11478 | -0.62224 | 0.57562 | 0.3723 | -0.14809 | -0.56395 | -0.37363 | 0.14745 | -36.4373 | 134.7034 | 130.1205 | 143.5559 | -45.2681 | -49.8583 |  | 0.90617 | 0.9387 | 1.0119 | 0.8908 | 0.9411 | 1.009 | -5.9995 | -118.1919 | 116.7623 | -6.1093 | -118.1915 | 116.8102

## LLG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.0509 | 1.8442 | 1.5898 | 1.0501 | 1.8445 | 1.5902 | 12.1346 | 21.2945 | 18.3574 | 12.126 | 21.2979 | 18.3626 | -1.0469 | 2.3276e-10 | 1.9876e-10 | 1.0223 | 3.2163 | 1.0692 | -6.783 | -1.6482e-10 | -1.4371e-10 | 6.7953 | 1.5128 | 2.7875 | 102.2015 | -12.2392 | -131.8848 | -77.7978 | 167.7394 | 48.1369 |  | 0.5656 | 0 | 0 | 0.5667 | 0.16689 | 0.16259 | 3.4274 | 0 | 0 | 3.6467 | -167.0699 | 117.1511
Line_1 | 0.52457 | 0.9226 | 0.79527 | 0.52507 | 0.92223 | 0.79512 | 6.0573 | 10.6532 | 9.1829 | 6.063 | 10.649 | 9.1813 | 0.50273 | 2.4141 | 0.80347 | -0.51115 | -1.6081 | -0.53461 | 3.3984 | 1.1352 | 2.0919 | -3.3977 | -0.75642 | -1.3937 | -77.8177 | 167.7161 | 48.1734 | 102.2022 | -12.2606 | -131.8631 |  | 0.56716 | 0.25041 | 0.24403 | 0.5667 | 0.16689 | 0.16259 | 3.7676 | -167.0994 | 117.1622 | 3.6467 | -167.0699 | 117.1511
Line_2 | 0.52457 | 0.9226 | 0.79527 | 0.52507 | 0.92223 | 0.79512 | 6.0573 | 10.6532 | 9.1829 | 6.063 | 10.649 | 9.1813 | 0.50273 | 2.4141 | 0.80347 | -0.51115 | -1.6081 | -0.53461 | 3.3984 | 1.1352 | 2.0919 | -3.3977 | -0.75642 | -1.3937 | -77.8177 | 167.7161 | 48.1734 | 102.2022 | -12.2606 | -131.8631 |  | 0.56716 | 0.25041 | 0.24403 | 0.5667 | 0.16689 | 0.16259 | 3.7676 | -167.0994 | 117.1622 | 3.6467 | -167.0699 | 117.1511

## LLG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.0509 | 1.8442 | 1.5898 | 1.0501 | 1.8445 | 1.5902 | 12.1346 | 21.2945 | 18.3574 | 12.126 | 21.2979 | 18.3626 | -1.0469 | 2.3276e-10 | 1.9876e-10 | 1.0223 | 3.2163 | 1.0692 | -6.783 | -1.6482e-10 | -1.4371e-10 | 6.7953 | 1.5128 | 2.7875 | 102.2015 | -12.2392 | -131.8848 | -77.7978 | 167.7394 | 48.1369 |  | 0.5656 | 0 | 0 | 0.5667 | 0.16689 | 0.16259 | 3.4274 | 0 | 0 | 3.6467 | -167.0699 | 117.1511
Line_1 | 0.52457 | 0.9226 | 0.79527 | 0.52507 | 0.92223 | 0.79512 | 6.0573 | 10.6532 | 9.1829 | 6.063 | 10.649 | 9.1813 | 0.50273 | 2.4141 | 0.80347 | -0.51115 | -1.6081 | -0.53461 | 3.3984 | 1.1352 | 2.0919 | -3.3977 | -0.75642 | -1.3937 | -77.8177 | 167.7161 | 48.1734 | 102.2022 | -12.2606 | -131.8631 |  | 0.56716 | 0.25041 | 0.24403 | 0.5667 | 0.16689 | 0.16259 | 3.7676 | -167.0994 | 117.1622 | 3.6467 | -167.0699 | 117.1511
Line_2 | 0.52457 | 0.9226 | 0.79527 | 0.52507 | 0.92223 | 0.79512 | 6.0573 | 10.6532 | 9.1829 | 6.063 | 10.649 | 9.1813 | 0.50273 | 2.4141 | 0.80347 | -0.51115 | -1.6081 | -0.53461 | 3.3984 | 1.1352 | 2.0919 | -3.3977 | -0.75642 | -1.3937 | -77.8177 | 167.7161 | 48.1734 | 102.2022 | -12.2606 | -131.8631 |  | 0.56716 | 0.25041 | 0.24403 | 0.5667 | 0.16689 | 0.16259 | 3.7676 | -167.0994 | 117.1622 | 3.6467 | -167.0699 | 117.1511

## LLG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.31394 | 0.49005 | 0.47354 | 0.31386 | 0.49011 | 0.47354 | 3.625 | 5.6587 | 5.4679 | 3.6241 | 5.6593 | 5.468 | -1.3756 | -4.0206 | -2.181 | 1.4185 | 4.1929 | 2.2667 | -3.7053 | -3.9829 | -4.6638 | 3.7332 | 4.1243 | 4.8289 | 108.6162 | 6.041 | -129.4013 | -71.3914 | -173.9668 | 50.6093 |  | 1.0903 | 1.0001 | 0.94159 | 1.102 | 1.0392 | 0.97557 | -1.7506 | -129.2291 | 115.536 | -2.1964 | -129.4398 | 115.4637
Line_1 | 0.15689 | 0.24511 | 0.23675 | 0.15693 | 0.24506 | 0.23677 | 1.8116 | 2.8303 | 2.7338 | 1.8121 | 2.8297 | 2.734 | 0.71944 | 2.1398 | 1.155 | -0.70925 | -2.0965 | -1.1333 | 1.8735 | 2.0979 | 2.4554 | -1.8666 | -2.0621 | -2.4144 | -71.4084 | -173.9735 | 50.6235 | 108.6086 | 6.0332 | -129.3907 |  | 1.1078 | 1.0588 | 0.99257 | 1.102 | 1.0392 | 0.97557 | -2.4157 | -129.5401 | 115.4302 | -2.1964 | -129.4398 | 115.4637
Line_2 | 0.15689 | 0.24511 | 0.23675 | 0.15693 | 0.24506 | 0.23677 | 1.8116 | 2.8303 | 2.7338 | 1.8121 | 2.8297 | 2.734 | 0.71944 | 2.1398 | 1.155 | -0.70925 | -2.0965 | -1.1333 | 1.8735 | 2.0979 | 2.4554 | -1.8666 | -2.0621 | -2.4144 | -71.4084 | -173.9735 | 50.6235 | 108.6086 | 6.0332 | -129.3907 |  | 1.1078 | 1.0588 | 0.99257 | 1.102 | 1.0392 | 0.97557 | -2.4157 | -129.5401 | 115.4302 | -2.1964 | -129.4398 | 115.4637

## LLG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.31394 | 0.49005 | 0.47354 | 0.31386 | 0.49011 | 0.47354 | 3.625 | 5.6587 | 5.4679 | 3.6241 | 5.6593 | 5.468 | -1.3756 | -4.0206 | -2.181 | 1.4185 | 4.1929 | 2.2667 | -3.7053 | -3.9829 | -4.6638 | 3.7332 | 4.1243 | 4.8289 | 108.6162 | 6.041 | -129.4013 | -71.3914 | -173.9668 | 50.6093 |  | 1.0903 | 1.0001 | 0.94159 | 1.102 | 1.0392 | 0.97557 | -1.7506 | -129.2291 | 115.536 | -2.1964 | -129.4398 | 115.4637
Line_1 | 0.15689 | 0.24511 | 0.23675 | 0.15693 | 0.24506 | 0.23677 | 1.8116 | 2.8303 | 2.7338 | 1.8121 | 2.8297 | 2.734 | 0.71944 | 2.1398 | 1.155 | -0.70925 | -2.0965 | -1.1333 | 1.8735 | 2.0979 | 2.4554 | -1.8666 | -2.0621 | -2.4144 | -71.4084 | -173.9735 | 50.6235 | 108.6086 | 6.0332 | -129.3907 |  | 1.1078 | 1.0588 | 0.99257 | 1.102 | 1.0392 | 0.97557 | -2.4157 | -129.5401 | 115.4302 | -2.1964 | -129.4398 | 115.4637
Line_2 | 0.15689 | 0.24511 | 0.23675 | 0.15693 | 0.24506 | 0.23677 | 1.8116 | 2.8303 | 2.7338 | 1.8121 | 2.8297 | 2.734 | 0.71944 | 2.1398 | 1.155 | -0.70925 | -2.0965 | -1.1333 | 1.8735 | 2.0979 | 2.4554 | -1.8666 | -2.0621 | -2.4144 | -71.4084 | -173.9735 | 50.6235 | 108.6086 | 6.0332 | -129.3907 |  | 1.1078 | 1.0588 | 0.99257 | 1.102 | 1.0392 | 0.97557 | -2.4157 | -129.5401 | 115.4302 | -2.1964 | -129.4398 | 115.4637

## LLG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.82589 | 1.4372 | 1.1966 | 0.8253 | 1.4373 | 1.197 | 9.5365 | 16.5955 | 13.8168 | 9.5297 | 16.5971 | 13.8213 | -1.2351 | -1.108e-10 | -8.8273e-11 | 1.439 | 3.3824 | 1.0265 | -4.579 | -4.1978e-11 | -4.5657e-11 | 4.3491 | 0.84191 | 1.9145 | 109.5051 | -1.6541 | -128.3392 | -70.4893 | 178.3228 | 51.6827 |  | 0.49731 | 0 | 0 | 0.48071 | 0.21001 | 0.15717 | 4.4094 | 0 | 0 | 1.2028 | -167.6997 | 113.484
Line_1 | 0.41236 | 0.71889 | 0.59853 | 0.41265 | 0.71867 | 0.59848 | 4.7615 | 8.301 | 6.9112 | 4.7648 | 8.2985 | 6.9106 | 0.76859 | 2.5383 | 0.77096 | -0.71951 | -1.6912 | -0.51324 | 2.1164 | 0.63125 | 1.4368 | -2.1746 | -0.42095 | -0.95724 | -70.506 | 178.3046 | 51.7124 | 109.5107 | -1.6772 | -128.3173 |  | 0.47289 | 0.3151 | 0.23594 | 0.48071 | 0.21001 | 0.15717 | -0.4649 | -167.7299 | 113.496 | 1.2028 | -167.6997 | 113.484
Line_2 | 0.41236 | 0.71889 | 0.59853 | 0.41265 | 0.71867 | 0.59848 | 4.7615 | 8.301 | 6.9112 | 4.7648 | 8.2985 | 6.9106 | 0.76859 | 2.5383 | 0.77096 | -0.71951 | -1.6912 | -0.51324 | 2.1164 | 0.63125 | 1.4368 | -2.1746 | -0.42095 | -0.95724 | -70.506 | 178.3046 | 51.7124 | 109.5107 | -1.6772 | -128.3173 |  | 0.47289 | 0.3151 | 0.23594 | 0.48071 | 0.21001 | 0.15717 | -0.4649 | -167.7299 | 113.496 | 1.2028 | -167.6997 | 113.484

## LLG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.82589 | 1.4372 | 1.1966 | 0.8253 | 1.4373 | 1.197 | 9.5365 | 16.5955 | 13.8168 | 9.5297 | 16.5971 | 13.8213 | -1.2351 | -1.108e-10 | -8.8273e-11 | 1.439 | 3.3824 | 1.0265 | -4.579 | -4.1978e-11 | -4.5657e-11 | 4.3491 | 0.84191 | 1.9145 | 109.5051 | -1.6541 | -128.3392 | -70.4893 | 178.3228 | 51.6827 |  | 0.49731 | 0 | 0 | 0.48071 | 0.21001 | 0.15717 | 4.4094 | 0 | 0 | 1.2028 | -167.6997 | 113.484
Line_1 | 0.41236 | 0.71889 | 0.59853 | 0.41265 | 0.71867 | 0.59848 | 4.7615 | 8.301 | 6.9112 | 4.7648 | 8.2985 | 6.9106 | 0.76859 | 2.5383 | 0.77096 | -0.71951 | -1.6912 | -0.51324 | 2.1164 | 0.63125 | 1.4368 | -2.1746 | -0.42095 | -0.95724 | -70.506 | 178.3046 | 51.7124 | 109.5107 | -1.6772 | -128.3173 |  | 0.47289 | 0.3151 | 0.23594 | 0.48071 | 0.21001 | 0.15717 | -0.4649 | -167.7299 | 113.496 | 1.2028 | -167.6997 | 113.484
Line_2 | 0.41236 | 0.71889 | 0.59853 | 0.41265 | 0.71867 | 0.59848 | 4.7615 | 8.301 | 6.9112 | 4.7648 | 8.2985 | 6.9106 | 0.76859 | 2.5383 | 0.77096 | -0.71951 | -1.6912 | -0.51324 | 2.1164 | 0.63125 | 1.4368 | -2.1746 | -0.42095 | -0.95724 | -70.506 | 178.3046 | 51.7124 | 109.5107 | -1.6772 | -128.3173 |  | 0.47289 | 0.3151 | 0.23594 | 0.48071 | 0.21001 | 0.15717 | -0.4649 | -167.7299 | 113.496 | 1.2028 | -167.6997 | 113.484

## LLG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.1075 | 0.29431 | 0.23631 | 0.10743 | 0.29433 | 0.23634 | 1.2413 | 3.3984 | 2.7287 | 1.2405 | 3.3986 | 2.729 | -1.0416 | -2.8486 | -1.511 | 1.044 | 2.967 | 1.5504 | -0.54356 | -0.71225 | -1.631 | 0.54092 | 0.7526 | 1.6851 | 150.7542 | 36.6981 | -111.5452 | -29.2362 | -143.3157 | 68.471 |  | 0.94654 | 0.86402 | 0.81482 | 0.94786 | 0.90065 | 0.83908 | -1.688 | -129.2638 | 115.643 | -1.8459 | -129.0822 | 115.8538
Line_1 | 0.053677 | 0.14719 | 0.11816 | 0.053713 | 0.14716 | 0.11817 | 0.6198 | 1.6996 | 1.3644 | 0.62023 | 1.6993 | 1.3645 | 0.5223 | 1.5133 | 0.78517 | -0.52198 | -1.4835 | -0.77522 | 0.26984 | 0.38654 | 0.85586 | -0.27046 | -0.3763 | -0.84254 | -29.2472 | -143.3271 | 68.4892 | 150.7638 | 36.6843 | -111.529 |  | 0.9485 | 0.91898 | 0.85124 | 0.94786 | 0.90065 | 0.83908 | -1.9244 | -128.9982 | 115.9557 | -1.8459 | -129.0822 | 115.8538
Line_2 | 0.053677 | 0.14719 | 0.11816 | 0.053713 | 0.14716 | 0.11817 | 0.6198 | 1.6996 | 1.3644 | 0.62023 | 1.6993 | 1.3645 | 0.5223 | 1.5133 | 0.78517 | -0.52198 | -1.4835 | -0.77522 | 0.26984 | 0.38654 | 0.85586 | -0.27046 | -0.3763 | -0.84254 | -29.2472 | -143.3271 | 68.4892 | 150.7638 | 36.6843 | -111.529 |  | 0.9485 | 0.91898 | 0.85124 | 0.94786 | 0.90065 | 0.83908 | -1.9244 | -128.9982 | 115.9557 | -1.8459 | -129.0822 | 115.8538

## LLG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.1075 | 0.29431 | 0.23631 | 0.10743 | 0.29433 | 0.23634 | 1.2413 | 3.3984 | 2.7287 | 1.2405 | 3.3986 | 2.729 | -1.0416 | -2.8486 | -1.511 | 1.044 | 2.967 | 1.5504 | -0.54356 | -0.71225 | -1.631 | 0.54092 | 0.7526 | 1.6851 | 150.7542 | 36.6981 | -111.5452 | -29.2362 | -143.3157 | 68.471 |  | 0.94654 | 0.86402 | 0.81482 | 0.94786 | 0.90065 | 0.83908 | -1.688 | -129.2638 | 115.643 | -1.8459 | -129.0822 | 115.8538
Line_1 | 0.053677 | 0.14719 | 0.11816 | 0.053713 | 0.14716 | 0.11817 | 0.6198 | 1.6996 | 1.3644 | 0.62023 | 1.6993 | 1.3645 | 0.5223 | 1.5133 | 0.78517 | -0.52198 | -1.4835 | -0.77522 | 0.26984 | 0.38654 | 0.85586 | -0.27046 | -0.3763 | -0.84254 | -29.2472 | -143.3271 | 68.4892 | 150.7638 | 36.6843 | -111.529 |  | 0.9485 | 0.91898 | 0.85124 | 0.94786 | 0.90065 | 0.83908 | -1.9244 | -128.9982 | 115.9557 | -1.8459 | -129.0822 | 115.8538
Line_2 | 0.053677 | 0.14719 | 0.11816 | 0.053713 | 0.14716 | 0.11817 | 0.6198 | 1.6996 | 1.3644 | 0.62023 | 1.6993 | 1.3645 | 0.5223 | 1.5133 | 0.78517 | -0.52198 | -1.4835 | -0.77522 | 0.26984 | 0.38654 | 0.85586 | -0.27046 | -0.3763 | -0.84254 | -29.2472 | -143.3271 | 68.4892 | 150.7638 | 36.6843 | -111.529 |  | 0.9485 | 0.91898 | 0.85124 | 0.94786 | 0.90065 | 0.83908 | -1.9244 | -128.9982 | 115.9557 | -1.8459 | -129.0822 | 115.8538