## LLL_max_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 1.7394 | 1.7394 | 4.0301 | 0 | 60.2556 | 60.2556 | -1e-07 | 4.72 | -1e-07 | 5.3553 | 107.5423 | -72.4577 | 0 | 0.11847 | 0 | -23.8492
Line_1 | 0.86972 | 0.86972 | 0 | 0 | 30.1278 | 30.1278 | 3.54 | -2.36 | 4.0165 | -2.6777 | -72.4577 | 107.5423 | 0.1777 | 0.11847 | -23.8492 | -23.8492
Line_2 | 0.86972 | 0.86972 | 0 | 0 | 30.1278 | 30.1278 | 3.54 | -2.36 | 4.0165 | -2.6777 | -72.4577 | 107.5423 | 0.1777 | 0.11847 | -23.8492 | -23.8492

## LLL_max_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 1.7394 | 1.7394 | 4.0301 | 0 | 60.2556 | 60.2556 | -1e-07 | 4.72 | -1e-07 | 5.3553 | 107.5423 | -72.4577 | 0 | 0.11847 | 0 | -23.8492
Line_1 | 0.86972 | 0.86972 | 0 | 0 | 30.1278 | 30.1278 | 3.54 | -2.36 | 4.0165 | -2.6777 | -72.4577 | 107.5423 | 0.1777 | 0.11847 | -23.8492 | -23.8492
Line_2 | 0.86972 | 0.86972 | 0 | 0 | 30.1278 | 30.1278 | 3.54 | -2.36 | 4.0165 | -2.6777 | -72.4577 | 107.5423 | 0.1777 | 0.11847 | -23.8492 | -23.8492

## LLL_max_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.51746 | 0.51746 | 1.048 | 0 | 17.9254 | 17.9254 | -10.4881 | 10.9059 | -13.3195 | 13.7934 | 120.4894 | -59.5106 | 0.94576 | 0.98095 | -7.7285 | -7.8425
Line_1 | 0.25873 | 0.25873 | 0 | 0 | 8.9627 | 8.9627 | 5.5574 | -5.4529 | 7.0152 | -6.8967 | -59.5106 | 120.4894 | 0.99855 | 0.98095 | -7.8965 | -7.8425
Line_2 | 0.25873 | 0.25873 | 0 | 0 | 8.9627 | 8.9627 | 5.5574 | -5.4529 | 7.0152 | -6.8967 | -59.5106 | 120.4894 | 0.99855 | 0.98095 | -7.8965 | -7.8425

## LLL_max_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.51746 | 0.51746 | 1.048 | 0 | 17.9254 | 17.9254 | -10.4881 | 10.9059 | -13.3195 | 13.7934 | 120.4894 | -59.5106 | 0.94576 | 0.98095 | -7.7285 | -7.8425
Line_1 | 0.25873 | 0.25873 | 0 | 0 | 8.9627 | 8.9627 | 5.5574 | -5.4529 | 7.0152 | -6.8967 | -59.5106 | 120.4894 | 0.99855 | 0.98095 | -7.8965 | -7.8425
Line_2 | 0.25873 | 0.25873 | 0 | 0 | 8.9627 | 8.9627 | 5.5574 | -5.4529 | 7.0152 | -6.8967 | -59.5106 | 120.4894 | 0.99855 | 0.98095 | -7.8965 | -7.8425

## LLL_min_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 1.3783 | 1.3783 | 3.412 | 0 | 47.7473 | 47.7473 | -1e-07 | 5.6904 | -1e-07 | 3.3627 | 114.7975 | -65.2025 | 0 | 0.13843 | 0 | -34.6217
Line_1 | 0.68917 | 0.68917 | 0 | 0 | 23.8737 | 23.8737 | 4.2678 | -2.8452 | 2.522 | -1.6814 | -65.2025 | 114.7975 | 0.20765 | 0.13843 | -34.6217 | -34.6217
Line_2 | 0.68917 | 0.68917 | 0 | 0 | 23.8737 | 23.8737 | 4.2678 | -2.8452 | 2.522 | -1.6814 | -65.2025 | 114.7975 | 0.20765 | 0.13843 | -34.6217 | -34.6217

## LLL_min_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 1.3783 | 1.3783 | 3.412 | 0 | 47.7473 | 47.7473 | -1e-07 | 5.6904 | -1e-07 | 3.3627 | 114.7975 | -65.2025 | 0 | 0.13843 | 0 | -34.6217
Line_1 | 0.68917 | 0.68917 | 0 | 0 | 23.8737 | 23.8737 | 4.2678 | -2.8452 | 2.522 | -1.6814 | -65.2025 | 114.7975 | 0.20765 | 0.13843 | -34.6217 | -34.6217
Line_2 | 0.68917 | 0.68917 | 0 | 0 | 23.8737 | 23.8737 | 4.2678 | -2.8452 | 2.522 | -1.6814 | -65.2025 | 114.7975 | 0.20765 | 0.13843 | -34.6217 | -34.6217

## LLL_min_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.30266 | 0.30266 | 0.74922 | 0 | 10.4846 | 10.4846 | -7.5715 | 7.8458 | -3.9965 | 4.1586 | 144.5132 | -35.4868 | 0.81658 | 0.84694 | -7.6601 | -7.5613
Line_1 | 0.15133 | 0.15133 | 0 | 0 | 5.2423 | 5.2423 | 3.9915 | -3.9229 | 2.1199 | -2.0793 | -35.4868 | 144.5132 | 0.86212 | 0.84694 | -7.5145 | -7.5613
Line_2 | 0.15133 | 0.15133 | 0 | 0 | 5.2423 | 5.2423 | 3.9915 | -3.9229 | 2.1199 | -2.0793 | -35.4868 | 144.5132 | 0.86212 | 0.84694 | -7.5145 | -7.5613

## LLL_min_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.30266 | 0.30266 | 0.74922 | 0 | 10.4846 | 10.4846 | -7.5715 | 7.8458 | -3.9965 | 4.1586 | 144.5132 | -35.4868 | 0.81658 | 0.84694 | -7.6601 | -7.5613
Line_1 | 0.15133 | 0.15133 | 0 | 0 | 5.2423 | 5.2423 | 3.9915 | -3.9229 | 2.1199 | -2.0793 | -35.4868 | 144.5132 | 0.86212 | 0.84694 | -7.5145 | -7.5613
Line_2 | 0.15133 | 0.15133 | 0 | 0 | 5.2423 | 5.2423 | 3.9915 | -3.9229 | 2.1199 | -2.0793 | -35.4868 | 144.5132 | 0.86212 | 0.84694 | -7.5145 | -7.5613

## LL_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.32048 | 1.5098 | 1.3931 | 0.32048 | 1.5098 | 1.3931 | 3.7006 | 17.4334 | 16.0862 | 3.7006 | 17.4334 | 16.0862 | -2.2014 | -10.0544 | 8.9537 | 2.2548 | 11.2397 | -7.9445 | -3.6682 | 0.67371 | -2.5078 | 3.7288 | 0.67115 | 3.6529 | 122.5535 | 5.4174 | -162.7693 | -57.4465 | -174.5826 | 17.2307 | 1.1561 | 0.57803 | 0.57803 | 1.1775 | 0.64587 | 0.54357 | 1.5839 | -178.4161 | -178.4161 | 1.3918 | -171.1654 | 172.538
Line_1 | 0.16024 | 0.75489 | 0.69655 | 0.16024 | 0.75489 | 0.69655 | 1.8503 | 8.7167 | 8.0431 | 1.8503 | 8.7167 | 8.0431 | 1.1408 | 5.9162 | -3.72 | -1.1274 | -5.6199 | 3.9723 | 1.8795 | 0.67179 | 2.1127 | -1.8644 | -0.33558 | -1.8264 | -57.4465 | -174.5826 | 17.2307 | 122.5535 | 5.4174 | -162.7693 | 1.1883 | 0.68308 | 0.53189 | 1.1775 | 0.64587 | 0.54357 | 1.2983 | -168.1044 | 167.6371 | 1.3918 | -171.1654 | 172.538
Line_2 | 0.16024 | 0.75489 | 0.69655 | 0.16024 | 0.75489 | 0.69655 | 1.8503 | 8.7167 | 8.0431 | 1.8503 | 8.7167 | 8.0431 | 1.1408 | 5.9162 | -3.72 | -1.1274 | -5.6199 | 3.9723 | 1.8795 | 0.67179 | 2.1127 | -1.8644 | -0.33558 | -1.8264 | -57.4465 | -174.5826 | 17.2307 | 122.5535 | 5.4174 | -162.7693 | 1.1883 | 0.68308 | 0.53189 | 1.1775 | 0.64587 | 0.54357 | 1.2983 | -168.1044 | 167.6371 | 1.3918 | -171.1654 | 172.538

## LL_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.32048 | 1.5098 | 1.3931 | 0.32048 | 1.5098 | 1.3931 | 3.7006 | 17.4334 | 16.0862 | 3.7006 | 17.4334 | 16.0862 | -2.2014 | -10.0544 | 8.9537 | 2.2548 | 11.2397 | -7.9445 | -3.6682 | 0.67371 | -2.5078 | 3.7288 | 0.67115 | 3.6529 | 122.5535 | 5.4174 | -162.7693 | -57.4465 | -174.5826 | 17.2307 | 1.1561 | 0.57803 | 0.57803 | 1.1775 | 0.64587 | 0.54357 | 1.5839 | -178.4161 | -178.4161 | 1.3918 | -171.1654 | 172.538
Line_1 | 0.16024 | 0.75489 | 0.69655 | 0.16024 | 0.75489 | 0.69655 | 1.8503 | 8.7167 | 8.0431 | 1.8503 | 8.7167 | 8.0431 | 1.1408 | 5.9162 | -3.72 | -1.1274 | -5.6199 | 3.9723 | 1.8795 | 0.67179 | 2.1127 | -1.8644 | -0.33558 | -1.8264 | -57.4465 | -174.5826 | 17.2307 | 122.5535 | 5.4174 | -162.7693 | 1.1883 | 0.68308 | 0.53189 | 1.1775 | 0.64587 | 0.54357 | 1.2983 | -168.1044 | 167.6371 | 1.3918 | -171.1654 | 172.538
Line_2 | 0.16024 | 0.75489 | 0.69655 | 0.16024 | 0.75489 | 0.69655 | 1.8503 | 8.7167 | 8.0431 | 1.8503 | 8.7167 | 8.0431 | 1.1408 | 5.9162 | -3.72 | -1.1274 | -5.6199 | 3.9723 | 1.8795 | 0.67179 | 2.1127 | -1.8644 | -0.33558 | -1.8264 | -57.4465 | -174.5826 | 17.2307 | 122.5535 | 5.4174 | -162.7693 | 1.1883 | 0.68308 | 0.53189 | 1.1775 | 0.64587 | 0.54357 | 1.2983 | -168.1044 | 167.6371 | 1.3918 | -171.1654 | 172.538

## LL_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.23496 | 0.62005 | 0.6638 | 0.23496 | 0.62005 | 0.6638 | 2.7131 | 7.1597 | 7.6649 | 2.7131 | 7.1597 | 7.6649 | -0.87371 | -6.4592 | -0.64541 | 0.90242 | 6.6591 | 0.87454 | -2.9829 | -3.0836 | -5.9544 | 3.0155 | 3.3104 | 6.2144 | 106.904 | 17.0933 | -142.1771 | -73.096 | -162.9067 | 37.8229 | 1.1456 | 0.99969 | 0.78139 | 1.1602 | 1.0387 | 0.81874 | 0.57818 | -137.3873 | 121.6367 | 0.24336 | -136.4737 | 119.8124
Line_1 | 0.11748 | 0.31003 | 0.3319 | 0.11748 | 0.31003 | 0.3319 | 1.3565 | 3.5799 | 3.8325 | 1.3565 | 3.5799 | 3.8325 | 0.45839 | 3.3796 | 0.49455 | -0.45121 | -3.3296 | -0.43727 | 1.5159 | 1.7119 | 3.1722 | -1.5077 | -1.6552 | -3.1072 | -73.096 | -162.9067 | 37.8229 | 106.904 | 17.0933 | -142.1771 | 1.1674 | 1.0583 | 0.83771 | 1.1602 | 1.0387 | 0.81874 | 0.079071 | -136.0422 | 118.9617 | 0.24336 | -136.4737 | 119.8124
Line_2 | 0.11748 | 0.31003 | 0.3319 | 0.11748 | 0.31003 | 0.3319 | 1.3565 | 3.5799 | 3.8325 | 1.3565 | 3.5799 | 3.8325 | 0.45839 | 3.3796 | 0.49455 | -0.45121 | -3.3296 | -0.43727 | 1.5159 | 1.7119 | 3.1722 | -1.5077 | -1.6552 | -3.1072 | -73.096 | -162.9067 | 37.8229 | 106.904 | 17.0933 | -142.1771 | 1.1674 | 1.0583 | 0.83771 | 1.1602 | 1.0387 | 0.81874 | 0.079071 | -136.0422 | 118.9617 | 0.24336 | -136.4737 | 119.8124

## LL_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.23496 | 0.62005 | 0.6638 | 0.23496 | 0.62005 | 0.6638 | 2.7131 | 7.1597 | 7.6649 | 2.7131 | 7.1597 | 7.6649 | -0.87371 | -6.4592 | -0.64541 | 0.90242 | 6.6591 | 0.87454 | -2.9829 | -3.0836 | -5.9544 | 3.0155 | 3.3104 | 6.2144 | 106.904 | 17.0933 | -142.1771 | -73.096 | -162.9067 | 37.8229 | 1.1456 | 0.99969 | 0.78139 | 1.1602 | 1.0387 | 0.81874 | 0.57818 | -137.3873 | 121.6367 | 0.24336 | -136.4737 | 119.8124
Line_1 | 0.11748 | 0.31003 | 0.3319 | 0.11748 | 0.31003 | 0.3319 | 1.3565 | 3.5799 | 3.8325 | 1.3565 | 3.5799 | 3.8325 | 0.45839 | 3.3796 | 0.49455 | -0.45121 | -3.3296 | -0.43727 | 1.5159 | 1.7119 | 3.1722 | -1.5077 | -1.6552 | -3.1072 | -73.096 | -162.9067 | 37.8229 | 106.904 | 17.0933 | -142.1771 | 1.1674 | 1.0583 | 0.83771 | 1.1602 | 1.0387 | 0.81874 | 0.079071 | -136.0422 | 118.9617 | 0.24336 | -136.4737 | 119.8124
Line_2 | 0.11748 | 0.31003 | 0.3319 | 0.11748 | 0.31003 | 0.3319 | 1.3565 | 3.5799 | 3.8325 | 1.3565 | 3.5799 | 3.8325 | 0.45839 | 3.3796 | 0.49455 | -0.45121 | -3.3296 | -0.43727 | 1.5159 | 1.7119 | 3.1722 | -1.5077 | -1.6552 | -3.1072 | -73.096 | -162.9067 | 37.8229 | 106.904 | 17.0933 | -142.1771 | 1.1674 | 1.0583 | 0.83771 | 1.1602 | 1.0387 | 0.81874 | 0.079071 | -136.0422 | 118.9617 | 0.24336 | -136.4737 | 119.8124

## LL_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.14393 | 1.2145 | 1.0782 | 0.14393 | 1.2145 | 1.0782 | 1.662 | 14.0243 | 12.4494 | 1.662 | 14.0243 | 12.4494 | -1.664 | -6.8035 | 5.9715 | 1.6847 | 8.2762 | -4.811 | -0.085413 | 1.7696 | -1.8123 | 0.097635 | -0.89926 | 2.4981 | 178.781 | 16.2989 | -161.3982 | -1.219 | -163.7011 | 18.6018 | 1.0025 | 0.50126 | 0.50126 | 1.0154 | 0.59361 | 0.43543 | 1.7195 | -178.2805 | -178.2805 | 2.0979 | -169.9023 | 171.1612
Line_1 | 0.071965 | 0.60727 | 0.53908 | 0.071965 | 0.60727 | 0.53908 | 0.83098 | 7.0121 | 6.2247 | 0.83098 | 7.0121 | 6.2247 | 0.8475 | 4.5063 | -2.1153 | -0.84233 | -4.1381 | 2.4055 | 0.051873 | -0.23205 | 1.4205 | -0.048818 | 0.44963 | -1.2491 | -1.219 | -163.7011 | 18.6018 | 178.781 | 16.2989 | -161.3982 | 1.0218 | 0.6435 | 0.40934 | 1.0154 | 0.59361 | 0.43543 | 2.2836 | -166.649 | 164.7195 | 2.0979 | -169.9023 | 171.1612
Line_2 | 0.071965 | 0.60727 | 0.53908 | 0.071965 | 0.60727 | 0.53908 | 0.83098 | 7.0121 | 6.2247 | 0.83098 | 7.0121 | 6.2247 | 0.8475 | 4.5063 | -2.1153 | -0.84233 | -4.1381 | 2.4055 | 0.051873 | -0.23205 | 1.4205 | -0.048818 | 0.44963 | -1.2491 | -1.219 | -163.7011 | 18.6018 | 178.781 | 16.2989 | -161.3982 | 1.0218 | 0.6435 | 0.40934 | 1.0154 | 0.59361 | 0.43543 | 2.2836 | -166.649 | 164.7195 | 2.0979 | -169.9023 | 171.1612

## LL_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.14393 | 1.2145 | 1.0782 | 0.14393 | 1.2145 | 1.0782 | 1.662 | 14.0243 | 12.4494 | 1.662 | 14.0243 | 12.4494 | -1.664 | -6.8035 | 5.9715 | 1.6847 | 8.2762 | -4.811 | -0.085413 | 1.7696 | -1.8123 | 0.097635 | -0.89926 | 2.4981 | 178.781 | 16.2989 | -161.3982 | -1.219 | -163.7011 | 18.6018 | 1.0025 | 0.50126 | 0.50126 | 1.0154 | 0.59361 | 0.43543 | 1.7195 | -178.2805 | -178.2805 | 2.0979 | -169.9023 | 171.1612
Line_1 | 0.071965 | 0.60727 | 0.53908 | 0.071965 | 0.60727 | 0.53908 | 0.83098 | 7.0121 | 6.2247 | 0.83098 | 7.0121 | 6.2247 | 0.8475 | 4.5063 | -2.1153 | -0.84233 | -4.1381 | 2.4055 | 0.051873 | -0.23205 | 1.4205 | -0.048818 | 0.44963 | -1.2491 | -1.219 | -163.7011 | 18.6018 | 178.781 | 16.2989 | -161.3982 | 1.0218 | 0.6435 | 0.40934 | 1.0154 | 0.59361 | 0.43543 | 2.2836 | -166.649 | 164.7195 | 2.0979 | -169.9023 | 171.1612
Line_2 | 0.071965 | 0.60727 | 0.53908 | 0.071965 | 0.60727 | 0.53908 | 0.83098 | 7.0121 | 6.2247 | 0.83098 | 7.0121 | 6.2247 | 0.8475 | 4.5063 | -2.1153 | -0.84233 | -4.1381 | 2.4055 | 0.051873 | -0.23205 | 1.4205 | -0.048818 | 0.44963 | -1.2491 | -1.219 | -163.7011 | 18.6018 | 178.781 | 16.2989 | -161.3982 | 1.0218 | 0.6435 | 0.40934 | 1.0154 | 0.59361 | 0.43543 | 2.2836 | -166.649 | 164.7195 | 2.0979 | -169.9023 | 171.1612

## LL_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.053172 | 0.44869 | 0.3983 | 0.053172 | 0.44869 | 0.3983 | 0.61398 | 5.181 | 4.5992 | 0.61398 | 5.181 | 4.5992 | -0.55942 | -4.4702 | -0.65138 | 0.56224 | 4.6712 | 0.80977 | 0.2469 | -0.04336 | -3.0398 | -0.24523 | 0.16214 | 3.1334 | -155.5905 | 41.9274 | -135.7696 | 24.4095 | -138.0726 | 44.2304 | 0.99594 | 0.86284 | 0.67595 | 0.99906 | 0.90214 | 0.70368 | 0.59555 | -137.5168 | 122.1359 | 0.84456 | -136.0846 | 119.7405
Line_1 | 0.026586 | 0.22434 | 0.19915 | 0.026586 | 0.22434 | 0.19915 | 0.30699 | 2.5905 | 2.2996 | 0.30699 | 2.5905 | 2.2996 | 0.28183 | 2.3858 | 0.44448 | -0.28112 | -2.3356 | -0.40488 | -0.1222 | 0.11076 | 1.5901 | 0.12261 | -0.081069 | -1.5667 | 24.4095 | -138.0726 | 44.2304 | -155.5905 | 41.9274 | -135.7696 | 1.0006 | 0.92199 | 0.71798 | 0.99906 | 0.90214 | 0.70368 | 0.96848 | -135.4145 | 118.6132 | 0.84456 | -136.0846 | 119.7405
Line_2 | 0.026586 | 0.22434 | 0.19915 | 0.026586 | 0.22434 | 0.19915 | 0.30699 | 2.5905 | 2.2996 | 0.30699 | 2.5905 | 2.2996 | 0.28183 | 2.3858 | 0.44448 | -0.28112 | -2.3356 | -0.40488 | -0.1222 | 0.11076 | 1.5901 | 0.12261 | -0.081069 | -1.5667 | 24.4095 | -138.0726 | 44.2304 | -155.5905 | 41.9274 | -135.7696 | 1.0006 | 0.92199 | 0.71798 | 0.99906 | 0.90214 | 0.70368 | 0.96848 | -135.4145 | 118.6132 | 0.84456 | -136.0846 | 119.7405

## LL_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.053172 | 0.44869 | 0.3983 | 0.053172 | 0.44869 | 0.3983 | 0.61398 | 5.181 | 4.5992 | 0.61398 | 5.181 | 4.5992 | -0.55942 | -4.4702 | -0.65138 | 0.56224 | 4.6712 | 0.80977 | 0.2469 | -0.04336 | -3.0398 | -0.24523 | 0.16214 | 3.1334 | -155.5905 | 41.9274 | -135.7696 | 24.4095 | -138.0726 | 44.2304 | 0.99594 | 0.86284 | 0.67595 | 0.99906 | 0.90214 | 0.70368 | 0.59555 | -137.5168 | 122.1359 | 0.84456 | -136.0846 | 119.7405
Line_1 | 0.026586 | 0.22434 | 0.19915 | 0.026586 | 0.22434 | 0.19915 | 0.30699 | 2.5905 | 2.2996 | 0.30699 | 2.5905 | 2.2996 | 0.28183 | 2.3858 | 0.44448 | -0.28112 | -2.3356 | -0.40488 | -0.1222 | 0.11076 | 1.5901 | 0.12261 | -0.081069 | -1.5667 | 24.4095 | -138.0726 | 44.2304 | -155.5905 | 41.9274 | -135.7696 | 1.0006 | 0.92199 | 0.71798 | 0.99906 | 0.90214 | 0.70368 | 0.96848 | -135.4145 | 118.6132 | 0.84456 | -136.0846 | 119.7405
Line_2 | 0.026586 | 0.22434 | 0.19915 | 0.026586 | 0.22434 | 0.19915 | 0.30699 | 2.5905 | 2.2996 | 0.30699 | 2.5905 | 2.2996 | 0.28183 | 2.3858 | 0.44448 | -0.28112 | -2.3356 | -0.40488 | -0.1222 | 0.11076 | 1.5901 | 0.12261 | -0.081069 | -1.5667 | 24.4095 | -138.0726 | 44.2304 | -155.5905 | 41.9274 | -135.7696 | 1.0006 | 0.92199 | 0.71798 | 0.99906 | 0.90214 | 0.70368 | 0.96848 | -135.4145 | 118.6132 | 0.84456 | -136.0846 | 119.7405

## LG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.7743 | 0.75373 | 0.86722 | 1.7772 | 0.75689 | 0.86949 | 20.488 | 8.7034 | 10.0138 | 20.5212 | 8.7398 | 10.04 | 6.251e-11 | -3.4024 | 17.4296 | 7.8906 | 6.1713 | -13.8835 | -6.7056e-11 | 12.1073 | 0.30546 | 3.783 | -10.4737 | 0.12824 | 118.0234 | 106.3237 | 134.5349 | -62.0314 | -73.7582 | -45.6261 |  | 0 | 1.445 | 1.7408 | 0.42642 | 1.3909 | 1.3829 | 0 | -147.9798 | 135.5389 | -36.4166 | -133.2509 | 133.8447
Line_1 | 0.8909 | 0.38078 | 0.43685 | 0.88859 | 0.37844 | 0.43475 | 10.2872 | 4.3968 | 5.0443 | 10.2606 | 4.3699 | 5.02 | 5.939 | 3.7949 | -6.0703 | -3.9453 | -3.0856 | 6.9417 | 2.8476 | -4.8469 | 0.17101 | -1.8915 | 5.2368 | -0.064119 | -62.056 | -73.7441 | -45.7596 | 117.9686 | 106.2418 | 134.3739 |  | 0.64025 | 1.4 | 1.2039 | 0.42642 | 1.3909 | 1.3829 | -36.4395 | -125.6847 | 132.6267 | -36.4166 | -133.2509 | 133.8447
Line_2 | 0.8909 | 0.38078 | 0.43685 | 0.88859 | 0.37844 | 0.43475 | 10.2872 | 4.3968 | 5.0443 | 10.2606 | 4.3699 | 5.02 | 5.939 | 3.7949 | -6.0703 | -3.9453 | -3.0856 | 6.9417 | 2.8476 | -4.8469 | 0.17101 | -1.8915 | 5.2368 | -0.064119 | -62.056 | -73.7441 | -45.7596 | 117.9686 | 106.2418 | 134.3739 |  | 0.64025 | 1.4 | 1.2039 | 0.42642 | 1.3909 | 1.3829 | -36.4395 | -125.6847 | 132.6267 | -36.4166 | -133.2509 | 133.8447

## LG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.7743 | 0.75373 | 0.86722 | 1.7772 | 0.75689 | 0.86949 | 20.488 | 8.7034 | 10.0138 | 20.5212 | 8.7398 | 10.04 | 6.251e-11 | -3.4024 | 17.4296 | 7.8906 | 6.1713 | -13.8835 | -6.7056e-11 | 12.1073 | 0.30546 | 3.783 | -10.4737 | 0.12824 | 118.0234 | 106.3237 | 134.5349 | -62.0314 | -73.7582 | -45.6261 |  | 0 | 1.445 | 1.7408 | 0.42642 | 1.3909 | 1.3829 | 0 | -147.9798 | 135.5389 | -36.4166 | -133.2509 | 133.8447
Line_1 | 0.8909 | 0.38078 | 0.43685 | 0.88859 | 0.37844 | 0.43475 | 10.2872 | 4.3968 | 5.0443 | 10.2606 | 4.3699 | 5.02 | 5.939 | 3.7949 | -6.0703 | -3.9453 | -3.0856 | 6.9417 | 2.8476 | -4.8469 | 0.17101 | -1.8915 | 5.2368 | -0.064119 | -62.056 | -73.7441 | -45.7596 | 117.9686 | 106.2418 | 134.3739 |  | 0.64025 | 1.4 | 1.2039 | 0.42642 | 1.3909 | 1.3829 | -36.4395 | -125.6847 | 132.6267 | -36.4166 | -133.2509 | 133.8447
Line_2 | 0.8909 | 0.38078 | 0.43685 | 0.88859 | 0.37844 | 0.43475 | 10.2872 | 4.3968 | 5.0443 | 10.2606 | 4.3699 | 5.02 | 5.939 | 3.7949 | -6.0703 | -3.9453 | -3.0856 | 6.9417 | 2.8476 | -4.8469 | 0.17101 | -1.8915 | 5.2368 | -0.064119 | -62.056 | -73.7441 | -45.7596 | 117.9686 | 106.2418 | 134.3739 |  | 0.64025 | 1.4 | 1.2039 | 0.42642 | 1.3909 | 1.3829 | -36.4395 | -125.6847 | 132.6267 | -36.4166 | -133.2509 | 133.8447

## LG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.76709 | 0.15967 | 0.41004 | 0.7682 | 0.16086 | 0.41051 | 8.8576 | 1.8438 | 4.7348 | 8.8705 | 1.8574 | 4.7402 | -3.8539 | -1.8585 | 5.0871 | 5.091 | 1.9943 | -4.4995 | -5.3338 | 1.3884 | -3.6529 | 6.1197 | -1.203 | 3.5634 | 120.3005 | 86.0674 | 164.3413 | -59.7346 | -93.8486 | -15.8135 |  | 0.74291 | 1.2582 | 1.3227 | 0.89741 | 1.2539 | 1.2108 | -5.5491 | -130.6944 | 128.6606 | -9.492 | -124.9485 | 125.8093
Line_1 | 0.38495 | 0.081143 | 0.20585 | 0.3841 | 0.080428 | 0.20526 | 4.445 | 0.93696 | 2.3769 | 4.4352 | 0.92871 | 2.3701 | 2.8614 | 1.0344 | -2.1097 | -2.5455 | -0.99715 | 2.2498 | 3.2614 | -0.56244 | 1.7603 | -3.0598 | 0.60152 | -1.7817 | -59.7384 | -93.5294 | -15.9818 | 120.2654 | 86.1514 | 164.1865 |  | 0.97608 | 1.2566 | 1.1559 | 0.89741 | 1.2539 | 1.2108 | -11.0005 | -122.0646 | 124.1772 | -9.492 | -124.9485 | 125.8093
Line_2 | 0.38495 | 0.081143 | 0.20585 | 0.3841 | 0.080428 | 0.20526 | 4.445 | 0.93696 | 2.3769 | 4.4352 | 0.92871 | 2.3701 | 2.8614 | 1.0344 | -2.1097 | -2.5455 | -0.99715 | 2.2498 | 3.2614 | -0.56244 | 1.7603 | -3.0598 | 0.60152 | -1.7817 | -59.7384 | -93.5294 | -15.9818 | 120.2654 | 86.1514 | 164.1865 |  | 0.97608 | 1.2566 | 1.1559 | 0.89741 | 1.2539 | 1.2108 | -11.0005 | -122.0646 | 124.1772 | -9.492 | -124.9485 | 125.8093

## LG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.76709 | 0.15967 | 0.41004 | 0.7682 | 0.16086 | 0.41051 | 8.8576 | 1.8438 | 4.7348 | 8.8705 | 1.8574 | 4.7402 | -3.8539 | -1.8585 | 5.0871 | 5.091 | 1.9943 | -4.4995 | -5.3338 | 1.3884 | -3.6529 | 6.1197 | -1.203 | 3.5634 | 120.3005 | 86.0674 | 164.3413 | -59.7346 | -93.8486 | -15.8135 |  | 0.74291 | 1.2582 | 1.3227 | 0.89741 | 1.2539 | 1.2108 | -5.5491 | -130.6944 | 128.6606 | -9.492 | -124.9485 | 125.8093
Line_1 | 0.38495 | 0.081143 | 0.20585 | 0.3841 | 0.080428 | 0.20526 | 4.445 | 0.93696 | 2.3769 | 4.4352 | 0.92871 | 2.3701 | 2.8614 | 1.0344 | -2.1097 | -2.5455 | -0.99715 | 2.2498 | 3.2614 | -0.56244 | 1.7603 | -3.0598 | 0.60152 | -1.7817 | -59.7384 | -93.5294 | -15.9818 | 120.2654 | 86.1514 | 164.1865 |  | 0.97608 | 1.2566 | 1.1559 | 0.89741 | 1.2539 | 1.2108 | -11.0005 | -122.0646 | 124.1772 | -9.492 | -124.9485 | 125.8093
Line_2 | 0.38495 | 0.081143 | 0.20585 | 0.3841 | 0.080428 | 0.20526 | 4.445 | 0.93696 | 2.3769 | 4.4352 | 0.92871 | 2.3701 | 2.8614 | 1.0344 | -2.1097 | -2.5455 | -0.99715 | 2.2498 | 3.2614 | -0.56244 | 1.7603 | -3.0598 | 0.60152 | -1.7817 | -59.7384 | -93.5294 | -15.9818 | 120.2654 | 86.1514 | 164.1865 |  | 0.97608 | 1.2566 | 1.1559 | 0.89741 | 1.2539 | 1.2108 | -11.0005 | -122.0646 | 124.1772 | -9.492 | -124.9485 | 125.8093

## LG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.1066 | 0.6396 | 0.57605 | 1.1083 | 0.64155 | 0.57799 | 12.7784 | 7.3855 | 6.6517 | 12.7977 | 7.408 | 6.674 | -1.9372e-11 | 3.094 | 10.994 | 6.4893 | 0.33575 | -7.9934 | 5.1928e-12 | 9.4975 | 0.45593 | 1.167 | -8.6794 | 0.23034 | 141.4011 | 134.6729 | 135.1218 | -38.7265 | -45.5286 | -45.1033 |  | 0 | 1.3525 | 1.6542 | 0.5152 | 1.1725 | 1.1982 | 0 | -153.371 | 137.4966 | -28.5319 | -133.3133 | 133.246
Line_1 | 0.55557 | 0.32226 | 0.29048 | 0.55416 | 0.32078 | 0.28899 | 6.4152 | 3.7212 | 3.3541 | 6.3988 | 3.704 | 3.337 | 4.8836 | 1.0337 | -3.2521 | -3.2447 | -0.16788 | 3.9967 | 0.8806 | -4.144 | 0.29252 | -0.5835 | 4.3397 | -0.11517 | -38.7966 | -45.6186 | -45.2054 | 141.2735 | 134.4714 | 134.8967 |  | 0.77353 | 1.1478 | 0.97349 | 0.5152 | 1.1725 | 1.1982 | -28.575 | -121.6121 | 129.6548 | -28.5319 | -133.3133 | 133.246
Line_2 | 0.55557 | 0.32226 | 0.29048 | 0.55416 | 0.32078 | 0.28899 | 6.4152 | 3.7212 | 3.3541 | 6.3988 | 3.704 | 3.337 | 4.8836 | 1.0337 | -3.2521 | -3.2447 | -0.16788 | 3.9967 | 0.8806 | -4.144 | 0.29252 | -0.5835 | 4.3397 | -0.11517 | -38.7966 | -45.6186 | -45.2054 | 141.2735 | 134.4714 | 134.8967 |  | 0.77353 | 1.1478 | 0.97349 | 0.5152 | 1.1725 | 1.1982 | -28.575 | -121.6121 | 129.6548 | -28.5319 | -133.3133 | 133.246

## LG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.1066 | 0.6396 | 0.57605 | 1.1083 | 0.64155 | 0.57799 | 12.7784 | 7.3855 | 6.6517 | 12.7977 | 7.408 | 6.674 | -1.9372e-11 | 3.094 | 10.994 | 6.4893 | 0.33575 | -7.9934 | 5.1928e-12 | 9.4975 | 0.45593 | 1.167 | -8.6794 | 0.23034 | 141.4011 | 134.6729 | 135.1218 | -38.7265 | -45.5286 | -45.1033 |  | 0 | 1.3525 | 1.6542 | 0.5152 | 1.1725 | 1.1982 | 0 | -153.371 | 137.4966 | -28.5319 | -133.3133 | 133.246
Line_1 | 0.55557 | 0.32226 | 0.29048 | 0.55416 | 0.32078 | 0.28899 | 6.4152 | 3.7212 | 3.3541 | 6.3988 | 3.704 | 3.337 | 4.8836 | 1.0337 | -3.2521 | -3.2447 | -0.16788 | 3.9967 | 0.8806 | -4.144 | 0.29252 | -0.5835 | 4.3397 | -0.11517 | -38.7966 | -45.6186 | -45.2054 | 141.2735 | 134.4714 | 134.8967 |  | 0.77353 | 1.1478 | 0.97349 | 0.5152 | 1.1725 | 1.1982 | -28.575 | -121.6121 | 129.6548 | -28.5319 | -133.3133 | 133.246
Line_2 | 0.55557 | 0.32226 | 0.29048 | 0.55416 | 0.32078 | 0.28899 | 6.4152 | 3.7212 | 3.3541 | 6.3988 | 3.704 | 3.337 | 4.8836 | 1.0337 | -3.2521 | -3.2447 | -0.16788 | 3.9967 | 0.8806 | -4.144 | 0.29252 | -0.5835 | 4.3397 | -0.11517 | -38.7966 | -45.6186 | -45.2054 | 141.2735 | 134.4714 | 134.8967 |  | 0.77353 | 1.1478 | 0.97349 | 0.5152 | 1.1725 | 1.1982 | -28.575 | -121.6121 | 129.6548 | -28.5319 | -133.3133 | 133.246

## LG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.45674 | 0.26398 | 0.23775 | 0.45743 | 0.26478 | 0.23855 | 5.2739 | 3.0482 | 2.7453 | 5.2819 | 3.0575 | 2.7545 | -2.327 | -0.028053 | 3.4481 | 3.4313 | 0.61997 | -2.9437 | -2.0463 | 3.3206 | -0.26853 | 2.2533 | -3.1844 | 0.38038 | 139.7985 | 133.0703 | 133.5192 | -40.3292 | -47.1312 | -46.7059 |  | 0.58755 | 1.0894 | 1.2598 | 0.77719 | 1.0611 | 1.0776 | 1.1257 | -136.4457 | 129.0662 | -7.0365 | -126.1143 | 125.9312
Line_1 | 0.2293 | 0.13301 | 0.11989 | 0.22871 | 0.13239 | 0.11927 | 2.6477 | 1.5358 | 1.3843 | 2.6409 | 1.5287 | 1.3773 | 1.9965 | 0.46012 | -1.3494 | -1.7157 | -0.30998 | 1.4718 | 1.1813 | -1.5624 | 0.21986 | -1.1267 | 1.5922 | -0.19019 | -40.3992 | -47.2212 | -46.808 | 139.6708 | 132.8688 | 133.2941 |  | 0.87618 | 1.0605 | 0.98759 | 0.77719 | 1.0611 | 1.0776 | -9.7872 | -120.8116 | 123.9379 | -7.0365 | -126.1143 | 125.9312
Line_2 | 0.2293 | 0.13301 | 0.11989 | 0.22871 | 0.13239 | 0.11927 | 2.6477 | 1.5358 | 1.3843 | 2.6409 | 1.5287 | 1.3773 | 1.9965 | 0.46012 | -1.3494 | -1.7157 | -0.30998 | 1.4718 | 1.1813 | -1.5624 | 0.21986 | -1.1267 | 1.5922 | -0.19019 | -40.3992 | -47.2212 | -46.808 | 139.6708 | 132.8688 | 133.2941 |  | 0.87618 | 1.0605 | 0.98759 | 0.77719 | 1.0611 | 1.0776 | -9.7872 | -120.8116 | 123.9379 | -7.0365 | -126.1143 | 125.9312

## LG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.45674 | 0.26398 | 0.23775 | 0.45743 | 0.26478 | 0.23855 | 5.2739 | 3.0482 | 2.7453 | 5.2819 | 3.0575 | 2.7545 | -2.327 | -0.028053 | 3.4481 | 3.4313 | 0.61997 | -2.9437 | -2.0463 | 3.3206 | -0.26853 | 2.2533 | -3.1844 | 0.38038 | 139.7985 | 133.0703 | 133.5192 | -40.3292 | -47.1312 | -46.7059 |  | 0.58755 | 1.0894 | 1.2598 | 0.77719 | 1.0611 | 1.0776 | 1.1257 | -136.4457 | 129.0662 | -7.0365 | -126.1143 | 125.9312
Line_1 | 0.2293 | 0.13301 | 0.11989 | 0.22871 | 0.13239 | 0.11927 | 2.6477 | 1.5358 | 1.3843 | 2.6409 | 1.5287 | 1.3773 | 1.9965 | 0.46012 | -1.3494 | -1.7157 | -0.30998 | 1.4718 | 1.1813 | -1.5624 | 0.21986 | -1.1267 | 1.5922 | -0.19019 | -40.3992 | -47.2212 | -46.808 | 139.6708 | 132.8688 | 133.2941 |  | 0.87618 | 1.0605 | 0.98759 | 0.77719 | 1.0611 | 1.0776 | -9.7872 | -120.8116 | 123.9379 | -7.0365 | -126.1143 | 125.9312
Line_2 | 0.2293 | 0.13301 | 0.11989 | 0.22871 | 0.13239 | 0.11927 | 2.6477 | 1.5358 | 1.3843 | 2.6409 | 1.5287 | 1.3773 | 1.9965 | 0.46012 | -1.3494 | -1.7157 | -0.30998 | 1.4718 | 1.1813 | -1.5624 | 0.21986 | -1.1267 | 1.5922 | -0.19019 | -40.3992 | -47.2212 | -46.808 | 139.6708 | 132.8688 | 133.2941 |  | 0.87618 | 1.0605 | 0.98759 | 0.77719 | 1.0611 | 1.0776 | -9.7872 | -120.8116 | 123.9379 | -7.0365 | -126.1143 | 125.9312

## LLG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.24891 | 2.0347 | 1.3263 | 0.25064 | 2.0354 | 1.3278 | 2.8741 | 23.4945 | 15.3152 | 2.8941 | 23.5024 | 15.3324 | 3.1224 | 3.1527e-11 | 1.9548e-11 | -2.5245 | 6.5083 | 0.77525 | 3.343 | -8.6476e-12 | -7.5688e-12 | -3.216 | 0.54832 | 4.1351 | -48.6335 | -12.6412 | -128.9107 | 131.0875 | 167.3024 | 51.1538 |  | 1.5916 | 0 | 0 | 1.4127 | 0.2779 | 0.2744 | -1.6798 | 0 | 0 | 2.956 | 172.1182 | 130.5353
Line_1 | 0.12676 | 1.0186 | 0.66451 | 0.12532 | 1.0177 | 0.66391 | 1.4637 | 11.7622 | 7.6732 | 1.447 | 11.7512 | 7.6662 | -1.1192 | 4.8894 | 0.58893 | 1.2623 | -3.2542 | -0.38762 | -1.5878 | 0.41402 | 3.1062 | 1.608 | -0.27416 | -2.0676 | 130.9276 | 167.2385 | 51.2706 | -48.9125 | -12.6976 | -128.8462 |  | 1.3272 | 0.41717 | 0.41203 | 1.4127 | 0.2779 | 0.2744 | 5.7486 | 172.0787 | 130.5349 | 2.956 | 172.1182 | 130.5353
Line_2 | 0.12676 | 1.0186 | 0.66451 | 0.12532 | 1.0177 | 0.66391 | 1.4637 | 11.7622 | 7.6732 | 1.447 | 11.7512 | 7.6662 | -1.1192 | 4.8894 | 0.58893 | 1.2623 | -3.2542 | -0.38762 | -1.5878 | 0.41402 | 3.1062 | 1.608 | -0.27416 | -2.0676 | 130.9276 | 167.2385 | 51.2706 | -48.9125 | -12.6976 | -128.8462 |  | 1.3272 | 0.41717 | 0.41203 | 1.4127 | 0.2779 | 0.2744 | 5.7486 | 172.0787 | 130.5349 | 2.956 | 172.1182 | 130.5353

## LLG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.24891 | 2.0347 | 1.3263 | 0.25064 | 2.0354 | 1.3278 | 2.8741 | 23.4945 | 15.3152 | 2.8941 | 23.5024 | 15.3324 | 3.1224 | 3.1527e-11 | 1.9548e-11 | -2.5245 | 6.5083 | 0.77525 | 3.343 | -8.6476e-12 | -7.5688e-12 | -3.216 | 0.54832 | 4.1351 | -48.6335 | -12.6412 | -128.9107 | 131.0875 | 167.3024 | 51.1538 |  | 1.5916 | 0 | 0 | 1.4127 | 0.2779 | 0.2744 | -1.6798 | 0 | 0 | 2.956 | 172.1182 | 130.5353
Line_1 | 0.12676 | 1.0186 | 0.66451 | 0.12532 | 1.0177 | 0.66391 | 1.4637 | 11.7622 | 7.6732 | 1.447 | 11.7512 | 7.6662 | -1.1192 | 4.8894 | 0.58893 | 1.2623 | -3.2542 | -0.38762 | -1.5878 | 0.41402 | 3.1062 | 1.608 | -0.27416 | -2.0676 | 130.9276 | 167.2385 | 51.2706 | -48.9125 | -12.6976 | -128.8462 |  | 1.3272 | 0.41717 | 0.41203 | 1.4127 | 0.2779 | 0.2744 | 5.7486 | 172.0787 | 130.5349 | 2.956 | 172.1182 | 130.5353
Line_2 | 0.12676 | 1.0186 | 0.66451 | 0.12532 | 1.0177 | 0.66391 | 1.4637 | 11.7622 | 7.6732 | 1.447 | 11.7512 | 7.6662 | -1.1192 | 4.8894 | 0.58893 | 1.2623 | -3.2542 | -0.38762 | -1.5878 | 0.41402 | 3.1062 | 1.608 | -0.27416 | -2.0676 | 130.9276 | 167.2385 | 51.2706 | -48.9125 | -12.6976 | -128.8462 |  | 1.3272 | 0.41717 | 0.41203 | 1.4127 | 0.2779 | 0.2744 | 5.7486 | 172.0787 | 130.5349 | 2.956 | 172.1182 | 130.5353

## LLG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.12736 | 0.68619 | 0.60192 | 0.12734 | 0.6866 | 0.60284 | 1.4707 | 7.9235 | 6.9504 | 1.4704 | 7.9282 | 6.9609 | 1.9455 | -1.559 | -5.358 | -1.8392 | 2.5085 | 5.7881 | -0.40604 | -6.9311 | -2.5359 | 0.30469 | 6.9858 | 3.3661 | 10.9954 | -15.1072 | -102.466 | -169.449 | 164.8178 | 77.5688 |  | 1.3514 | 0.89661 | 0.85288 | 1.2679 | 0.93622 | 0.96189 | -0.79323 | -117.7835 | 102.8615 | 1.1448 | -124.9346 | 107.7492
Line_1 | 0.063907 | 0.3438 | 0.30193 | 0.063668 | 0.3433 | 0.30142 | 0.73794 | 3.9698 | 3.4863 | 0.73518 | 3.9641 | 3.4805 | -0.89693 | 1.4916 | 3.0075 | 0.91962 | -1.2542 | -2.894 | 0.12204 | 3.5118 | 1.8895 | -0.15235 | -3.4929 | -1.683 | -170.0328 | 164.7371 | 77.6583 | 10.551 | -15.1822 | -102.4312 |  | 1.2267 | 0.96111 | 1.0188 | 1.2679 | 0.93622 | 0.96189 | 2.2191 | -128.2752 | 109.7979 | 1.1448 | -124.9346 | 107.7492
Line_2 | 0.063907 | 0.3438 | 0.30193 | 0.063668 | 0.3433 | 0.30142 | 0.73794 | 3.9698 | 3.4863 | 0.73518 | 3.9641 | 3.4805 | -0.89693 | 1.4916 | 3.0075 | 0.91962 | -1.2542 | -2.894 | 0.12204 | 3.5118 | 1.8895 | -0.15235 | -3.4929 | -1.683 | -170.0328 | 164.7371 | 77.6583 | 10.551 | -15.1822 | -102.4312 |  | 1.2267 | 0.96111 | 1.0188 | 1.2679 | 0.93622 | 0.96189 | 2.2191 | -128.2752 | 109.7979 | 1.1448 | -124.9346 | 107.7492

## LLG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.12736 | 0.68619 | 0.60192 | 0.12734 | 0.6866 | 0.60284 | 1.4707 | 7.9235 | 6.9504 | 1.4704 | 7.9282 | 6.9609 | 1.9455 | -1.559 | -5.358 | -1.8392 | 2.5085 | 5.7881 | -0.40604 | -6.9311 | -2.5359 | 0.30469 | 6.9858 | 3.3661 | 10.9954 | -15.1072 | -102.466 | -169.449 | 164.8178 | 77.5688 |  | 1.3514 | 0.89661 | 0.85288 | 1.2679 | 0.93622 | 0.96189 | -0.79323 | -117.7835 | 102.8615 | 1.1448 | -124.9346 | 107.7492
Line_1 | 0.063907 | 0.3438 | 0.30193 | 0.063668 | 0.3433 | 0.30142 | 0.73794 | 3.9698 | 3.4863 | 0.73518 | 3.9641 | 3.4805 | -0.89693 | 1.4916 | 3.0075 | 0.91962 | -1.2542 | -2.894 | 0.12204 | 3.5118 | 1.8895 | -0.15235 | -3.4929 | -1.683 | -170.0328 | 164.7371 | 77.6583 | 10.551 | -15.1822 | -102.4312 |  | 1.2267 | 0.96111 | 1.0188 | 1.2679 | 0.93622 | 0.96189 | 2.2191 | -128.2752 | 109.7979 | 1.1448 | -124.9346 | 107.7492
Line_2 | 0.063907 | 0.3438 | 0.30193 | 0.063668 | 0.3433 | 0.30142 | 0.73794 | 3.9698 | 3.4863 | 0.73518 | 3.9641 | 3.4805 | -0.89693 | 1.4916 | 3.0075 | 0.91962 | -1.2542 | -2.894 | 0.12204 | 3.5118 | 1.8895 | -0.15235 | -3.4929 | -1.683 | -170.0328 | 164.7371 | 77.6583 | 10.551 | -15.1822 | -102.4312 |  | 1.2267 | 0.96111 | 1.0188 | 1.2679 | 0.93622 | 0.96189 | 2.2191 | -128.2752 | 109.7979 | 1.1448 | -124.9346 | 107.7492

## LLG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.24548 | 1.5847 | 0.84176 | 0.24697 | 1.5847 | 0.84288 | 2.8346 | 18.298 | 9.7198 | 2.8518 | 18.2988 | 9.7327 | 2.493 | -2.1145e-11 | -6.6727e-12 | -1.8486 | 6.3956 | -0.09994 | 3.2157 | -2.5492e-11 | -1.6553e-11 | -2.8637 | -0.50789 | 2.5968 | -53.9058 | 3.4387 | -134.1974 | 125.8918 | -176.6236 | 45.8922 |  | 1.4355 | 0 | 0 | 1.1953 | 0.35061 | 0.26701 | -1.6913 | 0 | 0 | 3.0483 | 178.836 | 138.0962
Line_1 | 0.12439 | 0.79285 | 0.4216 | 0.12348 | 0.79236 | 0.42144 | 1.4364 | 9.155 | 4.8682 | 1.4259 | 9.1494 | 4.8663 | -0.76712 | 4.8025 | -0.070254 | 0.92431 | -3.1978 | 0.04997 | -1.3467 | -0.38079 | 1.951 | 1.4319 | 0.25395 | -1.2984 | 125.8915 | -176.679 | 46.0138 | -54.1082 | 3.3764 | -134.1078 |  | 1.079 | 0.52622 | 0.40103 | 1.1953 | 0.35061 | 0.26701 | 6.2237 | 178.7876 | 138.0761 | 3.0483 | 178.836 | 138.0962
Line_2 | 0.12439 | 0.79285 | 0.4216 | 0.12348 | 0.79236 | 0.42144 | 1.4364 | 9.155 | 4.8682 | 1.4259 | 9.1494 | 4.8663 | -0.76712 | 4.8025 | -0.070254 | 0.92431 | -3.1978 | 0.04997 | -1.3467 | -0.38079 | 1.951 | 1.4319 | 0.25395 | -1.2984 | 125.8915 | -176.679 | 46.0138 | -54.1082 | 3.3764 | -134.1078 |  | 1.079 | 0.52622 | 0.40103 | 1.1953 | 0.35061 | 0.26701 | 6.2237 | 178.7876 | 138.0761 | 3.0483 | 178.836 | 138.0962

## LLG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.24548 | 1.5847 | 0.84176 | 0.24697 | 1.5847 | 0.84288 | 2.8346 | 18.298 | 9.7198 | 2.8518 | 18.2988 | 9.7327 | 2.493 | -2.1145e-11 | -6.6727e-12 | -1.8486 | 6.3956 | -0.09994 | 3.2157 | -2.5492e-11 | -1.6553e-11 | -2.8637 | -0.50789 | 2.5968 | -53.9058 | 3.4387 | -134.1974 | 125.8918 | -176.6236 | 45.8922 |  | 1.4355 | 0 | 0 | 1.1953 | 0.35061 | 0.26701 | -1.6913 | 0 | 0 | 3.0483 | 178.836 | 138.0962
Line_1 | 0.12439 | 0.79285 | 0.4216 | 0.12348 | 0.79236 | 0.42144 | 1.4364 | 9.155 | 4.8682 | 1.4259 | 9.1494 | 4.8663 | -0.76712 | 4.8025 | -0.070254 | 0.92431 | -3.1978 | 0.04997 | -1.3467 | -0.38079 | 1.951 | 1.4319 | 0.25395 | -1.2984 | 125.8915 | -176.679 | 46.0138 | -54.1082 | 3.3764 | -134.1078 |  | 1.079 | 0.52622 | 0.40103 | 1.1953 | 0.35061 | 0.26701 | 6.2237 | 178.7876 | 138.0761 | 3.0483 | 178.836 | 138.0962
Line_2 | 0.12439 | 0.79285 | 0.4216 | 0.12348 | 0.79236 | 0.42144 | 1.4364 | 9.155 | 4.8682 | 1.4259 | 9.1494 | 4.8663 | -0.76712 | 4.8025 | -0.070254 | 0.92431 | -3.1978 | 0.04997 | -1.3467 | -0.38079 | 1.951 | 1.4319 | 0.25395 | -1.2984 | 125.8915 | -176.679 | 46.0138 | -54.1082 | 3.3764 | -134.1078 |  | 1.079 | 0.52622 | 0.40103 | 1.1953 | 0.35061 | 0.26701 | 6.2237 | 178.7876 | 138.0761 | 3.0483 | 178.836 | 138.0962

## LLG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.18515 | 0.39574 | 0.35529 | 0.18587 | 0.39564 | 0.35622 | 2.1379 | 4.5696 | 4.1026 | 2.1462 | 4.5684 | 4.1133 | 1.7635 | -1.7766 | -2.823 | -1.4666 | 2.4127 | 3.3099 | 1.9504 | -3.1727 | 0.010047 | -1.844 | 2.9222 | 0.47334 | -50.6852 | 5.347 | -79.208 | 129.1271 | -174.7892 | 100.7615 |  | 1.2299 | 0.79575 | 0.68811 | 1.0978 | 0.82951 | 0.81286 | -2.8036 | -113.9001 | 100.588 | 0.63132 | -124.3342 | 108.9002
Line_1 | 0.093426 | 0.19802 | 0.17858 | 0.092935 | 0.19782 | 0.17811 | 1.0788 | 2.2866 | 2.0621 | 1.0731 | 2.2842 | 2.0566 | -0.66132 | 1.3658 | 1.7804 | 0.73329 | -1.2064 | -1.6549 | -0.89744 | 1.4016 | 0.35667 | 0.92201 | -1.4611 | -0.23667 | 129.0756 | -174.9207 | 100.8127 | -50.8729 | 5.2108 | -79.2385 |  | 1.0334 | 0.85588 | 0.88055 | 1.0978 | 0.82951 | 0.81286 | 2.6894 | -129.1809 | 112.1409 | 0.63132 | -124.3342 | 108.9002
Line_2 | 0.093426 | 0.19802 | 0.17858 | 0.092935 | 0.19782 | 0.17811 | 1.0788 | 2.2866 | 2.0621 | 1.0731 | 2.2842 | 2.0566 | -0.66132 | 1.3658 | 1.7804 | 0.73329 | -1.2064 | -1.6549 | -0.89744 | 1.4016 | 0.35667 | 0.92201 | -1.4611 | -0.23667 | 129.0756 | -174.9207 | 100.8127 | -50.8729 | 5.2108 | -79.2385 |  | 1.0334 | 0.85588 | 0.88055 | 1.0978 | 0.82951 | 0.81286 | 2.6894 | -129.1809 | 112.1409 | 0.63132 | -124.3342 | 108.9002

## LLG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.18515 | 0.39574 | 0.35529 | 0.18587 | 0.39564 | 0.35622 | 2.1379 | 4.5696 | 4.1026 | 2.1462 | 4.5684 | 4.1133 | 1.7635 | -1.7766 | -2.823 | -1.4666 | 2.4127 | 3.3099 | 1.9504 | -3.1727 | 0.010047 | -1.844 | 2.9222 | 0.47334 | -50.6852 | 5.347 | -79.208 | 129.1271 | -174.7892 | 100.7615 |  | 1.2299 | 0.79575 | 0.68811 | 1.0978 | 0.82951 | 0.81286 | -2.8036 | -113.9001 | 100.588 | 0.63132 | -124.3342 | 108.9002
Line_1 | 0.093426 | 0.19802 | 0.17858 | 0.092935 | 0.19782 | 0.17811 | 1.0788 | 2.2866 | 2.0621 | 1.0731 | 2.2842 | 2.0566 | -0.66132 | 1.3658 | 1.7804 | 0.73329 | -1.2064 | -1.6549 | -0.89744 | 1.4016 | 0.35667 | 0.92201 | -1.4611 | -0.23667 | 129.0756 | -174.9207 | 100.8127 | -50.8729 | 5.2108 | -79.2385 |  | 1.0334 | 0.85588 | 0.88055 | 1.0978 | 0.82951 | 0.81286 | 2.6894 | -129.1809 | 112.1409 | 0.63132 | -124.3342 | 108.9002
Line_2 | 0.093426 | 0.19802 | 0.17858 | 0.092935 | 0.19782 | 0.17811 | 1.0788 | 2.2866 | 2.0621 | 1.0731 | 2.2842 | 2.0566 | -0.66132 | 1.3658 | 1.7804 | 0.73329 | -1.2064 | -1.6549 | -0.89744 | 1.4016 | 0.35667 | 0.92201 | -1.4611 | -0.23667 | 129.0756 | -174.9207 | 100.8127 | -50.8729 | 5.2108 | -79.2385 |  | 1.0334 | 0.85588 | 0.88055 | 1.0978 | 0.82951 | 0.81286 | 2.6894 | -129.1809 | 112.1409 | 0.63132 | -124.3342 | 108.9002