## LLL_max_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 4.283 | 4.283 | 0 | 9.0614 | 148.3662 | 148.3662 | 28.6163 | -1e-07 | 32.4685 | -1e-07 | -77.7798 | 102.2202 | 0.29171 | 0 | -29.1714 | 0
Line_1 | 0.9515 | 0.9515 | 0 | 1.8972 | 32.9609 | 32.9609 | 1.4123 | -1e-07 | 1.6025 | -1e-07 | -72.853 | 107.147 | 0.064805 | 0 | -24.2445 | 0
Line_2 | 0.9515 | 0.9515 | 0 | 1.8972 | 32.9609 | 32.9609 | 1.4123 | -1e-07 | 1.6025 | -1e-07 | -72.853 | 107.147 | 0.064805 | 0 | -24.2445 | 0

## LLL_max_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 4.283 | 4.283 | 0 | 9.0614 | 148.3662 | 148.3662 | 28.6163 | -1e-07 | 32.4685 | -1e-07 | -77.7798 | 102.2202 | 0.29171 | 0 | -29.1714 | 0
Line_1 | 0.9515 | 0.9515 | 0 | 1.8972 | 32.9609 | 32.9609 | 1.4123 | -1e-07 | 1.6025 | -1e-07 | -72.853 | 107.147 | 0.064805 | 0 | -24.2445 | 0
Line_2 | 0.9515 | 0.9515 | 0 | 1.8972 | 32.9609 | 32.9609 | 1.4123 | -1e-07 | 1.6025 | -1e-07 | -72.853 | 107.147 | 0.064805 | 0 | -24.2445 | 0

## LLL_max_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.8763 | 0.8763 | 0 | 1.9596 | 30.3558 | 30.3558 | 22.4252 | -21.2272 | 19.1954 | -17.8362 | -47.233 | 132.767 | 0.97242 | 0.91337 | -6.6703 | -7.1943
Line_1 | 0.31157 | 0.31157 | 0 | 0.57123 | 10.793 | 10.793 | 6.2226 | -6.0711 | 7.9384 | -7.7666 | -59.1798 | 120.8202 | 0.93455 | 0.91337 | -7.271 | -7.1943
Line_2 | 0.31157 | 0.31157 | 0 | 0.57123 | 10.793 | 10.793 | 6.2226 | -6.0711 | 7.9384 | -7.7666 | -59.1798 | 120.8202 | 0.93455 | 0.91337 | -7.271 | -7.1943

## LLL_max_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.8763 | 0.8763 | 0 | 1.9596 | 30.3558 | 30.3558 | 22.4252 | -21.2272 | 19.1954 | -17.8362 | -47.233 | 132.767 | 0.97242 | 0.91337 | -6.6703 | -7.1943
Line_1 | 0.31157 | 0.31157 | 0 | 0.57123 | 10.793 | 10.793 | 6.2226 | -6.0711 | 7.9384 | -7.7666 | -59.1798 | 120.8202 | 0.93455 | 0.91337 | -7.271 | -7.1943
Line_2 | 0.31157 | 0.31157 | 0 | 0.57123 | 10.793 | 10.793 | 6.2226 | -6.0711 | 7.9384 | -7.7666 | -59.1798 | 120.8202 | 0.93455 | 0.91337 | -7.271 | -7.1943

## LLL_min_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 3.6016 | 3.6016 | 0 | 6.8561 | 124.7634 | 124.7634 | 38.8525 | -1e-07 | 22.9597 | -1e-07 | -69.6723 | 110.3277 | 0.36172 | 0 | -39.0915 | 0
Line_1 | 0.77473 | 0.77473 | 0 | 1.4748 | 26.8374 | 26.8374 | 1.7977 | -1e-07 | 1.0624 | -1e-07 | -70.2749 | 109.7251 | 0.077808 | 0 | -39.6941 | 0
Line_2 | 0.77473 | 0.77473 | 0 | 1.4748 | 26.8374 | 26.8374 | 1.7977 | -1e-07 | 1.0624 | -1e-07 | -70.2749 | 109.7251 | 0.077808 | 0 | -39.6941 | 0

## LLL_min_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 3.6016 | 3.6016 | 0 | 6.8561 | 124.7634 | 124.7634 | 38.8525 | -1e-07 | 22.9597 | -1e-07 | -69.6723 | 110.3277 | 0.36172 | 0 | -39.0915 | 0
Line_1 | 0.77473 | 0.77473 | 0 | 1.4748 | 26.8374 | 26.8374 | 1.7977 | -1e-07 | 1.0624 | -1e-07 | -70.2749 | 109.7251 | 0.077808 | 0 | -39.6941 | 0
Line_2 | 0.77473 | 0.77473 | 0 | 1.4748 | 26.8374 | 26.8374 | 1.7977 | -1e-07 | 1.0624 | -1e-07 | -70.2749 | 109.7251 | 0.077808 | 0 | -39.6941 | 0

## LLL_min_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.88201 | 0.88201 | 0 | 1.679 | 30.5537 | 30.5537 | 19.072 | -16.7419 | 18.0132 | -16.6363 | -50.7266 | 129.2734 | 0.85861 | 0.77248 | -7.3619 | -5.9079
Line_1 | 0.18973 | 0.18973 | 0 | 0.36117 | 6.5723 | 6.5723 | 3.6713 | -3.5635 | 3.68 | -3.6162 | -51.3292 | 128.6708 | 0.79091 | 0.77248 | -6.2614 | -5.9079
Line_2 | 0.18973 | 0.18973 | 0 | 0.36117 | 6.5723 | 6.5723 | 3.6713 | -3.5635 | 3.68 | -3.6162 | -51.3292 | 128.6708 | 0.79091 | 0.77248 | -6.2614 | -5.9079

## LLL_min_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.88201 | 0.88201 | 0 | 1.679 | 30.5537 | 30.5537 | 19.072 | -16.7419 | 18.0132 | -16.6363 | -50.7266 | 129.2734 | 0.85861 | 0.77248 | -7.3619 | -5.9079
Line_1 | 0.18973 | 0.18973 | 0 | 0.36117 | 6.5723 | 6.5723 | 3.6713 | -3.5635 | 3.68 | -3.6162 | -51.3292 | 128.6708 | 0.79091 | 0.77248 | -6.2614 | -5.9079
Line_2 | 0.18973 | 0.18973 | 0 | 0.36117 | 6.5723 | 6.5723 | 3.6713 | -3.5635 | 3.68 | -3.6162 | -51.3292 | 128.6708 | 0.79091 | 0.77248 | -6.2614 | -5.9079

## LL_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.35595 | 3.6314 | 3.7936 | 0.35595 | 3.6314 | 3.7936 | 4.1102 | 41.9321 | 43.8052 | 4.1102 | 41.9321 | 43.8052 | -2.8809 | 31.035 | -18.1673 | 2.9468 | -24.1776 | 25.651 | -3.7882 | 2.3326 | 12.0075 | 3.8629 | 5.4478 | -3.5164 | 129.3592 | -165.2802 | 9.8274 | -50.6408 | 14.7198 | -170.1726 | 1.1579 | 0.74221 | 0.49713 | 1.1821 | 0.59105 | 0.59105 | 2.1065 | -160.9818 | 156.365 | 2.0217 | -177.9783 | -177.9783
Line_1 | 0.17798 | 0.82688 | 0.74081 | 0.17798 | 0.82688 | 0.74081 | 2.0551 | 9.548 | 8.5541 | 2.0551 | 9.548 | 8.5541 | 1.4899 | 5.9918 | -4.6142 | -1.4734 | -5.6362 | 4.8995 | 1.9502 | 0.12158 | 1.5713 | -1.9315 | 0.28182 | -1.2476 | -50.6408 | -175.1159 | 16.3071 | 129.3592 | 4.8841 | -163.6929 | 1.1942 | 0.62767 | 0.56983 | 1.1821 | 0.59105 | 0.59105 | 1.9805 | -173.9534 | 177.501 | 2.0217 | -177.9783 | -177.9783
Line_2 | 0.17798 | 0.82688 | 0.74081 | 0.17798 | 0.82688 | 0.74081 | 2.0551 | 9.548 | 8.5541 | 2.0551 | 9.548 | 8.5541 | 1.4899 | 5.9918 | -4.6142 | -1.4734 | -5.6362 | 4.8995 | 1.9502 | 0.12158 | 1.5713 | -1.9315 | 0.28182 | -1.2476 | -50.6408 | -175.1159 | 16.3071 | 129.3592 | 4.8841 | -163.6929 | 1.1942 | 0.62767 | 0.56983 | 1.1821 | 0.59105 | 0.59105 | 1.9805 | -173.9534 | 177.501 | 2.0217 | -177.9783 | -177.9783

## LL_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.35595 | 3.6314 | 3.7936 | 0.35595 | 3.6314 | 3.7936 | 4.1102 | 41.9321 | 43.8052 | 4.1102 | 41.9321 | 43.8052 | -2.8809 | 31.035 | -18.1673 | 2.9468 | -24.1776 | 25.651 | -3.7882 | 2.3326 | 12.0075 | 3.8629 | 5.4478 | -3.5164 | 129.3592 | -165.2802 | 9.8274 | -50.6408 | 14.7198 | -170.1726 | 1.1579 | 0.74221 | 0.49713 | 1.1821 | 0.59105 | 0.59105 | 2.1065 | -160.9818 | 156.365 | 2.0217 | -177.9783 | -177.9783
Line_1 | 0.17798 | 0.82688 | 0.74081 | 0.17798 | 0.82688 | 0.74081 | 2.0551 | 9.548 | 8.5541 | 2.0551 | 9.548 | 8.5541 | 1.4899 | 5.9918 | -4.6142 | -1.4734 | -5.6362 | 4.8995 | 1.9502 | 0.12158 | 1.5713 | -1.9315 | 0.28182 | -1.2476 | -50.6408 | -175.1159 | 16.3071 | 129.3592 | 4.8841 | -163.6929 | 1.1942 | 0.62767 | 0.56983 | 1.1821 | 0.59105 | 0.59105 | 1.9805 | -173.9534 | 177.501 | 2.0217 | -177.9783 | -177.9783
Line_2 | 0.17798 | 0.82688 | 0.74081 | 0.17798 | 0.82688 | 0.74081 | 2.0551 | 9.548 | 8.5541 | 2.0551 | 9.548 | 8.5541 | 1.4899 | 5.9918 | -4.6142 | -1.4734 | -5.6362 | 4.8995 | 1.9502 | 0.12158 | 1.5713 | -1.9315 | 0.28182 | -1.2476 | -50.6408 | -175.1159 | 16.3071 | 129.3592 | 4.8841 | -163.6929 | 1.1942 | 0.62767 | 0.56983 | 1.1821 | 0.59105 | 0.59105 | 1.9805 | -173.9534 | 177.501 | 2.0217 | -177.9783 | -177.9783

## LL_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.25737 | 1.3967 | 1.3626 | 0.25737 | 1.3967 | 1.3626 | 2.9719 | 16.1276 | 15.7336 | 2.9719 | 16.1276 | 15.7336 | -1.5571 | 16.583 | -0.024169 | 1.5915 | -15.5686 | 0.9896 | -3.0312 | 1.2162 | 13.0202 | 3.0703 | -0.065208 | -11.9248 | 118.302 | -138.8076 | 30.5822 | -61.698 | 41.1924 | -149.4178 | 1.1467 | 1.031 | 0.82754 | 1.1637 | 0.96535 | 0.76053 | 1.1134 | -134.6132 | 120.6885 | 0.90162 | -138.5676 | 125.3261
Line_1 | 0.12869 | 0.3798 | 0.37361 | 0.12869 | 0.3798 | 0.37361 | 1.4859 | 4.3855 | 4.314 | 1.4859 | 4.3855 | 4.314 | 0.80437 | 3.8907 | 0.077321 | -0.79576 | -3.8157 | -0.0047391 | 1.5449 | 1.9191 | 3.3633 | -1.5351 | -1.834 | -3.2809 | -61.698 | -164.2384 | 35.4088 | 118.302 | 15.7616 | -144.5912 | 1.1722 | 0.98922 | 0.77982 | 1.1637 | 0.96535 | 0.76053 | 0.79804 | -137.9837 | 124.0918 | 0.90162 | -138.5676 | 125.3261
Line_2 | 0.12869 | 0.3798 | 0.37361 | 0.12869 | 0.3798 | 0.37361 | 1.4859 | 4.3855 | 4.314 | 1.4859 | 4.3855 | 4.314 | 0.80437 | 3.8907 | 0.077321 | -0.79576 | -3.8157 | -0.0047391 | 1.5449 | 1.9191 | 3.3633 | -1.5351 | -1.834 | -3.2809 | -61.698 | -164.2384 | 35.4088 | 118.302 | 15.7616 | -144.5912 | 1.1722 | 0.98922 | 0.77982 | 1.1637 | 0.96535 | 0.76053 | 0.79804 | -137.9837 | 124.0918 | 0.90162 | -138.5676 | 125.3261

## LL_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.25737 | 1.3967 | 1.3626 | 0.25737 | 1.3967 | 1.3626 | 2.9719 | 16.1276 | 15.7336 | 2.9719 | 16.1276 | 15.7336 | -1.5571 | 16.583 | -0.024169 | 1.5915 | -15.5686 | 0.9896 | -3.0312 | 1.2162 | 13.0202 | 3.0703 | -0.065208 | -11.9248 | 118.302 | -138.8076 | 30.5822 | -61.698 | 41.1924 | -149.4178 | 1.1467 | 1.031 | 0.82754 | 1.1637 | 0.96535 | 0.76053 | 1.1134 | -134.6132 | 120.6885 | 0.90162 | -138.5676 | 125.3261
Line_1 | 0.12869 | 0.3798 | 0.37361 | 0.12869 | 0.3798 | 0.37361 | 1.4859 | 4.3855 | 4.314 | 1.4859 | 4.3855 | 4.314 | 0.80437 | 3.8907 | 0.077321 | -0.79576 | -3.8157 | -0.0047391 | 1.5449 | 1.9191 | 3.3633 | -1.5351 | -1.834 | -3.2809 | -61.698 | -164.2384 | 35.4088 | 118.302 | 15.7616 | -144.5912 | 1.1722 | 0.98922 | 0.77982 | 1.1637 | 0.96535 | 0.76053 | 0.79804 | -137.9837 | 124.0918 | 0.90162 | -138.5676 | 125.3261
Line_2 | 0.12869 | 0.3798 | 0.37361 | 0.12869 | 0.3798 | 0.37361 | 1.4859 | 4.3855 | 4.314 | 1.4859 | 4.3855 | 4.314 | 0.80437 | 3.8907 | 0.077321 | -0.79576 | -3.8157 | -0.0047391 | 1.5449 | 1.9191 | 3.3633 | -1.5351 | -1.834 | -3.2809 | -61.698 | -164.2384 | 35.4088 | 118.302 | 15.7616 | -144.5912 | 1.1722 | 0.98922 | 0.77982 | 1.1637 | 0.96535 | 0.76053 | 0.79804 | -137.9837 | 124.0918 | 0.90162 | -138.5676 | 125.3261

## LL_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.15892 | 3.0486 | 3.19 | 0.15892 | 3.0486 | 3.19 | 1.8351 | 35.2024 | 36.8347 | 1.8351 | 35.2024 | 36.8347 | -1.8248 | 26.2892 | -7.7754 | 1.8501 | -17.01 | 17.935 | -0.28017 | -0.30937 | 11.6491 | 0.29507 | 5.7929 | -5.6453 | 173.1413 | -158.99 | 19.6756 | -6.8587 | 21.01 | -160.3244 | 1.0061 | 0.74685 | 0.38023 | 1.0209 | 0.51046 | 0.51046 | 1.8699 | -159.6642 | 143.3972 | 2.2033 | -177.7967 | -177.7967
Line_1 | 0.079461 | 0.67052 | 0.59523 | 0.079461 | 0.67052 | 0.59523 | 0.91753 | 7.7425 | 6.8731 | 0.91753 | 7.7425 | 6.8731 | 0.93133 | 4.3581 | -3.093 | -0.92503 | -3.9093 | 3.4467 | 0.15126 | -0.3159 | 0.86397 | -0.14754 | 0.58117 | -0.65493 | -6.8587 | -169.3408 | 12.9622 | 173.1413 | 10.6592 | -167.0378 | 1.0283 | 0.56436 | 0.46725 | 1.0209 | 0.51046 | 0.51046 | 2.3664 | -173.4866 | 177.3556 | 2.2033 | -177.7967 | -177.7967
Line_2 | 0.079461 | 0.67052 | 0.59523 | 0.079461 | 0.67052 | 0.59523 | 0.91753 | 7.7425 | 6.8731 | 0.91753 | 7.7425 | 6.8731 | 0.93133 | 4.3581 | -3.093 | -0.92503 | -3.9093 | 3.4467 | 0.15126 | -0.3159 | 0.86397 | -0.14754 | 0.58117 | -0.65493 | -6.8587 | -169.3408 | 12.9622 | 173.1413 | 10.6592 | -167.0378 | 1.0283 | 0.56436 | 0.46725 | 1.0209 | 0.51046 | 0.51046 | 2.3664 | -173.4866 | 177.3556 | 2.2033 | -177.7967 | -177.7967

## LL_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.15892 | 3.0486 | 3.19 | 0.15892 | 3.0486 | 3.19 | 1.8351 | 35.2024 | 36.8347 | 1.8351 | 35.2024 | 36.8347 | -1.8248 | 26.2892 | -7.7754 | 1.8501 | -17.01 | 17.935 | -0.28017 | -0.30937 | 11.6491 | 0.29507 | 5.7929 | -5.6453 | 173.1413 | -158.99 | 19.6756 | -6.8587 | 21.01 | -160.3244 | 1.0061 | 0.74685 | 0.38023 | 1.0209 | 0.51046 | 0.51046 | 1.8699 | -159.6642 | 143.3972 | 2.2033 | -177.7967 | -177.7967
Line_1 | 0.079461 | 0.67052 | 0.59523 | 0.079461 | 0.67052 | 0.59523 | 0.91753 | 7.7425 | 6.8731 | 0.91753 | 7.7425 | 6.8731 | 0.93133 | 4.3581 | -3.093 | -0.92503 | -3.9093 | 3.4467 | 0.15126 | -0.3159 | 0.86397 | -0.14754 | 0.58117 | -0.65493 | -6.8587 | -169.3408 | 12.9622 | 173.1413 | 10.6592 | -167.0378 | 1.0283 | 0.56436 | 0.46725 | 1.0209 | 0.51046 | 0.51046 | 2.3664 | -173.4866 | 177.3556 | 2.2033 | -177.7967 | -177.7967
Line_2 | 0.079461 | 0.67052 | 0.59523 | 0.079461 | 0.67052 | 0.59523 | 0.91753 | 7.7425 | 6.8731 | 0.91753 | 7.7425 | 6.8731 | 0.93133 | 4.3581 | -3.093 | -0.92503 | -3.9093 | 3.4467 | 0.15126 | -0.3159 | 0.86397 | -0.14754 | 0.58117 | -0.65493 | -6.8587 | -169.3408 | 12.9622 | 173.1413 | 10.6592 | -167.0378 | 1.0283 | 0.56436 | 0.46725 | 1.0209 | 0.51046 | 0.51046 | 2.3664 | -173.4866 | 177.3556 | 2.2033 | -177.7967 | -177.7967

## LL_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.064112 | 1.2299 | 1.2869 | 0.064112 | 1.2299 | 1.2869 | 0.7403 | 14.2014 | 14.8599 | 0.7403 | 14.2014 | 14.8599 | -0.73023 | 12.9507 | 1.4179 | 0.73434 | -11.4405 | 0.23553 | 0.11457 | 1.7681 | 10.7707 | -0.11214 | -0.87564 | -9.7936 | -170.3183 | -142.4496 | 36.216 | 9.6817 | 37.5504 | -143.784 | 0.99846 | 0.92039 | 0.73107 | 1.0034 | 0.80795 | 0.65925 | 0.76513 | -134.6755 | 118.7162 | 0.99898 | -138.0728 | 127.5936
Line_1 | 0.032056 | 0.2705 | 0.24013 | 0.032056 | 0.2705 | 0.24013 | 0.37015 | 3.1235 | 2.7727 | 0.37015 | 3.1235 | 2.7727 | 0.36819 | 2.5137 | -0.19971 | -0.36717 | -2.4407 | 0.25728 | -0.055465 | 0.68473 | 1.8438 | 0.056071 | -0.64156 | -1.8097 | 9.6817 | -152.8004 | 29.5025 | -170.3183 | 27.1996 | -150.4975 | 1.0059 | 0.83411 | 0.66885 | 1.0034 | 0.80795 | 0.65925 | 1.115 | -137.563 | 125.6845 | 0.99898 | -138.0728 | 127.5936
Line_2 | 0.032056 | 0.2705 | 0.24013 | 0.032056 | 0.2705 | 0.24013 | 0.37015 | 3.1235 | 2.7727 | 0.37015 | 3.1235 | 2.7727 | 0.36819 | 2.5137 | -0.19971 | -0.36717 | -2.4407 | 0.25728 | -0.055465 | 0.68473 | 1.8438 | 0.056071 | -0.64156 | -1.8097 | 9.6817 | -152.8004 | 29.5025 | -170.3183 | 27.1996 | -150.4975 | 1.0059 | 0.83411 | 0.66885 | 1.0034 | 0.80795 | 0.65925 | 1.115 | -137.563 | 125.6845 | 0.99898 | -138.0728 | 127.5936

## LL_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.064112 | 1.2299 | 1.2869 | 0.064112 | 1.2299 | 1.2869 | 0.7403 | 14.2014 | 14.8599 | 0.7403 | 14.2014 | 14.8599 | -0.73023 | 12.9507 | 1.4179 | 0.73434 | -11.4405 | 0.23553 | 0.11457 | 1.7681 | 10.7707 | -0.11214 | -0.87564 | -9.7936 | -170.3183 | -142.4496 | 36.216 | 9.6817 | 37.5504 | -143.784 | 0.99846 | 0.92039 | 0.73107 | 1.0034 | 0.80795 | 0.65925 | 0.76513 | -134.6755 | 118.7162 | 0.99898 | -138.0728 | 127.5936
Line_1 | 0.032056 | 0.2705 | 0.24013 | 0.032056 | 0.2705 | 0.24013 | 0.37015 | 3.1235 | 2.7727 | 0.37015 | 3.1235 | 2.7727 | 0.36819 | 2.5137 | -0.19971 | -0.36717 | -2.4407 | 0.25728 | -0.055465 | 0.68473 | 1.8438 | 0.056071 | -0.64156 | -1.8097 | 9.6817 | -152.8004 | 29.5025 | -170.3183 | 27.1996 | -150.4975 | 1.0059 | 0.83411 | 0.66885 | 1.0034 | 0.80795 | 0.65925 | 1.115 | -137.563 | 125.6845 | 0.99898 | -138.0728 | 127.5936
Line_2 | 0.032056 | 0.2705 | 0.24013 | 0.032056 | 0.2705 | 0.24013 | 0.37015 | 3.1235 | 2.7727 | 0.37015 | 3.1235 | 2.7727 | 0.36819 | 2.5137 | -0.19971 | -0.36717 | -2.4407 | 0.25728 | -0.055465 | 0.68473 | 1.8438 | 0.056071 | -0.64156 | -1.8097 | 9.6817 | -152.8004 | 29.5025 | -170.3183 | 27.1996 | -150.4975 | 1.0059 | 0.83411 | 0.66885 | 1.0034 | 0.80795 | 0.65925 | 1.115 | -137.563 | 125.6845 | 0.99898 | -138.0728 | 127.5936

## LG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 2.4472 | 0.75927 | 0.67794 | 2.4446 | 0.76192 | 0.68002 | 28.2578 | 8.7673 | 7.8281 | 28.2279 | 8.7979 | 7.8521 | 6.0372 | -8.9448 | 10.1927 | 1.4912e-10 | 8.4315 | -10.7752 | 4.0309 | 7.3269 | 0.23172 | -9.0994e-11 | -7.3851 | 0.24634 | -75.3426 | 90.4874 | 130.7298 | 104.6706 | -89.506 | -49.4086 |  | 0.25689 | 1.3188 | 1.3024 | 0 | 1.274 | 1.3726 | -41.6125 | -128.8345 | 132.0321 | 0 | -130.7209 | 129.2817
Line_1 | 1.1214 | 0.38345 | 0.34206 | 1.119 | 0.38096 | 0.34001 | 12.9491 | 4.4277 | 3.9498 | 12.9206 | 4.3989 | 3.9261 | 2.7703 | 4.9637 | -4.6913 | 6.8132e-11 | -4.2157 | 5.3876 | 1.3953 | -3.2373 | 0.071765 | -4.1851e-11 | 3.6925 | -0.12317 | -75.1819 | -89.473 | -49.6492 | 104.8388 | 90.494 | 130.5914 |  | 0.23954 | 1.3384 | 1.1879 | 0 | 1.274 | 1.3726 | -48.4489 | -122.585 | 129.4744 | 0 | -130.7209 | 129.2817
Line_2 | 1.1214 | 0.38345 | 0.34206 | 1.119 | 0.38096 | 0.34001 | 12.9491 | 4.4277 | 3.9498 | 12.9206 | 4.3989 | 3.9261 | 2.7703 | 4.9637 | -4.6913 | 6.8132e-11 | -4.2157 | 5.3876 | 1.3953 | -3.2373 | 0.071765 | -4.1851e-11 | 3.6925 | -0.12317 | -75.1819 | -89.473 | -49.6492 | 104.8388 | 90.494 | 130.5914 |  | 0.23954 | 1.3384 | 1.1879 | 0 | 1.274 | 1.3726 | -48.4489 | -122.585 | 129.4744 | 0 | -130.7209 | 129.2817

## LG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 2.4472 | 0.75927 | 0.67794 | 2.4446 | 0.76192 | 0.68002 | 28.2578 | 8.7673 | 7.8281 | 28.2279 | 8.7979 | 7.8521 | 6.0372 | -8.9448 | 10.1927 | 1.4912e-10 | 8.4315 | -10.7752 | 4.0309 | 7.3269 | 0.23172 | -9.0994e-11 | -7.3851 | 0.24634 | -75.3426 | 90.4874 | 130.7298 | 104.6706 | -89.506 | -49.4086 |  | 0.25689 | 1.3188 | 1.3024 | 0 | 1.274 | 1.3726 | -41.6125 | -128.8345 | 132.0321 | 0 | -130.7209 | 129.2817
Line_1 | 1.1214 | 0.38345 | 0.34206 | 1.119 | 0.38096 | 0.34001 | 12.9491 | 4.4277 | 3.9498 | 12.9206 | 4.3989 | 3.9261 | 2.7703 | 4.9637 | -4.6913 | 6.8132e-11 | -4.2157 | 5.3876 | 1.3953 | -3.2373 | 0.071765 | -4.1851e-11 | 3.6925 | -0.12317 | -75.1819 | -89.473 | -49.6492 | 104.8388 | 90.494 | 130.5914 |  | 0.23954 | 1.3384 | 1.1879 | 0 | 1.274 | 1.3726 | -48.4489 | -122.585 | 129.4744 | 0 | -130.7209 | 129.2817
Line_2 | 1.1214 | 0.38345 | 0.34206 | 1.119 | 0.38096 | 0.34001 | 12.9491 | 4.4277 | 3.9498 | 12.9206 | 4.3989 | 3.9261 | 2.7703 | 4.9637 | -4.6913 | 6.8132e-11 | -4.2157 | 5.3876 | 1.3953 | -3.2373 | 0.071765 | -4.1851e-11 | 3.6925 | -0.12317 | -75.1819 | -89.473 | -49.6492 | 104.8388 | 90.494 | 130.5914 |  | 0.23954 | 1.3384 | 1.1879 | 0 | 1.274 | 1.3726 | -48.4489 | -122.585 | 129.4744 | 0 | -130.7209 | 129.2817

## LG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.58494 | 0.14954 | 0.32613 | 0.58421 | 0.15001 | 0.32644 | 6.7543 | 1.7268 | 3.7658 | 6.7459 | 1.7321 | 3.7694 | 5.0591 | -2.0955 | 2.4257 | -4.6667 | 2.0999 | -2.4641 | 3.5545 | 0.068371 | -3.622 | -3.3452 | -0.11649 | 3.7657 | -44.2628 | 60.3093 | -179.1268 | 135.7657 | -119.4487 | 0.74637 |  | 0.9154 | 1.2142 | 1.1576 | 0.85115 | 1.2142 | 1.1939 | -9.1715 | -121.5595 | 124.6837 | -8.5998 | -122.6239 | 123.9455
Line_1 | 0.41026 | 0.075414 | 0.16355 | 0.40952 | 0.075004 | 0.16322 | 4.7373 | 0.87081 | 1.8885 | 4.7287 | 0.86607 | 1.8847 | 2.8081 | 1.0638 | -1.1516 | -2.4964 | -1.0499 | 1.2321 | 3.3598 | -0.020043 | 1.8399 | -3.1571 | 0.058245 | -1.8829 | -60.2701 | -118.9776 | 0.51354 | 119.7345 | 60.5513 | -179.2536 |  | 0.92432 | 1.2219 | 1.1494 | 0.85115 | 1.2142 | 1.1939 | -10.1592 | -120.0569 | 122.5572 | -8.5998 | -122.6239 | 123.9455
Line_2 | 0.41026 | 0.075414 | 0.16355 | 0.40952 | 0.075004 | 0.16322 | 4.7373 | 0.87081 | 1.8885 | 4.7287 | 0.86607 | 1.8847 | 2.8081 | 1.0638 | -1.1516 | -2.4964 | -1.0499 | 1.2321 | 3.3598 | -0.020043 | 1.8399 | -3.1571 | 0.058245 | -1.8829 | -60.2701 | -118.9776 | 0.51354 | 119.7345 | 60.5513 | -179.2536 |  | 0.92432 | 1.2219 | 1.1494 | 0.85115 | 1.2142 | 1.1939 | -10.1592 | -120.0569 | 122.5572 | -8.5998 | -122.6239 | 123.9455

## LG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.58494 | 0.14954 | 0.32613 | 0.58421 | 0.15001 | 0.32644 | 6.7543 | 1.7268 | 3.7658 | 6.7459 | 1.7321 | 3.7694 | 5.0591 | -2.0955 | 2.4257 | -4.6667 | 2.0999 | -2.4641 | 3.5545 | 0.068371 | -3.622 | -3.3452 | -0.11649 | 3.7657 | -44.2628 | 60.3093 | -179.1268 | 135.7657 | -119.4487 | 0.74637 |  | 0.9154 | 1.2142 | 1.1576 | 0.85115 | 1.2142 | 1.1939 | -9.1715 | -121.5595 | 124.6837 | -8.5998 | -122.6239 | 123.9455
Line_1 | 0.41026 | 0.075414 | 0.16355 | 0.40952 | 0.075004 | 0.16322 | 4.7373 | 0.87081 | 1.8885 | 4.7287 | 0.86607 | 1.8847 | 2.8081 | 1.0638 | -1.1516 | -2.4964 | -1.0499 | 1.2321 | 3.3598 | -0.020043 | 1.8399 | -3.1571 | 0.058245 | -1.8829 | -60.2701 | -118.9776 | 0.51354 | 119.7345 | 60.5513 | -179.2536 |  | 0.92432 | 1.2219 | 1.1494 | 0.85115 | 1.2142 | 1.1939 | -10.1592 | -120.0569 | 122.5572 | -8.5998 | -122.6239 | 123.9455
Line_2 | 0.41026 | 0.075414 | 0.16355 | 0.40952 | 0.075004 | 0.16322 | 4.7373 | 0.87081 | 1.8885 | 4.7287 | 0.86607 | 1.8847 | 2.8081 | 1.0638 | -1.1516 | -2.4964 | -1.0499 | 1.2321 | 3.3598 | -0.020043 | 1.8399 | -3.1571 | 0.058245 | -1.8829 | -60.2701 | -118.9776 | 0.51354 | 119.7345 | 60.5513 | -179.2536 |  | 0.92432 | 1.2219 | 1.1494 | 0.85115 | 1.2142 | 1.1939 | -10.1592 | -120.0569 | 122.5572 | -8.5998 | -122.6239 | 123.9455

## LG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 2.1239 | 0.67464 | 0.55938 | 2.1219 | 0.67662 | 0.5612 | 24.5252 | 7.7901 | 6.4592 | 24.5013 | 7.8129 | 6.4801 | 8.5185 | -2.9388 | 7.3041 | -5.9172e-11 | 2.1506 | -8.0347 | 2.4153 | 8.4512 | 0.37849 | -5.4974e-12 | -8.003 | 0.084182 | -63.878 | 121.5925 | 128.8942 | 116.1467 | -58.5011 | -51.2433 |  | 0.36103 | 1.1486 | 1.1323 | 0 | 1.0607 | 1.24 | -48.0481 | -129.2332 | 131.8606 | 0 | -133.46 | 128.1564
Line_1 | 0.85833 | 0.34011 | 0.28229 | 0.85644 | 0.33831 | 0.2806 | 9.9112 | 3.9273 | 3.2596 | 9.8894 | 3.9064 | 3.2401 | 3.2692 | 2.2284 | -3.1096 | -2.3832e-11 | -1.0753 | 4.0173 | 0.98604 | -3.8475 | 0.054314 | -2.7128e-12 | 4.0015 | -0.042091 | -65.0804 | -58.6402 | -51.4559 | 114.9606 | 121.4989 | 128.7567 |  | 0.34452 | 1.1321 | 0.95413 | 0 | 1.0607 | 1.24 | -48.2962 | -118.5617 | 127.5435 | 0 | -133.46 | 128.1564
Line_2 | 0.85833 | 0.34011 | 0.28229 | 0.85644 | 0.33831 | 0.2806 | 9.9112 | 3.9273 | 3.2596 | 9.8894 | 3.9064 | 3.2401 | 3.2692 | 2.2284 | -3.1096 | -2.3832e-11 | -1.0753 | 4.0173 | 0.98604 | -3.8475 | 0.054314 | -2.7128e-12 | 4.0015 | -0.042091 | -65.0804 | -58.6402 | -51.4559 | 114.9606 | 121.4989 | 128.7567 |  | 0.34452 | 1.1321 | 0.95413 | 0 | 1.0607 | 1.24 | -48.2962 | -118.5617 | 127.5435 | 0 | -133.46 | 128.1564

## LG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 2.1239 | 0.67464 | 0.55938 | 2.1219 | 0.67662 | 0.5612 | 24.5252 | 7.7901 | 6.4592 | 24.5013 | 7.8129 | 6.4801 | 8.5185 | -2.9388 | 7.3041 | -5.9172e-11 | 2.1506 | -8.0347 | 2.4153 | 8.4512 | 0.37849 | -5.4974e-12 | -8.003 | 0.084182 | -63.878 | 121.5925 | 128.8942 | 116.1467 | -58.5011 | -51.2433 |  | 0.36103 | 1.1486 | 1.1323 | 0 | 1.0607 | 1.24 | -48.0481 | -129.2332 | 131.8606 | 0 | -133.46 | 128.1564
Line_1 | 0.85833 | 0.34011 | 0.28229 | 0.85644 | 0.33831 | 0.2806 | 9.9112 | 3.9273 | 3.2596 | 9.8894 | 3.9064 | 3.2401 | 3.2692 | 2.2284 | -3.1096 | -2.3832e-11 | -1.0753 | 4.0173 | 0.98604 | -3.8475 | 0.054314 | -2.7128e-12 | 4.0015 | -0.042091 | -65.0804 | -58.6402 | -51.4559 | 114.9606 | 121.4989 | 128.7567 |  | 0.34452 | 1.1321 | 0.95413 | 0 | 1.0607 | 1.24 | -48.2962 | -118.5617 | 127.5435 | 0 | -133.46 | 128.1564
Line_2 | 0.85833 | 0.34011 | 0.28229 | 0.85644 | 0.33831 | 0.2806 | 9.9112 | 3.9273 | 3.2596 | 9.8894 | 3.9064 | 3.2401 | 3.2692 | 2.2284 | -3.1096 | -2.3832e-11 | -1.0753 | 4.0173 | 0.98604 | -3.8475 | 0.054314 | -2.7128e-12 | 4.0015 | -0.042091 | -65.0804 | -58.6402 | -51.4559 | 114.9606 | 121.4989 | 128.7567 |  | 0.34452 | 1.1321 | 0.95413 | 0 | 1.0607 | 1.24 | -48.2962 | -118.5617 | 127.5435 | 0 | -133.46 | 128.1564

## LG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.64203 | 0.20393 | 0.16909 | 0.6414 | 0.20453 | 0.16964 | 7.4135 | 2.3548 | 1.9525 | 7.4063 | 2.3617 | 1.9588 | 4.5319 | -0.5307 | 1.8879 | -3.7515 | 0.46215 | -1.9602 | 3.9086 | 2.423 | -0.62197 | -3.6827 | -2.3864 | 0.66343 | -50.2526 | 135.2179 | 142.5197 | 129.7721 | -44.8757 | -37.6179 |  | 0.80726 | 1.0533 | 1.018 | 0.70981 | 1.0292 | 1.0565 | -9.4758 | -122.4278 | 124.2852 | -5.7577 | -123.9155 | 123.6836
Line_1 | 0.25946 | 0.10281 | 0.08533 | 0.25889 | 0.10226 | 0.084819 | 2.9959 | 1.1871 | 0.9853 | 2.9894 | 1.1808 | 0.97941 | 1.784 | 0.33917 | -0.90206 | -1.4831 | -0.23107 | 0.9801 | 1.612 | -1.1832 | 0.33252 | -1.5175 | 1.1932 | -0.33172 | -51.455 | -45.0148 | -37.8304 | 128.586 | 135.1243 | 142.3821 |  | 0.80255 | 1.0368 | 0.97574 | 0.70981 | 1.0292 | 1.0565 | -9.3547 | -119.0201 | 121.9348 | -5.7577 | -123.9155 | 123.6836
Line_2 | 0.25946 | 0.10281 | 0.08533 | 0.25889 | 0.10226 | 0.084819 | 2.9959 | 1.1871 | 0.9853 | 2.9894 | 1.1808 | 0.97941 | 1.784 | 0.33917 | -0.90206 | -1.4831 | -0.23107 | 0.9801 | 1.612 | -1.1832 | 0.33252 | -1.5175 | 1.1932 | -0.33172 | -51.455 | -45.0148 | -37.8304 | 128.586 | 135.1243 | 142.3821 |  | 0.80255 | 1.0368 | 0.97574 | 0.70981 | 1.0292 | 1.0565 | -9.3547 | -119.0201 | 121.9348 | -5.7577 | -123.9155 | 123.6836

## LG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.64203 | 0.20393 | 0.16909 | 0.6414 | 0.20453 | 0.16964 | 7.4135 | 2.3548 | 1.9525 | 7.4063 | 2.3617 | 1.9588 | 4.5319 | -0.5307 | 1.8879 | -3.7515 | 0.46215 | -1.9602 | 3.9086 | 2.423 | -0.62197 | -3.6827 | -2.3864 | 0.66343 | -50.2526 | 135.2179 | 142.5197 | 129.7721 | -44.8757 | -37.6179 |  | 0.80726 | 1.0533 | 1.018 | 0.70981 | 1.0292 | 1.0565 | -9.4758 | -122.4278 | 124.2852 | -5.7577 | -123.9155 | 123.6836
Line_1 | 0.25946 | 0.10281 | 0.08533 | 0.25889 | 0.10226 | 0.084819 | 2.9959 | 1.1871 | 0.9853 | 2.9894 | 1.1808 | 0.97941 | 1.784 | 0.33917 | -0.90206 | -1.4831 | -0.23107 | 0.9801 | 1.612 | -1.1832 | 0.33252 | -1.5175 | 1.1932 | -0.33172 | -51.455 | -45.0148 | -37.8304 | 128.586 | 135.1243 | 142.3821 |  | 0.80255 | 1.0368 | 0.97574 | 0.70981 | 1.0292 | 1.0565 | -9.3547 | -119.0201 | 121.9348 | -5.7577 | -123.9155 | 123.6836
Line_2 | 0.25946 | 0.10281 | 0.08533 | 0.25889 | 0.10226 | 0.084819 | 2.9959 | 1.1871 | 0.9853 | 2.9894 | 1.1808 | 0.97941 | 1.784 | 0.33917 | -0.90206 | -1.4831 | -0.23107 | 0.9801 | 1.612 | -1.1832 | 0.33252 | -1.5175 | 1.1932 | -0.33172 | -51.455 | -45.0148 | -37.8304 | 128.586 | 135.1243 | 142.3821 |  | 0.80255 | 1.0368 | 0.97574 | 0.70981 | 1.0292 | 1.0565 | -9.3547 | -119.0201 | 121.9348 | -5.7577 | -123.9155 | 123.6836

## LLG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.33406 | 3.7418 | 3.7802 | 0.33624 | 3.7417 | 3.7796 | 3.8573 | 43.207 | 43.6496 | 3.8826 | 43.2054 | 43.643 | 0.052768 | 8.8999 | 6.9966 | -0.30238 | 1.0204e-10 | 1.4608e-10 | 5.3406 | 4.8878 | 12.1857 | -5.4481 | -1.063e-10 | -1.5249e-11 | -86.1281 | -177.3537 | 21.696 | 93.8881 | 2.6797 | -158.3359 |  | 1.3846 | 0.235 | 0.32192 | 1.4054 | 0 | 0 | 3.3058 | -148.5782 | 81.8333 | 0.71136 | 0 | 0
Line_1 | 0.17017 | 1.1188 | 0.92912 | 0.16812 | 1.1176 | 0.92761 | 1.965 | 12.9185 | 10.7285 | 1.9413 | 12.9055 | 10.7111 | 0.093987 | 2.2254 | 0.97568 | 0.15119 | 4.1407e-11 | 2.7406e-11 | -2.5931 | -0.18128 | 1.9291 | 2.7241 | -1.492e-11 | -2.3416e-11 | 93.9563 | 156.2377 | 56.3032 | -86.1119 | -23.6738 | -123.7841 |  | 1.3205 | 0.17284 | 0.2015 | 1.4054 | 0 | 0 | 6.0321 | 151.5809 | 119.4749 | 0.71136 | 0 | 0
Line_2 | 0.17017 | 1.1188 | 0.92912 | 0.16812 | 1.1176 | 0.92761 | 1.965 | 12.9185 | 10.7285 | 1.9413 | 12.9055 | 10.7111 | 0.093987 | 2.2254 | 0.97568 | 0.15119 | 4.1407e-11 | 2.7406e-11 | -2.5931 | -0.18128 | 1.9291 | 2.7241 | -1.492e-11 | -2.3416e-11 | 93.9563 | 156.2377 | 56.3032 | -86.1119 | -23.6738 | -123.7841 |  | 1.3205 | 0.17284 | 0.2015 | 1.4054 | 0 | 0 | 6.0321 | 151.5809 | 119.4749 | 0.71136 | 0 | 0

## LLG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.33406 | 3.7418 | 3.7802 | 0.33624 | 3.7417 | 3.7796 | 3.8573 | 43.207 | 43.6496 | 3.8826 | 43.2054 | 43.643 | 0.052768 | 8.8999 | 6.9966 | -0.30238 | 1.0204e-10 | 1.4608e-10 | 5.3406 | 4.8878 | 12.1857 | -5.4481 | -1.063e-10 | -1.5249e-11 | -86.1281 | -177.3537 | 21.696 | 93.8881 | 2.6797 | -158.3359 |  | 1.3846 | 0.235 | 0.32192 | 1.4054 | 0 | 0 | 3.3058 | -148.5782 | 81.8333 | 0.71136 | 0 | 0
Line_1 | 0.17017 | 1.1188 | 0.92912 | 0.16812 | 1.1176 | 0.92761 | 1.965 | 12.9185 | 10.7285 | 1.9413 | 12.9055 | 10.7111 | 0.093987 | 2.2254 | 0.97568 | 0.15119 | 4.1407e-11 | 2.7406e-11 | -2.5931 | -0.18128 | 1.9291 | 2.7241 | -1.492e-11 | -2.3416e-11 | 93.9563 | 156.2377 | 56.3032 | -86.1119 | -23.6738 | -123.7841 |  | 1.3205 | 0.17284 | 0.2015 | 1.4054 | 0 | 0 | 6.0321 | 151.5809 | 119.4749 | 0.71136 | 0 | 0
Line_2 | 0.17017 | 1.1188 | 0.92912 | 0.16812 | 1.1176 | 0.92761 | 1.965 | 12.9185 | 10.7285 | 1.9413 | 12.9055 | 10.7111 | 0.093987 | 2.2254 | 0.97568 | 0.15119 | 4.1407e-11 | 2.7406e-11 | -2.5931 | -0.18128 | 1.9291 | 2.7241 | -1.492e-11 | -2.3416e-11 | 93.9563 | 156.2377 | 56.3032 | -86.1119 | -23.6738 | -123.7841 |  | 1.3205 | 0.17284 | 0.2015 | 1.4054 | 0 | 0 | 6.0321 | 151.5809 | 119.4749 | 0.71136 | 0 | 0

## LLG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.074158 | 0.7855 | 0.78478 | 0.073835 | 0.78562 | 0.7844 | 0.85631 | 9.0701 | 9.0619 | 0.85257 | 9.0715 | 9.0575 | 0.69939 | 7.7589 | 5.0995 | -0.69864 | -7.3851 | -4.7306 | -0.7713 | 3.1016 | 7.1861 | 0.78974 | -2.9894 | -6.5625 | 50.221 | -146.6358 | 54.7175 | -130.2903 | 33.4171 | -125.3286 |  | 1.2159 | 0.92125 | 0.97239 | 1.2367 | 0.87826 | 0.89316 | 2.4216 | -124.8467 | 109.357 | 1.2072 | -124.5454 | 108.8853
Line_1 | 0.036655 | 0.38749 | 0.34835 | 0.036917 | 0.38705 | 0.34784 | 0.42325 | 4.4744 | 4.0224 | 0.42628 | 4.4692 | 4.0165 | -0.35128 | 1.7193 | 3.0914 | 0.34932 | -1.4498 | -2.9529 | 0.36669 | 3.6572 | 2.2861 | -0.39487 | -3.6476 | -2.037 | -131.2921 | 167.0514 | 74.3641 | 49.7097 | -12.8697 | -105.7134 |  | 1.1998 | 0.90319 | 0.95586 | 1.2367 | 0.87826 | 0.89316 | 2.4785 | -128.1267 | 110.8468 | 1.2072 | -124.5454 | 108.8853
Line_2 | 0.036655 | 0.38749 | 0.34835 | 0.036917 | 0.38705 | 0.34784 | 0.42325 | 4.4744 | 4.0224 | 0.42628 | 4.4692 | 4.0165 | -0.35128 | 1.7193 | 3.0914 | 0.34932 | -1.4498 | -2.9529 | 0.36669 | 3.6572 | 2.2861 | -0.39487 | -3.6476 | -2.037 | -131.2921 | 167.0514 | 74.3641 | 49.7097 | -12.8697 | -105.7134 |  | 1.1998 | 0.90319 | 0.95586 | 1.2367 | 0.87826 | 0.89316 | 2.4785 | -128.1267 | 110.8468 | 1.2072 | -124.5454 | 108.8853

## LLG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.074158 | 0.7855 | 0.78478 | 0.073835 | 0.78562 | 0.7844 | 0.85631 | 9.0701 | 9.0619 | 0.85257 | 9.0715 | 9.0575 | 0.69939 | 7.7589 | 5.0995 | -0.69864 | -7.3851 | -4.7306 | -0.7713 | 3.1016 | 7.1861 | 0.78974 | -2.9894 | -6.5625 | 50.221 | -146.6358 | 54.7175 | -130.2903 | 33.4171 | -125.3286 |  | 1.2159 | 0.92125 | 0.97239 | 1.2367 | 0.87826 | 0.89316 | 2.4216 | -124.8467 | 109.357 | 1.2072 | -124.5454 | 108.8853
Line_1 | 0.036655 | 0.38749 | 0.34835 | 0.036917 | 0.38705 | 0.34784 | 0.42325 | 4.4744 | 4.0224 | 0.42628 | 4.4692 | 4.0165 | -0.35128 | 1.7193 | 3.0914 | 0.34932 | -1.4498 | -2.9529 | 0.36669 | 3.6572 | 2.2861 | -0.39487 | -3.6476 | -2.037 | -131.2921 | 167.0514 | 74.3641 | 49.7097 | -12.8697 | -105.7134 |  | 1.1998 | 0.90319 | 0.95586 | 1.2367 | 0.87826 | 0.89316 | 2.4785 | -128.1267 | 110.8468 | 1.2072 | -124.5454 | 108.8853
Line_2 | 0.036655 | 0.38749 | 0.34835 | 0.036917 | 0.38705 | 0.34784 | 0.42325 | 4.4744 | 4.0224 | 0.42628 | 4.4692 | 4.0165 | -0.35128 | 1.7193 | 3.0914 | 0.34932 | -1.4498 | -2.9529 | 0.36669 | 3.6572 | 2.2861 | -0.39487 | -3.6476 | -2.037 | -131.2921 | 167.0514 | 74.3641 | 49.7097 | -12.8697 | -105.7134 |  | 1.1998 | 0.90319 | 0.95586 | 1.2367 | 0.87826 | 0.89316 | 2.4785 | -128.1267 | 110.8468 | 1.2072 | -124.5454 | 108.8853

## LLG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.39775 | 3.1986 | 3.1447 | 0.39951 | 3.1986 | 3.1441 | 4.5928 | 36.9345 | 36.3124 | 4.6131 | 36.9348 | 36.3045 | 2.1305 | 11.868 | 9.987 | -2.5902 | -1.1904e-10 | -3.9309e-11 | 5.0849 | 1.3836 | 10.688 | -5.0516 | -8.5895e-11 | -1.4042e-10 | -63.6675 | -170.0319 | 30.8667 | 116.2547 | 10.0011 | -149.1645 |  | 1.2004 | 0.3235 | 0.40283 | 1.2306 | 0 | 0 | 3.5992 | -163.382 | 77.8087 | -0.89203 | 0 | 0
Line_1 | 0.20133 | 0.95829 | 0.62677 | 0.19975 | 0.95751 | 0.6256 | 2.3248 | 11.0653 | 7.2373 | 2.3065 | 11.0564 | 7.2238 | -0.78886 | 2.9417 | 0.82501 | 1.2951 | -2.1494e-11 | -2.0552e-11 | -2.3713 | -0.67008 | 1.7133 | 2.5258 | -3.8326e-11 | -2.0481e-11 | 116.1557 | 165.0147 | 60.3987 | -63.7453 | -14.9005 | -119.7032 |  | 1.0749 | 0.27266 | 0.26275 | 1.2306 | 0 | 0 | 7.7547 | 152.1824 | 124.6862 | -0.89203 | 0 | 0
Line_2 | 0.20133 | 0.95829 | 0.62677 | 0.19975 | 0.95751 | 0.6256 | 2.3248 | 11.0653 | 7.2373 | 2.3065 | 11.0564 | 7.2238 | -0.78886 | 2.9417 | 0.82501 | 1.2951 | -2.1494e-11 | -2.0552e-11 | -2.3713 | -0.67008 | 1.7133 | 2.5258 | -3.8326e-11 | -2.0481e-11 | 116.1557 | 165.0147 | 60.3987 | -63.7453 | -14.9005 | -119.7032 |  | 1.0749 | 0.27266 | 0.26275 | 1.2306 | 0 | 0 | 7.7547 | 152.1824 | 124.6862 | -0.89203 | 0 | 0

## LLG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.39775 | 3.1986 | 3.1447 | 0.39951 | 3.1986 | 3.1441 | 4.5928 | 36.9345 | 36.3124 | 4.6131 | 36.9348 | 36.3045 | 2.1305 | 11.868 | 9.987 | -2.5902 | -1.1904e-10 | -3.9309e-11 | 5.0849 | 1.3836 | 10.688 | -5.0516 | -8.5895e-11 | -1.4042e-10 | -63.6675 | -170.0319 | 30.8667 | 116.2547 | 10.0011 | -149.1645 |  | 1.2004 | 0.3235 | 0.40283 | 1.2306 | 0 | 0 | 3.5992 | -163.382 | 77.8087 | -0.89203 | 0 | 0
Line_1 | 0.20133 | 0.95829 | 0.62677 | 0.19975 | 0.95751 | 0.6256 | 2.3248 | 11.0653 | 7.2373 | 2.3065 | 11.0564 | 7.2238 | -0.78886 | 2.9417 | 0.82501 | 1.2951 | -2.1494e-11 | -2.0552e-11 | -2.3713 | -0.67008 | 1.7133 | 2.5258 | -3.8326e-11 | -2.0481e-11 | 116.1557 | 165.0147 | 60.3987 | -63.7453 | -14.9005 | -119.7032 |  | 1.0749 | 0.27266 | 0.26275 | 1.2306 | 0 | 0 | 7.7547 | 152.1824 | 124.6862 | -0.89203 | 0 | 0
Line_2 | 0.20133 | 0.95829 | 0.62677 | 0.19975 | 0.95751 | 0.6256 | 2.3248 | 11.0653 | 7.2373 | 2.3065 | 11.0564 | 7.2238 | -0.78886 | 2.9417 | 0.82501 | 1.2951 | -2.1494e-11 | -2.0552e-11 | -2.3713 | -0.67008 | 1.7133 | 2.5258 | -3.8326e-11 | -2.0481e-11 | 116.1557 | 165.0147 | 60.3987 | -63.7453 | -14.9005 | -119.7032 |  | 1.0749 | 0.27266 | 0.26275 | 1.2306 | 0 | 0 | 7.7547 | 152.1824 | 124.6862 | -0.89203 | 0 | 0

## LLG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.15272 | 0.77258 | 0.82827 | 0.15331 | 0.77267 | 0.82789 | 1.7634 | 8.921 | 9.5641 | 1.7703 | 8.9221 | 9.5596 | 1.1001 | 6.3532 | 4.7952 | -1.1602 | -5.6733 | -3.9752 | 1.5166 | 3.5808 | 6.6204 | -1.5101 | -3.6249 | -5.7954 | -52.3277 | -154.8118 | 54.6935 | 127.5896 | 25.2347 | -125.3412 |  | 1.0625 | 0.81748 | 0.85472 | 1.0757 | 0.75459 | 0.73515 | 1.7154 | -125.4054 | 108.7773 | 0.055524 | -122.1889 | 110.2119
Line_1 | 0.077191 | 0.25314 | 0.20814 | 0.076656 | 0.25288 | 0.20764 | 0.89133 | 2.923 | 2.4034 | 0.88514 | 2.92 | 2.3976 | -0.51349 | 1.2034 | 1.7633 | 0.58009 | -0.95936 | -1.6153 | -0.74146 | 1.9136 | 0.8757 | 0.75506 | -1.9835 | -0.70522 | 127.4775 | 173.5113 | 86.6921 | -52.4104 | -6.3777 | -93.3731 |  | 1.0119 | 0.77337 | 0.81917 | 1.0757 | 0.75459 | 0.73515 | 2.7733 | -128.6523 | 113.1021 | 0.055524 | -122.1889 | 110.2119
Line_2 | 0.077191 | 0.25314 | 0.20814 | 0.076656 | 0.25288 | 0.20764 | 0.89133 | 2.923 | 2.4034 | 0.88514 | 2.92 | 2.3976 | -0.51349 | 1.2034 | 1.7633 | 0.58009 | -0.95936 | -1.6153 | -0.74146 | 1.9136 | 0.8757 | 0.75506 | -1.9835 | -0.70522 | 127.4775 | 173.5113 | 86.6921 | -52.4104 | -6.3777 | -93.3731 |  | 1.0119 | 0.77337 | 0.81917 | 1.0757 | 0.75459 | 0.73515 | 2.7733 | -128.6523 | 113.1021 | 0.055524 | -122.1889 | 110.2119

## LLG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.15272 | 0.77258 | 0.82827 | 0.15331 | 0.77267 | 0.82789 | 1.7634 | 8.921 | 9.5641 | 1.7703 | 8.9221 | 9.5596 | 1.1001 | 6.3532 | 4.7952 | -1.1602 | -5.6733 | -3.9752 | 1.5166 | 3.5808 | 6.6204 | -1.5101 | -3.6249 | -5.7954 | -52.3277 | -154.8118 | 54.6935 | 127.5896 | 25.2347 | -125.3412 |  | 1.0625 | 0.81748 | 0.85472 | 1.0757 | 0.75459 | 0.73515 | 1.7154 | -125.4054 | 108.7773 | 0.055524 | -122.1889 | 110.2119
Line_1 | 0.077191 | 0.25314 | 0.20814 | 0.076656 | 0.25288 | 0.20764 | 0.89133 | 2.923 | 2.4034 | 0.88514 | 2.92 | 2.3976 | -0.51349 | 1.2034 | 1.7633 | 0.58009 | -0.95936 | -1.6153 | -0.74146 | 1.9136 | 0.8757 | 0.75506 | -1.9835 | -0.70522 | 127.4775 | 173.5113 | 86.6921 | -52.4104 | -6.3777 | -93.3731 |  | 1.0119 | 0.77337 | 0.81917 | 1.0757 | 0.75459 | 0.73515 | 2.7733 | -128.6523 | 113.1021 | 0.055524 | -122.1889 | 110.2119
Line_2 | 0.077191 | 0.25314 | 0.20814 | 0.076656 | 0.25288 | 0.20764 | 0.89133 | 2.923 | 2.4034 | 0.88514 | 2.92 | 2.3976 | -0.51349 | 1.2034 | 1.7633 | 0.58009 | -0.95936 | -1.6153 | -0.74146 | 1.9136 | 0.8757 | 0.75506 | -1.9835 | -0.70522 | 127.4775 | 173.5113 | 86.6921 | -52.4104 | -6.3777 | -93.3731 |  | 1.0119 | 0.77337 | 0.81917 | 1.0757 | 0.75459 | 0.73515 | 2.7733 | -128.6523 | 113.1021 | 0.055524 | -122.1889 | 110.2119