## LLL_max_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 4.283 | 4.283 | 0 | 9.0614 | 148.3662 | 148.3662 | 28.6163 | -1e-07 | 32.4685 | -1e-07 | -77.7798 | 102.2202 | 0.29171 | 0 | -29.1714 | 0
Line_1 | 0.9515 | 0.9515 | 0 | 1.8972 | 32.9609 | 32.9609 | 1.4123 | -1e-07 | 1.6025 | -1e-07 | -72.853 | 107.147 | 0.064805 | 0 | -24.2445 | 0
Line_2 | 0.9515 | 0.9515 | 0 | 1.8972 | 32.9609 | 32.9609 | 1.4123 | -1e-07 | 1.6025 | -1e-07 | -72.853 | 107.147 | 0.064805 | 0 | -24.2445 | 0

## LLL_max_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 4.283 | 4.283 | 0 | 9.0614 | 148.3662 | 148.3662 | 28.6163 | -1e-07 | 32.4685 | -1e-07 | -77.7798 | 102.2202 | 0.29171 | 0 | -29.1714 | 0
Line_1 | 0.9515 | 0.9515 | 0 | 1.8972 | 32.9609 | 32.9609 | 1.4123 | -1e-07 | 1.6025 | -1e-07 | -72.853 | 107.147 | 0.064805 | 0 | -24.2445 | 0
Line_2 | 0.9515 | 0.9515 | 0 | 1.8972 | 32.9609 | 32.9609 | 1.4123 | -1e-07 | 1.6025 | -1e-07 | -72.853 | 107.147 | 0.064805 | 0 | -24.2445 | 0

## LLL_max_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.8763 | 0.8763 | 0 | 1.9596 | 30.3558 | 30.3558 | 22.4252 | -21.2272 | 19.1954 | -17.8362 | -47.233 | 132.767 | 0.97242 | 0.91337 | -6.6703 | -7.1943
Line_1 | 0.31157 | 0.31157 | 0 | 0.57123 | 10.793 | 10.793 | 6.2226 | -6.0711 | 7.9384 | -7.7666 | -59.1798 | 120.8202 | 0.93455 | 0.91337 | -7.271 | -7.1943
Line_2 | 0.31157 | 0.31157 | 0 | 0.57123 | 10.793 | 10.793 | 6.2226 | -6.0711 | 7.9384 | -7.7666 | -59.1798 | 120.8202 | 0.93455 | 0.91337 | -7.271 | -7.1943

## LLL_max_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.8763 | 0.8763 | 0 | 1.9596 | 30.3558 | 30.3558 | 22.4252 | -21.2272 | 19.1954 | -17.8362 | -47.233 | 132.767 | 0.97242 | 0.91337 | -6.6703 | -7.1943
Line_1 | 0.31157 | 0.31157 | 0 | 0.57123 | 10.793 | 10.793 | 6.2226 | -6.0711 | 7.9384 | -7.7666 | -59.1798 | 120.8202 | 0.93455 | 0.91337 | -7.271 | -7.1943
Line_2 | 0.31157 | 0.31157 | 0 | 0.57123 | 10.793 | 10.793 | 6.2226 | -6.0711 | 7.9384 | -7.7666 | -59.1798 | 120.8202 | 0.93455 | 0.91337 | -7.271 | -7.1943

## LLL_min_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 3.6016 | 3.6016 | 0 | 6.8561 | 124.7634 | 124.7634 | 38.8525 | -1e-07 | 22.9597 | -1e-07 | -69.6723 | 110.3277 | 0.36172 | 0 | -39.0915 | 0
Line_1 | 0.77473 | 0.77473 | 0 | 1.4748 | 26.8374 | 26.8374 | 1.7977 | -1e-07 | 1.0624 | -1e-07 | -70.2749 | 109.7251 | 0.077808 | 0 | -39.6941 | 0
Line_2 | 0.77473 | 0.77473 | 0 | 1.4748 | 26.8374 | 26.8374 | 1.7977 | -1e-07 | 1.0624 | -1e-07 | -70.2749 | 109.7251 | 0.077808 | 0 | -39.6941 | 0

## LLL_min_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 3.6016 | 3.6016 | 0 | 6.8561 | 124.7634 | 124.7634 | 38.8525 | -1e-07 | 22.9597 | -1e-07 | -69.6723 | 110.3277 | 0.36172 | 0 | -39.0915 | 0
Line_1 | 0.77473 | 0.77473 | 0 | 1.4748 | 26.8374 | 26.8374 | 1.7977 | -1e-07 | 1.0624 | -1e-07 | -70.2749 | 109.7251 | 0.077808 | 0 | -39.6941 | 0
Line_2 | 0.77473 | 0.77473 | 0 | 1.4748 | 26.8374 | 26.8374 | 1.7977 | -1e-07 | 1.0624 | -1e-07 | -70.2749 | 109.7251 | 0.077808 | 0 | -39.6941 | 0

## LLL_min_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.88201 | 0.88201 | 0 | 1.679 | 30.5537 | 30.5537 | 19.072 | -16.7419 | 18.0132 | -16.6363 | -50.7266 | 129.2734 | 0.85861 | 0.77248 | -7.3619 | -5.9079
Line_1 | 0.18973 | 0.18973 | 0 | 0.36117 | 6.5723 | 6.5723 | 3.6713 | -3.5635 | 3.68 | -3.6162 | -51.3292 | 128.6708 | 0.79091 | 0.77248 | -6.2614 | -5.9079
Line_2 | 0.18973 | 0.18973 | 0 | 0.36117 | 6.5723 | 6.5723 | 3.6713 | -3.5635 | 3.68 | -3.6162 | -51.3292 | 128.6708 | 0.79091 | 0.77248 | -6.2614 | -5.9079

## LLL_min_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.88201 | 0.88201 | 0 | 1.679 | 30.5537 | 30.5537 | 19.072 | -16.7419 | 18.0132 | -16.6363 | -50.7266 | 129.2734 | 0.85861 | 0.77248 | -7.3619 | -5.9079
Line_1 | 0.18973 | 0.18973 | 0 | 0.36117 | 6.5723 | 6.5723 | 3.6713 | -3.5635 | 3.68 | -3.6162 | -51.3292 | 128.6708 | 0.79091 | 0.77248 | -6.2614 | -5.9079
Line_2 | 0.18973 | 0.18973 | 0 | 0.36117 | 6.5723 | 6.5723 | 3.6713 | -3.5635 | 3.68 | -3.6162 | -51.3292 | 128.6708 | 0.79091 | 0.77248 | -6.2614 | -5.9079

## LL_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.35595 | 3.6314 | 3.7936 | 0.35595 | 3.6314 | 3.7936 | 4.1102 | 41.9321 | 43.8052 | 4.1102 | 41.9321 | 43.8052 | -2.8809 | 31.035 | -18.1673 | 2.9468 | -24.1776 | 25.651 | -3.7882 | 2.3326 | 12.0075 | 3.8629 | 5.4478 | -3.5164 | 129.3592 | -165.2802 | 9.8274 | -50.6408 | 14.7198 | -170.1726 | 1.1579 | 0.74221 | 0.49713 | 1.1821 | 0.59105 | 0.59105 | 2.1065 | -160.9818 | 156.365 | 2.0217 | -177.9783 | -177.9783
Line_1 | 0.17798 | 0.82688 | 0.74081 | 0.17798 | 0.82688 | 0.74081 | 2.0551 | 9.548 | 8.5541 | 2.0551 | 9.548 | 8.5541 | 1.4899 | 5.9918 | -4.6142 | -1.4734 | -5.6362 | 4.8995 | 1.9502 | 0.12158 | 1.5713 | -1.9315 | 0.28182 | -1.2476 | -50.6408 | -175.1159 | 16.3071 | 129.3592 | 4.8841 | -163.6929 | 1.1942 | 0.62767 | 0.56983 | 1.1821 | 0.59105 | 0.59105 | 1.9805 | -173.9534 | 177.501 | 2.0217 | -177.9783 | -177.9783
Line_2 | 0.17798 | 0.82688 | 0.74081 | 0.17798 | 0.82688 | 0.74081 | 2.0551 | 9.548 | 8.5541 | 2.0551 | 9.548 | 8.5541 | 1.4899 | 5.9918 | -4.6142 | -1.4734 | -5.6362 | 4.8995 | 1.9502 | 0.12158 | 1.5713 | -1.9315 | 0.28182 | -1.2476 | -50.6408 | -175.1159 | 16.3071 | 129.3592 | 4.8841 | -163.6929 | 1.1942 | 0.62767 | 0.56983 | 1.1821 | 0.59105 | 0.59105 | 1.9805 | -173.9534 | 177.501 | 2.0217 | -177.9783 | -177.9783

## LL_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.35595 | 3.6314 | 3.7936 | 0.35595 | 3.6314 | 3.7936 | 4.1102 | 41.9321 | 43.8052 | 4.1102 | 41.9321 | 43.8052 | -2.8809 | 31.035 | -18.1673 | 2.9468 | -24.1776 | 25.651 | -3.7882 | 2.3326 | 12.0075 | 3.8629 | 5.4478 | -3.5164 | 129.3592 | -165.2802 | 9.8274 | -50.6408 | 14.7198 | -170.1726 | 1.1579 | 0.74221 | 0.49713 | 1.1821 | 0.59105 | 0.59105 | 2.1065 | -160.9818 | 156.365 | 2.0217 | -177.9783 | -177.9783
Line_1 | 0.17798 | 0.82688 | 0.74081 | 0.17798 | 0.82688 | 0.74081 | 2.0551 | 9.548 | 8.5541 | 2.0551 | 9.548 | 8.5541 | 1.4899 | 5.9918 | -4.6142 | -1.4734 | -5.6362 | 4.8995 | 1.9502 | 0.12158 | 1.5713 | -1.9315 | 0.28182 | -1.2476 | -50.6408 | -175.1159 | 16.3071 | 129.3592 | 4.8841 | -163.6929 | 1.1942 | 0.62767 | 0.56983 | 1.1821 | 0.59105 | 0.59105 | 1.9805 | -173.9534 | 177.501 | 2.0217 | -177.9783 | -177.9783
Line_2 | 0.17798 | 0.82688 | 0.74081 | 0.17798 | 0.82688 | 0.74081 | 2.0551 | 9.548 | 8.5541 | 2.0551 | 9.548 | 8.5541 | 1.4899 | 5.9918 | -4.6142 | -1.4734 | -5.6362 | 4.8995 | 1.9502 | 0.12158 | 1.5713 | -1.9315 | 0.28182 | -1.2476 | -50.6408 | -175.1159 | 16.3071 | 129.3592 | 4.8841 | -163.6929 | 1.1942 | 0.62767 | 0.56983 | 1.1821 | 0.59105 | 0.59105 | 1.9805 | -173.9534 | 177.501 | 2.0217 | -177.9783 | -177.9783

## LL_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.25737 | 1.3967 | 1.3626 | 0.25737 | 1.3967 | 1.3626 | 2.9719 | 16.1276 | 15.7336 | 2.9719 | 16.1276 | 15.7336 | -1.5571 | 16.583 | -0.024169 | 1.5915 | -15.5686 | 0.9896 | -3.0312 | 1.2162 | 13.0202 | 3.0703 | -0.065208 | -11.9248 | 118.302 | -138.8076 | 30.5822 | -61.698 | 41.1924 | -149.4178 | 1.1467 | 1.031 | 0.82754 | 1.1637 | 0.96535 | 0.76053 | 1.1134 | -134.6132 | 120.6885 | 0.90162 | -138.5676 | 125.3261
Line_1 | 0.12869 | 0.3798 | 0.37361 | 0.12869 | 0.3798 | 0.37361 | 1.4859 | 4.3855 | 4.314 | 1.4859 | 4.3855 | 4.314 | 0.80437 | 3.8907 | 0.077321 | -0.79576 | -3.8157 | -0.0047391 | 1.5449 | 1.9191 | 3.3633 | -1.5351 | -1.834 | -3.2809 | -61.698 | -164.2384 | 35.4088 | 118.302 | 15.7616 | -144.5912 | 1.1722 | 0.98922 | 0.77982 | 1.1637 | 0.96535 | 0.76053 | 0.79804 | -137.9837 | 124.0918 | 0.90162 | -138.5676 | 125.3261
Line_2 | 0.12869 | 0.3798 | 0.37361 | 0.12869 | 0.3798 | 0.37361 | 1.4859 | 4.3855 | 4.314 | 1.4859 | 4.3855 | 4.314 | 0.80437 | 3.8907 | 0.077321 | -0.79576 | -3.8157 | -0.0047391 | 1.5449 | 1.9191 | 3.3633 | -1.5351 | -1.834 | -3.2809 | -61.698 | -164.2384 | 35.4088 | 118.302 | 15.7616 | -144.5912 | 1.1722 | 0.98922 | 0.77982 | 1.1637 | 0.96535 | 0.76053 | 0.79804 | -137.9837 | 124.0918 | 0.90162 | -138.5676 | 125.3261

## LL_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.25737 | 1.3967 | 1.3626 | 0.25737 | 1.3967 | 1.3626 | 2.9719 | 16.1276 | 15.7336 | 2.9719 | 16.1276 | 15.7336 | -1.5571 | 16.583 | -0.024169 | 1.5915 | -15.5686 | 0.9896 | -3.0312 | 1.2162 | 13.0202 | 3.0703 | -0.065208 | -11.9248 | 118.302 | -138.8076 | 30.5822 | -61.698 | 41.1924 | -149.4178 | 1.1467 | 1.031 | 0.82754 | 1.1637 | 0.96535 | 0.76053 | 1.1134 | -134.6132 | 120.6885 | 0.90162 | -138.5676 | 125.3261
Line_1 | 0.12869 | 0.3798 | 0.37361 | 0.12869 | 0.3798 | 0.37361 | 1.4859 | 4.3855 | 4.314 | 1.4859 | 4.3855 | 4.314 | 0.80437 | 3.8907 | 0.077321 | -0.79576 | -3.8157 | -0.0047391 | 1.5449 | 1.9191 | 3.3633 | -1.5351 | -1.834 | -3.2809 | -61.698 | -164.2384 | 35.4088 | 118.302 | 15.7616 | -144.5912 | 1.1722 | 0.98922 | 0.77982 | 1.1637 | 0.96535 | 0.76053 | 0.79804 | -137.9837 | 124.0918 | 0.90162 | -138.5676 | 125.3261
Line_2 | 0.12869 | 0.3798 | 0.37361 | 0.12869 | 0.3798 | 0.37361 | 1.4859 | 4.3855 | 4.314 | 1.4859 | 4.3855 | 4.314 | 0.80437 | 3.8907 | 0.077321 | -0.79576 | -3.8157 | -0.0047391 | 1.5449 | 1.9191 | 3.3633 | -1.5351 | -1.834 | -3.2809 | -61.698 | -164.2384 | 35.4088 | 118.302 | 15.7616 | -144.5912 | 1.1722 | 0.98922 | 0.77982 | 1.1637 | 0.96535 | 0.76053 | 0.79804 | -137.9837 | 124.0918 | 0.90162 | -138.5676 | 125.3261

## LL_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.15892 | 3.0486 | 3.19 | 0.15892 | 3.0486 | 3.19 | 1.8351 | 35.2024 | 36.8347 | 1.8351 | 35.2024 | 36.8347 | -1.8248 | 26.2892 | -7.7754 | 1.8501 | -17.01 | 17.935 | -0.28017 | -0.30937 | 11.6491 | 0.29507 | 5.7929 | -5.6453 | 173.1413 | -158.99 | 19.6756 | -6.8587 | 21.01 | -160.3244 | 1.0061 | 0.74685 | 0.38023 | 1.0209 | 0.51046 | 0.51046 | 1.8699 | -159.6642 | 143.3972 | 2.2033 | -177.7967 | -177.7967
Line_1 | 0.079461 | 0.67052 | 0.59523 | 0.079461 | 0.67052 | 0.59523 | 0.91753 | 7.7425 | 6.8731 | 0.91753 | 7.7425 | 6.8731 | 0.93133 | 4.3581 | -3.093 | -0.92503 | -3.9093 | 3.4467 | 0.15126 | -0.3159 | 0.86397 | -0.14754 | 0.58117 | -0.65493 | -6.8587 | -169.3408 | 12.9622 | 173.1413 | 10.6592 | -167.0378 | 1.0283 | 0.56436 | 0.46725 | 1.0209 | 0.51046 | 0.51046 | 2.3664 | -173.4866 | 177.3556 | 2.2033 | -177.7967 | -177.7967
Line_2 | 0.079461 | 0.67052 | 0.59523 | 0.079461 | 0.67052 | 0.59523 | 0.91753 | 7.7425 | 6.8731 | 0.91753 | 7.7425 | 6.8731 | 0.93133 | 4.3581 | -3.093 | -0.92503 | -3.9093 | 3.4467 | 0.15126 | -0.3159 | 0.86397 | -0.14754 | 0.58117 | -0.65493 | -6.8587 | -169.3408 | 12.9622 | 173.1413 | 10.6592 | -167.0378 | 1.0283 | 0.56436 | 0.46725 | 1.0209 | 0.51046 | 0.51046 | 2.3664 | -173.4866 | 177.3556 | 2.2033 | -177.7967 | -177.7967

## LL_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.15892 | 3.0486 | 3.19 | 0.15892 | 3.0486 | 3.19 | 1.8351 | 35.2024 | 36.8347 | 1.8351 | 35.2024 | 36.8347 | -1.8248 | 26.2892 | -7.7754 | 1.8501 | -17.01 | 17.935 | -0.28017 | -0.30937 | 11.6491 | 0.29507 | 5.7929 | -5.6453 | 173.1413 | -158.99 | 19.6756 | -6.8587 | 21.01 | -160.3244 | 1.0061 | 0.74685 | 0.38023 | 1.0209 | 0.51046 | 0.51046 | 1.8699 | -159.6642 | 143.3972 | 2.2033 | -177.7967 | -177.7967
Line_1 | 0.079461 | 0.67052 | 0.59523 | 0.079461 | 0.67052 | 0.59523 | 0.91753 | 7.7425 | 6.8731 | 0.91753 | 7.7425 | 6.8731 | 0.93133 | 4.3581 | -3.093 | -0.92503 | -3.9093 | 3.4467 | 0.15126 | -0.3159 | 0.86397 | -0.14754 | 0.58117 | -0.65493 | -6.8587 | -169.3408 | 12.9622 | 173.1413 | 10.6592 | -167.0378 | 1.0283 | 0.56436 | 0.46725 | 1.0209 | 0.51046 | 0.51046 | 2.3664 | -173.4866 | 177.3556 | 2.2033 | -177.7967 | -177.7967
Line_2 | 0.079461 | 0.67052 | 0.59523 | 0.079461 | 0.67052 | 0.59523 | 0.91753 | 7.7425 | 6.8731 | 0.91753 | 7.7425 | 6.8731 | 0.93133 | 4.3581 | -3.093 | -0.92503 | -3.9093 | 3.4467 | 0.15126 | -0.3159 | 0.86397 | -0.14754 | 0.58117 | -0.65493 | -6.8587 | -169.3408 | 12.9622 | 173.1413 | 10.6592 | -167.0378 | 1.0283 | 0.56436 | 0.46725 | 1.0209 | 0.51046 | 0.51046 | 2.3664 | -173.4866 | 177.3556 | 2.2033 | -177.7967 | -177.7967

## LL_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.064112 | 1.2299 | 1.2869 | 0.064112 | 1.2299 | 1.2869 | 0.7403 | 14.2014 | 14.8599 | 0.7403 | 14.2014 | 14.8599 | -0.73023 | 12.9507 | 1.4179 | 0.73434 | -11.4405 | 0.23553 | 0.11457 | 1.7681 | 10.7707 | -0.11214 | -0.87564 | -9.7936 | -170.3183 | -142.4496 | 36.216 | 9.6817 | 37.5504 | -143.784 | 0.99846 | 0.92039 | 0.73107 | 1.0034 | 0.80795 | 0.65925 | 0.76513 | -134.6755 | 118.7162 | 0.99898 | -138.0728 | 127.5936
Line_1 | 0.032056 | 0.2705 | 0.24013 | 0.032056 | 0.2705 | 0.24013 | 0.37015 | 3.1235 | 2.7727 | 0.37015 | 3.1235 | 2.7727 | 0.36819 | 2.5137 | -0.19971 | -0.36717 | -2.4407 | 0.25728 | -0.055465 | 0.68473 | 1.8438 | 0.056071 | -0.64156 | -1.8097 | 9.6817 | -152.8004 | 29.5025 | -170.3183 | 27.1996 | -150.4975 | 1.0059 | 0.83411 | 0.66885 | 1.0034 | 0.80795 | 0.65925 | 1.115 | -137.563 | 125.6845 | 0.99898 | -138.0728 | 127.5936
Line_2 | 0.032056 | 0.2705 | 0.24013 | 0.032056 | 0.2705 | 0.24013 | 0.37015 | 3.1235 | 2.7727 | 0.37015 | 3.1235 | 2.7727 | 0.36819 | 2.5137 | -0.19971 | -0.36717 | -2.4407 | 0.25728 | -0.055465 | 0.68473 | 1.8438 | 0.056071 | -0.64156 | -1.8097 | 9.6817 | -152.8004 | 29.5025 | -170.3183 | 27.1996 | -150.4975 | 1.0059 | 0.83411 | 0.66885 | 1.0034 | 0.80795 | 0.65925 | 1.115 | -137.563 | 125.6845 | 0.99898 | -138.0728 | 127.5936

## LL_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.064112 | 1.2299 | 1.2869 | 0.064112 | 1.2299 | 1.2869 | 0.7403 | 14.2014 | 14.8599 | 0.7403 | 14.2014 | 14.8599 | -0.73023 | 12.9507 | 1.4179 | 0.73434 | -11.4405 | 0.23553 | 0.11457 | 1.7681 | 10.7707 | -0.11214 | -0.87564 | -9.7936 | -170.3183 | -142.4496 | 36.216 | 9.6817 | 37.5504 | -143.784 | 0.99846 | 0.92039 | 0.73107 | 1.0034 | 0.80795 | 0.65925 | 0.76513 | -134.6755 | 118.7162 | 0.99898 | -138.0728 | 127.5936
Line_1 | 0.032056 | 0.2705 | 0.24013 | 0.032056 | 0.2705 | 0.24013 | 0.37015 | 3.1235 | 2.7727 | 0.37015 | 3.1235 | 2.7727 | 0.36819 | 2.5137 | -0.19971 | -0.36717 | -2.4407 | 0.25728 | -0.055465 | 0.68473 | 1.8438 | 0.056071 | -0.64156 | -1.8097 | 9.6817 | -152.8004 | 29.5025 | -170.3183 | 27.1996 | -150.4975 | 1.0059 | 0.83411 | 0.66885 | 1.0034 | 0.80795 | 0.65925 | 1.115 | -137.563 | 125.6845 | 0.99898 | -138.0728 | 127.5936
Line_2 | 0.032056 | 0.2705 | 0.24013 | 0.032056 | 0.2705 | 0.24013 | 0.37015 | 3.1235 | 2.7727 | 0.37015 | 3.1235 | 2.7727 | 0.36819 | 2.5137 | -0.19971 | -0.36717 | -2.4407 | 0.25728 | -0.055465 | 0.68473 | 1.8438 | 0.056071 | -0.64156 | -1.8097 | 9.6817 | -152.8004 | 29.5025 | -170.3183 | 27.1996 | -150.4975 | 1.0059 | 0.83411 | 0.66885 | 1.0034 | 0.80795 | 0.65925 | 1.115 | -137.563 | 125.6845 | 0.99898 | -138.0728 | 127.5936

## LG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.7801 | 0.96365 | 0.87942 | 1.7772 | 0.96682 | 0.88199 | 20.5552 | 11.1272 | 10.1547 | 20.5208 | 11.1639 | 10.1843 | 1.6365 | -9.5123 | 15.003 | 8.6735e-11 | 10.0383 | -14.6327 | 1.8695 | 11.6734 | 2.8589 | -6.8742e-11 | -11.1568 | -2.4428 | -72.6124 | 93.0587 | 123.1226 | 107.4246 | -86.9635 | -57.0018 |  | 0.12087 | 1.3533 | 1.504 | 0 | 1.3443 | 1.4567 | -23.8099 | -137.766 | 133.9111 | 0 | -134.984 | 132.4759
Line_1 | 1.1529 | 0.48625 | 0.44351 | 1.1501 | 0.48341 | 0.44099 | 13.3122 | 5.6148 | 5.1212 | 13.2798 | 5.5819 | 5.0921 | 3.1774 | 6.1306 | -6.2556 | 5.7781e-11 | -5.0192 | 7.3164 | 1.5141 | -4.9508 | -1.156 | -4.2318e-11 | 5.5784 | 1.2214 | -74.78 | -86.9511 | -57.1735 | 105.2448 | 93.0365 | 122.9982 |  | 0.26439 | 1.4034 | 1.2422 | 0 | 1.3443 | 1.4567 | -49.3013 | -125.8737 | 133.2967 | 0 | -134.984 | 132.4759
Line_2 | 1.1529 | 0.48625 | 0.44351 | 1.1501 | 0.48341 | 0.44099 | 13.3122 | 5.6148 | 5.1212 | 13.2798 | 5.5819 | 5.0921 | 3.1774 | 6.1306 | -6.2556 | 5.7781e-11 | -5.0192 | 7.3164 | 1.5141 | -4.9508 | -1.156 | -4.2318e-11 | 5.5784 | 1.2214 | -74.78 | -86.9511 | -57.1735 | 105.2448 | 93.0365 | 122.9982 |  | 0.26439 | 1.4034 | 1.2422 | 0 | 1.3443 | 1.4567 | -49.3013 | -125.8737 | 133.2967 | 0 | -134.984 | 132.4759

## LG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.7801 | 0.96365 | 0.87942 | 1.7772 | 0.96682 | 0.88199 | 20.5552 | 11.1272 | 10.1547 | 20.5208 | 11.1639 | 10.1843 | 1.6365 | -9.5123 | 15.003 | 8.6735e-11 | 10.0383 | -14.6327 | 1.8695 | 11.6734 | 2.8589 | -6.8742e-11 | -11.1568 | -2.4428 | -72.6124 | 93.0587 | 123.1226 | 107.4246 | -86.9635 | -57.0018 |  | 0.12087 | 1.3533 | 1.504 | 0 | 1.3443 | 1.4567 | -23.8099 | -137.766 | 133.9111 | 0 | -134.984 | 132.4759
Line_1 | 1.1529 | 0.48625 | 0.44351 | 1.1501 | 0.48341 | 0.44099 | 13.3122 | 5.6148 | 5.1212 | 13.2798 | 5.5819 | 5.0921 | 3.1774 | 6.1306 | -6.2556 | 5.7781e-11 | -5.0192 | 7.3164 | 1.5141 | -4.9508 | -1.156 | -4.2318e-11 | 5.5784 | 1.2214 | -74.78 | -86.9511 | -57.1735 | 105.2448 | 93.0365 | 122.9982 |  | 0.26439 | 1.4034 | 1.2422 | 0 | 1.3443 | 1.4567 | -49.3013 | -125.8737 | 133.2967 | 0 | -134.984 | 132.4759
Line_2 | 1.1529 | 0.48625 | 0.44351 | 1.1501 | 0.48341 | 0.44099 | 13.3122 | 5.6148 | 5.1212 | 13.2798 | 5.5819 | 5.0921 | 3.1774 | 6.1306 | -6.2556 | 5.7781e-11 | -5.0192 | 7.3164 | 1.5141 | -4.9508 | -1.156 | -4.2318e-11 | 5.5784 | 1.2214 | -74.78 | -86.9511 | -57.1735 | 105.2448 | 93.0365 | 122.9982 |  | 0.26439 | 1.4034 | 1.2422 | 0 | 1.3443 | 1.4567 | -49.3013 | -125.8737 | 133.2967 | 0 | -134.984 | 132.4759

## LG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.45047 | 0.2154 | 0.37985 | 0.4496 | 0.21635 | 0.38035 | 5.2016 | 2.4872 | 4.3861 | 5.1915 | 2.4982 | 4.3919 | 3.7148 | -2.7535 | 4.0411 | -3.606 | 2.7875 | -3.9793 | 2.344 | 1.4009 | -3.4685 | -2.2152 | -1.3848 | 3.5481 | -40.6876 | 82.0806 | 167.7903 | 139.3853 | -97.8069 | -12.3482 |  | 0.84446 | 1.2421 | 1.2142 | 0.81519 | 1.2459 | 1.2139 | -8.4366 | -124.8855 | 127.151 | -9.0527 | -124.2242 | 125.9299
Line_1 | 0.45093 | 0.10896 | 0.19074 | 0.45 | 0.10818 | 0.19017 | 5.2069 | 1.2581 | 2.2024 | 5.1962 | 1.2491 | 2.1959 | 3.0446 | 1.4481 | -1.8578 | -2.6273 | -1.3938 | 1.9896 | 3.5742 | -0.6284 | 1.7315 | -3.3227 | 0.69239 | -1.7741 | -60.7283 | -97.5428 | -12.5704 | 119.2807 | 82.1931 | 167.6518 |  | 0.90173 | 1.2547 | 1.1531 | 0.81519 | 1.2459 | 1.2139 | -11.1533 | -121.0009 | 124.4453 | -9.0527 | -124.2242 | 125.9299
Line_2 | 0.45093 | 0.10896 | 0.19074 | 0.45 | 0.10818 | 0.19017 | 5.2069 | 1.2581 | 2.2024 | 5.1962 | 1.2491 | 2.1959 | 3.0446 | 1.4481 | -1.8578 | -2.6273 | -1.3938 | 1.9896 | 3.5742 | -0.6284 | 1.7315 | -3.3227 | 0.69239 | -1.7741 | -60.7283 | -97.5428 | -12.5704 | 119.2807 | 82.1931 | 167.6518 |  | 0.90173 | 1.2547 | 1.1531 | 0.81519 | 1.2459 | 1.2139 | -11.1533 | -121.0009 | 124.4453 | -9.0527 | -124.2242 | 125.9299

## LG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.45047 | 0.2154 | 0.37985 | 0.4496 | 0.21635 | 0.38035 | 5.2016 | 2.4872 | 4.3861 | 5.1915 | 2.4982 | 4.3919 | 3.7148 | -2.7535 | 4.0411 | -3.606 | 2.7875 | -3.9793 | 2.344 | 1.4009 | -3.4685 | -2.2152 | -1.3848 | 3.5481 | -40.6876 | 82.0806 | 167.7903 | 139.3853 | -97.8069 | -12.3482 |  | 0.84446 | 1.2421 | 1.2142 | 0.81519 | 1.2459 | 1.2139 | -8.4366 | -124.8855 | 127.151 | -9.0527 | -124.2242 | 125.9299
Line_1 | 0.45093 | 0.10896 | 0.19074 | 0.45 | 0.10818 | 0.19017 | 5.2069 | 1.2581 | 2.2024 | 5.1962 | 1.2491 | 2.1959 | 3.0446 | 1.4481 | -1.8578 | -2.6273 | -1.3938 | 1.9896 | 3.5742 | -0.6284 | 1.7315 | -3.3227 | 0.69239 | -1.7741 | -60.7283 | -97.5428 | -12.5704 | 119.2807 | 82.1931 | 167.6518 |  | 0.90173 | 1.2547 | 1.1531 | 0.81519 | 1.2459 | 1.2139 | -11.1533 | -121.0009 | 124.4453 | -9.0527 | -124.2242 | 125.9299
Line_2 | 0.45093 | 0.10896 | 0.19074 | 0.45 | 0.10818 | 0.19017 | 5.2069 | 1.2581 | 2.2024 | 5.1962 | 1.2491 | 2.1959 | 3.0446 | 1.4481 | -1.8578 | -2.6273 | -1.3938 | 1.9896 | 3.5742 | -0.6284 | 1.7315 | -3.3227 | 0.69239 | -1.7741 | -60.7283 | -97.5428 | -12.5704 | 119.2807 | 82.1931 | 167.6518 |  | 0.90173 | 1.2547 | 1.1531 | 0.81519 | 1.2459 | 1.2139 | -11.1533 | -121.0009 | 124.4453 | -9.0527 | -124.2242 | 125.9299

## LG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.5872 | 0.84802 | 0.74018 | 1.585 | 0.85027 | 0.7423 | 18.3277 | 9.7921 | 8.5469 | 18.3025 | 9.8181 | 8.5714 | 2.5008 | -1.6555 | 11.7281 | -4.3137e-11 | 2.4095 | -11.2026 | 1.494 | 11.1241 | 1.8446 | 1.691e-12 | -10.7271 | -1.558 | -58.8513 | 119.2761 | 123.2943 | 121.214 | -60.8406 | -56.8512 |  | 0.15895 | 1.1485 | 1.3891 | 0 | 1.1198 | 1.3196 | -27.9971 | -142.2593 | 132.2328 | 0 | -138.1812 | 131.0665
Line_1 | 0.88064 | 0.42722 | 0.37317 | 0.87851 | 0.42513 | 0.37115 | 10.1687 | 4.9331 | 4.309 | 10.1442 | 4.909 | 4.2857 | 3.7547 | 2.8607 | -4.2094 | -2.3903e-11 | -1.2047 | 5.6013 | 1.0032 | -5.0837 | -0.63328 | -1.0801e-12 | 5.3635 | 0.77901 | -63.6683 | -60.9578 | -57.0073 | 116.382 | 119.1594 | 123.1488 |  | 0.38219 | 1.1825 | 0.98786 | 0 | 1.1198 | 1.3196 | -48.7095 | -121.5906 | 131.5485 | 0 | -138.1812 | 131.0665
Line_2 | 0.88064 | 0.42722 | 0.37317 | 0.87851 | 0.42513 | 0.37115 | 10.1687 | 4.9331 | 4.309 | 10.1442 | 4.909 | 4.2857 | 3.7547 | 2.8607 | -4.2094 | -2.3903e-11 | -1.2047 | 5.6013 | 1.0032 | -5.0837 | -0.63328 | -1.0801e-12 | 5.3635 | 0.77901 | -63.6683 | -60.9578 | -57.0073 | 116.382 | 119.1594 | 123.1488 |  | 0.38219 | 1.1825 | 0.98786 | 0 | 1.1198 | 1.3196 | -48.7095 | -121.5906 | 131.5485 | 0 | -138.1812 | 131.0665

## LG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.5872 | 0.84802 | 0.74018 | 1.585 | 0.85027 | 0.7423 | 18.3277 | 9.7921 | 8.5469 | 18.3025 | 9.8181 | 8.5714 | 2.5008 | -1.6555 | 11.7281 | -4.3137e-11 | 2.4095 | -11.2026 | 1.494 | 11.1241 | 1.8446 | 1.691e-12 | -10.7271 | -1.558 | -58.8513 | 119.2761 | 123.2943 | 121.214 | -60.8406 | -56.8512 |  | 0.15895 | 1.1485 | 1.3891 | 0 | 1.1198 | 1.3196 | -27.9971 | -142.2593 | 132.2328 | 0 | -138.1812 | 131.0665
Line_1 | 0.88064 | 0.42722 | 0.37317 | 0.87851 | 0.42513 | 0.37115 | 10.1687 | 4.9331 | 4.309 | 10.1442 | 4.909 | 4.2857 | 3.7547 | 2.8607 | -4.2094 | -2.3903e-11 | -1.2047 | 5.6013 | 1.0032 | -5.0837 | -0.63328 | -1.0801e-12 | 5.3635 | 0.77901 | -63.6683 | -60.9578 | -57.0073 | 116.382 | 119.1594 | 123.1488 |  | 0.38219 | 1.1825 | 0.98786 | 0 | 1.1198 | 1.3196 | -48.7095 | -121.5906 | 131.5485 | 0 | -138.1812 | 131.0665
Line_2 | 0.88064 | 0.42722 | 0.37317 | 0.87851 | 0.42513 | 0.37115 | 10.1687 | 4.9331 | 4.309 | 10.1442 | 4.909 | 4.2857 | 3.7547 | 2.8607 | -4.2094 | -2.3903e-11 | -1.2047 | 5.6013 | 1.0032 | -5.0837 | -0.63328 | -1.0801e-12 | 5.3635 | 0.77901 | -63.6683 | -60.9578 | -57.0073 | 116.382 | 119.1594 | 123.1488 |  | 0.38219 | 1.1825 | 0.98786 | 0 | 1.1198 | 1.3196 | -48.7095 | -121.5906 | 131.5485 | 0 | -138.1812 | 131.0665

## LG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.526 | 0.28103 | 0.24529 | 0.52527 | 0.28177 | 0.24599 | 6.0737 | 3.245 | 2.8324 | 6.0653 | 3.2536 | 2.8405 | 3.3078 | -0.72856 | 3.0958 | -3.0322 | 0.81716 | -3.0449 | 2.9459 | 3.3515 | -0.4419 | -2.7745 | -3.3124 | 0.47062 | -47.8701 | 130.2572 | 134.2755 | 132.1951 | -49.8595 | -45.87 |  | 0.72928 | 1.0569 | 1.1041 | 0.67762 | 1.0486 | 1.0847 | -6.1824 | -127.4785 | 126.1519 | -5.3453 | -126.0016 | 125.344
Line_1 | 0.29184 | 0.14158 | 0.12367 | 0.29113 | 0.14089 | 0.123 | 3.3698 | 1.6348 | 1.428 | 3.3617 | 1.6268 | 1.4202 | 1.9597 | 0.59399 | -1.3754 | -1.5451 | -0.40858 | 1.5225 | 1.7895 | -1.6301 | 0.25057 | -1.6739 | 1.6562 | -0.23531 | -52.6871 | -49.9767 | -46.0261 | 127.3631 | 130.1405 | 134.13 |  | 0.78751 | 1.0613 | 0.97905 | 0.67762 | 1.0486 | 1.0847 | -10.2867 | -119.9561 | 123.649 | -5.3453 | -126.0016 | 125.344
Line_2 | 0.29184 | 0.14158 | 0.12367 | 0.29113 | 0.14089 | 0.123 | 3.3698 | 1.6348 | 1.428 | 3.3617 | 1.6268 | 1.4202 | 1.9597 | 0.59399 | -1.3754 | -1.5451 | -0.40858 | 1.5225 | 1.7895 | -1.6301 | 0.25057 | -1.6739 | 1.6562 | -0.23531 | -52.6871 | -49.9767 | -46.0261 | 127.3631 | 130.1405 | 134.13 |  | 0.78751 | 1.0613 | 0.97905 | 0.67762 | 1.0486 | 1.0847 | -10.2867 | -119.9561 | 123.649 | -5.3453 | -126.0016 | 125.344

## LG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.526 | 0.28103 | 0.24529 | 0.52527 | 0.28177 | 0.24599 | 6.0737 | 3.245 | 2.8324 | 6.0653 | 3.2536 | 2.8405 | 3.3078 | -0.72856 | 3.0958 | -3.0322 | 0.81716 | -3.0449 | 2.9459 | 3.3515 | -0.4419 | -2.7745 | -3.3124 | 0.47062 | -47.8701 | 130.2572 | 134.2755 | 132.1951 | -49.8595 | -45.87 |  | 0.72928 | 1.0569 | 1.1041 | 0.67762 | 1.0486 | 1.0847 | -6.1824 | -127.4785 | 126.1519 | -5.3453 | -126.0016 | 125.344
Line_1 | 0.29184 | 0.14158 | 0.12367 | 0.29113 | 0.14089 | 0.123 | 3.3698 | 1.6348 | 1.428 | 3.3617 | 1.6268 | 1.4202 | 1.9597 | 0.59399 | -1.3754 | -1.5451 | -0.40858 | 1.5225 | 1.7895 | -1.6301 | 0.25057 | -1.6739 | 1.6562 | -0.23531 | -52.6871 | -49.9767 | -46.0261 | 127.3631 | 130.1405 | 134.13 |  | 0.78751 | 1.0613 | 0.97905 | 0.67762 | 1.0486 | 1.0847 | -10.2867 | -119.9561 | 123.649 | -5.3453 | -126.0016 | 125.344
Line_2 | 0.29184 | 0.14158 | 0.12367 | 0.29113 | 0.14089 | 0.123 | 3.3698 | 1.6348 | 1.428 | 3.3617 | 1.6268 | 1.4202 | 1.9597 | 0.59399 | -1.3754 | -1.5451 | -0.40858 | 1.5225 | 1.7895 | -1.6301 | 0.25057 | -1.6739 | 1.6562 | -0.23531 | -52.6871 | -49.9767 | -46.0261 | 127.3631 | 130.1405 | 134.13 |  | 0.78751 | 1.0613 | 0.97905 | 0.67762 | 1.0486 | 1.0847 | -10.2867 | -119.9561 | 123.649 | -5.3453 | -126.0016 | 125.344

## LLG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.44819 | 3.6937 | 3.738 | 0.45062 | 3.6941 | 3.7373 | 5.1753 | 42.6516 | 43.1624 | 5.2033 | 42.6556 | 43.1551 | 0.89084 | 7.0905 | 7.2678 | -0.78427 | 8.5667e-11 | 1.1372e-10 | 7.7293 | 8.0672 | 8.2257 | -7.6519 | -7.8108e-11 | 1.9879e-11 | -83.4543 | -171.241 | 15.6403 | 96.5138 | 8.7964 | -164.3958 |  | 1.5034 | 0.25182 | 0.25431 | 1.4783 | 0 | 0 | -0.028874 | -122.5543 | 64.1784 | 0.66172 | 0 | 0
Line_1 | 0.22748 | 1.1282 | 0.92875 | 0.22531 | 1.127 | 0.92716 | 2.6267 | 13.0276 | 10.7243 | 2.6017 | 13.0137 | 10.7059 | -0.030977 | 2.3395 | 1.0163 | 0.39213 | 3.4893e-11 | 2.4504e-11 | -3.6408 | -0.21197 | 1.9966 | 3.8259 | -5.7812e-12 | -1.4827e-11 | 96.542 | 155.7549 | 56.7882 | -83.4862 | -24.1533 | -123.3027 |  | 1.3861 | 0.18031 | 0.20891 | 1.4783 | 0 | 0 | 6.0545 | 150.5776 | 119.8102 | 0.66172 | 0 | 0
Line_2 | 0.22748 | 1.1282 | 0.92875 | 0.22531 | 1.127 | 0.92716 | 2.6267 | 13.0276 | 10.7243 | 2.6017 | 13.0137 | 10.7059 | -0.030977 | 2.3395 | 1.0163 | 0.39213 | 3.4893e-11 | 2.4504e-11 | -3.6408 | -0.21197 | 1.9966 | 3.8259 | -5.7812e-12 | -1.4827e-11 | 96.542 | 155.7549 | 56.7882 | -83.4862 | -24.1533 | -123.3027 |  | 1.3861 | 0.18031 | 0.20891 | 1.4783 | 0 | 0 | 6.0545 | 150.5776 | 119.8102 | 0.66172 | 0 | 0

## LLG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.44819 | 3.6937 | 3.738 | 0.45062 | 3.6941 | 3.7373 | 5.1753 | 42.6516 | 43.1624 | 5.2033 | 42.6556 | 43.1551 | 0.89084 | 7.0905 | 7.2678 | -0.78427 | 8.5667e-11 | 1.1372e-10 | 7.7293 | 8.0672 | 8.2257 | -7.6519 | -7.8108e-11 | 1.9879e-11 | -83.4543 | -171.241 | 15.6403 | 96.5138 | 8.7964 | -164.3958 |  | 1.5034 | 0.25182 | 0.25431 | 1.4783 | 0 | 0 | -0.028874 | -122.5543 | 64.1784 | 0.66172 | 0 | 0
Line_1 | 0.22748 | 1.1282 | 0.92875 | 0.22531 | 1.127 | 0.92716 | 2.6267 | 13.0276 | 10.7243 | 2.6017 | 13.0137 | 10.7059 | -0.030977 | 2.3395 | 1.0163 | 0.39213 | 3.4893e-11 | 2.4504e-11 | -3.6408 | -0.21197 | 1.9966 | 3.8259 | -5.7812e-12 | -1.4827e-11 | 96.542 | 155.7549 | 56.7882 | -83.4862 | -24.1533 | -123.3027 |  | 1.3861 | 0.18031 | 0.20891 | 1.4783 | 0 | 0 | 6.0545 | 150.5776 | 119.8102 | 0.66172 | 0 | 0
Line_2 | 0.22748 | 1.1282 | 0.92875 | 0.22531 | 1.127 | 0.92716 | 2.6267 | 13.0276 | 10.7243 | 2.6017 | 13.0137 | 10.7059 | -0.030977 | 2.3395 | 1.0163 | 0.39213 | 3.4893e-11 | 2.4504e-11 | -3.6408 | -0.21197 | 1.9966 | 3.8259 | -5.7812e-12 | -1.4827e-11 | 96.542 | 155.7549 | 56.7882 | -83.4862 | -24.1533 | -123.3027 |  | 1.3861 | 0.18031 | 0.20891 | 1.4783 | 0 | 0 | 6.0545 | 150.5776 | 119.8102 | 0.66172 | 0 | 0

## LLG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.082481 | 0.79686 | 0.74836 | 0.08289 | 0.79727 | 0.74788 | 0.95241 | 9.2013 | 8.6413 | 0.95714 | 9.2061 | 8.6357 | 1.1952 | 7.9671 | 4.0696 | -1.1949 | -7.643 | -3.769 | 0.24177 | 2.4869 | 6.9657 | -0.25132 | -2.1037 | -6.6364 | -9.8716 | -138.3193 | 46.6326 | 169.5402 | 41.7416 | -133.4293 |  | 1.2803 | 0.90707 | 0.93358 | 1.2758 | 0.86109 | 0.88377 | 1.5643 | -120.9839 | 106.3373 | 1.4177 | -122.8689 | 106.977
Line_1 | 0.04193 | 0.40785 | 0.37518 | 0.041445 | 0.40729 | 0.37451 | 0.48417 | 4.7094 | 4.3322 | 0.47857 | 4.703 | 4.3245 | -0.5768 | 1.4536 | 3.5154 | 0.59746 | -1.1216 | -3.3225 | -0.14893 | 3.894 | 2.1929 | 0.12566 | -3.8913 | -1.8888 | 168.6001 | 163.1219 | 77.4365 | -10.4598 | -16.7895 | -102.6407 |  | 1.2304 | 0.88259 | 0.95639 | 1.2758 | 0.86109 | 0.88377 | 3.0776 | -127.3478 | 109.3923 | 1.4177 | -122.8689 | 106.977
Line_2 | 0.04193 | 0.40785 | 0.37518 | 0.041445 | 0.40729 | 0.37451 | 0.48417 | 4.7094 | 4.3322 | 0.47857 | 4.703 | 4.3245 | -0.5768 | 1.4536 | 3.5154 | 0.59746 | -1.1216 | -3.3225 | -0.14893 | 3.894 | 2.1929 | 0.12566 | -3.8913 | -1.8888 | 168.6001 | 163.1219 | 77.4365 | -10.4598 | -16.7895 | -102.6407 |  | 1.2304 | 0.88259 | 0.95639 | 1.2758 | 0.86109 | 0.88377 | 3.0776 | -127.3478 | 109.3923 | 1.4177 | -122.8689 | 106.977

## LLG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.082481 | 0.79686 | 0.74836 | 0.08289 | 0.79727 | 0.74788 | 0.95241 | 9.2013 | 8.6413 | 0.95714 | 9.2061 | 8.6357 | 1.1952 | 7.9671 | 4.0696 | -1.1949 | -7.643 | -3.769 | 0.24177 | 2.4869 | 6.9657 | -0.25132 | -2.1037 | -6.6364 | -9.8716 | -138.3193 | 46.6326 | 169.5402 | 41.7416 | -133.4293 |  | 1.2803 | 0.90707 | 0.93358 | 1.2758 | 0.86109 | 0.88377 | 1.5643 | -120.9839 | 106.3373 | 1.4177 | -122.8689 | 106.977
Line_1 | 0.04193 | 0.40785 | 0.37518 | 0.041445 | 0.40729 | 0.37451 | 0.48417 | 4.7094 | 4.3322 | 0.47857 | 4.703 | 4.3245 | -0.5768 | 1.4536 | 3.5154 | 0.59746 | -1.1216 | -3.3225 | -0.14893 | 3.894 | 2.1929 | 0.12566 | -3.8913 | -1.8888 | 168.6001 | 163.1219 | 77.4365 | -10.4598 | -16.7895 | -102.6407 |  | 1.2304 | 0.88259 | 0.95639 | 1.2758 | 0.86109 | 0.88377 | 3.0776 | -127.3478 | 109.3923 | 1.4177 | -122.8689 | 106.977
Line_2 | 0.04193 | 0.40785 | 0.37518 | 0.041445 | 0.40729 | 0.37451 | 0.48417 | 4.7094 | 4.3322 | 0.47857 | 4.703 | 4.3245 | -0.5768 | 1.4536 | 3.5154 | 0.59746 | -1.1216 | -3.3225 | -0.14893 | 3.894 | 2.1929 | 0.12566 | -3.8913 | -1.8888 | 168.6001 | 163.1219 | 77.4365 | -10.4598 | -16.7895 | -102.6407 |  | 1.2304 | 0.88259 | 0.95639 | 1.2758 | 0.86109 | 0.88377 | 3.0776 | -127.3478 | 109.3923 | 1.4177 | -122.8689 | 106.977

## LLG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.49742 | 3.1515 | 3.1063 | 0.49934 | 3.1521 | 3.1054 | 5.7438 | 36.3903 | 35.8687 | 5.7658 | 36.3974 | 35.8579 | 3.5539 | 9.9181 | 9.6279 | -3.3032 | -1.078e-10 | -7.5722e-12 | 6.802 | 5.8841 | 5.6697 | -6.6889 | -7.925e-11 | -1.3289e-10 | -64.4453 | -164.1799 | 24.9009 | 115.4456 | 15.8573 | -155.1345 |  | 1.3361 | 0.3169 | 0.31151 | 1.2938 | 0 | 0 | -2.0317 | -133.5006 | 55.3941 | -0.83581 | 0 | 0
Line_1 | 0.25134 | 0.96792 | 0.61975 | 0.24967 | 0.9671 | 0.61851 | 2.9022 | 11.1766 | 7.1563 | 2.8829 | 11.1671 | 7.1419 | -0.97899 | 3.091 | 0.84985 | 1.6516 | -1.5869e-11 | -1.6811e-11 | -3.122 | -0.72523 | 1.7619 | 3.3444 | -3.7859e-11 | -2.0498e-11 | 115.3679 | 164.8326 | 61.0673 | -64.5544 | -15.0793 | -119.0399 |  | 1.1274 | 0.28407 | 0.27335 | 1.2938 | 0 | 0 | 7.9579 | 151.6281 | 125.3169 | -0.83581 | 0 | 0
Line_2 | 0.25134 | 0.96792 | 0.61975 | 0.24967 | 0.9671 | 0.61851 | 2.9022 | 11.1766 | 7.1563 | 2.8829 | 11.1671 | 7.1419 | -0.97899 | 3.091 | 0.84985 | 1.6516 | -1.5869e-11 | -1.6811e-11 | -3.122 | -0.72523 | 1.7619 | 3.3444 | -3.7859e-11 | -2.0498e-11 | 115.3679 | 164.8326 | 61.0673 | -64.5544 | -15.0793 | -119.0399 |  | 1.1274 | 0.28407 | 0.27335 | 1.2938 | 0 | 0 | 7.9579 | 151.6281 | 125.3169 | -0.83581 | 0 | 0

## LLG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.49742 | 3.1515 | 3.1063 | 0.49934 | 3.1521 | 3.1054 | 5.7438 | 36.3903 | 35.8687 | 5.7658 | 36.3974 | 35.8579 | 3.5539 | 9.9181 | 9.6279 | -3.3032 | -1.078e-10 | -7.5722e-12 | 6.802 | 5.8841 | 5.6697 | -6.6889 | -7.925e-11 | -1.3289e-10 | -64.4453 | -164.1799 | 24.9009 | 115.4456 | 15.8573 | -155.1345 |  | 1.3361 | 0.3169 | 0.31151 | 1.2938 | 0 | 0 | -2.0317 | -133.5006 | 55.3941 | -0.83581 | 0 | 0
Line_1 | 0.25134 | 0.96792 | 0.61975 | 0.24967 | 0.9671 | 0.61851 | 2.9022 | 11.1766 | 7.1563 | 2.8829 | 11.1671 | 7.1419 | -0.97899 | 3.091 | 0.84985 | 1.6516 | -1.5869e-11 | -1.6811e-11 | -3.122 | -0.72523 | 1.7619 | 3.3444 | -3.7859e-11 | -2.0498e-11 | 115.3679 | 164.8326 | 61.0673 | -64.5544 | -15.0793 | -119.0399 |  | 1.1274 | 0.28407 | 0.27335 | 1.2938 | 0 | 0 | 7.9579 | 151.6281 | 125.3169 | -0.83581 | 0 | 0
Line_2 | 0.25134 | 0.96792 | 0.61975 | 0.24967 | 0.9671 | 0.61851 | 2.9022 | 11.1766 | 7.1563 | 2.8829 | 11.1671 | 7.1419 | -0.97899 | 3.091 | 0.84985 | 1.6516 | -1.5869e-11 | -1.6811e-11 | -3.122 | -0.72523 | 1.7619 | 3.3444 | -3.7859e-11 | -2.0498e-11 | 115.3679 | 164.8326 | 61.0673 | -64.5544 | -15.0793 | -119.0399 |  | 1.1274 | 0.28407 | 0.27335 | 1.2938 | 0 | 0 | 7.9579 | 151.6281 | 125.3169 | -0.83581 | 0 | 0

## LLG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.21774 | 0.7709 | 0.7931 | 0.21846 | 0.7713 | 0.79251 | 2.5142 | 8.9016 | 9.1579 | 2.5226 | 8.9062 | 9.1511 | 1.6379 | 6.4928 | 3.9235 | -1.5908 | -5.9048 | -3.2901 | 2.3227 | 3.3994 | 6.0899 | -2.3056 | -3.0424 | -5.7191 | -55.4071 | -147.5741 | 48.349 | 124.4815 | 32.4808 | -131.6945 |  | 1.1304 | 0.82332 | 0.79106 | 1.1104 | 0.74583 | 0.721 | -0.59841 | -119.9393 | 105.5568 | -0.12235 | -120.2595 | 108.3949
Line_1 | 0.10988 | 0.26905 | 0.23111 | 0.10923 | 0.26871 | 0.23047 | 1.2687 | 3.1067 | 2.6686 | 1.2613 | 3.1028 | 2.6613 | -0.67809 | 1.0629 | 2.0331 | 0.79539 | -0.75602 | -1.8206 | -1.1251 | 2.0997 | 0.8155 | 1.1528 | -2.1872 | -0.60603 | 124.3882 | 168.6855 | 90.0374 | -55.5185 | -11.1914 | -90.0165 |  | 1.0354 | 0.75753 | 0.82086 | 1.1104 | 0.74583 | 0.721 | 3.3122 | -128.1642 | 111.8939 | -0.12235 | -120.2595 | 108.3949
Line_2 | 0.10988 | 0.26905 | 0.23111 | 0.10923 | 0.26871 | 0.23047 | 1.2687 | 3.1067 | 2.6686 | 1.2613 | 3.1028 | 2.6613 | -0.67809 | 1.0629 | 2.0331 | 0.79539 | -0.75602 | -1.8206 | -1.1251 | 2.0997 | 0.8155 | 1.1528 | -2.1872 | -0.60603 | 124.3882 | 168.6855 | 90.0374 | -55.5185 | -11.1914 | -90.0165 |  | 1.0354 | 0.75753 | 0.82086 | 1.1104 | 0.74583 | 0.721 | 3.3122 | -128.1642 | 111.8939 | -0.12235 | -120.2595 | 108.3949

## LLG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.21774 | 0.7709 | 0.7931 | 0.21846 | 0.7713 | 0.79251 | 2.5142 | 8.9016 | 9.1579 | 2.5226 | 8.9062 | 9.1511 | 1.6379 | 6.4928 | 3.9235 | -1.5908 | -5.9048 | -3.2901 | 2.3227 | 3.3994 | 6.0899 | -2.3056 | -3.0424 | -5.7191 | -55.4071 | -147.5741 | 48.349 | 124.4815 | 32.4808 | -131.6945 |  | 1.1304 | 0.82332 | 0.79106 | 1.1104 | 0.74583 | 0.721 | -0.59841 | -119.9393 | 105.5568 | -0.12235 | -120.2595 | 108.3949
Line_1 | 0.10988 | 0.26905 | 0.23111 | 0.10923 | 0.26871 | 0.23047 | 1.2687 | 3.1067 | 2.6686 | 1.2613 | 3.1028 | 2.6613 | -0.67809 | 1.0629 | 2.0331 | 0.79539 | -0.75602 | -1.8206 | -1.1251 | 2.0997 | 0.8155 | 1.1528 | -2.1872 | -0.60603 | 124.3882 | 168.6855 | 90.0374 | -55.5185 | -11.1914 | -90.0165 |  | 1.0354 | 0.75753 | 0.82086 | 1.1104 | 0.74583 | 0.721 | 3.3122 | -128.1642 | 111.8939 | -0.12235 | -120.2595 | 108.3949
Line_2 | 0.10988 | 0.26905 | 0.23111 | 0.10923 | 0.26871 | 0.23047 | 1.2687 | 3.1067 | 2.6686 | 1.2613 | 3.1028 | 2.6613 | -0.67809 | 1.0629 | 2.0331 | 0.79539 | -0.75602 | -1.8206 | -1.1251 | 2.0997 | 0.8155 | 1.1528 | -2.1872 | -0.60603 | 124.3882 | 168.6855 | 90.0374 | -55.5185 | -11.1914 | -90.0165 |  | 1.0354 | 0.75753 | 0.82086 | 1.1104 | 0.74583 | 0.721 | 3.3122 | -128.1642 | 111.8939 | -0.12235 | -120.2595 | 108.3949