## LLL_max_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 4.283 | 4.283 | 0 | 9.2778 | 148.3662 | 148.3662 | 28.6163 | -1e-07 | 32.4685 | -1e-07 | -77.7798 | 102.2202 | 0.29171 | 0 | -29.1714 | 0
Line_1 | 0 | 0 | 0 | 5.2796e-10 | 0 | 0 | 0 | 1.6014e-19 | 0 | -1.2512e-19 | 0 | 0 | 0 | 0 | 0 | 0
Line_2 | 0 | 0 | 0 | 5.2797e-10 | 0 | 0 | 0 | 1.6014e-19 | 0 | -1.2512e-19 | 0 | 0 | 0 | 0 | 0 | 0

## LLL_max_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 4.283 | 4.283 | 0 | 9.2778 | 148.3662 | 148.3662 | 28.6163 | -1e-07 | 32.4685 | -1e-07 | -77.7798 | 102.2202 | 0.29171 | 0 | -29.1714 | 0
Line_1 | 0 | 0 | 0 | 5.2796e-10 | 0 | 0 | 0 | 1.6014e-19 | 0 | -1.2512e-19 | 0 | 0 | 0 | 0 | 0 | 0
Line_2 | 0 | 0 | 0 | 5.2797e-10 | 0 | 0 | 0 | 1.6014e-19 | 0 | -1.2512e-19 | 0 | 0 | 0 | 0 | 0 | 0

## LLL_max_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 1.3097 | 1.3097 | 0 | 2.8371 | 45.3689 | 45.3689 | 28.405 | -25.7292 | 28.7652 | -25.7292 | -54.5297 | 125.4703 | 0.89106 | 0.80202 | -9.1687 | -9.5297
Line_1 | 0 | 0 | 0 | 1.6145e-10 | 0 | 0 | 0 | -2.495e-09 | 0 | 1.6066e-09 | 0 | 0 | 0.80202 | 0.80202 | -9.5297 | -9.5297
Line_2 | 0 | 0 | 0 | 1.6145e-10 | 0 | 0 | 0 | -2.495e-09 | 0 | 1.6066e-09 | 0 | 0 | 0.80202 | 0.80202 | -9.5297 | -9.5297

## LLL_max_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 1.3097 | 1.3097 | 0 | 2.8371 | 45.3689 | 45.3689 | 28.405 | -25.7292 | 28.7652 | -25.7292 | -54.5297 | 125.4703 | 0.89106 | 0.80202 | -9.1687 | -9.5297
Line_1 | 0 | 0 | 0 | 1.6145e-10 | 0 | 0 | 0 | -2.495e-09 | 0 | 1.6066e-09 | 0 | 0 | 0.80202 | 0.80202 | -9.5297 | -9.5297
Line_2 | 0 | 0 | 0 | 1.6145e-10 | 0 | 0 | 0 | -2.495e-09 | 0 | 1.6066e-09 | 0 | 0 | 0.80202 | 0.80202 | -9.5297 | -9.5297

## LLL_min_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 3.6016 | 3.6016 | 0 | 6.8381 | 124.7634 | 124.7634 | 38.8525 | -1e-07 | 22.9597 | -1e-07 | -69.6723 | 110.3277 | 0.36172 | 0 | -39.0915 | 0
Line_1 | 0 | 0 | 0 | 4.7997e-10 | 0 | 0 | 0 | 1.7303e-20 | 0 | 6.3209e-20 | 0 | 0 | 0 | 0 | 0 | 0
Line_2 | 0 | 0 | 0 | 4.7997e-10 | 0 | 0 | 0 | 1.7303e-20 | 0 | 6.3209e-20 | 0 | 0 | 0 | 0 | 0 | 0

## LLL_min_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 3.6016 | 3.6016 | 0 | 6.8381 | 124.7634 | 124.7634 | 38.8525 | -1e-07 | 22.9597 | -1e-07 | -69.6723 | 110.3277 | 0.36172 | 0 | -39.0915 | 0
Line_1 | 0 | 0 | 0 | 4.7997e-10 | 0 | 0 | 0 | 1.7303e-20 | 0 | 6.3209e-20 | 0 | 0 | 0 | 0 | 0 | 0
Line_2 | 0 | 0 | 0 | 4.7997e-10 | 0 | 0 | 0 | 1.7303e-20 | 0 | 6.3209e-20 | 0 | 0 | 0 | 0 | 0 | 0

## LLL_min_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 1.1462 | 1.1462 | 0 | 2.1763 | 39.7072 | 39.7072 | 23.6436 | -19.7082 | 22.0338 | -19.7082 | -52.6343 | 127.3657 | 0.81393 | 0.70193 | -9.6527 | -7.6343
Line_1 | 0 | 0 | 0 | 1.5275e-10 | 0 | 0 | 0 | -2.233e-09 | 0 | 1.0258e-09 | 0 | 0 | 0.70193 | 0.70193 | -7.6343 | -7.6343
Line_2 | 0 | 0 | 0 | 1.5275e-10 | 0 | 0 | 0 | -2.233e-09 | 0 | 1.0258e-09 | 0 | 0 | 0.70193 | 0.70193 | -7.6343 | -7.6343

## LLL_min_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 1.1462 | 1.1462 | 0 | 2.1763 | 39.7072 | 39.7072 | 23.6436 | -19.7082 | 22.0338 | -19.7082 | -52.6343 | 127.3657 | 0.81393 | 0.70193 | -9.6527 | -7.6343
Line_1 | 0 | 0 | 0 | 1.5275e-10 | 0 | 0 | 0 | -2.233e-09 | 0 | 1.0258e-09 | 0 | 0 | 0.70193 | 0.70193 | -7.6343 | -7.6343
Line_2 | 0 | 0 | 0 | 1.5275e-10 | 0 | 0 | 0 | -2.233e-09 | 0 | 1.0258e-09 | 0 | 0 | 0.70193 | 0.70193 | -7.6343 | -7.6343

## LL_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 3.7092 | 3.7092 | 0 | 3.7092 | 3.7092 | 0 | 42.8296 | 42.8296 | 0 | 42.8296 | 42.8296 | -5.2106e-15 | 30.1766 | -15.8685 | -1.5632e-14 | -23.0225 | 23.0225 | 1.0421e-14 | 3.131 | 13.1032 | -1.5632e-14 | 4.9861 | -4.9861 | 0 | -167.7798 | 12.2202 | 0 | 12.2202 | -167.7798 | 1.1 | 0.70836 | 0.48049 | 1.1 | 0.55 | 0.55 | 1.1069e-11 | -161.8563 | 152.6723 | 1.1075e-11 | 180 | -180
Line_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.2106e-14 | 1.3027e-14 | 1.0421e-14 | 2.6053e-14 | 2.6053e-15 | -1.0421e-14 | -1.5632e-14 | -1.9211e-09 | 1.9211e-09 | 1.0421e-14 | 1.9211e-09 | -1.9211e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.55 | 0.55 | 1.1 | 0.55 | 0.55 | 1.1084e-11 | -180 | 180 | 1.1075e-11 | 180 | -180
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.2106e-14 | 1.3027e-14 | 1.0421e-14 | 2.6053e-14 | 2.6053e-15 | -1.0421e-14 | -1.5632e-14 | -1.9211e-09 | 1.9211e-09 | 1.0421e-14 | 1.9211e-09 | -1.9211e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.55 | 0.55 | 1.1 | 0.55 | 0.55 | 1.1084e-11 | -180 | 180 | 1.1075e-11 | 180 | -180

## LL_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 3.7092 | 3.7092 | 0 | 3.7092 | 3.7092 | 0 | 42.8296 | 42.8296 | 0 | 42.8296 | 42.8296 | -5.2106e-15 | 30.1766 | -15.8685 | -1.5632e-14 | -23.0225 | 23.0225 | 1.0421e-14 | 3.131 | 13.1032 | -1.5632e-14 | 4.9861 | -4.9861 | 0 | -167.7798 | 12.2202 | 0 | 12.2202 | -167.7798 | 1.1 | 0.70836 | 0.48049 | 1.1 | 0.55 | 0.55 | 1.1069e-11 | -161.8563 | 152.6723 | 1.1075e-11 | 180 | -180
Line_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.2106e-14 | 1.3027e-14 | 1.0421e-14 | 2.6053e-14 | 2.6053e-15 | -1.0421e-14 | -1.5632e-14 | -1.9211e-09 | 1.9211e-09 | 1.0421e-14 | 1.9211e-09 | -1.9211e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.55 | 0.55 | 1.1 | 0.55 | 0.55 | 1.1084e-11 | -180 | 180 | 1.1075e-11 | 180 | -180
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.2106e-14 | 1.3027e-14 | 1.0421e-14 | 2.6053e-14 | 2.6053e-15 | -1.0421e-14 | -1.5632e-14 | -1.9211e-09 | 1.9211e-09 | 1.0421e-14 | 1.9211e-09 | -1.9211e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.55 | 0.55 | 1.1 | 0.55 | 0.55 | 1.1084e-11 | -180 | 180 | 1.1075e-11 | 180 | -180

## LL_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 1.7631 | 1.7631 | 0 | 1.7631 | 1.7631 | 0 | 20.3584 | 20.3584 | 0 | 20.3584 | 20.3584 | 0 | 19.0761 | -0.30087 | -5.2106e-15 | -17.4596 | 1.9173 | 0 | 3.9919 | 15.2185 | -5.2106e-15 | -2.1579 | -13.3845 | 0 | -149.913 | 30.087 | 0 | 30.087 | -149.913 | 1.1 | 0.95731 | 0.74767 | 1.1 | 0.86414 | 0.66415 | 4.9323e-12 | -138.0936 | 121.2196 | 4.9355e-12 | -142.8673 | 128.239
Line_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.2106e-15 | 4.734e-10 | 1.0338e-09 | -8.9769e-28 | -4.734e-10 | -1.0337e-09 | -1.3027e-14 | -1.3544e-09 | 3.8387e-10 | 1.0421e-14 | 1.3544e-09 | -3.8387e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.86414 | 0.66415 | 1.1 | 0.86414 | 0.66415 | 4.9417e-12 | -142.8673 | 128.239 | 4.9355e-12 | -142.8673 | 128.239
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.2106e-15 | 4.734e-10 | 1.0338e-09 | -8.9769e-28 | -4.734e-10 | -1.0337e-09 | -1.3027e-14 | -1.3544e-09 | 3.8387e-10 | 1.0421e-14 | 1.3544e-09 | -3.8387e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.86414 | 0.66415 | 1.1 | 0.86414 | 0.66415 | 4.9417e-12 | -142.8673 | 128.239 | 4.9355e-12 | -142.8673 | 128.239

## LL_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 1.7631 | 1.7631 | 0 | 1.7631 | 1.7631 | 0 | 20.3584 | 20.3584 | 0 | 20.3584 | 20.3584 | 0 | 19.0761 | -0.30087 | -5.2106e-15 | -17.4596 | 1.9173 | 0 | 3.9919 | 15.2185 | -5.2106e-15 | -2.1579 | -13.3845 | 0 | -149.913 | 30.087 | 0 | 30.087 | -149.913 | 1.1 | 0.95731 | 0.74767 | 1.1 | 0.86414 | 0.66415 | 4.9323e-12 | -138.0936 | 121.2196 | 4.9355e-12 | -142.8673 | 128.239
Line_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.2106e-15 | 4.734e-10 | 1.0338e-09 | -8.9769e-28 | -4.734e-10 | -1.0337e-09 | -1.3027e-14 | -1.3544e-09 | 3.8387e-10 | 1.0421e-14 | 1.3544e-09 | -3.8387e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.86414 | 0.66415 | 1.1 | 0.86414 | 0.66415 | 4.9417e-12 | -142.8673 | 128.239 | 4.9355e-12 | -142.8673 | 128.239
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.2106e-15 | 4.734e-10 | 1.0338e-09 | -8.9769e-28 | -4.734e-10 | -1.0337e-09 | -1.3027e-14 | -1.3544e-09 | 3.8387e-10 | 1.0421e-14 | 1.3544e-09 | -3.8387e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.86414 | 0.66415 | 1.1 | 0.86414 | 0.66415 | 4.9417e-12 | -142.8673 | 128.239 | 4.9355e-12 | -142.8673 | 128.239

## LL_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 3.1191 | 3.1191 | 0 | 3.1191 | 3.1191 | 0 | 36.0161 | 36.0161 | 0 | 36.0161 | 36.0161 | -4.737e-15 | 26.5997 | -7.1734 | 2.3685e-15 | -16.8865 | 16.8865 | 9.4739e-15 | -0.51586 | 11.9957 | -1.4211e-14 | 6.2558 | -6.2558 | 0 | -159.6723 | 20.3277 | 0 | 20.3277 | -159.6723 | 1 | 0.73869 | 0.38808 | 1 | 0.5 | 0.5 | 3.6589e-12 | -160.7833 | 141.207 | 3.6896e-12 | -180 | 180
Line_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -9.4739e-15 | 1.1842e-14 | -2.3684e-15 | 9.4739e-15 | -4.737e-15 | 2.3685e-15 | -4.737e-15 | -1.5877e-09 | 1.5877e-09 | 9.4739e-15 | 1.5877e-09 | -1.5877e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 3.7037e-12 | -180 | 180 | 3.6896e-12 | -180 | 180
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -9.4739e-15 | 1.1842e-14 | -2.3684e-15 | 9.4739e-15 | -4.737e-15 | 2.3685e-15 | -4.737e-15 | -1.5877e-09 | 1.5877e-09 | 9.4739e-15 | 1.5877e-09 | -1.5877e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 3.7037e-12 | -180 | 180 | 3.6896e-12 | -180 | 180

## LL_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 3.1191 | 3.1191 | 0 | 3.1191 | 3.1191 | 0 | 36.0161 | 36.0161 | 0 | 36.0161 | 36.0161 | -4.737e-15 | 26.5997 | -7.1734 | 2.3685e-15 | -16.8865 | 16.8865 | 9.4739e-15 | -0.51586 | 11.9957 | -1.4211e-14 | 6.2558 | -6.2558 | 0 | -159.6723 | 20.3277 | 0 | 20.3277 | -159.6723 | 1 | 0.73869 | 0.38808 | 1 | 0.5 | 0.5 | 3.6589e-12 | -160.7833 | 141.207 | 3.6896e-12 | -180 | 180
Line_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -9.4739e-15 | 1.1842e-14 | -2.3684e-15 | 9.4739e-15 | -4.737e-15 | 2.3685e-15 | -4.737e-15 | -1.5877e-09 | 1.5877e-09 | 9.4739e-15 | 1.5877e-09 | -1.5877e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 3.7037e-12 | -180 | 180 | 3.6896e-12 | -180 | 180
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -9.4739e-15 | 1.1842e-14 | -2.3684e-15 | 9.4739e-15 | -4.737e-15 | 2.3685e-15 | -4.737e-15 | -1.5877e-09 | 1.5877e-09 | 9.4739e-15 | 1.5877e-09 | -1.5877e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 3.7037e-12 | -180 | 180 | 3.6896e-12 | -180 | 180

## LL_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 1.5183 | 1.5183 | 0 | 1.5183 | 1.5183 | 0 | 17.5318 | 17.5318 | 0 | 17.5318 | 17.5318 | -5.3291e-15 | 15.3932 | 0.73601 | 3.5527e-15 | -13.0917 | 1.5655 | -1.073e-28 | 2.3135 | 11.9328 | -4.737e-15 | -0.95344 | -10.5727 | 0 | -146.7238 | 33.2762 | 0 | 33.2762 | -146.7238 | 1 | 0.88788 | 0.68193 | 1 | 0.74872 | 0.60963 | 1.1536e-12 | -138.1765 | 119.7467 | 1.1657e-12 | -142.5584 | 131.6989
Line_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.3685e-15 | 4.7979e-10 | 8.2616e-10 | -1.9275e-28 | -4.7979e-10 | -8.2616e-10 | -9.4739e-15 | -1.0532e-09 | 4.5325e-10 | 9.4739e-15 | 1.0532e-09 | -4.5325e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.74872 | 0.60963 | 1 | 0.74872 | 0.60963 | 1.1755e-12 | -142.5584 | 131.6989 | 1.1657e-12 | -142.5584 | 131.6989
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.3685e-15 | 4.7979e-10 | 8.2616e-10 | -1.9275e-28 | -4.7979e-10 | -8.2616e-10 | -9.4739e-15 | -1.0532e-09 | 4.5325e-10 | 9.4739e-15 | 1.0532e-09 | -4.5325e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.74872 | 0.60963 | 1 | 0.74872 | 0.60963 | 1.1755e-12 | -142.5584 | 131.6989 | 1.1657e-12 | -142.5584 | 131.6989

## LL_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 1.5183 | 1.5183 | 0 | 1.5183 | 1.5183 | 0 | 17.5318 | 17.5318 | 0 | 17.5318 | 17.5318 | -5.3291e-15 | 15.3932 | 0.73601 | 3.5527e-15 | -13.0917 | 1.5655 | -1.073e-28 | 2.3135 | 11.9328 | -4.737e-15 | -0.95344 | -10.5727 | 0 | -146.7238 | 33.2762 | 0 | 33.2762 | -146.7238 | 1 | 0.88788 | 0.68193 | 1 | 0.74872 | 0.60963 | 1.1536e-12 | -138.1765 | 119.7467 | 1.1657e-12 | -142.5584 | 131.6989
Line_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.3685e-15 | 4.7979e-10 | 8.2616e-10 | -1.9275e-28 | -4.7979e-10 | -8.2616e-10 | -9.4739e-15 | -1.0532e-09 | 4.5325e-10 | 9.4739e-15 | 1.0532e-09 | -4.5325e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.74872 | 0.60963 | 1 | 0.74872 | 0.60963 | 1.1755e-12 | -142.5584 | 131.6989 | 1.1657e-12 | -142.5584 | 131.6989
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.3685e-15 | 4.7979e-10 | 8.2616e-10 | -1.9275e-28 | -4.7979e-10 | -8.2616e-10 | -9.4739e-15 | -1.0532e-09 | 4.5325e-10 | 9.4739e-15 | 1.0532e-09 | -4.5325e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.74872 | 0.60963 | 1 | 0.74872 | 0.60963 | 1.1755e-12 | -142.5584 | 131.6989 | 1.1657e-12 | -142.5584 | 131.6989

## LG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.03239 | 0.016195 | 0.016195 | 0.026985 | 0.0216 | 0.0216 | 0.37401 | 0.187 | 0.187 | 0.3116 | 0.24942 | 0.24942 | 0.00022107 | -0.17578 | 0.1805 | -1.6755e-14 | 0.23558 | -0.23962 | 0.00049272 | 0.30796 | 0.30501 | 6.714e-14 | -0.41003 | -0.40695 | -89.5254 | 90.4745 | 90.4745 | 90.5564 | -89.6277 | -89.6277 |  | 0.0014439 | 1.8962 | 1.8952 | 0 | 1.896 | 1.8934 | -23.6902 | -149.8083 | 149.8581 | 0 | -149.7489 | 149.8817
Line_1 | 0.0162 | 0.0162 | 0.0162 | 0.0108 | 0.0108 | 0.0108 | 0.18707 | 0.18707 | 0.18707 | 0.12471 | 0.12471 | 0.12471 | 0.00080826 | 0.1778 | -0.17861 | -6.792e-15 | -0.11779 | 0.11981 | 0.00032156 | -0.30703 | -0.30507 | 2.685e-14 | 0.20502 | 0.20347 | -89.6844 | -89.6844 | -89.6844 | 90.3723 | 90.3723 | 90.3723 |  | 0.0046501 | 1.8966 | 1.8897 | 0 | 1.896 | 1.8934 | -67.99 | -149.6099 | 149.9683 | 0 | -149.7489 | 149.8817
Line_2 | 0.0162 | 0.0162 | 0.0162 | 0.0108 | 0.0108 | 0.0108 | 0.18707 | 0.18707 | 0.18707 | 0.12471 | 0.12471 | 0.12471 | 0.00080826 | 0.1778 | -0.17861 | -6.792e-15 | -0.11779 | 0.11981 | 0.00032156 | -0.30703 | -0.30507 | 2.685e-14 | 0.20502 | 0.20347 | -89.6844 | -89.6844 | -89.6844 | 90.3723 | 90.3723 | 90.3723 |  | 0.0046501 | 1.8966 | 1.8897 | 0 | 1.896 | 1.8934 | -67.99 | -149.6099 | 149.9683 | 0 | -149.7489 | 149.8817

## LG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.03239 | 0.016195 | 0.016195 | 0.026985 | 0.0216 | 0.0216 | 0.37401 | 0.187 | 0.187 | 0.3116 | 0.24942 | 0.24942 | 0.00022107 | -0.17578 | 0.1805 | -1.6755e-14 | 0.23558 | -0.23962 | 0.00049272 | 0.30796 | 0.30501 | 6.714e-14 | -0.41003 | -0.40695 | -89.5254 | 90.4745 | 90.4745 | 90.5564 | -89.6277 | -89.6277 |  | 0.0014439 | 1.8962 | 1.8952 | 0 | 1.896 | 1.8934 | -23.6902 | -149.8083 | 149.8581 | 0 | -149.7489 | 149.8817
Line_1 | 0.0162 | 0.0162 | 0.0162 | 0.0108 | 0.0108 | 0.0108 | 0.18707 | 0.18707 | 0.18707 | 0.12471 | 0.12471 | 0.12471 | 0.00080826 | 0.1778 | -0.17861 | -6.792e-15 | -0.11779 | 0.11981 | 0.00032156 | -0.30703 | -0.30507 | 2.685e-14 | 0.20502 | 0.20347 | -89.6844 | -89.6844 | -89.6844 | 90.3723 | 90.3723 | 90.3723 |  | 0.0046501 | 1.8966 | 1.8897 | 0 | 1.896 | 1.8934 | -67.99 | -149.6099 | 149.9683 | 0 | -149.7489 | 149.8817
Line_2 | 0.0162 | 0.0162 | 0.0162 | 0.0108 | 0.0108 | 0.0108 | 0.18707 | 0.18707 | 0.18707 | 0.12471 | 0.12471 | 0.12471 | 0.00080826 | 0.1778 | -0.17861 | -6.792e-15 | -0.11779 | 0.11981 | 0.00032156 | -0.30703 | -0.30507 | 2.685e-14 | 0.20502 | 0.20347 | -89.6844 | -89.6844 | -89.6844 | 90.3723 | 90.3723 | 90.3723 |  | 0.0046501 | 1.8966 | 1.8897 | 0 | 1.896 | 1.8934 | -67.99 | -149.6099 | 149.9683 | 0 | -149.7489 | 149.8817

## LG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.031772 | 0.015886 | 0.015886 | 0.02647 | 0.021188 | 0.021188 | 0.36687 | 0.18344 | 0.18344 | 0.30565 | 0.24466 | 0.24466 | 0.0077836 | -0.17052 | 0.17885 | -0.0063165 | 0.22853 | -0.23746 | 0.008045 | 0.30149 | 0.29209 | -0.0062985 | -0.40142 | -0.38972 | -88.4594 | 91.5405 | 91.5405 | 91.6224 | -88.5617 | -88.5617 |  | 0.030512 | 1.8882 | 1.8671 | 0.029184 | 1.888 | 1.8653 | -42.5134 | -148.9672 | 150.0616 | -43.4594 | -148.9088 | 150.0843
Line_1 | 0.015891 | 0.015891 | 0.015891 | 0.010594 | 0.010594 | 0.010594 | 0.1835 | 0.1835 | 0.1835 | 0.12233 | 0.12233 | 0.12233 | 0.0045539 | 0.17248 | -0.17703 | -0.0025199 | -0.11427 | 0.11873 | 0.0041066 | -0.30059 | -0.29216 | -0.0025289 | 0.20071 | 0.19486 | -88.6184 | -88.6184 | -88.6184 | 91.4383 | 91.4383 | 91.4383 |  | 0.033418 | 1.8886 | 1.8617 | 0.029184 | 1.888 | 1.8653 | -46.575 | -148.7718 | 150.1688 | -43.4594 | -148.9088 | 150.0843
Line_2 | 0.015891 | 0.015891 | 0.015891 | 0.010594 | 0.010594 | 0.010594 | 0.1835 | 0.1835 | 0.1835 | 0.12233 | 0.12233 | 0.12233 | 0.0045539 | 0.17248 | -0.17703 | -0.0025199 | -0.11427 | 0.11873 | 0.0041066 | -0.30059 | -0.29216 | -0.0025289 | 0.20071 | 0.19486 | -88.6184 | -88.6184 | -88.6184 | 91.4383 | 91.4383 | 91.4383 |  | 0.033418 | 1.8886 | 1.8617 | 0.029184 | 1.888 | 1.8653 | -46.575 | -148.7718 | 150.1688 | -43.4594 | -148.9088 | 150.0843

## LG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.031772 | 0.015886 | 0.015886 | 0.02647 | 0.021188 | 0.021188 | 0.36687 | 0.18344 | 0.18344 | 0.30565 | 0.24466 | 0.24466 | 0.0077836 | -0.17052 | 0.17885 | -0.0063165 | 0.22853 | -0.23746 | 0.008045 | 0.30149 | 0.29209 | -0.0062985 | -0.40142 | -0.38972 | -88.4594 | 91.5405 | 91.5405 | 91.6224 | -88.5617 | -88.5617 |  | 0.030512 | 1.8882 | 1.8671 | 0.029184 | 1.888 | 1.8653 | -42.5134 | -148.9672 | 150.0616 | -43.4594 | -148.9088 | 150.0843
Line_1 | 0.015891 | 0.015891 | 0.015891 | 0.010594 | 0.010594 | 0.010594 | 0.1835 | 0.1835 | 0.1835 | 0.12233 | 0.12233 | 0.12233 | 0.0045539 | 0.17248 | -0.17703 | -0.0025199 | -0.11427 | 0.11873 | 0.0041066 | -0.30059 | -0.29216 | -0.0025289 | 0.20071 | 0.19486 | -88.6184 | -88.6184 | -88.6184 | 91.4383 | 91.4383 | 91.4383 |  | 0.033418 | 1.8886 | 1.8617 | 0.029184 | 1.888 | 1.8653 | -46.575 | -148.7718 | 150.1688 | -43.4594 | -148.9088 | 150.0843
Line_2 | 0.015891 | 0.015891 | 0.015891 | 0.010594 | 0.010594 | 0.010594 | 0.1835 | 0.1835 | 0.1835 | 0.12233 | 0.12233 | 0.12233 | 0.0045539 | 0.17248 | -0.17703 | -0.0025199 | -0.11427 | 0.11873 | 0.0041066 | -0.30059 | -0.29216 | -0.0025289 | 0.20071 | 0.19486 | -88.6184 | -88.6184 | -88.6184 | 91.4383 | 91.4383 | 91.4383 |  | 0.033418 | 1.8886 | 1.8617 | 0.029184 | 1.888 | 1.8653 | -46.575 | -148.7718 | 150.1688 | -43.4594 | -148.9088 | 150.0843

## LG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.029436 | 0.014718 | 0.014718 | 0.024524 | 0.01963 | 0.01963 | 0.3399 | 0.16995 | 0.16995 | 0.28318 | 0.22667 | 0.22667 | 0.00035061 | -0.14342 | 0.15091 | -5.2118e-14 | 0.19308 | -0.19949 | 0.00041236 | 0.25542 | 0.25081 | -5.5736e-14 | -0.33978 | -0.33497 | -89.1025 | 90.8974 | 90.8974 | 91.0545 | -89.2988 | -89.2988 |  | 0.0015924 | 1.7236 | 1.7223 | 0 | 1.7241 | 1.72 | -39.4753 | -149.7882 | 149.8635 | 0 | -149.6905 | 149.9251
Line_1 | 0.014723 | 0.014723 | 0.014723 | 0.0098152 | 0.0098152 | 0.0098152 | 0.17001 | 0.17001 | 0.17001 | 0.11334 | 0.11334 | 0.11334 | 0.0012817 | 0.14658 | -0.14786 | -2.0721e-14 | -0.096542 | 0.099747 | 0.00026558 | -0.25429 | -0.25125 | -2.2435e-14 | 0.16989 | 0.16749 | -89.4077 | -89.4077 | -89.4077 | 90.7012 | 90.7012 | 90.7012 |  | 0.0076993 | 1.7265 | 1.7148 | 0 | 1.7241 | 1.72 | -77.7013 | -149.4475 | 150.1151 | 0 | -149.6905 | 149.9251
Line_2 | 0.014723 | 0.014723 | 0.014723 | 0.0098152 | 0.0098152 | 0.0098152 | 0.17001 | 0.17001 | 0.17001 | 0.11334 | 0.11334 | 0.11334 | 0.0012817 | 0.14658 | -0.14786 | -2.0721e-14 | -0.096542 | 0.099747 | 0.00026558 | -0.25429 | -0.25125 | -2.2435e-14 | 0.16989 | 0.16749 | -89.4077 | -89.4077 | -89.4077 | 90.7012 | 90.7012 | 90.7012 |  | 0.0076993 | 1.7265 | 1.7148 | 0 | 1.7241 | 1.72 | -77.7013 | -149.4475 | 150.1151 | 0 | -149.6905 | 149.9251

## LG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.029436 | 0.014718 | 0.014718 | 0.024524 | 0.01963 | 0.01963 | 0.3399 | 0.16995 | 0.16995 | 0.28318 | 0.22667 | 0.22667 | 0.00035061 | -0.14342 | 0.15091 | -5.2118e-14 | 0.19308 | -0.19949 | 0.00041236 | 0.25542 | 0.25081 | -5.5736e-14 | -0.33978 | -0.33497 | -89.1025 | 90.8974 | 90.8974 | 91.0545 | -89.2988 | -89.2988 |  | 0.0015924 | 1.7236 | 1.7223 | 0 | 1.7241 | 1.72 | -39.4753 | -149.7882 | 149.8635 | 0 | -149.6905 | 149.9251
Line_1 | 0.014723 | 0.014723 | 0.014723 | 0.0098152 | 0.0098152 | 0.0098152 | 0.17001 | 0.17001 | 0.17001 | 0.11334 | 0.11334 | 0.11334 | 0.0012817 | 0.14658 | -0.14786 | -2.0721e-14 | -0.096542 | 0.099747 | 0.00026558 | -0.25429 | -0.25125 | -2.2435e-14 | 0.16989 | 0.16749 | -89.4077 | -89.4077 | -89.4077 | 90.7012 | 90.7012 | 90.7012 |  | 0.0076993 | 1.7265 | 1.7148 | 0 | 1.7241 | 1.72 | -77.7013 | -149.4475 | 150.1151 | 0 | -149.6905 | 149.9251
Line_2 | 0.014723 | 0.014723 | 0.014723 | 0.0098152 | 0.0098152 | 0.0098152 | 0.17001 | 0.17001 | 0.17001 | 0.11334 | 0.11334 | 0.11334 | 0.0012817 | 0.14658 | -0.14786 | -2.0721e-14 | -0.096542 | 0.099747 | 0.00026558 | -0.25429 | -0.25125 | -2.2435e-14 | 0.16989 | 0.16749 | -89.4077 | -89.4077 | -89.4077 | 90.7012 | 90.7012 | 90.7012 |  | 0.0076993 | 1.7265 | 1.7148 | 0 | 1.7241 | 1.72 | -77.7013 | -149.4475 | 150.1151 | 0 | -149.6905 | 149.9251

## LG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.028871 | 0.014435 | 0.014435 | 0.024053 | 0.019253 | 0.019253 | 0.33337 | 0.16669 | 0.16669 | 0.27774 | 0.22232 | 0.22232 | 0.0065887 | -0.13911 | 0.14943 | -0.0052225 | 0.18728 | -0.1976 | 0.0066481 | 0.24997 | 0.24012 | -0.005194 | -0.33253 | -0.32072 | -88.045 | 91.9549 | 91.9549 | 92.112 | -88.2412 | -88.2412 |  | 0.028077 | 1.7162 | 1.6968 | 0.02652 | 1.7167 | 1.6944 | -42.7879 | -148.9496 | 150.0603 | -43.045 | -148.8533 | 150.1205
Line_1 | 0.01444 | 0.01444 | 0.01444 | 0.0096266 | 0.0096266 | 0.0096266 | 0.16674 | 0.16674 | 0.16674 | 0.11116 | 0.11116 | 0.11116 | 0.0043429 | 0.14217 | -0.14651 | -0.0020773 | -0.093641 | 0.098801 | 0.0033988 | -0.24888 | -0.24056 | -0.0020916 | 0.16627 | 0.16036 | -88.3502 | -88.3502 | -88.3502 | 91.7588 | 91.7588 | 91.7588 |  | 0.033074 | 1.719 | 1.6893 | 0.02652 | 1.7167 | 1.6944 | -50.3034 | -148.6136 | 150.3071 | -43.045 | -148.8533 | 150.1205
Line_2 | 0.01444 | 0.01444 | 0.01444 | 0.0096266 | 0.0096266 | 0.0096266 | 0.16674 | 0.16674 | 0.16674 | 0.11116 | 0.11116 | 0.11116 | 0.0043429 | 0.14217 | -0.14651 | -0.0020773 | -0.093641 | 0.098801 | 0.0033988 | -0.24888 | -0.24056 | -0.0020916 | 0.16627 | 0.16036 | -88.3502 | -88.3502 | -88.3502 | 91.7588 | 91.7588 | 91.7588 |  | 0.033074 | 1.719 | 1.6893 | 0.02652 | 1.7167 | 1.6944 | -50.3034 | -148.6136 | 150.3071 | -43.045 | -148.8533 | 150.1205

## LG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.028871 | 0.014435 | 0.014435 | 0.024053 | 0.019253 | 0.019253 | 0.33337 | 0.16669 | 0.16669 | 0.27774 | 0.22232 | 0.22232 | 0.0065887 | -0.13911 | 0.14943 | -0.0052225 | 0.18728 | -0.1976 | 0.0066481 | 0.24997 | 0.24012 | -0.005194 | -0.33253 | -0.32072 | -88.045 | 91.9549 | 91.9549 | 92.112 | -88.2412 | -88.2412 |  | 0.028077 | 1.7162 | 1.6968 | 0.02652 | 1.7167 | 1.6944 | -42.7879 | -148.9496 | 150.0603 | -43.045 | -148.8533 | 150.1205
Line_1 | 0.01444 | 0.01444 | 0.01444 | 0.0096266 | 0.0096266 | 0.0096266 | 0.16674 | 0.16674 | 0.16674 | 0.11116 | 0.11116 | 0.11116 | 0.0043429 | 0.14217 | -0.14651 | -0.0020773 | -0.093641 | 0.098801 | 0.0033988 | -0.24888 | -0.24056 | -0.0020916 | 0.16627 | 0.16036 | -88.3502 | -88.3502 | -88.3502 | 91.7588 | 91.7588 | 91.7588 |  | 0.033074 | 1.719 | 1.6893 | 0.02652 | 1.7167 | 1.6944 | -50.3034 | -148.6136 | 150.3071 | -43.045 | -148.8533 | 150.1205
Line_2 | 0.01444 | 0.01444 | 0.01444 | 0.0096266 | 0.0096266 | 0.0096266 | 0.16674 | 0.16674 | 0.16674 | 0.11116 | 0.11116 | 0.11116 | 0.0043429 | 0.14217 | -0.14651 | -0.0020773 | -0.093641 | 0.098801 | 0.0033988 | -0.24888 | -0.24056 | -0.0020916 | 0.16627 | 0.16036 | -88.3502 | -88.3502 | -88.3502 | 91.7588 | 91.7588 | 91.7588 |  | 0.033074 | 1.719 | 1.6893 | 0.02652 | 1.7167 | 1.6944 | -50.3034 | -148.6136 | 150.3071 | -43.045 | -148.8533 | 150.1205

## LLG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.0081428 | 3.7083 | 3.71 | 0.01086 | 3.7089 | 3.7094 | 0.094024 | 42.82 | 42.8393 | 0.12541 | 42.8266 | 42.8326 | 0.0011178 | 7.1476 | 7.1606 | -0.0010218 | 7.1787e-11 | 5.5017e-11 | 0.1549 | 8.1332 | 8.101 | -0.20653 | -3.026e-11 | 3.3673e-11 | -89.592 | -167.8414 | 12.2817 | 90.3058 | 12.1996 | -167.7593 |  | 1.6475 | 0.25286 | 0.25239 | 1.6469 | 0 | 0 | -0.0054444 | -119.1506 | 60.8078 | 0.02234 | 0 | 0
Line_1 | 0.0081454 | 0.0081454 | 0.0081454 | 0.0054302 | 0.0054302 | 0.0054302 | 0.094055 | 0.094055 | 0.094055 | 0.062703 | 0.062703 | 0.062703 | -0.00040866 | 0.00020433 | 0.00020433 | 0.0005109 | 2.1691e-14 | 6.4884e-14 | -0.15482 | 8.1289e-05 | 8.1289e-05 | 0.10327 | 1.1198e-13 | -6.8604e-14 | 90.2491 | 90.2491 | 90.2491 | -89.6942 | -89.6942 | -89.6942 |  | 1.6461 | 0.002338 | 0.002338 | 1.6469 | 0 | 0 | 0.097838 | 111.9435 | 111.9435 | 0.02234 | 0 | 0
Line_2 | 0.0081454 | 0.0081454 | 0.0081454 | 0.0054302 | 0.0054302 | 0.0054302 | 0.094055 | 0.094055 | 0.094055 | 0.062703 | 0.062703 | 0.062703 | -0.00040866 | 0.00020433 | 0.00020433 | 0.0005109 | 2.1691e-14 | 6.4884e-14 | -0.15482 | 8.1289e-05 | 8.1289e-05 | 0.10327 | 1.1198e-13 | -6.8604e-14 | 90.2491 | 90.2491 | 90.2491 | -89.6942 | -89.6942 | -89.6942 |  | 1.6461 | 0.002338 | 0.002338 | 1.6469 | 0 | 0 | 0.097838 | 111.9435 | 111.9435 | 0.02234 | 0 | 0

## LLG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.0081428 | 3.7083 | 3.71 | 0.01086 | 3.7089 | 3.7094 | 0.094024 | 42.82 | 42.8393 | 0.12541 | 42.8266 | 42.8326 | 0.0011178 | 7.1476 | 7.1606 | -0.0010218 | 7.1787e-11 | 5.5017e-11 | 0.1549 | 8.1332 | 8.101 | -0.20653 | -3.026e-11 | 3.3673e-11 | -89.592 | -167.8414 | 12.2817 | 90.3058 | 12.1996 | -167.7593 |  | 1.6475 | 0.25286 | 0.25239 | 1.6469 | 0 | 0 | -0.0054444 | -119.1506 | 60.8078 | 0.02234 | 0 | 0
Line_1 | 0.0081454 | 0.0081454 | 0.0081454 | 0.0054302 | 0.0054302 | 0.0054302 | 0.094055 | 0.094055 | 0.094055 | 0.062703 | 0.062703 | 0.062703 | -0.00040866 | 0.00020433 | 0.00020433 | 0.0005109 | 2.1691e-14 | 6.4884e-14 | -0.15482 | 8.1289e-05 | 8.1289e-05 | 0.10327 | 1.1198e-13 | -6.8604e-14 | 90.2491 | 90.2491 | 90.2491 | -89.6942 | -89.6942 | -89.6942 |  | 1.6461 | 0.002338 | 0.002338 | 1.6469 | 0 | 0 | 0.097838 | 111.9435 | 111.9435 | 0.02234 | 0 | 0
Line_2 | 0.0081454 | 0.0081454 | 0.0081454 | 0.0054302 | 0.0054302 | 0.0054302 | 0.094055 | 0.094055 | 0.094055 | 0.062703 | 0.062703 | 0.062703 | -0.00040866 | 0.00020433 | 0.00020433 | 0.0005109 | 2.1691e-14 | 6.4884e-14 | -0.15482 | 8.1289e-05 | 8.1289e-05 | 0.10327 | 1.1198e-13 | -6.8604e-14 | 90.2491 | 90.2491 | 90.2491 | -89.6942 | -89.6942 | -89.6942 |  | 1.6461 | 0.002338 | 0.002338 | 1.6469 | 0 | 0 | 0.097838 | 111.9435 | 111.9435 | 0.02234 | 0 | 0

## LLG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.0080643 | 1.1319 | 1.1365 | 0.010756 | 1.1335 | 1.135 | 0.093118 | 13.0705 | 13.1233 | 0.1242 | 13.0883 | 13.1055 | 0.0020718 | 7.086 | 7.1169 | -0.002301 | -6.4395 | -6.4253 | 0.15291 | 7.1049 | 7.2782 | -0.20387 | -6.3391 | -6.5257 | -89.0502 | -144.6978 | 35.6378 | 90.8476 | 35.4139 | -144.4734 |  | 1.6422 | 0.76772 | 0.77568 | 1.6416 | 0.6904 | 0.69879 | 0.17347 | -99.6217 | 81.2797 | 0.20095 | -100.0362 | 80.9708
Line_1 | 0.008067 | 0.008067 | 0.008067 | 0.0053779 | 0.0053779 | 0.0053779 | 0.093149 | 0.093149 | 0.093149 | 0.062099 | 0.062099 | 0.062099 | -0.0013739 | -0.062964 | 0.064338 | 0.0011505 | 0.042102 | -0.042751 | -0.15283 | 0.01216 | -0.011022 | 0.10194 | -0.0080951 | 0.0074434 | 90.7908 | 90.7908 | 90.7908 | -89.1524 | -89.1524 | -89.1524 |  | 1.6408 | 0.68844 | 0.70077 | 1.6416 | 0.6904 | 0.69879 | 0.27577 | -100.1398 | 81.0697 | 0.20095 | -100.0362 | 80.9708
Line_2 | 0.008067 | 0.008067 | 0.008067 | 0.0053779 | 0.0053779 | 0.0053779 | 0.093149 | 0.093149 | 0.093149 | 0.062099 | 0.062099 | 0.062099 | -0.0013739 | -0.062964 | 0.064338 | 0.0011505 | 0.042102 | -0.042751 | -0.15283 | 0.01216 | -0.011022 | 0.10194 | -0.0080951 | 0.0074434 | 90.7908 | 90.7908 | 90.7908 | -89.1524 | -89.1524 | -89.1524 |  | 1.6408 | 0.68844 | 0.70077 | 1.6416 | 0.6904 | 0.69879 | 0.27577 | -100.1398 | 81.0697 | 0.20095 | -100.0362 | 80.9708

## LLG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.0080643 | 1.1319 | 1.1365 | 0.010756 | 1.1335 | 1.135 | 0.093118 | 13.0705 | 13.1233 | 0.1242 | 13.0883 | 13.1055 | 0.0020718 | 7.086 | 7.1169 | -0.002301 | -6.4395 | -6.4253 | 0.15291 | 7.1049 | 7.2782 | -0.20387 | -6.3391 | -6.5257 | -89.0502 | -144.6978 | 35.6378 | 90.8476 | 35.4139 | -144.4734 |  | 1.6422 | 0.76772 | 0.77568 | 1.6416 | 0.6904 | 0.69879 | 0.17347 | -99.6217 | 81.2797 | 0.20095 | -100.0362 | 80.9708
Line_1 | 0.008067 | 0.008067 | 0.008067 | 0.0053779 | 0.0053779 | 0.0053779 | 0.093149 | 0.093149 | 0.093149 | 0.062099 | 0.062099 | 0.062099 | -0.0013739 | -0.062964 | 0.064338 | 0.0011505 | 0.042102 | -0.042751 | -0.15283 | 0.01216 | -0.011022 | 0.10194 | -0.0080951 | 0.0074434 | 90.7908 | 90.7908 | 90.7908 | -89.1524 | -89.1524 | -89.1524 |  | 1.6408 | 0.68844 | 0.70077 | 1.6416 | 0.6904 | 0.69879 | 0.27577 | -100.1398 | 81.0697 | 0.20095 | -100.0362 | 80.9708
Line_2 | 0.008067 | 0.008067 | 0.008067 | 0.0053779 | 0.0053779 | 0.0053779 | 0.093149 | 0.093149 | 0.093149 | 0.062099 | 0.062099 | 0.062099 | -0.0013739 | -0.062964 | 0.064338 | 0.0011505 | 0.042102 | -0.042751 | -0.15283 | 0.01216 | -0.011022 | 0.10194 | -0.0080951 | 0.0074434 | 90.7908 | 90.7908 | 90.7908 | -89.1524 | -89.1524 | -89.1524 |  | 1.6408 | 0.68844 | 0.70077 | 1.6416 | 0.6904 | 0.69879 | 0.27577 | -100.1398 | 81.0697 | 0.20095 | -100.0362 | 80.9708

## LLG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.0074019 | 3.1178 | 3.1203 | 0.0098722 | 3.1187 | 3.1195 | 0.08547 | 36.0018 | 36.0304 | 0.11399 | 36.0117 | 36.0205 | 0.0017733 | 9.7096 | 9.7166 | -0.0016211 | -1.3582e-10 | 4.5347e-11 | 0.12799 | 5.763 | 5.7169 | -0.17065 | -1.2813e-10 | -1.8514e-10 | -89.2201 | -159.7364 | 20.3917 | 90.5837 | 20.3062 | -159.6508 |  | 1.4976 | 0.31363 | 0.31289 | 1.4971 | 0 | 0 | -0.013869 | -129.0459 | 50.8627 | 0.039475 | 0 | 0
Line_1 | 0.0074042 | 0.0074042 | 0.0074042 | 0.0049361 | 0.0049361 | 0.0049361 | 0.085497 | 0.085497 | 0.085497 | 0.056997 | 0.056997 | 0.056997 | -0.00064832 | 0.00032416 | 0.00032416 | 0.00081053 | 2.6345e-13 | -2.5143e-13 | -0.12793 | 6.7168e-05 | 6.7168e-05 | 0.085327 | -1.3393e-13 | -1.666e-13 | 90.4748 | 90.4748 | 90.4748 | -89.4163 | -89.4163 | -89.4163 |  | 1.4963 | 0.003872 | 0.003872 | 1.4971 | 0 | 0 | 0.18443 | 102.1812 | 102.1812 | 0.039475 | 0 | 0
Line_2 | 0.0074042 | 0.0074042 | 0.0074042 | 0.0049361 | 0.0049361 | 0.0049361 | 0.085497 | 0.085497 | 0.085497 | 0.056997 | 0.056997 | 0.056997 | -0.00064832 | 0.00032416 | 0.00032416 | 0.00081053 | 2.6345e-13 | -2.5143e-13 | -0.12793 | 6.7168e-05 | 6.7168e-05 | 0.085327 | -1.3393e-13 | -1.666e-13 | 90.4748 | 90.4748 | 90.4748 | -89.4163 | -89.4163 | -89.4163 |  | 1.4963 | 0.003872 | 0.003872 | 1.4971 | 0 | 0 | 0.18443 | 102.1812 | 102.1812 | 0.039475 | 0 | 0

## LLG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.0074019 | 3.1178 | 3.1203 | 0.0098722 | 3.1187 | 3.1195 | 0.08547 | 36.0018 | 36.0304 | 0.11399 | 36.0117 | 36.0205 | 0.0017733 | 9.7096 | 9.7166 | -0.0016211 | -1.3582e-10 | 4.5347e-11 | 0.12799 | 5.763 | 5.7169 | -0.17065 | -1.2813e-10 | -1.8514e-10 | -89.2201 | -159.7364 | 20.3917 | 90.5837 | 20.3062 | -159.6508 |  | 1.4976 | 0.31363 | 0.31289 | 1.4971 | 0 | 0 | -0.013869 | -129.0459 | 50.8627 | 0.039475 | 0 | 0
Line_1 | 0.0074042 | 0.0074042 | 0.0074042 | 0.0049361 | 0.0049361 | 0.0049361 | 0.085497 | 0.085497 | 0.085497 | 0.056997 | 0.056997 | 0.056997 | -0.00064832 | 0.00032416 | 0.00032416 | 0.00081053 | 2.6345e-13 | -2.5143e-13 | -0.12793 | 6.7168e-05 | 6.7168e-05 | 0.085327 | -1.3393e-13 | -1.666e-13 | 90.4748 | 90.4748 | 90.4748 | -89.4163 | -89.4163 | -89.4163 |  | 1.4963 | 0.003872 | 0.003872 | 1.4971 | 0 | 0 | 0.18443 | 102.1812 | 102.1812 | 0.039475 | 0 | 0
Line_2 | 0.0074042 | 0.0074042 | 0.0074042 | 0.0049361 | 0.0049361 | 0.0049361 | 0.085497 | 0.085497 | 0.085497 | 0.056997 | 0.056997 | 0.056997 | -0.00064832 | 0.00032416 | 0.00032416 | 0.00081053 | 2.6345e-13 | -2.5143e-13 | -0.12793 | 6.7168e-05 | 6.7168e-05 | 0.085327 | -1.3393e-13 | -1.666e-13 | 90.4748 | 90.4748 | 90.4748 | -89.4163 | -89.4163 | -89.4163 |  | 1.4963 | 0.003872 | 0.003872 | 1.4971 | 0 | 0 | 0.18443 | 102.1812 | 102.1812 | 0.039475 | 0 | 0

## LLG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.0073301 | 0.99053 | 0.99484 | 0.0097765 | 0.99199 | 0.99337 | 0.084641 | 11.4376 | 11.4874 | 0.11289 | 11.4545 | 11.4704 | 0.0025451 | 5.8971 | 5.925 | -0.002661 | -4.9307 | -4.9235 | 0.12633 | 5.4419 | 5.5755 | -0.16844 | -4.8525 | -5.0018 | -88.682 | -142.8058 | 37.5363 | 91.1218 | 37.3076 | -142.5764 |  | 1.4928 | 0.70157 | 0.70824 | 1.4923 | 0.60395 | 0.61188 | 0.16386 | -100.1051 | 80.7953 | 0.21673 | -98.1508 | 82.8754
Line_1 | 0.0073324 | 0.0073324 | 0.0073324 | 0.0048883 | 0.0048883 | 0.0048883 | 0.084668 | 0.084668 | 0.084668 | 0.056445 | 0.056445 | 0.056445 | -0.0014377 | -0.050165 | 0.051602 | 0.0013305 | 0.033644 | -0.03418 | -0.12627 | 0.0082095 | -0.0072672 | 0.084219 | -0.005493 | 0.0049537 | 91.0129 | 91.0129 | 91.0129 | -88.8782 | -88.8782 | -88.8782 |  | 1.4914 | 0.60037 | 0.61548 | 1.4923 | 0.60395 | 0.61188 | 0.36055 | -98.2812 | 82.9966 | 0.21673 | -98.1508 | 82.8754
Line_2 | 0.0073324 | 0.0073324 | 0.0073324 | 0.0048883 | 0.0048883 | 0.0048883 | 0.084668 | 0.084668 | 0.084668 | 0.056445 | 0.056445 | 0.056445 | -0.0014377 | -0.050165 | 0.051602 | 0.0013305 | 0.033644 | -0.03418 | -0.12627 | 0.0082095 | -0.0072672 | 0.084219 | -0.005493 | 0.0049537 | 91.0129 | 91.0129 | 91.0129 | -88.8782 | -88.8782 | -88.8782 |  | 1.4914 | 0.60037 | 0.61548 | 1.4923 | 0.60395 | 0.61188 | 0.36055 | -98.2812 | 82.9966 | 0.21673 | -98.1508 | 82.8754

## LLG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.0073301 | 0.99053 | 0.99484 | 0.0097765 | 0.99199 | 0.99337 | 0.084641 | 11.4376 | 11.4874 | 0.11289 | 11.4545 | 11.4704 | 0.0025451 | 5.8971 | 5.925 | -0.002661 | -4.9307 | -4.9235 | 0.12633 | 5.4419 | 5.5755 | -0.16844 | -4.8525 | -5.0018 | -88.682 | -142.8058 | 37.5363 | 91.1218 | 37.3076 | -142.5764 |  | 1.4928 | 0.70157 | 0.70824 | 1.4923 | 0.60395 | 0.61188 | 0.16386 | -100.1051 | 80.7953 | 0.21673 | -98.1508 | 82.8754
Line_1 | 0.0073324 | 0.0073324 | 0.0073324 | 0.0048883 | 0.0048883 | 0.0048883 | 0.084668 | 0.084668 | 0.084668 | 0.056445 | 0.056445 | 0.056445 | -0.0014377 | -0.050165 | 0.051602 | 0.0013305 | 0.033644 | -0.03418 | -0.12627 | 0.0082095 | -0.0072672 | 0.084219 | -0.005493 | 0.0049537 | 91.0129 | 91.0129 | 91.0129 | -88.8782 | -88.8782 | -88.8782 |  | 1.4914 | 0.60037 | 0.61548 | 1.4923 | 0.60395 | 0.61188 | 0.36055 | -98.2812 | 82.9966 | 0.21673 | -98.1508 | 82.8754
Line_2 | 0.0073324 | 0.0073324 | 0.0073324 | 0.0048883 | 0.0048883 | 0.0048883 | 0.084668 | 0.084668 | 0.084668 | 0.056445 | 0.056445 | 0.056445 | -0.0014377 | -0.050165 | 0.051602 | 0.0013305 | 0.033644 | -0.03418 | -0.12627 | 0.0082095 | -0.0072672 | 0.084219 | -0.005493 | 0.0049537 | 91.0129 | 91.0129 | 91.0129 | -88.8782 | -88.8782 | -88.8782 |  | 1.4914 | 0.60037 | 0.61548 | 1.4923 | 0.60395 | 0.61188 | 0.36055 | -98.2812 | 82.9966 | 0.21673 | -98.1508 | 82.8754