## LLL_max_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 3.4587 | 3.4587 | 0 | 0 | 119.8128 | 119.8128 | 37.3233 | -18.6616 | 42.3476 | -21.1738 | -71.7883 | 108.2117 | 0.47113 | 0.23557 | -23.1798 | -23.1798
Line_1 | 3.4587 | 3.4587 | 6.7756 | 0 | 119.8128 | 119.8128 | -1e-07 | 18.6616 | -1e-07 | 21.1738 | 108.2117 | -71.7883 | 0 | 0.23557 | 0 | -23.1798
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23557 | 0.23557 | -23.1798 | -23.1798

## LLL_max_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 3.4587 | 3.4587 | 0 | 0 | 119.8128 | 119.8128 | 37.3233 | -18.6616 | 42.3476 | -21.1738 | -71.7883 | 108.2117 | 0.47113 | 0.23557 | -23.1798 | -23.1798
Line_1 | 3.4587 | 3.4587 | 6.7756 | 0 | 119.8128 | 119.8128 | -1e-07 | 18.6616 | -1e-07 | 21.1738 | 108.2117 | -71.7883 | 0 | 0.23557 | 0 | -23.1798
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23557 | 0.23557 | -23.1798 | -23.1798

## LLL_max_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 1.2119 | 1.2119 | 0 | 0 | 41.9813 | 41.9813 | 26.6127 | -24.3216 | 27.2296 | -24.63 | -54.0862 | 125.9138 | 0.90694 | 0.82453 | -8.4298 | -8.7252
Line_1 | 1.2119 | 1.2119 | 2.3741 | 0 | 41.9813 | 41.9813 | -22.0304 | 24.3216 | -22.0304 | 24.63 | 125.9138 | -54.0862 | 0.74213 | 0.82453 | -9.0862 | -8.7252
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.82453 | 0.82453 | -8.7252 | -8.7252

## LLL_max_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 1.2119 | 1.2119 | 0 | 0 | 41.9813 | 41.9813 | 26.6127 | -24.3216 | 27.2296 | -24.63 | -54.0862 | 125.9138 | 0.90694 | 0.82453 | -8.4298 | -8.7252
Line_1 | 1.2119 | 1.2119 | 2.3741 | 0 | 41.9813 | 41.9813 | -22.0304 | 24.3216 | -22.0304 | 24.63 | 125.9138 | -54.0862 | 0.74213 | 0.82453 | -9.0862 | -8.7252
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.82453 | 0.82453 | -8.7252 | -8.7252

## LLL_min_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 2.7686 | 2.7686 | 0 | 0 | 95.9057 | 95.9057 | 45.916 | -22.958 | 27.1338 | -13.5669 | -59.5744 | 120.4256 | 0.55611 | 0.27805 | -28.9937 | -28.9937
Line_1 | 2.7686 | 2.7686 | 4.6525 | 0 | 95.9057 | 95.9057 | -1e-07 | 22.958 | -1e-07 | 13.5669 | 120.4256 | -59.5744 | 0 | 0.27805 | 0 | -28.9937
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27805 | 0.27805 | -28.9937 | -28.9937

## LLL_min_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 2.7686 | 2.7686 | 0 | 0 | 95.9057 | 95.9057 | 45.916 | -22.958 | 27.1338 | -13.5669 | -59.5744 | 120.4256 | 0.55611 | 0.27805 | -28.9937 | -28.9937
Line_1 | 2.7686 | 2.7686 | 4.6525 | 0 | 95.9057 | 95.9057 | -1e-07 | 22.958 | -1e-07 | 13.5669 | 120.4256 | -59.5744 | 0 | 0.27805 | 0 | -28.9937
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27805 | 0.27805 | -28.9937 | -28.9937

## LLL_min_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 1.0349 | 1.0349 | 0 | 0 | 35.8516 | 35.8516 | 22.4832 | -19.2749 | 19.8585 | -17.9626 | -50.3977 | 129.6023 | 0.83671 | 0.7349 | -8.9447 | -7.416
Line_1 | 1.0349 | 1.0349 | 1.7392 | 0 | 35.8516 | 35.8516 | -16.0667 | 19.2749 | -16.0667 | 17.9626 | 129.6023 | -50.3977 | 0.63377 | 0.7349 | -5.3977 | -7.416
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7349 | 0.7349 | -7.416 | -7.416

## LLL_min_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 1.0349 | 1.0349 | 0 | 0 | 35.8516 | 35.8516 | 22.4832 | -19.2749 | 19.8585 | -17.9626 | -50.3977 | 129.6023 | 0.83671 | 0.7349 | -8.9447 | -7.416
Line_1 | 1.0349 | 1.0349 | 1.7392 | 0 | 35.8516 | 35.8516 | -16.0667 | 19.2749 | -16.0667 | 17.9626 | 129.6023 | -50.3977 | 0.63377 | 0.7349 | -5.3977 | -7.416
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7349 | 0.7349 | -7.416 | -7.416

## LL_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 2.9953 | 2.9953 | 0 | 2.9953 | 2.9953 | 0 | 34.587 | 34.587 | 0 | 34.587 | 34.587 | -1.0421e-14 | 27.4008 | -8.7391 | 1.5632e-14 | -22.7354 | 13.4045 | 2.0843e-14 | 4.6417 | 16.5321 | -1.0421e-14 | 0.65175 | -11.2386 | 0 | -161.7883 | 18.2117 | 0 | 18.2117 | -161.7883 | 1.1 | 0.80351 | 0.54066 | 1.1 | 0.65761 | 0.50575 | -9.7269e-12 | -152.1736 | 136.0734 | -9.7269e-12 | -163.4303 | 158.2346
Line_1 | 0 | 2.9953 | 2.9953 | 0 | 2.9953 | 2.9953 | 0 | 34.587 | 34.587 | 0 | 34.587 | 34.587 | 1.0421e-14 | -18.0699 | 18.0699 | -5.2106e-15 | 22.7354 | -13.4045 | -5.2106e-15 | 5.9452 | -5.9452 | 2.0843e-14 | -0.65175 | 11.2386 | 0 | 18.2117 | -161.7883 | 0 | -161.7883 | 18.2117 | 1.1 | 0.55 | 0.55 | 1.1 | 0.65761 | 0.50575 | -9.7252e-12 | 180 | -180 | -9.7269e-12 | -163.4303 | 158.2346
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4051e-10 | 6.644e-10 | 1.0421e-14 | -3.4051e-10 | -6.644e-10 | 0 | -1.8234e-09 | 1.2625e-09 | 1.5632e-14 | 1.8234e-09 | -1.2624e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.65761 | 0.50575 | 1.1 | 0.65761 | 0.50575 | -9.7212e-12 | -163.4303 | 158.2346 | -9.7269e-12 | -163.4303 | 158.2346

## LL_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 2.9953 | 2.9953 | 0 | 2.9953 | 2.9953 | 0 | 34.587 | 34.587 | 0 | 34.587 | 34.587 | -1.0421e-14 | 27.4008 | -8.7391 | 1.5632e-14 | -22.7354 | 13.4045 | 2.0843e-14 | 4.6417 | 16.5321 | -1.0421e-14 | 0.65175 | -11.2386 | 0 | -161.7883 | 18.2117 | 0 | 18.2117 | -161.7883 | 1.1 | 0.80351 | 0.54066 | 1.1 | 0.65761 | 0.50575 | -9.7269e-12 | -152.1736 | 136.0734 | -9.7269e-12 | -163.4303 | 158.2346
Line_1 | 0 | 2.9953 | 2.9953 | 0 | 2.9953 | 2.9953 | 0 | 34.587 | 34.587 | 0 | 34.587 | 34.587 | 1.0421e-14 | -18.0699 | 18.0699 | -5.2106e-15 | 22.7354 | -13.4045 | -5.2106e-15 | 5.9452 | -5.9452 | 2.0843e-14 | -0.65175 | 11.2386 | 0 | 18.2117 | -161.7883 | 0 | -161.7883 | 18.2117 | 1.1 | 0.55 | 0.55 | 1.1 | 0.65761 | 0.50575 | -9.7252e-12 | 180 | -180 | -9.7269e-12 | -163.4303 | 158.2346
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4051e-10 | 6.644e-10 | 1.0421e-14 | -3.4051e-10 | -6.644e-10 | 0 | -1.8234e-09 | 1.2625e-09 | 1.5632e-14 | 1.8234e-09 | -1.2624e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.65761 | 0.50575 | 1.1 | 0.65761 | 0.50575 | -9.7212e-12 | -163.4303 | 158.2346 | -9.7269e-12 | -163.4303 | 158.2346

## LL_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 1.5688 | 1.5688 | 0 | 1.5688 | 1.5688 | 0 | 18.1144 | 18.1144 | 0 | 18.1144 | 18.1144 | -7.816e-15 | 17.2205 | 0.20321 | 7.816e-15 | -15.9408 | 1.0765 | 2.6053e-15 | 3.8735 | 14.2393 | 2.6053e-15 | -2.4216 | -12.7873 | 0 | -148.6532 | 31.3468 | 0 | 31.3468 | -148.6532 | 1.1 | 0.97441 | 0.78616 | 1.1 | 0.89011 | 0.70842 | -4.2294e-12 | -135.9762 | 120.5292 | -4.232e-12 | -140.0155 | 126.1589
Line_1 | 0 | 1.5688 | 1.5688 | 0 | 1.5688 | 1.5688 | 0 | 18.1144 | 18.1144 | 0 | 18.1144 | 18.1144 | 2.6053e-15 | -14.6611 | 2.3562 | -2.6053e-15 | 15.9408 | -1.0765 | 2.6053e-15 | -0.96958 | -11.3353 | 7.816e-15 | 2.4216 | 12.7873 | 0 | 31.3468 | -148.6532 | 0 | -148.6532 | 31.3468 | 1.1 | 0.81113 | 0.63914 | 1.1 | 0.89011 | 0.70842 | -4.2325e-12 | -144.8696 | 133.0893 | -4.232e-12 | -140.0155 | 126.1589
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.0421e-14 | 4.6819e-10 | 1.0007e-09 | 1.0421e-14 | -4.6817e-10 | -1.0007e-09 | -5.2106e-15 | -1.2288e-09 | 3.0655e-10 | 1.3027e-14 | 1.2288e-09 | -3.0655e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.89011 | 0.70842 | 1.1 | 0.89011 | 0.70842 | -4.2289e-12 | -140.0155 | 126.1589 | -4.232e-12 | -140.0155 | 126.1589

## LL_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 1.5688 | 1.5688 | 0 | 1.5688 | 1.5688 | 0 | 18.1144 | 18.1144 | 0 | 18.1144 | 18.1144 | -7.816e-15 | 17.2205 | 0.20321 | 7.816e-15 | -15.9408 | 1.0765 | 2.6053e-15 | 3.8735 | 14.2393 | 2.6053e-15 | -2.4216 | -12.7873 | 0 | -148.6532 | 31.3468 | 0 | 31.3468 | -148.6532 | 1.1 | 0.97441 | 0.78616 | 1.1 | 0.89011 | 0.70842 | -4.2294e-12 | -135.9762 | 120.5292 | -4.232e-12 | -140.0155 | 126.1589
Line_1 | 0 | 1.5688 | 1.5688 | 0 | 1.5688 | 1.5688 | 0 | 18.1144 | 18.1144 | 0 | 18.1144 | 18.1144 | 2.6053e-15 | -14.6611 | 2.3562 | -2.6053e-15 | 15.9408 | -1.0765 | 2.6053e-15 | -0.96958 | -11.3353 | 7.816e-15 | 2.4216 | 12.7873 | 0 | 31.3468 | -148.6532 | 0 | -148.6532 | 31.3468 | 1.1 | 0.81113 | 0.63914 | 1.1 | 0.89011 | 0.70842 | -4.2325e-12 | -144.8696 | 133.0893 | -4.232e-12 | -140.0155 | 126.1589
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.0421e-14 | 4.6819e-10 | 1.0007e-09 | 1.0421e-14 | -4.6817e-10 | -1.0007e-09 | -5.2106e-15 | -1.2288e-09 | 3.0655e-10 | 1.3027e-14 | 1.2288e-09 | -3.0655e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.89011 | 0.70842 | 1.1 | 0.89011 | 0.70842 | -4.2289e-12 | -140.0155 | 126.1589 | -4.232e-12 | -140.0155 | 126.1589

## LL_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 2.3976 | 2.3976 | 0 | 2.3976 | 2.3976 | 0 | 27.6856 | 27.6856 | 0 | 27.6856 | 27.6856 | -9.4739e-15 | 23.4155 | -0.45749 | 1.0658e-14 | -17.676 | 6.197 | 4.737e-15 | -0.22679 | 13.7937 | -7.1054e-15 | 3.6185 | -10.402 | 0 | -149.5744 | 30.4256 | 0 | 30.4256 | -149.5744 | 1 | 0.8458 | 0.4985 | 1 | 0.65169 | 0.43734 | 9.1248e-13 | -150.1294 | 122.3252 | 9.2649e-13 | -161.1438 | 151.2099
Line_1 | 0 | 2.3976 | 2.3976 | 0 | 2.3976 | 2.3976 | 0 | 27.6856 | 27.6856 | 0 | 27.6856 | 27.6856 | 1.1842e-15 | -11.9365 | 11.9365 | 1.532e-28 | 17.676 | -6.197 | 7.1054e-15 | 7.0103 | -7.0103 | -9.4739e-15 | -3.6185 | 10.402 | 0 | 30.4256 | -149.5744 | 0 | -149.5744 | 30.4256 | 1 | 0.5 | 0.5 | 1 | 0.65169 | 0.43734 | 9.2982e-13 | -180 | 180 | 9.2649e-13 | -161.1438 | 151.2099
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.1842e-15 | 2.4222e-10 | 6.7019e-10 | 1.149e-28 | -2.4221e-10 | -6.7019e-10 | 2.3685e-15 | -1.5722e-09 | 8.3093e-10 | -7.1054e-15 | 1.5722e-09 | -8.3092e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.65169 | 0.43734 | 1 | 0.65169 | 0.43734 | 9.0584e-13 | -161.1438 | 151.2099 | 9.2649e-13 | -161.1438 | 151.2099

## LL_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 2.3976 | 2.3976 | 0 | 2.3976 | 2.3976 | 0 | 27.6856 | 27.6856 | 0 | 27.6856 | 27.6856 | -9.4739e-15 | 23.4155 | -0.45749 | 1.0658e-14 | -17.676 | 6.197 | 4.737e-15 | -0.22679 | 13.7937 | -7.1054e-15 | 3.6185 | -10.402 | 0 | -149.5744 | 30.4256 | 0 | 30.4256 | -149.5744 | 1 | 0.8458 | 0.4985 | 1 | 0.65169 | 0.43734 | 9.1248e-13 | -150.1294 | 122.3252 | 9.2649e-13 | -161.1438 | 151.2099
Line_1 | 0 | 2.3976 | 2.3976 | 0 | 2.3976 | 2.3976 | 0 | 27.6856 | 27.6856 | 0 | 27.6856 | 27.6856 | 1.1842e-15 | -11.9365 | 11.9365 | 1.532e-28 | 17.676 | -6.197 | 7.1054e-15 | 7.0103 | -7.0103 | -9.4739e-15 | -3.6185 | 10.402 | 0 | 30.4256 | -149.5744 | 0 | -149.5744 | 30.4256 | 1 | 0.5 | 0.5 | 1 | 0.65169 | 0.43734 | 9.2982e-13 | -180 | 180 | 9.2649e-13 | -161.1438 | 151.2099
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.1842e-15 | 2.4222e-10 | 6.7019e-10 | 1.149e-28 | -2.4221e-10 | -6.7019e-10 | 2.3685e-15 | -1.5722e-09 | 8.3093e-10 | -7.1054e-15 | 1.5722e-09 | -8.3092e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.65169 | 0.43734 | 1 | 0.65169 | 0.43734 | 9.0584e-13 | -161.1438 | 151.2099 | 9.2649e-13 | -161.1438 | 151.2099

## LL_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 1.3081 | 1.3081 | 0 | 1.3081 | 1.3081 | 0 | 15.105 | 15.105 | 0 | 15.105 | 15.105 | -5.3291e-15 | 13.7181 | 1.6719 | 6.5133e-15 | -12.0096 | 0.036546 | 9.4739e-15 | 1.7406 | 10.8539 | -9.4739e-15 | -0.73098 | -9.8443 | 0 | -142.8911 | 37.1089 | 0 | 37.1089 | -142.8911 | 1 | 0.91546 | 0.72704 | 1 | 0.79654 | 0.65173 | -3.3082e-13 | -135.6599 | 118.3519 | -3.2174e-13 | -139.408 | 127.3216
Line_1 | 0 | 1.3081 | 1.3081 | 0 | 1.3081 | 1.3081 | 0 | 15.105 | 15.105 | 0 | 15.105 | 15.105 | 5.3291e-15 | -10.3011 | 1.745 | -4.1448e-15 | 12.0096 | -0.036546 | -2.3685e-15 | 0.27863 | -8.8347 | 2.3275e-29 | 0.73098 | 9.8443 | 0 | 37.1089 | -142.8911 | 0 | -142.8911 | 37.1089 | 1 | 0.68221 | 0.59619 | 1 | 0.79654 | 0.65173 | -3.2057e-13 | -144.4405 | 138.2821 | -3.2174e-13 | -139.408 | 127.3216
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.7764e-15 | 4.2826e-10 | 8.1277e-10 | 1.7764e-15 | -4.2826e-10 | -8.1277e-10 | 1.0329e-29 | -9.7051e-10 | 3.0453e-10 | -2.3685e-15 | 9.7051e-10 | -3.0453e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.79654 | 0.65173 | 1 | 0.79654 | 0.65173 | -3.3315e-13 | -139.408 | 127.3216 | -3.2174e-13 | -139.408 | 127.3216

## LL_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 1.3081 | 1.3081 | 0 | 1.3081 | 1.3081 | 0 | 15.105 | 15.105 | 0 | 15.105 | 15.105 | -5.3291e-15 | 13.7181 | 1.6719 | 6.5133e-15 | -12.0096 | 0.036546 | 9.4739e-15 | 1.7406 | 10.8539 | -9.4739e-15 | -0.73098 | -9.8443 | 0 | -142.8911 | 37.1089 | 0 | 37.1089 | -142.8911 | 1 | 0.91546 | 0.72704 | 1 | 0.79654 | 0.65173 | -3.3082e-13 | -135.6599 | 118.3519 | -3.2174e-13 | -139.408 | 127.3216
Line_1 | 0 | 1.3081 | 1.3081 | 0 | 1.3081 | 1.3081 | 0 | 15.105 | 15.105 | 0 | 15.105 | 15.105 | 5.3291e-15 | -10.3011 | 1.745 | -4.1448e-15 | 12.0096 | -0.036546 | -2.3685e-15 | 0.27863 | -8.8347 | 2.3275e-29 | 0.73098 | 9.8443 | 0 | 37.1089 | -142.8911 | 0 | -142.8911 | 37.1089 | 1 | 0.68221 | 0.59619 | 1 | 0.79654 | 0.65173 | -3.2057e-13 | -144.4405 | 138.2821 | -3.2174e-13 | -139.408 | 127.3216
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.7764e-15 | 4.2826e-10 | 8.1277e-10 | 1.7764e-15 | -4.2826e-10 | -8.1277e-10 | 1.0329e-29 | -9.7051e-10 | 3.0453e-10 | -2.3685e-15 | 9.7051e-10 | -3.0453e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.79654 | 0.65173 | 1 | 0.79654 | 0.65173 | -3.3315e-13 | -139.408 | 127.3216 | -3.2174e-13 | -139.408 | 127.3216

## LG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.016442 | 0.016446 | 0.016446 | 0.021924 | 0.010964 | 0.010964 | 0.18985 | 0.1899 | 0.1899 | 0.25315 | 0.1266 | 0.1266 | 0.00070797 | 0.18138 | -0.18042 | -0.00091628 | -0.12075 | 0.12045 | 0.00055753 | -0.31442 | -0.31586 | -0.00054824 | 0.20973 | 0.21069 | 89.7484 | -90.2279 | -90.2279 | -90.2457 | 89.7721 | 89.7721 |  | 0.0047465 | 1.9115 | 1.9155 | 0.0042179 | 1.9116 | 1.917 | 127.9688 | -150.2481 | 150.0364 | 120.6479 | -150.2973 | 150.0143
Line_1 | 0.032888 | 0 | 0 | 0.027407 | 0.0054802 | 0.0054802 | 0.37975 | 0 | 0 | 0.31647 | 0.06328 | 0.06328 | 2.6557e-14 | -6.7439e-09 | -6.767e-09 | 0.0011454 | 0.060271 | -0.060292 | -1.5766e-13 | -3.8835e-09 | 3.8703e-09 | 0.00068548 | -0.10488 | -0.10526 | -90.2397 | 0 | 0 | 89.7488 | -90.1824 | -90.1824 |  | 0 | 1.9122 | 1.9155 | 0.0042179 | 1.9116 | 1.917 | 0 | -150.2345 | 150.0626 | 120.6479 | -150.2973 | 150.0143
Line_2 | 0 | 0 | 0 | 0.0054836 | 0.0054836 | 0.0054836 | 0 | 0 | 0 | 0.063319 | 0.063319 | 0.063319 | -1.0159e-11 | -6.7418e-09 | -6.7861e-09 | -0.00022912 | 0.060475 | -0.060163 | 1.8182e-11 | -3.8925e-09 | 3.867e-09 | -0.00013724 | -0.10485 | -0.10542 | 0 | 0 | 0 | -90.2733 | -90.2733 | -90.2733 |  | 0.0051522 | 1.9114 | 1.9177 | 0.0042179 | 1.9116 | 1.917 | 118.9596 | -150.3253 | 149.9967 | 120.6479 | -150.2973 | 150.0143

## LG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.016442 | 0.016446 | 0.016446 | 0.021924 | 0.010964 | 0.010964 | 0.18985 | 0.1899 | 0.1899 | 0.25315 | 0.1266 | 0.1266 | 0.00070797 | 0.18138 | -0.18042 | -0.00091628 | -0.12075 | 0.12045 | 0.00055753 | -0.31442 | -0.31586 | -0.00054824 | 0.20973 | 0.21069 | 89.7484 | -90.2279 | -90.2279 | -90.2457 | 89.7721 | 89.7721 |  | 0.0047465 | 1.9115 | 1.9155 | 0.0042179 | 1.9116 | 1.917 | 127.9688 | -150.2481 | 150.0364 | 120.6479 | -150.2973 | 150.0143
Line_1 | 0.032888 | 0 | 0 | 0.027407 | 0.0054802 | 0.0054802 | 0.37975 | 0 | 0 | 0.31647 | 0.06328 | 0.06328 | 2.6557e-14 | -6.7439e-09 | -6.767e-09 | 0.0011454 | 0.060271 | -0.060292 | -1.5766e-13 | -3.8835e-09 | 3.8703e-09 | 0.00068548 | -0.10488 | -0.10526 | -90.2397 | 0 | 0 | 89.7488 | -90.1824 | -90.1824 |  | 0 | 1.9122 | 1.9155 | 0.0042179 | 1.9116 | 1.917 | 0 | -150.2345 | 150.0626 | 120.6479 | -150.2973 | 150.0143
Line_2 | 0 | 0 | 0 | 0.0054836 | 0.0054836 | 0.0054836 | 0 | 0 | 0 | 0.063319 | 0.063319 | 0.063319 | -1.0159e-11 | -6.7418e-09 | -6.7861e-09 | -0.00022912 | 0.060475 | -0.060163 | 1.8182e-11 | -3.8925e-09 | 3.867e-09 | -0.00013724 | -0.10485 | -0.10542 | 0 | 0 | 0 | -90.2733 | -90.2733 | -90.2733 |  | 0.0051522 | 1.9114 | 1.9177 | 0.0042179 | 1.9116 | 1.917 | 118.9596 | -150.3253 | 149.9967 | 120.6479 | -150.2973 | 150.0143

## LG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.016655 | 0.016659 | 0.016659 | 0.022208 | 0.011106 | 0.011106 | 0.19232 | 0.19236 | 0.19236 | 0.25644 | 0.12824 | 0.12824 | 0.0035002 | 0.1851 | -0.18134 | -0.0046391 | -0.12322 | 0.12107 | 0.0033469 | -0.31884 | -0.32512 | -0.0042622 | 0.21268 | 0.21686 | 88.9938 | -90.9824 | -90.9824 | -91.0002 | 89.0176 | 89.0176 |  | 0.025181 | 1.9166 | 1.9353 | 0.024566 | 1.9167 | 1.9368 | 132.7119 | -150.8449 | 149.866 | 131.5753 | -150.8946 | 149.8434
Line_1 | 0.033314 | 0 | 0 | 0.027763 | 0.0055513 | 0.0055513 | 0.38468 | 0 | 0 | 0.32058 | 0.0641 | 0.0641 | -0.0055492 | -6.8388e-09 | -6.9656e-09 | 0.0057989 | 0.061508 | -0.060604 | -0.0055492 | -3.9633e-09 | 3.8901e-09 | 0.0053288 | -0.10635 | -0.10835 | -90.9943 | 0 | 0 | 88.9943 | -90.937 | -90.937 |  | 0.020401 | 1.9173 | 1.9353 | 0.024566 | 1.9167 | 1.9368 | 134.0057 | -150.8312 | 149.8923 | 131.5753 | -150.8946 | 149.8434
Line_2 | 0 | 0 | 0 | 0.0055548 | 0.0055548 | 0.0055548 | 0 | 0 | 0 | 0.064141 | 0.064141 | 0.064141 | -6.949e-11 | -6.8366e-09 | -6.9849e-09 | -0.0011598 | 0.061715 | -0.06047 | 7.7735e-11 | -3.9722e-09 | 3.8867e-09 | -0.0010666 | -0.10632 | -0.10851 | 0 | 0 | 0 | -91.0278 | -91.0278 | -91.0278 |  | 0.025462 | 1.9165 | 1.9375 | 0.024566 | 1.9167 | 1.9368 | 130.8062 | -150.9229 | 149.8255 | 131.5753 | -150.8946 | 149.8434

## LG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.016655 | 0.016659 | 0.016659 | 0.022208 | 0.011106 | 0.011106 | 0.19232 | 0.19236 | 0.19236 | 0.25644 | 0.12824 | 0.12824 | 0.0035002 | 0.1851 | -0.18134 | -0.0046391 | -0.12322 | 0.12107 | 0.0033469 | -0.31884 | -0.32512 | -0.0042622 | 0.21268 | 0.21686 | 88.9938 | -90.9824 | -90.9824 | -91.0002 | 89.0176 | 89.0176 |  | 0.025181 | 1.9166 | 1.9353 | 0.024566 | 1.9167 | 1.9368 | 132.7119 | -150.8449 | 149.866 | 131.5753 | -150.8946 | 149.8434
Line_1 | 0.033314 | 0 | 0 | 0.027763 | 0.0055513 | 0.0055513 | 0.38468 | 0 | 0 | 0.32058 | 0.0641 | 0.0641 | -0.0055492 | -6.8388e-09 | -6.9656e-09 | 0.0057989 | 0.061508 | -0.060604 | -0.0055492 | -3.9633e-09 | 3.8901e-09 | 0.0053288 | -0.10635 | -0.10835 | -90.9943 | 0 | 0 | 88.9943 | -90.937 | -90.937 |  | 0.020401 | 1.9173 | 1.9353 | 0.024566 | 1.9167 | 1.9368 | 134.0057 | -150.8312 | 149.8923 | 131.5753 | -150.8946 | 149.8434
Line_2 | 0 | 0 | 0 | 0.0055548 | 0.0055548 | 0.0055548 | 0 | 0 | 0 | 0.064141 | 0.064141 | 0.064141 | -6.949e-11 | -6.8366e-09 | -6.9849e-09 | -0.0011598 | 0.061715 | -0.06047 | 7.7735e-11 | -3.9722e-09 | 3.8867e-09 | -0.0010666 | -0.10632 | -0.10851 | 0 | 0 | 0 | -91.0278 | -91.0278 | -91.0278 |  | 0.025462 | 1.9165 | 1.9375 | 0.024566 | 1.9167 | 1.9368 | 130.8062 | -150.9229 | 149.8255 | 131.5753 | -150.8946 | 149.8434

## LG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.01495 | 0.014953 | 0.014953 | 0.019934 | 0.0099687 | 0.0099687 | 0.17263 | 0.17266 | 0.17266 | 0.23018 | 0.11511 | 0.11511 | 0.0011238 | 0.15029 | -0.14877 | -0.0014545 | -0.099916 | 0.099452 | 0.00046023 | -0.25941 | -0.26164 | -0.00045239 | 0.17303 | 0.17453 | 89.5267 | -90.4285 | -90.4285 | -90.4621 | 89.5715 | 89.5715 |  | 0.0070349 | 1.7363 | 1.7432 | 0.0066173 | 1.7358 | 1.7451 | 111.7965 | -150.3429 | 149.9499 | 106.8154 | -150.425 | 149.895
Line_1 | 0.029903 | 0 | 0 | 0.02492 | 0.0049828 | 0.0049828 | 0.34529 | 0 | 0 | 0.28775 | 0.057536 | 0.057536 | -1.258e-13 | -5.5678e-09 | -5.603e-09 | 0.0018181 | 0.049811 | -0.049843 | -1.1485e-13 | -3.215e-09 | 3.1947e-09 | 0.00056588 | -0.086566 | -0.08716 | -90.4509 | 0 | 0 | 89.5272 | -90.3413 | -90.3413 |  | 0 | 1.7373 | 1.7429 | 0.0066173 | 1.7358 | 1.7451 | 0 | -150.3112 | 149.9946 | 106.8154 | -150.425 | 149.895
Line_2 | 0 | 0 | 0 | 0.0049859 | 0.0049859 | 0.0049859 | 0 | 0 | 0 | 0.057572 | 0.057572 | 0.057572 | -8.3733e-12 | -5.5579e-09 | -5.6266e-09 | -0.00036368 | 0.050105 | -0.049609 | 2.8854e-11 | -3.2269e-09 | 3.1873e-09 | -0.00011349 | -0.086468 | -0.087365 | 0 | 0 | 0 | -90.5157 | -90.5157 | -90.5157 |  | 0.0081756 | 1.7353 | 1.7461 | 0.0066173 | 1.7358 | 1.7451 | 105.7324 | -150.474 | 149.8564 | 106.8154 | -150.425 | 149.895

## LG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.01495 | 0.014953 | 0.014953 | 0.019934 | 0.0099687 | 0.0099687 | 0.17263 | 0.17266 | 0.17266 | 0.23018 | 0.11511 | 0.11511 | 0.0011238 | 0.15029 | -0.14877 | -0.0014545 | -0.099916 | 0.099452 | 0.00046023 | -0.25941 | -0.26164 | -0.00045239 | 0.17303 | 0.17453 | 89.5267 | -90.4285 | -90.4285 | -90.4621 | 89.5715 | 89.5715 |  | 0.0070349 | 1.7363 | 1.7432 | 0.0066173 | 1.7358 | 1.7451 | 111.7965 | -150.3429 | 149.9499 | 106.8154 | -150.425 | 149.895
Line_1 | 0.029903 | 0 | 0 | 0.02492 | 0.0049828 | 0.0049828 | 0.34529 | 0 | 0 | 0.28775 | 0.057536 | 0.057536 | -1.258e-13 | -5.5678e-09 | -5.603e-09 | 0.0018181 | 0.049811 | -0.049843 | -1.1485e-13 | -3.215e-09 | 3.1947e-09 | 0.00056588 | -0.086566 | -0.08716 | -90.4509 | 0 | 0 | 89.5272 | -90.3413 | -90.3413 |  | 0 | 1.7373 | 1.7429 | 0.0066173 | 1.7358 | 1.7451 | 0 | -150.3112 | 149.9946 | 106.8154 | -150.425 | 149.895
Line_2 | 0 | 0 | 0 | 0.0049859 | 0.0049859 | 0.0049859 | 0 | 0 | 0 | 0.057572 | 0.057572 | 0.057572 | -8.3733e-12 | -5.5579e-09 | -5.6266e-09 | -0.00036368 | 0.050105 | -0.049609 | 2.8854e-11 | -3.2269e-09 | 3.1873e-09 | -0.00011349 | -0.086468 | -0.087365 | 0 | 0 | 0 | -90.5157 | -90.5157 | -90.5157 |  | 0.0081756 | 1.7353 | 1.7461 | 0.0066173 | 1.7358 | 1.7451 | 105.7324 | -150.474 | 149.8564 | 106.8154 | -150.425 | 149.895

## LG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.015143 | 0.015146 | 0.015146 | 0.020192 | 0.010098 | 0.010098 | 0.17486 | 0.17489 | 0.17489 | 0.23316 | 0.1166 | 0.1166 | 0.0034456 | 0.15336 | -0.1495 | -0.0045497 | -0.10196 | 0.099951 | 0.0027665 | -0.26302 | -0.26929 | -0.0035228 | 0.17545 | 0.17963 | 88.7693 | -91.1859 | -91.1859 | -91.2195 | 88.8141 | 88.8141 |  | 0.02527 | 1.7409 | 1.7611 | 0.024679 | 1.7404 | 1.763 | 127.5308 | -150.9412 | 149.7765 | 126.5305 | -151.0241 | 149.7208
Line_1 | 0.03029 | 0 | 0 | 0.025242 | 0.0050472 | 0.0050472 | 0.34975 | 0 | 0 | 0.29147 | 0.05828 | 0.05828 | -0.0045873 | -5.6454e-09 | -5.7669e-09 | 0.0056869 | 0.050829 | -0.050097 | -0.0045873 | -3.2808e-09 | 3.2107e-09 | 0.004405 | -0.087773 | -0.089709 | -91.2083 | 0 | 0 | 88.7698 | -91.0987 | -91.0987 |  | 0.018548 | 1.7419 | 1.7608 | 0.024679 | 1.7404 | 1.763 | 133.7917 | -150.9092 | 149.8214 | 126.5305 | -151.0241 | 149.7208
Line_2 | 0 | 0 | 0 | 0.0050503 | 0.0050503 | 0.0050503 | 0 | 0 | 0 | 0.058316 | 0.058316 | 0.058316 | -5.7412e-11 | -5.6353e-09 | -5.7908e-09 | -0.0011371 | 0.051127 | -0.049855 | 7.8427e-11 | -3.2927e-09 | 3.2029e-09 | -0.00088217 | -0.087673 | -0.089917 | 0 | 0 | 0 | -91.2731 | -91.2731 | -91.2731 |  | 0.026111 | 1.7399 | 1.7641 | 0.024679 | 1.7404 | 1.763 | 124.9984 | -151.0735 | 149.6818 | 126.5305 | -151.0241 | 149.7208

## LG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.015143 | 0.015146 | 0.015146 | 0.020192 | 0.010098 | 0.010098 | 0.17486 | 0.17489 | 0.17489 | 0.23316 | 0.1166 | 0.1166 | 0.0034456 | 0.15336 | -0.1495 | -0.0045497 | -0.10196 | 0.099951 | 0.0027665 | -0.26302 | -0.26929 | -0.0035228 | 0.17545 | 0.17963 | 88.7693 | -91.1859 | -91.1859 | -91.2195 | 88.8141 | 88.8141 |  | 0.02527 | 1.7409 | 1.7611 | 0.024679 | 1.7404 | 1.763 | 127.5308 | -150.9412 | 149.7765 | 126.5305 | -151.0241 | 149.7208
Line_1 | 0.03029 | 0 | 0 | 0.025242 | 0.0050472 | 0.0050472 | 0.34975 | 0 | 0 | 0.29147 | 0.05828 | 0.05828 | -0.0045873 | -5.6454e-09 | -5.7669e-09 | 0.0056869 | 0.050829 | -0.050097 | -0.0045873 | -3.2808e-09 | 3.2107e-09 | 0.004405 | -0.087773 | -0.089709 | -91.2083 | 0 | 0 | 88.7698 | -91.0987 | -91.0987 |  | 0.018548 | 1.7419 | 1.7608 | 0.024679 | 1.7404 | 1.763 | 133.7917 | -150.9092 | 149.8214 | 126.5305 | -151.0241 | 149.7208
Line_2 | 0 | 0 | 0 | 0.0050503 | 0.0050503 | 0.0050503 | 0 | 0 | 0 | 0.058316 | 0.058316 | 0.058316 | -5.7412e-11 | -5.6353e-09 | -5.7908e-09 | -0.0011371 | 0.051127 | -0.049855 | 7.8427e-11 | -3.2927e-09 | 3.2029e-09 | -0.00088217 | -0.087673 | -0.089917 | 0 | 0 | 0 | -91.2731 | -91.2731 | -91.2731 |  | 0.026111 | 1.7399 | 1.7641 | 0.024679 | 1.7404 | 1.763 | 124.9984 | -151.0735 | 149.6818 | 126.5305 | -151.0241 | 149.7208

## LLG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.0081859 | 2.9953 | 2.9953 | 0.0054573 | 2.9962 | 2.9945 | 0.094523 | 34.587 | 34.587 | 0.063015 | 34.5969 | 34.577 | 0.00027356 | 9.3225 | 9.3391 | -0.00013937 | -4.6653 | -4.6656 | -0.15618 | 10.6304 | 10.5433 | 0.10415 | -5.3452 | -5.2417 | 89.858 | -161.7883 | 18.2118 | -90.142 | 18.2612 | -161.8378 |  | 1.6523 | 0.4088 | 0.40723 | 1.6527 | 0.20507 | 0.20295 | -0.041671 | -113.0378 | 66.6777 | -0.065361 | -112.8536 | 66.4906
Line_1 | 0 | 2.9979 | 2.9928 | 0.0027278 | 2.997 | 2.9936 | 0 | 34.6169 | 34.5573 | 0.031498 | 34.6069 | 34.5671 | -3.3474e-09 | 6.2813e-11 | 5.5903e-11 | 2.8395e-05 | 4.6713 | 4.6597 | -3.3482e-12 | -3.8717e-11 | 3.0683e-11 | -0.052057 | 5.3427 | 5.2443 | 0 | 18.3602 | -161.937 | 89.9034 | -161.6893 | 18.1126 |  | 1.6525 | 0 | 0 | 1.6527 | 0.20507 | 0.20295 | -0.028439 | 0 | 0 | -0.065361 | -112.8536 | 66.4906
Line_2 | 0 | 0 | 0 | 0.0027295 | 0.0027295 | 0.0027295 | 0 | 0 | 0 | 0.031518 | 0.031518 | 0.031518 | -3.3508e-09 | 6.6716e-10 | 3.3438e-10 | 0.00011097 | -0.0059641 | 0.0058738 | -9.3844e-12 | 1.0438e-10 | -6.578e-10 | -0.052089 | 0.0024907 | -0.0025323 | 0 | 0 | 0 | 89.8126 | 89.8126 | 89.8126 |  | 1.6529 | 0.20541 | 0.20262 | 1.6527 | 0.20507 | 0.20295 | -0.080517 | -112.7619 | 66.3966 | -0.065361 | -112.8536 | 66.4906

## LLG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.0081859 | 2.9953 | 2.9953 | 0.0054573 | 2.9962 | 2.9945 | 0.094523 | 34.587 | 34.587 | 0.063015 | 34.5969 | 34.577 | 0.00027356 | 9.3225 | 9.3391 | -0.00013937 | -4.6653 | -4.6656 | -0.15618 | 10.6304 | 10.5433 | 0.10415 | -5.3452 | -5.2417 | 89.858 | -161.7883 | 18.2118 | -90.142 | 18.2612 | -161.8378 |  | 1.6523 | 0.4088 | 0.40723 | 1.6527 | 0.20507 | 0.20295 | -0.041671 | -113.0378 | 66.6777 | -0.065361 | -112.8536 | 66.4906
Line_1 | 0 | 2.9979 | 2.9928 | 0.0027278 | 2.997 | 2.9936 | 0 | 34.6169 | 34.5573 | 0.031498 | 34.6069 | 34.5671 | -3.3474e-09 | 6.2813e-11 | 5.5903e-11 | 2.8395e-05 | 4.6713 | 4.6597 | -3.3482e-12 | -3.8717e-11 | 3.0683e-11 | -0.052057 | 5.3427 | 5.2443 | 0 | 18.3602 | -161.937 | 89.9034 | -161.6893 | 18.1126 |  | 1.6525 | 0 | 0 | 1.6527 | 0.20507 | 0.20295 | -0.028439 | 0 | 0 | -0.065361 | -112.8536 | 66.4906
Line_2 | 0 | 0 | 0 | 0.0027295 | 0.0027295 | 0.0027295 | 0 | 0 | 0 | 0.031518 | 0.031518 | 0.031518 | -3.3508e-09 | 6.6716e-10 | 3.3438e-10 | 0.00011097 | -0.0059641 | 0.0058738 | -9.3844e-12 | 1.0438e-10 | -6.578e-10 | -0.052089 | 0.0024907 | -0.0025323 | 0 | 0 | 0 | 89.8126 | 89.8126 | 89.8126 |  | 1.6529 | 0.20541 | 0.20262 | 1.6527 | 0.20507 | 0.20295 | -0.080517 | -112.7619 | 66.3966 | -0.065361 | -112.8536 | 66.4906

## LLG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.0082387 | 1.0495 | 1.0495 | 0.0054925 | 1.0512 | 1.0479 | 0.095132 | 12.119 | 12.119 | 0.063421 | 12.1378 | 12.1002 | 0.00095592 | 6.6461 | 6.6603 | -0.00059372 | -6.0978 | -6.0633 | -0.15752 | 6.8834 | 6.7314 | 0.10504 | -6.2337 | -6.0816 | 89.4854 | -144.0862 | 35.9139 | -90.5146 | 36.0342 | -144.2069 |  | 1.6558 | 0.78952 | 0.78138 | 1.6563 | 0.71843 | 0.70972 | -0.16692 | -98.0813 | 81.2182 | -0.19078 | -98.3342 | 80.8791
Line_1 | 0 | 1.0544 | 1.0447 | 0.0027454 | 1.0528 | 1.0463 | 0 | 12.1757 | 12.0627 | 0.031701 | 12.1568 | 12.0814 | -3.3762e-09 | -5.5593 | -5.4566 | 0.00025514 | 6.1203 | 6.0411 | -1.7946e-11 | -5.5593 | -5.4566 | -0.052504 | 6.2306 | 6.0849 | 0 | 36.2739 | -144.4496 | 89.5308 | -143.8458 | 35.672 |  | 1.656 | 0.64571 | 0.63972 | 1.6563 | 0.71843 | 0.70972 | -0.15366 | -98.7261 | 80.5504 | -0.19078 | -98.3342 | 80.8791
Line_2 | 0 | 0 | 0 | 0.0027471 | 0.0027471 | 0.0027471 | 0 | 0 | 0 | 0.031721 | 0.031721 | 0.031721 | -3.3796e-09 | 7.9947e-10 | 3.7412e-10 | 0.00033857 | -0.02258 | 0.022262 | -2.4035e-11 | 1.0713e-09 | -1.8059e-09 | -0.052537 | 0.0030827 | -0.0033513 | 0 | 0 | 0 | 89.44 | 89.44 | 89.44 |  | 1.6564 | 0.71884 | 0.70931 | 1.6563 | 0.71843 | 0.70972 | -0.20603 | -98.3157 | 80.8599 | -0.19078 | -98.3342 | 80.8791

## LLG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.0082387 | 1.0495 | 1.0495 | 0.0054925 | 1.0512 | 1.0479 | 0.095132 | 12.119 | 12.119 | 0.063421 | 12.1378 | 12.1002 | 0.00095592 | 6.6461 | 6.6603 | -0.00059372 | -6.0978 | -6.0633 | -0.15752 | 6.8834 | 6.7314 | 0.10504 | -6.2337 | -6.0816 | 89.4854 | -144.0862 | 35.9139 | -90.5146 | 36.0342 | -144.2069 |  | 1.6558 | 0.78952 | 0.78138 | 1.6563 | 0.71843 | 0.70972 | -0.16692 | -98.0813 | 81.2182 | -0.19078 | -98.3342 | 80.8791
Line_1 | 0 | 1.0544 | 1.0447 | 0.0027454 | 1.0528 | 1.0463 | 0 | 12.1757 | 12.0627 | 0.031701 | 12.1568 | 12.0814 | -3.3762e-09 | -5.5593 | -5.4566 | 0.00025514 | 6.1203 | 6.0411 | -1.7946e-11 | -5.5593 | -5.4566 | -0.052504 | 6.2306 | 6.0849 | 0 | 36.2739 | -144.4496 | 89.5308 | -143.8458 | 35.672 |  | 1.656 | 0.64571 | 0.63972 | 1.6563 | 0.71843 | 0.70972 | -0.15366 | -98.7261 | 80.5504 | -0.19078 | -98.3342 | 80.8791
Line_2 | 0 | 0 | 0 | 0.0027471 | 0.0027471 | 0.0027471 | 0 | 0 | 0 | 0.031721 | 0.031721 | 0.031721 | -3.3796e-09 | 7.9947e-10 | 3.7412e-10 | 0.00033857 | -0.02258 | 0.022262 | -2.4035e-11 | 1.0713e-09 | -1.8059e-09 | -0.052537 | 0.0030827 | -0.0033513 | 0 | 0 | 0 | 89.44 | 89.44 | 89.44 |  | 1.6564 | 0.71884 | 0.70931 | 1.6563 | 0.71843 | 0.70972 | -0.20603 | -98.3157 | 80.8599 | -0.19078 | -98.3342 | 80.8791

## LLG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.007442 | 2.3976 | 2.3976 | 0.0049613 | 2.3989 | 2.3964 | 0.085933 | 27.6856 | 27.6856 | 0.057288 | 27.7003 | 27.671 | 0.0004341 | 11.4932 | 11.4648 | -0.00022115 | -5.7668 | -5.7124 | -0.12908 | 6.838 | 6.7289 | 0.086077 | -3.4564 | -3.3271 | 89.7295 | -149.5745 | 30.4256 | -90.2705 | 30.4765 | -149.6254 |  | 1.5021 | 0.48305 | 0.48016 | 1.5025 | 0.24272 | 0.2389 | -0.077771 | -118.8236 | 60.8352 | -0.12325 | -118.5864 | 60.5926
Line_1 | 0 | 2.4015 | 2.3939 | 0.0024799 | 2.4002 | 2.3951 | 0 | 27.7296 | 27.6418 | 0.028635 | 27.715 | 27.6563 | -2.767e-09 | -1.3288e-10 | 1.1522e-11 | 4.5058e-05 | 5.7729 | 5.7064 | -5.0217e-12 | -1.0275e-10 | -1.5035e-10 | -0.043025 | 3.4531 | 3.3304 | 0 | 30.5782 | -149.7275 | 89.8167 | -149.4727 | 30.3236 |  | 1.5023 | 0 | 0 | 1.5025 | 0.24272 | 0.2389 | -0.052363 | 0 | 0 | -0.12325 | -118.5864 | 60.5926
Line_2 | 0 | 0 | 0 | 0.0024814 | 0.0024814 | 0.0024814 | 0 | 0 | 0 | 0.028653 | 0.028653 | 0.028653 | -2.7697e-09 | 6.7476e-10 | 2.3486e-10 | 0.00017609 | -0.0061274 | 0.0059841 | -1.4673e-11 | 2.3842e-11 | -7.5312e-10 | -0.043052 | 0.0032895 | -0.0033239 | 0 | 0 | 0 | 89.6424 | 89.6424 | 89.6424 |  | 1.5027 | 0.24331 | 0.23831 | 1.5025 | 0.24272 | 0.2389 | -0.15235 | -118.4688 | 60.4705 | -0.12325 | -118.5864 | 60.5926

## LLG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.007442 | 2.3976 | 2.3976 | 0.0049613 | 2.3989 | 2.3964 | 0.085933 | 27.6856 | 27.6856 | 0.057288 | 27.7003 | 27.671 | 0.0004341 | 11.4932 | 11.4648 | -0.00022115 | -5.7668 | -5.7124 | -0.12908 | 6.838 | 6.7289 | 0.086077 | -3.4564 | -3.3271 | 89.7295 | -149.5745 | 30.4256 | -90.2705 | 30.4765 | -149.6254 |  | 1.5021 | 0.48305 | 0.48016 | 1.5025 | 0.24272 | 0.2389 | -0.077771 | -118.8236 | 60.8352 | -0.12325 | -118.5864 | 60.5926
Line_1 | 0 | 2.4015 | 2.3939 | 0.0024799 | 2.4002 | 2.3951 | 0 | 27.7296 | 27.6418 | 0.028635 | 27.715 | 27.6563 | -2.767e-09 | -1.3288e-10 | 1.1522e-11 | 4.5058e-05 | 5.7729 | 5.7064 | -5.0217e-12 | -1.0275e-10 | -1.5035e-10 | -0.043025 | 3.4531 | 3.3304 | 0 | 30.5782 | -149.7275 | 89.8167 | -149.4727 | 30.3236 |  | 1.5023 | 0 | 0 | 1.5025 | 0.24272 | 0.2389 | -0.052363 | 0 | 0 | -0.12325 | -118.5864 | 60.5926
Line_2 | 0 | 0 | 0 | 0.0024814 | 0.0024814 | 0.0024814 | 0 | 0 | 0 | 0.028653 | 0.028653 | 0.028653 | -2.7697e-09 | 6.7476e-10 | 2.3486e-10 | 0.00017609 | -0.0061274 | 0.0059841 | -1.4673e-11 | 2.3842e-11 | -7.5312e-10 | -0.043052 | 0.0032895 | -0.0033239 | 0 | 0 | 0 | 89.6424 | 89.6424 | 89.6424 |  | 1.5027 | 0.24331 | 0.23831 | 1.5025 | 0.24272 | 0.2389 | -0.15235 | -118.4688 | 60.4705 | -0.12325 | -118.5864 | 60.5926

## LLG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.0074898 | 0.89629 | 0.89629 | 0.0049932 | 0.89791 | 0.89468 | 0.086485 | 10.3495 | 10.3495 | 0.057657 | 10.3681 | 10.3309 | 0.0010008 | 5.6255 | 5.616 | -0.0005981 | -4.8453 | -4.7925 | -0.13018 | 5.0313 | 4.898 | 0.086814 | -4.5598 | -4.4217 | 89.356 | -140.3978 | 39.6025 | -90.644 | 39.7238 | -140.5195 |  | 1.5053 | 0.72924 | 0.72002 | 1.5057 | 0.64172 | 0.63119 | -0.20349 | -98.5895 | 80.6954 | -0.24923 | -97.0148 | 82.176
Line_1 | 0 | 0.90115 | 0.89147 | 0.0024958 | 0.89953 | 0.89307 | 0 | 10.4056 | 10.2938 | 0.028819 | 10.3869 | 10.3123 | -2.7907e-09 | -4.0604 | -3.9736 | 0.00023291 | 4.8637 | 4.7744 | -1.7143e-11 | -4.0604 | -3.9736 | -0.043394 | 4.5578 | 4.4239 | 0 | 39.9657 | -140.7649 | 89.4432 | -140.1552 | 39.3581 |  | 1.5055 | 0.55184 | 0.54591 | 1.5057 | 0.64172 | 0.63119 | -0.178 | -95.0343 | 84.2351 | -0.24923 | -97.0148 | 82.176
Line_2 | 0 | 0 | 0 | 0.0024974 | 0.0024974 | 0.0024974 | 0 | 0 | 0 | 0.028837 | 0.028837 | 0.028837 | -2.7933e-09 | 6.5486e-10 | 3.6802e-10 | 0.00036519 | -0.018395 | 0.018063 | -2.6841e-11 | 9.2071e-10 | -1.4183e-09 | -0.04342 | 0.0020255 | -0.0022475 | 0 | 0 | 0 | 89.2689 | 89.2689 | 89.2689 |  | 1.5059 | 0.64247 | 0.63045 | 1.5057 | 0.64172 | 0.63119 | -0.27848 | -96.9932 | 82.1531 | -0.24923 | -97.0148 | 82.176

## LLG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.0074898 | 0.89629 | 0.89629 | 0.0049932 | 0.89791 | 0.89468 | 0.086485 | 10.3495 | 10.3495 | 0.057657 | 10.3681 | 10.3309 | 0.0010008 | 5.6255 | 5.616 | -0.0005981 | -4.8453 | -4.7925 | -0.13018 | 5.0313 | 4.898 | 0.086814 | -4.5598 | -4.4217 | 89.356 | -140.3978 | 39.6025 | -90.644 | 39.7238 | -140.5195 |  | 1.5053 | 0.72924 | 0.72002 | 1.5057 | 0.64172 | 0.63119 | -0.20349 | -98.5895 | 80.6954 | -0.24923 | -97.0148 | 82.176
Line_1 | 0 | 0.90115 | 0.89147 | 0.0024958 | 0.89953 | 0.89307 | 0 | 10.4056 | 10.2938 | 0.028819 | 10.3869 | 10.3123 | -2.7907e-09 | -4.0604 | -3.9736 | 0.00023291 | 4.8637 | 4.7744 | -1.7143e-11 | -4.0604 | -3.9736 | -0.043394 | 4.5578 | 4.4239 | 0 | 39.9657 | -140.7649 | 89.4432 | -140.1552 | 39.3581 |  | 1.5055 | 0.55184 | 0.54591 | 1.5057 | 0.64172 | 0.63119 | -0.178 | -95.0343 | 84.2351 | -0.24923 | -97.0148 | 82.176
Line_2 | 0 | 0 | 0 | 0.0024974 | 0.0024974 | 0.0024974 | 0 | 0 | 0 | 0.028837 | 0.028837 | 0.028837 | -2.7933e-09 | 6.5486e-10 | 3.6802e-10 | 0.00036519 | -0.018395 | 0.018063 | -2.6841e-11 | 9.2071e-10 | -1.4183e-09 | -0.04342 | 0.0020255 | -0.0022475 | 0 | 0 | 0 | 89.2689 | 89.2689 | 89.2689 |  | 1.5059 | 0.64247 | 0.63045 | 1.5057 | 0.64172 | 0.63119 | -0.27848 | -96.9932 | 82.1531 | -0.24923 | -97.0148 | 82.176