## LLL_max_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 1.7394 | 1.7394 | 4.0301 | 0 | 60.2556 | 60.2556 | -1e-07 | 4.72 | -1e-07 | 5.3553 | 107.5423 | -72.4577 | 0 | 0.11847 | 0 | -23.8492
Line_1 | 0.86972 | 0.86972 | 0 | 0 | 30.1278 | 30.1278 | 3.54 | -2.36 | 4.0165 | -2.6777 | -72.4577 | 107.5423 | 0.1777 | 0.11847 | -23.8492 | -23.8492
Line_2 | 0.86972 | 0.86972 | 0 | 0 | 30.1278 | 30.1278 | 3.54 | -2.36 | 4.0165 | -2.6777 | -72.4577 | 107.5423 | 0.1777 | 0.11847 | -23.8492 | -23.8492

## LLL_max_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 1.7394 | 1.7394 | 4.0301 | 0 | 60.2556 | 60.2556 | -1e-07 | 4.72 | -1e-07 | 5.3553 | 107.5423 | -72.4577 | 0 | 0.11847 | 0 | -23.8492
Line_1 | 0.86972 | 0.86972 | 0 | 0 | 30.1278 | 30.1278 | 3.54 | -2.36 | 4.0165 | -2.6777 | -72.4577 | 107.5423 | 0.1777 | 0.11847 | -23.8492 | -23.8492
Line_2 | 0.86972 | 0.86972 | 0 | 0 | 30.1278 | 30.1278 | 3.54 | -2.36 | 4.0165 | -2.6777 | -72.4577 | 107.5423 | 0.1777 | 0.11847 | -23.8492 | -23.8492

## LLL_max_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.51746 | 0.51746 | 1.048 | 0 | 17.9254 | 17.9254 | -10.4881 | 10.9059 | -13.3195 | 13.7934 | 120.4894 | -59.5106 | 0.94576 | 0.98095 | -7.7285 | -7.8425
Line_1 | 0.25873 | 0.25873 | 0 | 0 | 8.9627 | 8.9627 | 5.5574 | -5.4529 | 7.0152 | -6.8967 | -59.5106 | 120.4894 | 0.99855 | 0.98095 | -7.8965 | -7.8425
Line_2 | 0.25873 | 0.25873 | 0 | 0 | 8.9627 | 8.9627 | 5.5574 | -5.4529 | 7.0152 | -6.8967 | -59.5106 | 120.4894 | 0.99855 | 0.98095 | -7.8965 | -7.8425

## LLL_max_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.51746 | 0.51746 | 1.048 | 0 | 17.9254 | 17.9254 | -10.4881 | 10.9059 | -13.3195 | 13.7934 | 120.4894 | -59.5106 | 0.94576 | 0.98095 | -7.7285 | -7.8425
Line_1 | 0.25873 | 0.25873 | 0 | 0 | 8.9627 | 8.9627 | 5.5574 | -5.4529 | 7.0152 | -6.8967 | -59.5106 | 120.4894 | 0.99855 | 0.98095 | -7.8965 | -7.8425
Line_2 | 0.25873 | 0.25873 | 0 | 0 | 8.9627 | 8.9627 | 5.5574 | -5.4529 | 7.0152 | -6.8967 | -59.5106 | 120.4894 | 0.99855 | 0.98095 | -7.8965 | -7.8425

## LLL_min_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 1.3783 | 1.3783 | 3.412 | 0 | 47.7473 | 47.7473 | -1e-07 | 5.6904 | -1e-07 | 3.3627 | 114.7975 | -65.2025 | 0 | 0.13843 | 0 | -34.6217
Line_1 | 0.68917 | 0.68917 | 0 | 0 | 23.8737 | 23.8737 | 4.2678 | -2.8452 | 2.522 | -1.6814 | -65.2025 | 114.7975 | 0.20765 | 0.13843 | -34.6217 | -34.6217
Line_2 | 0.68917 | 0.68917 | 0 | 0 | 23.8737 | 23.8737 | 4.2678 | -2.8452 | 2.522 | -1.6814 | -65.2025 | 114.7975 | 0.20765 | 0.13843 | -34.6217 | -34.6217

## LLL_min_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 1.3783 | 1.3783 | 3.412 | 0 | 47.7473 | 47.7473 | -1e-07 | 5.6904 | -1e-07 | 3.3627 | 114.7975 | -65.2025 | 0 | 0.13843 | 0 | -34.6217
Line_1 | 0.68917 | 0.68917 | 0 | 0 | 23.8737 | 23.8737 | 4.2678 | -2.8452 | 2.522 | -1.6814 | -65.2025 | 114.7975 | 0.20765 | 0.13843 | -34.6217 | -34.6217
Line_2 | 0.68917 | 0.68917 | 0 | 0 | 23.8737 | 23.8737 | 4.2678 | -2.8452 | 2.522 | -1.6814 | -65.2025 | 114.7975 | 0.20765 | 0.13843 | -34.6217 | -34.6217

## LLL_min_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.30266 | 0.30266 | 0.74922 | 0 | 10.4846 | 10.4846 | -7.5715 | 7.8458 | -3.9965 | 4.1586 | 144.5132 | -35.4868 | 0.81658 | 0.84694 | -7.6601 | -7.5613
Line_1 | 0.15133 | 0.15133 | 0 | 0 | 5.2423 | 5.2423 | 3.9915 | -3.9229 | 2.1199 | -2.0793 | -35.4868 | 144.5132 | 0.86212 | 0.84694 | -7.5145 | -7.5613
Line_2 | 0.15133 | 0.15133 | 0 | 0 | 5.2423 | 5.2423 | 3.9915 | -3.9229 | 2.1199 | -2.0793 | -35.4868 | 144.5132 | 0.86212 | 0.84694 | -7.5145 | -7.5613

## LLL_min_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.30266 | 0.30266 | 0.74922 | 0 | 10.4846 | 10.4846 | -7.5715 | 7.8458 | -3.9965 | 4.1586 | 144.5132 | -35.4868 | 0.81658 | 0.84694 | -7.6601 | -7.5613
Line_1 | 0.15133 | 0.15133 | 0 | 0 | 5.2423 | 5.2423 | 3.9915 | -3.9229 | 2.1199 | -2.0793 | -35.4868 | 144.5132 | 0.86212 | 0.84694 | -7.5145 | -7.5613
Line_2 | 0.15133 | 0.15133 | 0 | 0 | 5.2423 | 5.2423 | 3.9915 | -3.9229 | 2.1199 | -2.0793 | -35.4868 | 144.5132 | 0.86212 | 0.84694 | -7.5145 | -7.5613

## LL_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.32048 | 1.5098 | 1.3931 | 0.32048 | 1.5098 | 1.3931 | 3.7006 | 17.4334 | 16.0862 | 3.7006 | 17.4334 | 16.0862 | -2.2014 | -10.0544 | 8.9537 | 2.2548 | 11.2397 | -7.9445 | -3.6682 | 0.67371 | -2.5078 | 3.7288 | 0.67115 | 3.6529 | 122.5535 | 5.4174 | -162.7693 | -57.4465 | -174.5826 | 17.2307 | 1.1561 | 0.57803 | 0.57803 | 1.1775 | 0.64587 | 0.54357 | 1.5839 | -178.4161 | -178.4161 | 1.3918 | -171.1654 | 172.538
Line_1 | 0.16024 | 0.75489 | 0.69655 | 0.16024 | 0.75489 | 0.69655 | 1.8503 | 8.7167 | 8.0431 | 1.8503 | 8.7167 | 8.0431 | 1.1408 | 5.9162 | -3.72 | -1.1274 | -5.6199 | 3.9723 | 1.8795 | 0.67179 | 2.1127 | -1.8644 | -0.33558 | -1.8264 | -57.4465 | -174.5826 | 17.2307 | 122.5535 | 5.4174 | -162.7693 | 1.1883 | 0.68308 | 0.53189 | 1.1775 | 0.64587 | 0.54357 | 1.2983 | -168.1044 | 167.6371 | 1.3918 | -171.1654 | 172.538
Line_2 | 0.16024 | 0.75489 | 0.69655 | 0.16024 | 0.75489 | 0.69655 | 1.8503 | 8.7167 | 8.0431 | 1.8503 | 8.7167 | 8.0431 | 1.1408 | 5.9162 | -3.72 | -1.1274 | -5.6199 | 3.9723 | 1.8795 | 0.67179 | 2.1127 | -1.8644 | -0.33558 | -1.8264 | -57.4465 | -174.5826 | 17.2307 | 122.5535 | 5.4174 | -162.7693 | 1.1883 | 0.68308 | 0.53189 | 1.1775 | 0.64587 | 0.54357 | 1.2983 | -168.1044 | 167.6371 | 1.3918 | -171.1654 | 172.538

## LL_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.32048 | 1.5098 | 1.3931 | 0.32048 | 1.5098 | 1.3931 | 3.7006 | 17.4334 | 16.0862 | 3.7006 | 17.4334 | 16.0862 | -2.2014 | -10.0544 | 8.9537 | 2.2548 | 11.2397 | -7.9445 | -3.6682 | 0.67371 | -2.5078 | 3.7288 | 0.67115 | 3.6529 | 122.5535 | 5.4174 | -162.7693 | -57.4465 | -174.5826 | 17.2307 | 1.1561 | 0.57803 | 0.57803 | 1.1775 | 0.64587 | 0.54357 | 1.5839 | -178.4161 | -178.4161 | 1.3918 | -171.1654 | 172.538
Line_1 | 0.16024 | 0.75489 | 0.69655 | 0.16024 | 0.75489 | 0.69655 | 1.8503 | 8.7167 | 8.0431 | 1.8503 | 8.7167 | 8.0431 | 1.1408 | 5.9162 | -3.72 | -1.1274 | -5.6199 | 3.9723 | 1.8795 | 0.67179 | 2.1127 | -1.8644 | -0.33558 | -1.8264 | -57.4465 | -174.5826 | 17.2307 | 122.5535 | 5.4174 | -162.7693 | 1.1883 | 0.68308 | 0.53189 | 1.1775 | 0.64587 | 0.54357 | 1.2983 | -168.1044 | 167.6371 | 1.3918 | -171.1654 | 172.538
Line_2 | 0.16024 | 0.75489 | 0.69655 | 0.16024 | 0.75489 | 0.69655 | 1.8503 | 8.7167 | 8.0431 | 1.8503 | 8.7167 | 8.0431 | 1.1408 | 5.9162 | -3.72 | -1.1274 | -5.6199 | 3.9723 | 1.8795 | 0.67179 | 2.1127 | -1.8644 | -0.33558 | -1.8264 | -57.4465 | -174.5826 | 17.2307 | 122.5535 | 5.4174 | -162.7693 | 1.1883 | 0.68308 | 0.53189 | 1.1775 | 0.64587 | 0.54357 | 1.2983 | -168.1044 | 167.6371 | 1.3918 | -171.1654 | 172.538

## LL_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.23496 | 0.62005 | 0.6638 | 0.23496 | 0.62005 | 0.6638 | 2.7131 | 7.1597 | 7.6649 | 2.7131 | 7.1597 | 7.6649 | -0.87371 | -6.4592 | -0.64541 | 0.90242 | 6.6591 | 0.87454 | -2.9829 | -3.0836 | -5.9544 | 3.0155 | 3.3104 | 6.2144 | 106.904 | 17.0933 | -142.1771 | -73.096 | -162.9067 | 37.8229 | 1.1456 | 0.99969 | 0.78139 | 1.1602 | 1.0387 | 0.81874 | 0.57818 | -137.3873 | 121.6367 | 0.24336 | -136.4737 | 119.8124
Line_1 | 0.11748 | 0.31003 | 0.3319 | 0.11748 | 0.31003 | 0.3319 | 1.3565 | 3.5799 | 3.8325 | 1.3565 | 3.5799 | 3.8325 | 0.45839 | 3.3796 | 0.49455 | -0.45121 | -3.3296 | -0.43727 | 1.5159 | 1.7119 | 3.1722 | -1.5077 | -1.6552 | -3.1072 | -73.096 | -162.9067 | 37.8229 | 106.904 | 17.0933 | -142.1771 | 1.1674 | 1.0583 | 0.83771 | 1.1602 | 1.0387 | 0.81874 | 0.079071 | -136.0422 | 118.9617 | 0.24336 | -136.4737 | 119.8124
Line_2 | 0.11748 | 0.31003 | 0.3319 | 0.11748 | 0.31003 | 0.3319 | 1.3565 | 3.5799 | 3.8325 | 1.3565 | 3.5799 | 3.8325 | 0.45839 | 3.3796 | 0.49455 | -0.45121 | -3.3296 | -0.43727 | 1.5159 | 1.7119 | 3.1722 | -1.5077 | -1.6552 | -3.1072 | -73.096 | -162.9067 | 37.8229 | 106.904 | 17.0933 | -142.1771 | 1.1674 | 1.0583 | 0.83771 | 1.1602 | 1.0387 | 0.81874 | 0.079071 | -136.0422 | 118.9617 | 0.24336 | -136.4737 | 119.8124

## LL_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.23496 | 0.62005 | 0.6638 | 0.23496 | 0.62005 | 0.6638 | 2.7131 | 7.1597 | 7.6649 | 2.7131 | 7.1597 | 7.6649 | -0.87371 | -6.4592 | -0.64541 | 0.90242 | 6.6591 | 0.87454 | -2.9829 | -3.0836 | -5.9544 | 3.0155 | 3.3104 | 6.2144 | 106.904 | 17.0933 | -142.1771 | -73.096 | -162.9067 | 37.8229 | 1.1456 | 0.99969 | 0.78139 | 1.1602 | 1.0387 | 0.81874 | 0.57818 | -137.3873 | 121.6367 | 0.24336 | -136.4737 | 119.8124
Line_1 | 0.11748 | 0.31003 | 0.3319 | 0.11748 | 0.31003 | 0.3319 | 1.3565 | 3.5799 | 3.8325 | 1.3565 | 3.5799 | 3.8325 | 0.45839 | 3.3796 | 0.49455 | -0.45121 | -3.3296 | -0.43727 | 1.5159 | 1.7119 | 3.1722 | -1.5077 | -1.6552 | -3.1072 | -73.096 | -162.9067 | 37.8229 | 106.904 | 17.0933 | -142.1771 | 1.1674 | 1.0583 | 0.83771 | 1.1602 | 1.0387 | 0.81874 | 0.079071 | -136.0422 | 118.9617 | 0.24336 | -136.4737 | 119.8124
Line_2 | 0.11748 | 0.31003 | 0.3319 | 0.11748 | 0.31003 | 0.3319 | 1.3565 | 3.5799 | 3.8325 | 1.3565 | 3.5799 | 3.8325 | 0.45839 | 3.3796 | 0.49455 | -0.45121 | -3.3296 | -0.43727 | 1.5159 | 1.7119 | 3.1722 | -1.5077 | -1.6552 | -3.1072 | -73.096 | -162.9067 | 37.8229 | 106.904 | 17.0933 | -142.1771 | 1.1674 | 1.0583 | 0.83771 | 1.1602 | 1.0387 | 0.81874 | 0.079071 | -136.0422 | 118.9617 | 0.24336 | -136.4737 | 119.8124

## LL_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.14393 | 1.2145 | 1.0782 | 0.14393 | 1.2145 | 1.0782 | 1.662 | 14.0243 | 12.4494 | 1.662 | 14.0243 | 12.4494 | -1.664 | -6.8035 | 5.9715 | 1.6847 | 8.2762 | -4.811 | -0.085413 | 1.7696 | -1.8123 | 0.097635 | -0.89926 | 2.4981 | 178.781 | 16.2989 | -161.3982 | -1.219 | -163.7011 | 18.6018 | 1.0025 | 0.50126 | 0.50126 | 1.0154 | 0.59361 | 0.43543 | 1.7195 | -178.2805 | -178.2805 | 2.0979 | -169.9023 | 171.1612
Line_1 | 0.071965 | 0.60727 | 0.53908 | 0.071965 | 0.60727 | 0.53908 | 0.83098 | 7.0121 | 6.2247 | 0.83098 | 7.0121 | 6.2247 | 0.8475 | 4.5063 | -2.1153 | -0.84233 | -4.1381 | 2.4055 | 0.051873 | -0.23205 | 1.4205 | -0.048818 | 0.44963 | -1.2491 | -1.219 | -163.7011 | 18.6018 | 178.781 | 16.2989 | -161.3982 | 1.0218 | 0.6435 | 0.40934 | 1.0154 | 0.59361 | 0.43543 | 2.2836 | -166.649 | 164.7195 | 2.0979 | -169.9023 | 171.1612
Line_2 | 0.071965 | 0.60727 | 0.53908 | 0.071965 | 0.60727 | 0.53908 | 0.83098 | 7.0121 | 6.2247 | 0.83098 | 7.0121 | 6.2247 | 0.8475 | 4.5063 | -2.1153 | -0.84233 | -4.1381 | 2.4055 | 0.051873 | -0.23205 | 1.4205 | -0.048818 | 0.44963 | -1.2491 | -1.219 | -163.7011 | 18.6018 | 178.781 | 16.2989 | -161.3982 | 1.0218 | 0.6435 | 0.40934 | 1.0154 | 0.59361 | 0.43543 | 2.2836 | -166.649 | 164.7195 | 2.0979 | -169.9023 | 171.1612

## LL_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.14393 | 1.2145 | 1.0782 | 0.14393 | 1.2145 | 1.0782 | 1.662 | 14.0243 | 12.4494 | 1.662 | 14.0243 | 12.4494 | -1.664 | -6.8035 | 5.9715 | 1.6847 | 8.2762 | -4.811 | -0.085413 | 1.7696 | -1.8123 | 0.097635 | -0.89926 | 2.4981 | 178.781 | 16.2989 | -161.3982 | -1.219 | -163.7011 | 18.6018 | 1.0025 | 0.50126 | 0.50126 | 1.0154 | 0.59361 | 0.43543 | 1.7195 | -178.2805 | -178.2805 | 2.0979 | -169.9023 | 171.1612
Line_1 | 0.071965 | 0.60727 | 0.53908 | 0.071965 | 0.60727 | 0.53908 | 0.83098 | 7.0121 | 6.2247 | 0.83098 | 7.0121 | 6.2247 | 0.8475 | 4.5063 | -2.1153 | -0.84233 | -4.1381 | 2.4055 | 0.051873 | -0.23205 | 1.4205 | -0.048818 | 0.44963 | -1.2491 | -1.219 | -163.7011 | 18.6018 | 178.781 | 16.2989 | -161.3982 | 1.0218 | 0.6435 | 0.40934 | 1.0154 | 0.59361 | 0.43543 | 2.2836 | -166.649 | 164.7195 | 2.0979 | -169.9023 | 171.1612
Line_2 | 0.071965 | 0.60727 | 0.53908 | 0.071965 | 0.60727 | 0.53908 | 0.83098 | 7.0121 | 6.2247 | 0.83098 | 7.0121 | 6.2247 | 0.8475 | 4.5063 | -2.1153 | -0.84233 | -4.1381 | 2.4055 | 0.051873 | -0.23205 | 1.4205 | -0.048818 | 0.44963 | -1.2491 | -1.219 | -163.7011 | 18.6018 | 178.781 | 16.2989 | -161.3982 | 1.0218 | 0.6435 | 0.40934 | 1.0154 | 0.59361 | 0.43543 | 2.2836 | -166.649 | 164.7195 | 2.0979 | -169.9023 | 171.1612

## LL_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.053172 | 0.44869 | 0.3983 | 0.053172 | 0.44869 | 0.3983 | 0.61398 | 5.181 | 4.5992 | 0.61398 | 5.181 | 4.5992 | -0.55942 | -4.4702 | -0.65138 | 0.56224 | 4.6712 | 0.80977 | 0.2469 | -0.04336 | -3.0398 | -0.24523 | 0.16214 | 3.1334 | -155.5905 | 41.9274 | -135.7696 | 24.4095 | -138.0726 | 44.2304 | 0.99594 | 0.86284 | 0.67595 | 0.99906 | 0.90214 | 0.70368 | 0.59555 | -137.5168 | 122.1359 | 0.84456 | -136.0846 | 119.7405
Line_1 | 0.026586 | 0.22434 | 0.19915 | 0.026586 | 0.22434 | 0.19915 | 0.30699 | 2.5905 | 2.2996 | 0.30699 | 2.5905 | 2.2996 | 0.28183 | 2.3858 | 0.44448 | -0.28112 | -2.3356 | -0.40488 | -0.1222 | 0.11076 | 1.5901 | 0.12261 | -0.081069 | -1.5667 | 24.4095 | -138.0726 | 44.2304 | -155.5905 | 41.9274 | -135.7696 | 1.0006 | 0.92199 | 0.71798 | 0.99906 | 0.90214 | 0.70368 | 0.96848 | -135.4145 | 118.6132 | 0.84456 | -136.0846 | 119.7405
Line_2 | 0.026586 | 0.22434 | 0.19915 | 0.026586 | 0.22434 | 0.19915 | 0.30699 | 2.5905 | 2.2996 | 0.30699 | 2.5905 | 2.2996 | 0.28183 | 2.3858 | 0.44448 | -0.28112 | -2.3356 | -0.40488 | -0.1222 | 0.11076 | 1.5901 | 0.12261 | -0.081069 | -1.5667 | 24.4095 | -138.0726 | 44.2304 | -155.5905 | 41.9274 | -135.7696 | 1.0006 | 0.92199 | 0.71798 | 0.99906 | 0.90214 | 0.70368 | 0.96848 | -135.4145 | 118.6132 | 0.84456 | -136.0846 | 119.7405

## LL_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.053172 | 0.44869 | 0.3983 | 0.053172 | 0.44869 | 0.3983 | 0.61398 | 5.181 | 4.5992 | 0.61398 | 5.181 | 4.5992 | -0.55942 | -4.4702 | -0.65138 | 0.56224 | 4.6712 | 0.80977 | 0.2469 | -0.04336 | -3.0398 | -0.24523 | 0.16214 | 3.1334 | -155.5905 | 41.9274 | -135.7696 | 24.4095 | -138.0726 | 44.2304 | 0.99594 | 0.86284 | 0.67595 | 0.99906 | 0.90214 | 0.70368 | 0.59555 | -137.5168 | 122.1359 | 0.84456 | -136.0846 | 119.7405
Line_1 | 0.026586 | 0.22434 | 0.19915 | 0.026586 | 0.22434 | 0.19915 | 0.30699 | 2.5905 | 2.2996 | 0.30699 | 2.5905 | 2.2996 | 0.28183 | 2.3858 | 0.44448 | -0.28112 | -2.3356 | -0.40488 | -0.1222 | 0.11076 | 1.5901 | 0.12261 | -0.081069 | -1.5667 | 24.4095 | -138.0726 | 44.2304 | -155.5905 | 41.9274 | -135.7696 | 1.0006 | 0.92199 | 0.71798 | 0.99906 | 0.90214 | 0.70368 | 0.96848 | -135.4145 | 118.6132 | 0.84456 | -136.0846 | 119.7405
Line_2 | 0.026586 | 0.22434 | 0.19915 | 0.026586 | 0.22434 | 0.19915 | 0.30699 | 2.5905 | 2.2996 | 0.30699 | 2.5905 | 2.2996 | 0.28183 | 2.3858 | 0.44448 | -0.28112 | -2.3356 | -0.40488 | -0.1222 | 0.11076 | 1.5901 | 0.12261 | -0.081069 | -1.5667 | 24.4095 | -138.0726 | 44.2304 | -155.5905 | 41.9274 | -135.7696 | 1.0006 | 0.92199 | 0.71798 | 0.99906 | 0.90214 | 0.70368 | 0.96848 | -135.4145 | 118.6132 | 0.84456 | -136.0846 | 119.7405

## LG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.7627 | 0.69382 | 0.81759 | 1.7654 | 0.69685 | 0.81967 | 20.3534 | 8.0115 | 9.4407 | 20.3856 | 8.0465 | 9.4648 | 7.0378e-11 | -3.2815 | 15.9828 | 7.5511 | 5.7247 | -12.7789 | -7.4828e-11 | 10.8764 | -0.72092 | 3.7907 | -9.4464 | 0.98298 | 117.4727 | 106.9525 | 137.5582 | -62.5785 | -73.1332 | -42.6123 |  | 0 | 1.418 | 1.6947 | 0.41447 | 1.3727 | 1.3541 | 0 | -146.2587 | 134.9756 | -35.9219 | -131.9163 | 132.989
Line_1 | 0.88494 | 0.35067 | 0.41182 | 0.88272 | 0.34842 | 0.40984 | 10.2185 | 4.0492 | 4.7552 | 10.1928 | 4.0233 | 4.7324 | 5.6832 | 3.4893 | -5.6032 | -3.7756 | -2.8624 | 6.3895 | 2.8528 | -4.3833 | 0.55593 | -1.8953 | 4.7232 | -0.49149 | -62.5995 | -73.1186 | -42.7603 | 117.4215 | 106.8668 | 137.3877 |  | 0.6223 | 1.3836 | 1.1841 | 0.41447 | 1.3727 | 1.3541 | -35.9444 | -124.5974 | 131.5736 | -35.9219 | -131.9163 | 132.989
Line_2 | 0.88494 | 0.35067 | 0.41182 | 0.88272 | 0.34842 | 0.40984 | 10.2185 | 4.0492 | 4.7552 | 10.1928 | 4.0233 | 4.7324 | 5.6832 | 3.4893 | -5.6032 | -3.7756 | -2.8624 | 6.3895 | 2.8528 | -4.3833 | 0.55593 | -1.8953 | 4.7232 | -0.49149 | -62.5995 | -73.1186 | -42.7603 | 117.4215 | 106.8668 | 137.3877 |  | 0.6223 | 1.3836 | 1.1841 | 0.41447 | 1.3727 | 1.3541 | -35.9444 | -124.5974 | 131.5736 | -35.9219 | -131.9163 | 132.989

## LG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.7627 | 0.69382 | 0.81759 | 1.7654 | 0.69685 | 0.81967 | 20.3534 | 8.0115 | 9.4407 | 20.3856 | 8.0465 | 9.4648 | 7.0378e-11 | -3.2815 | 15.9828 | 7.5511 | 5.7247 | -12.7789 | -7.4828e-11 | 10.8764 | -0.72092 | 3.7907 | -9.4464 | 0.98298 | 117.4727 | 106.9525 | 137.5582 | -62.5785 | -73.1332 | -42.6123 |  | 0 | 1.418 | 1.6947 | 0.41447 | 1.3727 | 1.3541 | 0 | -146.2587 | 134.9756 | -35.9219 | -131.9163 | 132.989
Line_1 | 0.88494 | 0.35067 | 0.41182 | 0.88272 | 0.34842 | 0.40984 | 10.2185 | 4.0492 | 4.7552 | 10.1928 | 4.0233 | 4.7324 | 5.6832 | 3.4893 | -5.6032 | -3.7756 | -2.8624 | 6.3895 | 2.8528 | -4.3833 | 0.55593 | -1.8953 | 4.7232 | -0.49149 | -62.5995 | -73.1186 | -42.7603 | 117.4215 | 106.8668 | 137.3877 |  | 0.6223 | 1.3836 | 1.1841 | 0.41447 | 1.3727 | 1.3541 | -35.9444 | -124.5974 | 131.5736 | -35.9219 | -131.9163 | 132.989
Line_2 | 0.88494 | 0.35067 | 0.41182 | 0.88272 | 0.34842 | 0.40984 | 10.2185 | 4.0492 | 4.7552 | 10.1928 | 4.0233 | 4.7324 | 5.6832 | 3.4893 | -5.6032 | -3.7756 | -2.8624 | 6.3895 | 2.8528 | -4.3833 | 0.55593 | -1.8953 | 4.7232 | -0.49149 | -62.5995 | -73.1186 | -42.7603 | 117.4215 | 106.8668 | 137.3877 |  | 0.6223 | 1.3836 | 1.1841 | 0.41447 | 1.3727 | 1.3541 | -35.9444 | -124.5974 | 131.5736 | -35.9219 | -131.9163 | 132.989

## LG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.73966 | 0.12153 | 0.39884 | 0.74071 | 0.1226 | 0.39924 | 8.5409 | 1.4033 | 4.6054 | 8.5529 | 1.4157 | 4.6101 | -4.0161 | -1.478 | 4.471 | 5.1202 | 1.5613 | -3.9433 | -5.1238 | 0.95867 | -3.9467 | 5.871 | -0.82546 | 3.8543 | 121.452 | 83.6007 | 169.7262 | -58.5787 | -96.2458 | -10.4238 |  | 0.76224 | 1.2554 | 1.2949 | 0.9108 | 1.2475 | 1.1961 | -6.6376 | -129.3678 | 128.2901 | -9.6713 | -124.1119 | 125.2305
Line_1 | 0.37114 | 0.061921 | 0.20015 | 0.37035 | 0.061301 | 0.19962 | 4.2855 | 0.715 | 2.3111 | 4.2765 | 0.70784 | 2.305 | 2.8424 | 0.80402 | -1.846 | -2.5601 | -0.78063 | 1.9717 | 3.1267 | -0.38629 | 1.9054 | -2.9355 | 0.41273 | -1.9271 | -58.5778 | -95.7982 | -10.5901 | 121.4213 | 83.7542 | 169.5762 |  | 0.98601 | 1.2476 | 1.1479 | 0.9108 | 1.2475 | 1.1961 | -10.8512 | -121.46 | 123.5034 | -9.6713 | -124.1119 | 125.2305
Line_2 | 0.37114 | 0.061921 | 0.20015 | 0.37035 | 0.061301 | 0.19962 | 4.2855 | 0.715 | 2.3111 | 4.2765 | 0.70784 | 2.305 | 2.8424 | 0.80402 | -1.846 | -2.5601 | -0.78063 | 1.9717 | 3.1267 | -0.38629 | 1.9054 | -2.9355 | 0.41273 | -1.9271 | -58.5778 | -95.7982 | -10.5901 | 121.4213 | 83.7542 | 169.5762 |  | 0.98601 | 1.2476 | 1.1479 | 0.9108 | 1.2475 | 1.1961 | -10.8512 | -121.46 | 123.5034 | -9.6713 | -124.1119 | 125.2305

## LG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.73966 | 0.12153 | 0.39884 | 0.74071 | 0.1226 | 0.39924 | 8.5409 | 1.4033 | 4.6054 | 8.5529 | 1.4157 | 4.6101 | -4.0161 | -1.478 | 4.471 | 5.1202 | 1.5613 | -3.9433 | -5.1238 | 0.95867 | -3.9467 | 5.871 | -0.82546 | 3.8543 | 121.452 | 83.6007 | 169.7262 | -58.5787 | -96.2458 | -10.4238 |  | 0.76224 | 1.2554 | 1.2949 | 0.9108 | 1.2475 | 1.1961 | -6.6376 | -129.3678 | 128.2901 | -9.6713 | -124.1119 | 125.2305
Line_1 | 0.37114 | 0.061921 | 0.20015 | 0.37035 | 0.061301 | 0.19962 | 4.2855 | 0.715 | 2.3111 | 4.2765 | 0.70784 | 2.305 | 2.8424 | 0.80402 | -1.846 | -2.5601 | -0.78063 | 1.9717 | 3.1267 | -0.38629 | 1.9054 | -2.9355 | 0.41273 | -1.9271 | -58.5778 | -95.7982 | -10.5901 | 121.4213 | 83.7542 | 169.5762 |  | 0.98601 | 1.2476 | 1.1479 | 0.9108 | 1.2475 | 1.1961 | -10.8512 | -121.46 | 123.5034 | -9.6713 | -124.1119 | 125.2305
Line_2 | 0.37114 | 0.061921 | 0.20015 | 0.37035 | 0.061301 | 0.19962 | 4.2855 | 0.715 | 2.3111 | 4.2765 | 0.70784 | 2.305 | 2.8424 | 0.80402 | -1.846 | -2.5601 | -0.78063 | 1.9717 | 3.1267 | -0.38629 | 1.9054 | -2.9355 | 0.41273 | -1.9271 | -58.5778 | -95.7982 | -10.5901 | 121.4213 | 83.7542 | 169.5762 |  | 0.98601 | 1.2476 | 1.1479 | 0.9108 | 1.2475 | 1.1961 | -10.8512 | -121.46 | 123.5034 | -9.6713 | -124.1119 | 125.2305

## LG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.0967 | 0.59263 | 0.52746 | 1.0984 | 0.59444 | 0.52919 | 12.6637 | 6.8432 | 6.0905 | 12.6834 | 6.864 | 6.1106 | -2.2985e-11 | 2.8459 | 9.7374 | 6.1677 | 0.19675 | -7.1055 | 5.9961e-12 | 8.5759 | -0.31323 | 1.348 | -7.9327 | 0.7844 | 139.6999 | 137.0738 | 138.8615 | -40.4194 | -43.139 | -41.3835 |  | 0 | 1.3204 | 1.5996 | 0.49776 | 1.1561 | 1.1699 | 0 | -151.2847 | 137.0191 | -28.0906 | -131.7182 | 132.317
Line_1 | 0.55059 | 0.29863 | 0.26599 | 0.54921 | 0.29722 | 0.2646 | 6.3576 | 3.4483 | 3.0714 | 6.3417 | 3.432 | 3.0553 | 4.6414 | 0.86675 | -2.9002 | -3.0838 | -0.098377 | 3.5527 | 1.016 | -3.8141 | 0.51558 | -0.67401 | 3.9664 | -0.3922 | -40.4808 | -43.2394 | -41.5054 | 139.5806 | 136.861 | 138.6165 |  | 0.74733 | 1.1343 | 0.95909 | 0.49776 | 1.1561 | 1.1699 | -28.1329 | -120.4364 | 128.4143 | -28.0906 | -131.7182 | 132.317
Line_2 | 0.55059 | 0.29863 | 0.26599 | 0.54921 | 0.29722 | 0.2646 | 6.3576 | 3.4483 | 3.0714 | 6.3417 | 3.432 | 3.0553 | 4.6414 | 0.86675 | -2.9002 | -3.0838 | -0.098377 | 3.5527 | 1.016 | -3.8141 | 0.51558 | -0.67401 | 3.9664 | -0.3922 | -40.4808 | -43.2394 | -41.5054 | 139.5806 | 136.861 | 138.6165 |  | 0.74733 | 1.1343 | 0.95909 | 0.49776 | 1.1561 | 1.1699 | -28.1329 | -120.4364 | 128.4143 | -28.0906 | -131.7182 | 132.317

## LG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.0967 | 0.59263 | 0.52746 | 1.0984 | 0.59444 | 0.52919 | 12.6637 | 6.8432 | 6.0905 | 12.6834 | 6.864 | 6.1106 | -2.2985e-11 | 2.8459 | 9.7374 | 6.1677 | 0.19675 | -7.1055 | 5.9961e-12 | 8.5759 | -0.31323 | 1.348 | -7.9327 | 0.7844 | 139.6999 | 137.0738 | 138.8615 | -40.4194 | -43.139 | -41.3835 |  | 0 | 1.3204 | 1.5996 | 0.49776 | 1.1561 | 1.1699 | 0 | -151.2847 | 137.0191 | -28.0906 | -131.7182 | 132.317
Line_1 | 0.55059 | 0.29863 | 0.26599 | 0.54921 | 0.29722 | 0.2646 | 6.3576 | 3.4483 | 3.0714 | 6.3417 | 3.432 | 3.0553 | 4.6414 | 0.86675 | -2.9002 | -3.0838 | -0.098377 | 3.5527 | 1.016 | -3.8141 | 0.51558 | -0.67401 | 3.9664 | -0.3922 | -40.4808 | -43.2394 | -41.5054 | 139.5806 | 136.861 | 138.6165 |  | 0.74733 | 1.1343 | 0.95909 | 0.49776 | 1.1561 | 1.1699 | -28.1329 | -120.4364 | 128.4143 | -28.0906 | -131.7182 | 132.317
Line_2 | 0.55059 | 0.29863 | 0.26599 | 0.54921 | 0.29722 | 0.2646 | 6.3576 | 3.4483 | 3.0714 | 6.3417 | 3.432 | 3.0553 | 4.6414 | 0.86675 | -2.9002 | -3.0838 | -0.098377 | 3.5527 | 1.016 | -3.8141 | 0.51558 | -0.67401 | 3.9664 | -0.3922 | -40.4808 | -43.2394 | -41.5054 | 139.5806 | 136.861 | 138.6165 |  | 0.74733 | 1.1343 | 0.95909 | 0.49776 | 1.1561 | 1.1699 | -28.1329 | -120.4364 | 128.4143 | -28.0906 | -131.7182 | 132.317

## LG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.43779 | 0.23657 | 0.21055 | 0.43847 | 0.23729 | 0.21125 | 5.0552 | 2.7317 | 2.4313 | 5.0631 | 2.74 | 2.4393 | -2.4801 | 0.22471 | 2.8903 | 3.4631 | 0.2669 | -2.4778 | -1.7609 | 2.9942 | -0.63994 | 1.9836 | -2.8958 | 0.71121 | 142.6608 | 140.0347 | 141.8224 | -37.4585 | -40.1781 | -38.4225 |  | 0.6017 | 1.0992 | 1.2176 | 0.78826 | 1.0613 | 1.0568 | -1.9639 | -134.2571 | 129.338 | -7.6549 | -124.9121 | 125.5623
Line_1 | 0.21979 | 0.11921 | 0.10618 | 0.21924 | 0.11865 | 0.10562 | 2.5379 | 1.3765 | 1.226 | 2.5315 | 1.37 | 1.2196 | 1.9819 | 0.25789 | -1.1391 | -1.7316 | -0.13345 | 1.2389 | 1.0499 | -1.4273 | 0.37537 | -0.99182 | 1.4479 | -0.35561 | -37.5199 | -40.2785 | -38.5445 | 142.5415 | 139.8219 | 141.5775 |  | 0.88374 | 1.0537 | 0.97822 | 0.78826 | 1.0613 | 1.0568 | -9.6085 | -120.0367 | 123.2168 | -7.6549 | -124.9121 | 125.5623
Line_2 | 0.21979 | 0.11921 | 0.10618 | 0.21924 | 0.11865 | 0.10562 | 2.5379 | 1.3765 | 1.226 | 2.5315 | 1.37 | 1.2196 | 1.9819 | 0.25789 | -1.1391 | -1.7316 | -0.13345 | 1.2389 | 1.0499 | -1.4273 | 0.37537 | -0.99182 | 1.4479 | -0.35561 | -37.5199 | -40.2785 | -38.5445 | 142.5415 | 139.8219 | 141.5775 |  | 0.88374 | 1.0537 | 0.97822 | 0.78826 | 1.0613 | 1.0568 | -9.6085 | -120.0367 | 123.2168 | -7.6549 | -124.9121 | 125.5623

## LG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.43779 | 0.23657 | 0.21055 | 0.43847 | 0.23729 | 0.21125 | 5.0552 | 2.7317 | 2.4313 | 5.0631 | 2.74 | 2.4393 | -2.4801 | 0.22471 | 2.8903 | 3.4631 | 0.2669 | -2.4778 | -1.7609 | 2.9942 | -0.63994 | 1.9836 | -2.8958 | 0.71121 | 142.6608 | 140.0347 | 141.8224 | -37.4585 | -40.1781 | -38.4225 |  | 0.6017 | 1.0992 | 1.2176 | 0.78826 | 1.0613 | 1.0568 | -1.9639 | -134.2571 | 129.338 | -7.6549 | -124.9121 | 125.5623
Line_1 | 0.21979 | 0.11921 | 0.10618 | 0.21924 | 0.11865 | 0.10562 | 2.5379 | 1.3765 | 1.226 | 2.5315 | 1.37 | 1.2196 | 1.9819 | 0.25789 | -1.1391 | -1.7316 | -0.13345 | 1.2389 | 1.0499 | -1.4273 | 0.37537 | -0.99182 | 1.4479 | -0.35561 | -37.5199 | -40.2785 | -38.5445 | 142.5415 | 139.8219 | 141.5775 |  | 0.88374 | 1.0537 | 0.97822 | 0.78826 | 1.0613 | 1.0568 | -9.6085 | -120.0367 | 123.2168 | -7.6549 | -124.9121 | 125.5623
Line_2 | 0.21979 | 0.11921 | 0.10618 | 0.21924 | 0.11865 | 0.10562 | 2.5379 | 1.3765 | 1.226 | 2.5315 | 1.37 | 1.2196 | 1.9819 | 0.25789 | -1.1391 | -1.7316 | -0.13345 | 1.2389 | 1.0499 | -1.4273 | 0.37537 | -0.99182 | 1.4479 | -0.35561 | -37.5199 | -40.2785 | -38.5445 | 142.5415 | 139.8219 | 141.5775 |  | 0.88374 | 1.0537 | 0.97822 | 0.78826 | 1.0613 | 1.0568 | -9.6085 | -120.0367 | 123.2168 | -7.6549 | -124.9121 | 125.5623

## LLG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.22697 | 2.0309 | 1.3314 | 0.22861 | 2.0316 | 1.3328 | 2.6208 | 23.4511 | 15.3734 | 2.6398 | 23.4589 | 15.3904 | 2.9634 | 3.5783e-11 | 2.2423e-11 | -2.4224 | 6.4396 | 0.77317 | 2.8593 | -1.2284e-11 | -9.8949e-12 | -2.7768 | 0.57328 | 4.1146 | -45.5534 | -12.6246 | -129.0008 | 134.1228 | 167.3197 | 51.0629 |  | 1.5713 | 0 | 0 | 1.3959 | 0.27559 | 0.27202 | -1.5781 | 0 | 0 | 3.022 | 172.407 | 130.4205
Line_1 | 0.11571 | 1.0167 | 0.66701 | 0.1143 | 1.0158 | 0.66642 | 1.3361 | 11.7403 | 7.702 | 1.3199 | 11.7295 | 7.6952 | -1.0823 | 4.8377 | 0.58721 | 1.2112 | -3.2198 | -0.38658 | -1.379 | 0.43268 | 3.0907 | 1.3884 | -0.28664 | -2.0573 | 133.914 | 167.2565 | 51.178 | -45.8772 | -12.6803 | -128.9371 |  | 1.3121 | 0.4137 | 0.40846 | 1.3959 | 0.27559 | 0.27202 | 5.7893 | 172.3675 | 130.4203 | 3.022 | 172.407 | 130.4205
Line_2 | 0.11571 | 1.0167 | 0.66701 | 0.1143 | 1.0158 | 0.66642 | 1.3361 | 11.7403 | 7.702 | 1.3199 | 11.7295 | 7.6952 | -1.0823 | 4.8377 | 0.58721 | 1.2112 | -3.2198 | -0.38658 | -1.379 | 0.43268 | 3.0907 | 1.3884 | -0.28664 | -2.0573 | 133.914 | 167.2565 | 51.178 | -45.8772 | -12.6803 | -128.9371 |  | 1.3121 | 0.4137 | 0.40846 | 1.3959 | 0.27559 | 0.27202 | 5.7893 | 172.3675 | 130.4203 | 3.022 | 172.407 | 130.4205

## LLG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.22697 | 2.0309 | 1.3314 | 0.22861 | 2.0316 | 1.3328 | 2.6208 | 23.4511 | 15.3734 | 2.6398 | 23.4589 | 15.3904 | 2.9634 | 3.5783e-11 | 2.2423e-11 | -2.4224 | 6.4396 | 0.77317 | 2.8593 | -1.2284e-11 | -9.8949e-12 | -2.7768 | 0.57328 | 4.1146 | -45.5534 | -12.6246 | -129.0008 | 134.1228 | 167.3197 | 51.0629 |  | 1.5713 | 0 | 0 | 1.3959 | 0.27559 | 0.27202 | -1.5781 | 0 | 0 | 3.022 | 172.407 | 130.4205
Line_1 | 0.11571 | 1.0167 | 0.66701 | 0.1143 | 1.0158 | 0.66642 | 1.3361 | 11.7403 | 7.702 | 1.3199 | 11.7295 | 7.6952 | -1.0823 | 4.8377 | 0.58721 | 1.2112 | -3.2198 | -0.38658 | -1.379 | 0.43268 | 3.0907 | 1.3884 | -0.28664 | -2.0573 | 133.914 | 167.2565 | 51.178 | -45.8772 | -12.6803 | -128.9371 |  | 1.3121 | 0.4137 | 0.40846 | 1.3959 | 0.27559 | 0.27202 | 5.7893 | 172.3675 | 130.4203 | 3.022 | 172.407 | 130.4205
Line_2 | 0.11571 | 1.0167 | 0.66701 | 0.1143 | 1.0158 | 0.66642 | 1.3361 | 11.7403 | 7.702 | 1.3199 | 11.7295 | 7.6952 | -1.0823 | 4.8377 | 0.58721 | 1.2112 | -3.2198 | -0.38658 | -1.379 | 0.43268 | 3.0907 | 1.3884 | -0.28664 | -2.0573 | 133.914 | 167.2565 | 51.178 | -45.8772 | -12.6803 | -128.9371 |  | 1.3121 | 0.4137 | 0.40846 | 1.3959 | 0.27559 | 0.27202 | 5.7893 | 172.3675 | 130.4203 | 3.022 | 172.407 | 130.4205

## LLG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.13306 | 0.67986 | 0.58135 | 0.13289 | 0.68026 | 0.5822 | 1.5364 | 7.8504 | 6.7129 | 1.5345 | 7.855 | 6.7227 | 1.8872 | -1.8719 | -5.2007 | -1.798 | 2.7757 | 5.5658 | -0.8006 | -6.7588 | -2.5983 | 0.68814 | 6.8333 | 3.371 | 22.6335 | -13.3332 | -103.0188 | -157.7622 | 166.5956 | 77.02 |  | 1.3343 | 0.89336 | 0.86605 | 1.2546 | 0.93897 | 0.96793 | -0.35396 | -118.8141 | 103.5281 | 1.2947 | -125.5116 | 108.2222
Line_1 | 0.066571 | 0.34061 | 0.29155 | 0.066444 | 0.34013 | 0.2911 | 0.76869 | 3.933 | 3.3666 | 0.76723 | 3.9275 | 3.3613 | -0.88057 | 1.614 | 2.8797 | 0.899 | -1.3879 | -2.7829 | 0.31145 | 3.4403 | 1.8775 | -0.34407 | -3.4167 | -1.6855 | -158.3154 | 166.5199 | 77.1127 | 22.2378 | -13.4044 | -102.98 |  | 1.2151 | 0.96621 | 1.0211 | 1.2546 | 0.93897 | 0.96793 | 2.2062 | -128.6135 | 110.216 | 1.2947 | -125.5116 | 108.2222
Line_2 | 0.066571 | 0.34061 | 0.29155 | 0.066444 | 0.34013 | 0.2911 | 0.76869 | 3.933 | 3.3666 | 0.76723 | 3.9275 | 3.3613 | -0.88057 | 1.614 | 2.8797 | 0.899 | -1.3879 | -2.7829 | 0.31145 | 3.4403 | 1.8775 | -0.34407 | -3.4167 | -1.6855 | -158.3154 | 166.5199 | 77.1127 | 22.2378 | -13.4044 | -102.98 |  | 1.2151 | 0.96621 | 1.0211 | 1.2546 | 0.93897 | 0.96793 | 2.2062 | -128.6135 | 110.216 | 1.2947 | -125.5116 | 108.2222

## LLG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.13306 | 0.67986 | 0.58135 | 0.13289 | 0.68026 | 0.5822 | 1.5364 | 7.8504 | 6.7129 | 1.5345 | 7.855 | 6.7227 | 1.8872 | -1.8719 | -5.2007 | -1.798 | 2.7757 | 5.5658 | -0.8006 | -6.7588 | -2.5983 | 0.68814 | 6.8333 | 3.371 | 22.6335 | -13.3332 | -103.0188 | -157.7622 | 166.5956 | 77.02 |  | 1.3343 | 0.89336 | 0.86605 | 1.2546 | 0.93897 | 0.96793 | -0.35396 | -118.8141 | 103.5281 | 1.2947 | -125.5116 | 108.2222
Line_1 | 0.066571 | 0.34061 | 0.29155 | 0.066444 | 0.34013 | 0.2911 | 0.76869 | 3.933 | 3.3666 | 0.76723 | 3.9275 | 3.3613 | -0.88057 | 1.614 | 2.8797 | 0.899 | -1.3879 | -2.7829 | 0.31145 | 3.4403 | 1.8775 | -0.34407 | -3.4167 | -1.6855 | -158.3154 | 166.5199 | 77.1127 | 22.2378 | -13.4044 | -102.98 |  | 1.2151 | 0.96621 | 1.0211 | 1.2546 | 0.93897 | 0.96793 | 2.2062 | -128.6135 | 110.216 | 1.2947 | -125.5116 | 108.2222
Line_2 | 0.066571 | 0.34061 | 0.29155 | 0.066444 | 0.34013 | 0.2911 | 0.76869 | 3.933 | 3.3666 | 0.76723 | 3.9275 | 3.3613 | -0.88057 | 1.614 | 2.8797 | 0.899 | -1.3879 | -2.7829 | 0.31145 | 3.4403 | 1.8775 | -0.34407 | -3.4167 | -1.6855 | -158.3154 | 166.5199 | 77.1127 | 22.2378 | -13.4044 | -102.98 |  | 1.2151 | 0.96621 | 1.0211 | 1.2546 | 0.93897 | 0.96793 | 2.2062 | -128.6135 | 110.216 | 1.2947 | -125.5116 | 108.2222

## LLG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.22451 | 1.5812 | 0.84929 | 0.22595 | 1.5813 | 0.85039 | 2.5924 | 18.258 | 9.8068 | 2.609 | 18.2588 | 9.8195 | 2.3343 | -2.3202e-11 | -7.9516e-12 | -1.7481 | 6.3307 | -0.083714 | 2.8329 | -2.5565e-11 | -1.7019e-11 | -2.5352 | -0.46895 | 2.5937 | -52.0748 | 3.3545 | -134.077 | 127.6959 | -176.7071 | 46.0106 |  | 1.416 | 0 | 0 | 1.1803 | 0.34767 | 0.26428 | -1.5637 | 0 | 0 | 3.1083 | 179.0564 | 137.8592
Line_1 | 0.11387 | 0.79112 | 0.42535 | 0.11297 | 0.79063 | 0.4252 | 1.3149 | 9.135 | 4.9115 | 1.3045 | 9.1294 | 4.9097 | -0.73141 | 4.7537 | -0.05818 | 0.87406 | -3.1654 | 0.041857 | -1.1959 | -0.3516 | 1.9487 | 1.2676 | 0.23448 | -1.2969 | 127.6824 | -176.7617 | 46.1295 | -52.3041 | 3.2929 | -133.9894 |  | 1.0662 | 0.5218 | 0.39693 | 1.1803 | 0.34767 | 0.26428 | 6.2334 | 179.0082 | 137.8396 | 3.1083 | 179.0564 | 137.8592
Line_2 | 0.11387 | 0.79112 | 0.42535 | 0.11297 | 0.79063 | 0.4252 | 1.3149 | 9.135 | 4.9115 | 1.3045 | 9.1294 | 4.9097 | -0.73141 | 4.7537 | -0.05818 | 0.87406 | -3.1654 | 0.041857 | -1.1959 | -0.3516 | 1.9487 | 1.2676 | 0.23448 | -1.2969 | 127.6824 | -176.7617 | 46.1295 | -52.3041 | 3.2929 | -133.9894 |  | 1.0662 | 0.5218 | 0.39693 | 1.1803 | 0.34767 | 0.26428 | 6.2334 | 179.0082 | 137.8396 | 3.1083 | 179.0564 | 137.8592

## LLG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.22451 | 1.5812 | 0.84929 | 0.22595 | 1.5813 | 0.85039 | 2.5924 | 18.258 | 9.8068 | 2.609 | 18.2588 | 9.8195 | 2.3343 | -2.3202e-11 | -7.9516e-12 | -1.7481 | 6.3307 | -0.083714 | 2.8329 | -2.5565e-11 | -1.7019e-11 | -2.5352 | -0.46895 | 2.5937 | -52.0748 | 3.3545 | -134.077 | 127.6959 | -176.7071 | 46.0106 |  | 1.416 | 0 | 0 | 1.1803 | 0.34767 | 0.26428 | -1.5637 | 0 | 0 | 3.1083 | 179.0564 | 137.8592
Line_1 | 0.11387 | 0.79112 | 0.42535 | 0.11297 | 0.79063 | 0.4252 | 1.3149 | 9.135 | 4.9115 | 1.3045 | 9.1294 | 4.9097 | -0.73141 | 4.7537 | -0.05818 | 0.87406 | -3.1654 | 0.041857 | -1.1959 | -0.3516 | 1.9487 | 1.2676 | 0.23448 | -1.2969 | 127.6824 | -176.7617 | 46.1295 | -52.3041 | 3.2929 | -133.9894 |  | 1.0662 | 0.5218 | 0.39693 | 1.1803 | 0.34767 | 0.26428 | 6.2334 | 179.0082 | 137.8396 | 3.1083 | 179.0564 | 137.8592
Line_2 | 0.11387 | 0.79112 | 0.42535 | 0.11297 | 0.79063 | 0.4252 | 1.3149 | 9.135 | 4.9115 | 1.3045 | 9.1294 | 4.9097 | -0.73141 | 4.7537 | -0.05818 | 0.87406 | -3.1654 | 0.041857 | -1.1959 | -0.3516 | 1.9487 | 1.2676 | 0.23448 | -1.2969 | 127.6824 | -176.7617 | 46.1295 | -52.3041 | 3.2929 | -133.9894 |  | 1.0662 | 0.5218 | 0.39693 | 1.1803 | 0.34767 | 0.26428 | 6.2334 | 179.0082 | 137.8396 | 3.1083 | 179.0564 | 137.8592

## LLG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.16449 | 0.39617 | 0.3371 | 0.16516 | 0.3961 | 0.33798 | 1.8994 | 4.5746 | 3.8925 | 1.9071 | 4.5737 | 3.9027 | 1.671 | -1.9693 | -2.7555 | -1.4226 | 2.5852 | 3.1689 | 1.5846 | -2.9983 | -0.010024 | -1.5033 | 2.7763 | 0.46156 | -45.3909 | 8.1183 | -78.983 | 134.404 | -172.0102 | 100.9961 |  | 1.2124 | 0.78415 | 0.7079 | 1.0853 | 0.82942 | 0.82054 | -1.9103 | -115.1794 | 101.2254 | 0.98437 | -124.9687 | 109.2832
Line_1 | 0.08304 | 0.19825 | 0.16943 | 0.082579 | 0.19805 | 0.16899 | 0.95886 | 2.2892 | 1.9564 | 0.95354 | 2.2869 | 1.9513 | -0.65147 | 1.4472 | 1.6912 | 0.71128 | -1.2926 | -1.5844 | -0.73304 | 1.3356 | 0.34269 | 0.75164 | -1.3881 | -0.23078 | 134.3413 | -172.133 | 101.0563 | -45.596 | 7.9898 | -79.0039 |  | 1.0228 | 0.86025 | 0.88203 | 1.0853 | 0.82942 | 0.82054 | 2.7132 | -129.43 | 112.5112 | 0.98437 | -124.9687 | 109.2832
Line_2 | 0.08304 | 0.19825 | 0.16943 | 0.082579 | 0.19805 | 0.16899 | 0.95886 | 2.2892 | 1.9564 | 0.95354 | 2.2869 | 1.9513 | -0.65147 | 1.4472 | 1.6912 | 0.71128 | -1.2926 | -1.5844 | -0.73304 | 1.3356 | 0.34269 | 0.75164 | -1.3881 | -0.23078 | 134.3413 | -172.133 | 101.0563 | -45.596 | 7.9898 | -79.0039 |  | 1.0228 | 0.86025 | 0.88203 | 1.0853 | 0.82942 | 0.82054 | 2.7132 | -129.43 | 112.5112 | 0.98437 | -124.9687 | 109.2832

## LLG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.16449 | 0.39617 | 0.3371 | 0.16516 | 0.3961 | 0.33798 | 1.8994 | 4.5746 | 3.8925 | 1.9071 | 4.5737 | 3.9027 | 1.671 | -1.9693 | -2.7555 | -1.4226 | 2.5852 | 3.1689 | 1.5846 | -2.9983 | -0.010024 | -1.5033 | 2.7763 | 0.46156 | -45.3909 | 8.1183 | -78.983 | 134.404 | -172.0102 | 100.9961 |  | 1.2124 | 0.78415 | 0.7079 | 1.0853 | 0.82942 | 0.82054 | -1.9103 | -115.1794 | 101.2254 | 0.98437 | -124.9687 | 109.2832
Line_1 | 0.08304 | 0.19825 | 0.16943 | 0.082579 | 0.19805 | 0.16899 | 0.95886 | 2.2892 | 1.9564 | 0.95354 | 2.2869 | 1.9513 | -0.65147 | 1.4472 | 1.6912 | 0.71128 | -1.2926 | -1.5844 | -0.73304 | 1.3356 | 0.34269 | 0.75164 | -1.3881 | -0.23078 | 134.3413 | -172.133 | 101.0563 | -45.596 | 7.9898 | -79.0039 |  | 1.0228 | 0.86025 | 0.88203 | 1.0853 | 0.82942 | 0.82054 | 2.7132 | -129.43 | 112.5112 | 0.98437 | -124.9687 | 109.2832
Line_2 | 0.08304 | 0.19825 | 0.16943 | 0.082579 | 0.19805 | 0.16899 | 0.95886 | 2.2892 | 1.9564 | 0.95354 | 2.2869 | 1.9513 | -0.65147 | 1.4472 | 1.6912 | 0.71128 | -1.2926 | -1.5844 | -0.73304 | 1.3356 | 0.34269 | 0.75164 | -1.3881 | -0.23078 | 134.3413 | -172.133 | 101.0563 | -45.596 | 7.9898 | -79.0039 |  | 1.0228 | 0.86025 | 0.88203 | 1.0853 | 0.82942 | 0.82054 | 2.7132 | -129.43 | 112.5112 | 0.98437 | -124.9687 | 109.2832