## LLL_max_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 3.3036 | 3.3036 | 0 | 0 | 114.4404 | 114.4404 | 37.7713 | -20.7457 | 43.3355 | -24.018 | -70.8485 | 109.1515 | 0.50232 | 0.27733 | -21.9239 | -21.6675
Line_1 | 4.0718 | 4.0718 | 7.8074 | 0 | 141.0522 | 141.0522 | -1e-07 | 25.8644 | -1e-07 | 29.3462 | 109.7241 | -70.2759 | 0 | 0.27733 | 0 | -21.6675
Line_2 | 0.76909 | 0.76909 | 0 | 0 | 26.6421 | 26.6421 | 6.0414 | -5.1187 | 6.3751 | -5.3281 | -67.816 | 112.184 | 0.32967 | 0.27733 | -21.2767 | -21.6675

## LLL_max_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 3.3036 | 3.3036 | 0 | 0 | 114.4404 | 114.4404 | 37.7713 | -20.7457 | 43.3355 | -24.018 | -70.8485 | 109.1515 | 0.50232 | 0.27733 | -21.9239 | -21.6675
Line_1 | 4.0718 | 4.0718 | 7.8074 | 0 | 141.0522 | 141.0522 | -1e-07 | 25.8644 | -1e-07 | 29.3462 | 109.7241 | -70.2759 | 0 | 0.27733 | 0 | -21.6675
Line_2 | 0.76909 | 0.76909 | 0 | 0 | 26.6421 | 26.6421 | 6.0414 | -5.1187 | 6.3751 | -5.3281 | -67.816 | 112.184 | 0.32967 | 0.27733 | -21.2767 | -21.6675

## LLL_max_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.77289 | 0.77289 | 0 | 0 | 26.7736 | 26.7736 | 20.4887 | -19.5569 | 16.8303 | -15.773 | -45.3926 | 134.6074 | 0.99034 | 0.93842 | -5.9915 | -6.5057
Line_1 | 1.057 | 1.057 | 2.0668 | 0 | 36.615 | 36.615 | -23.4304 | 25.1732 | -21.4091 | 23.3865 | 130.6015 | -49.3985 | 0.86682 | 0.93842 | -6.9796 | -6.5057
Line_2 | 0.29104 | 0.29104 | 0 | 0 | 10.0818 | 10.0818 | 5.7485 | -5.6164 | 7.7635 | -7.6135 | -60.0901 | 119.9099 | 0.95817 | 0.93842 | -6.6085 | -6.5057

## LLL_max_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.77289 | 0.77289 | 0 | 0 | 26.7736 | 26.7736 | 20.4887 | -19.5569 | 16.8303 | -15.773 | -45.3926 | 134.6074 | 0.99034 | 0.93842 | -5.9915 | -6.5057
Line_1 | 1.057 | 1.057 | 2.0668 | 0 | 36.615 | 36.615 | -23.4304 | 25.1732 | -21.4091 | 23.3865 | 130.6015 | -49.3985 | 0.86682 | 0.93842 | -6.9796 | -6.5057
Line_2 | 0.29104 | 0.29104 | 0 | 0 | 10.0818 | 10.0818 | 5.7485 | -5.6164 | 7.7635 | -7.6135 | -60.0901 | 119.9099 | 0.95817 | 0.93842 | -6.6085 | -6.5057

## LLL_min_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 2.6307 | 2.6307 | 0 | 0 | 91.1286 | 91.1286 | 45.9418 | -25.214 | 27.0858 | -14.8368 | -57.966 | 122.034 | 0.58524 | 0.32103 | -27.4438 | -27.4919
Line_1 | 3.1965 | 3.1965 | 5.555 | 0 | 110.73 | 110.73 | -1e-07 | 30.6038 | -1e-07 | 18.0852 | 121.9273 | -58.0727 | 0 | 0.32103 | 0 | -27.4919
Line_2 | 0.56587 | 0.56587 | 0 | 0 | 19.6023 | 19.6023 | 6.3489 | -5.3898 | 3.8151 | -3.2484 | -58.5686 | 121.4314 | 0.37786 | 0.32103 | -27.5665 | -27.4919

## LLL_min_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 2.6307 | 2.6307 | 0 | 0 | 91.1286 | 91.1286 | 45.9418 | -25.214 | 27.0858 | -14.8368 | -57.966 | 122.034 | 0.58524 | 0.32103 | -27.4438 | -27.4919
Line_1 | 3.1965 | 3.1965 | 5.555 | 0 | 110.73 | 110.73 | -1e-07 | 30.6038 | -1e-07 | 18.0852 | 121.9273 | -58.0727 | 0 | 0.32103 | 0 | -27.4919
Line_2 | 0.56587 | 0.56587 | 0 | 0 | 19.6023 | 19.6023 | 6.3489 | -5.3898 | 3.8151 | -3.2484 | -58.5686 | 121.4314 | 0.37786 | 0.32103 | -27.5665 | -27.4919

## LLL_min_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.76941 | 0.76941 | 0 | 0 | 26.6531 | 26.6531 | 18.1535 | -16.3803 | 15.0311 | -13.9833 | -46.4658 | 133.5342 | 0.88427 | 0.80805 | -6.841 | -5.9797
Line_1 | 0.93491 | 0.93491 | 1.6247 | 0 | 32.3861 | 32.3861 | -17.2541 | 19.872 | -15.481 | 17.028 | 133.4275 | -46.5725 | 0.71577 | 0.80805 | -4.6729 | -5.9797
Line_2 | 0.1655 | 0.1655 | 0 | 0 | 5.7333 | 5.7333 | 3.5737 | -3.4917 | 3.0933 | -3.0448 | -47.0684 | 132.9316 | 0.8244 | 0.80805 | -6.1904 | -5.9797

## LLL_min_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.76941 | 0.76941 | 0 | 0 | 26.6531 | 26.6531 | 18.1535 | -16.3803 | 15.0311 | -13.9833 | -46.4658 | 133.5342 | 0.88427 | 0.80805 | -6.841 | -5.9797
Line_1 | 0.93491 | 0.93491 | 1.6247 | 0 | 32.3861 | 32.3861 | -17.2541 | 19.872 | -15.481 | 17.028 | 133.4275 | -46.5725 | 0.71577 | 0.80805 | -4.6729 | -5.9797
Line_2 | 0.1655 | 0.1655 | 0 | 0 | 5.7333 | 5.7333 | 3.5737 | -3.4917 | 3.0933 | -3.0448 | -47.0684 | 132.9316 | 0.8244 | 0.80805 | -6.1904 | -5.9797

## LL_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.34465 | 2.8163 | 2.9394 | 0.34465 | 2.8163 | 2.9394 | 3.9797 | 32.5201 | 33.9408 | 3.9797 | 32.5201 | 33.9408 | -2.8467 | 27.5894 | -9.8021 | 2.9085 | -23.4649 | 14.2948 | -3.6108 | 3.3833 | 16.3211 | 3.6809 | 1.2964 | -11.2236 | 130.3426 | -157.3314 | 16.2542 | -49.6574 | 22.6686 | -163.7458 | 1.1554 | 0.85474 | 0.56093 | 1.1788 | 0.72265 | 0.53548 | 2.0909 | -150.3401 | 137.2424 | 2.0284 | -160.4937 | 158.117
Line_1 | 0.19448 | 3.4668 | 3.5514 | 0.19448 | 3.4668 | 3.5514 | 2.2456 | 40.0309 | 41.0075 | 2.2456 | 40.0309 | 41.0075 | 1.8069 | -22.6769 | 23.5803 | -1.7872 | 28.9265 | -17.0221 | 1.975 | 7.4181 | -6.4306 | -1.9527 | -0.32717 | 13.8717 | -45.5053 | 20.1544 | -162.7055 | 134.4947 | -159.8456 | 17.2945 | 1.192 | 0.59602 | 0.59602 | 1.1788 | 0.72265 | 0.53548 | 2.0403 | -177.9597 | -177.9597 | 2.0284 | -160.4937 | 158.117
Line_2 | 0.15134 | 0.66475 | 0.6148 | 0.15134 | 0.66475 | 0.6148 | 1.7476 | 7.6758 | 7.0991 | 1.7476 | 7.6758 | 7.0991 | 1.1332 | 5.6914 | -2.5307 | -1.1212 | -5.4616 | 2.7272 | 1.7417 | 1.2299 | 2.8712 | -1.7282 | -0.96922 | -2.6482 | -54.9959 | -170.5566 | 22.2743 | 125.0041 | 9.4434 | -157.7257 | 1.189 | 0.75859 | 0.53912 | 1.1788 | 0.72265 | 0.53548 | 1.9557 | -158.3623 | 153.6676 | 2.0284 | -160.4937 | 158.117

## LL_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.34465 | 2.8163 | 2.9394 | 0.34465 | 2.8163 | 2.9394 | 3.9797 | 32.5201 | 33.9408 | 3.9797 | 32.5201 | 33.9408 | -2.8467 | 27.5894 | -9.8021 | 2.9085 | -23.4649 | 14.2948 | -3.6108 | 3.3833 | 16.3211 | 3.6809 | 1.2964 | -11.2236 | 130.3426 | -157.3314 | 16.2542 | -49.6574 | 22.6686 | -163.7458 | 1.1554 | 0.85474 | 0.56093 | 1.1788 | 0.72265 | 0.53548 | 2.0909 | -150.3401 | 137.2424 | 2.0284 | -160.4937 | 158.117
Line_1 | 0.19448 | 3.4668 | 3.5514 | 0.19448 | 3.4668 | 3.5514 | 2.2456 | 40.0309 | 41.0075 | 2.2456 | 40.0309 | 41.0075 | 1.8069 | -22.6769 | 23.5803 | -1.7872 | 28.9265 | -17.0221 | 1.975 | 7.4181 | -6.4306 | -1.9527 | -0.32717 | 13.8717 | -45.5053 | 20.1544 | -162.7055 | 134.4947 | -159.8456 | 17.2945 | 1.192 | 0.59602 | 0.59602 | 1.1788 | 0.72265 | 0.53548 | 2.0403 | -177.9597 | -177.9597 | 2.0284 | -160.4937 | 158.117
Line_2 | 0.15134 | 0.66475 | 0.6148 | 0.15134 | 0.66475 | 0.6148 | 1.7476 | 7.6758 | 7.0991 | 1.7476 | 7.6758 | 7.0991 | 1.1332 | 5.6914 | -2.5307 | -1.1212 | -5.4616 | 2.7272 | 1.7417 | 1.2299 | 2.8712 | -1.7282 | -0.96922 | -2.6482 | -54.9959 | -170.5566 | 22.2743 | 125.0041 | 9.4434 | -157.7257 | 1.189 | 0.75859 | 0.53912 | 1.1788 | 0.72265 | 0.53548 | 1.9557 | -158.3623 | 153.6676 | 2.0284 | -160.4937 | 158.117

## LL_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.26375 | 1.2082 | 1.1737 | 0.26375 | 1.2082 | 1.1737 | 3.0455 | 13.9508 | 13.5526 | 3.0455 | 13.9508 | 13.5526 | -1.7236 | 14.6366 | 0.36638 | 1.7598 | -13.8776 | 0.34995 | -3.0377 | 0.70931 | 11.719 | 3.0787 | 0.15191 | -10.9062 | 120.8148 | -135.4144 | 31.9789 | -59.1852 | 44.5856 | -148.0211 | 1.1468 | 1.0504 | 0.86513 | 1.1644 | 0.99481 | 0.80515 | 1.244 | -132.6399 | 120.1882 | 1.0629 | -136.0415 | 123.8167
Line_1 | 0.14172 | 1.5139 | 1.518 | 0.14172 | 1.5139 | 1.518 | 1.6364 | 17.4815 | 17.5279 | 1.6364 | 17.4815 | 17.5279 | 1.1337 | -16.1122 | 1.4292 | -1.1232 | 17.3041 | -0.23098 | 1.5511 | -0.38203 | -12.7512 | -1.5392 | 1.7343 | 14.1107 | -52.8182 | 38.235 | -147.1211 | 127.1818 | -141.765 | 32.8789 | 1.174 | 0.92193 | 0.73203 | 1.1644 | 0.99481 | 0.80515 | 1.0196 | -140.4067 | 129.274 | 1.0629 | -136.0415 | 123.8167
Line_2 | 0.1239 | 0.3405 | 0.34491 | 0.1239 | 0.3405 | 0.34491 | 1.4307 | 3.9318 | 3.9827 | 1.4307 | 3.9318 | 3.9827 | 0.64456 | 3.4868 | 0.18083 | -0.63657 | -3.4265 | -0.11897 | 1.5486 | 1.9546 | 3.2746 | -1.5395 | -1.8862 | -3.2044 | -66.4724 | -164.8737 | 35.9428 | 113.5276 | 15.1263 | -144.0572 | 1.1724 | 1.0167 | 0.82347 | 1.1644 | 0.99481 | 0.80515 | 0.92914 | -135.5993 | 122.7821 | 1.0629 | -136.0415 | 123.8167

## LL_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.26375 | 1.2082 | 1.1737 | 0.26375 | 1.2082 | 1.1737 | 3.0455 | 13.9508 | 13.5526 | 3.0455 | 13.9508 | 13.5526 | -1.7236 | 14.6366 | 0.36638 | 1.7598 | -13.8776 | 0.34995 | -3.0377 | 0.70931 | 11.719 | 3.0787 | 0.15191 | -10.9062 | 120.8148 | -135.4144 | 31.9789 | -59.1852 | 44.5856 | -148.0211 | 1.1468 | 1.0504 | 0.86513 | 1.1644 | 0.99481 | 0.80515 | 1.244 | -132.6399 | 120.1882 | 1.0629 | -136.0415 | 123.8167
Line_1 | 0.14172 | 1.5139 | 1.518 | 0.14172 | 1.5139 | 1.518 | 1.6364 | 17.4815 | 17.5279 | 1.6364 | 17.4815 | 17.5279 | 1.1337 | -16.1122 | 1.4292 | -1.1232 | 17.3041 | -0.23098 | 1.5511 | -0.38203 | -12.7512 | -1.5392 | 1.7343 | 14.1107 | -52.8182 | 38.235 | -147.1211 | 127.1818 | -141.765 | 32.8789 | 1.174 | 0.92193 | 0.73203 | 1.1644 | 0.99481 | 0.80515 | 1.0196 | -140.4067 | 129.274 | 1.0629 | -136.0415 | 123.8167
Line_2 | 0.1239 | 0.3405 | 0.34491 | 0.1239 | 0.3405 | 0.34491 | 1.4307 | 3.9318 | 3.9827 | 1.4307 | 3.9318 | 3.9827 | 0.64456 | 3.4868 | 0.18083 | -0.63657 | -3.4265 | -0.11897 | 1.5486 | 1.9546 | 3.2746 | -1.5395 | -1.8862 | -3.2044 | -66.4724 | -164.8737 | 35.9428 | 113.5276 | 15.1263 | -144.0572 | 1.1724 | 1.0167 | 0.82347 | 1.1644 | 0.99481 | 0.80515 | 0.92914 | -135.5993 | 122.7821 | 1.0629 | -136.0415 | 123.8167

## LL_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.14068 | 2.2375 | 2.3511 | 0.14068 | 2.2375 | 2.3511 | 1.6245 | 25.8369 | 27.1481 | 1.6245 | 25.8369 | 27.1481 | -1.6231 | 22.5203 | -0.019694 | 1.6429 | -17.5218 | 5.5385 | -0.15684 | -0.52064 | 13.7841 | 0.16852 | 3.4745 | -10.5228 | 176.1521 | -146.6212 | 31.3043 | -3.8479 | 33.3788 | -148.6957 | 1.0038 | 0.87187 | 0.50774 | 1.0166 | 0.69137 | 0.43802 | 1.6715 | -147.9456 | 121.3861 | 2.0088 | -157.8373 | 149.0637
Line_1 | 0.088507 | 2.7229 | 2.7871 | 0.088507 | 2.7229 | 2.7871 | 1.022 | 31.441 | 32.1826 | 1.022 | 31.441 | 32.1826 | 1.0131 | -14.0477 | 14.5542 | -1.0053 | 21.4498 | -6.7988 | 0.26704 | 7.8991 | -7.7655 | -0.26242 | -3.5248 | 12.3486 | -12.6212 | 31.4946 | -149.7721 | 167.3788 | -148.5054 | 30.2279 | 1.0252 | 0.51259 | 0.51259 | 1.0166 | 0.69137 | 0.43802 | 2.1453 | -177.8547 | -177.8547 | 2.0088 | -157.8373 | 149.0637
Line_2 | 0.054898 | 0.49207 | 0.43864 | 0.054898 | 0.49207 | 0.43864 | 0.6339 | 5.682 | 5.065 | 0.6339 | 5.682 | 5.065 | 0.64057 | 4.1698 | -1.0682 | -0.63756 | -3.928 | 1.2602 | -0.092125 | 0.092595 | 1.9394 | 0.093903 | 0.050265 | -1.8258 | 10.3873 | -157.1042 | 24.4491 | -169.6127 | 22.8958 | -155.5509 | 1.0209 | 0.73405 | 0.43713 | 1.0166 | 0.69137 | 0.43802 | 2.2033 | -155.8321 | 143.2941 | 2.0088 | -157.8373 | 149.0637

## LL_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.14068 | 2.2375 | 2.3511 | 0.14068 | 2.2375 | 2.3511 | 1.6245 | 25.8369 | 27.1481 | 1.6245 | 25.8369 | 27.1481 | -1.6231 | 22.5203 | -0.019694 | 1.6429 | -17.5218 | 5.5385 | -0.15684 | -0.52064 | 13.7841 | 0.16852 | 3.4745 | -10.5228 | 176.1521 | -146.6212 | 31.3043 | -3.8479 | 33.3788 | -148.6957 | 1.0038 | 0.87187 | 0.50774 | 1.0166 | 0.69137 | 0.43802 | 1.6715 | -147.9456 | 121.3861 | 2.0088 | -157.8373 | 149.0637
Line_1 | 0.088507 | 2.7229 | 2.7871 | 0.088507 | 2.7229 | 2.7871 | 1.022 | 31.441 | 32.1826 | 1.022 | 31.441 | 32.1826 | 1.0131 | -14.0477 | 14.5542 | -1.0053 | 21.4498 | -6.7988 | 0.26704 | 7.8991 | -7.7655 | -0.26242 | -3.5248 | 12.3486 | -12.6212 | 31.4946 | -149.7721 | 167.3788 | -148.5054 | 30.2279 | 1.0252 | 0.51259 | 0.51259 | 1.0166 | 0.69137 | 0.43802 | 2.1453 | -177.8547 | -177.8547 | 2.0088 | -157.8373 | 149.0637
Line_2 | 0.054898 | 0.49207 | 0.43864 | 0.054898 | 0.49207 | 0.43864 | 0.6339 | 5.682 | 5.065 | 0.6339 | 5.682 | 5.065 | 0.64057 | 4.1698 | -1.0682 | -0.63756 | -3.928 | 1.2602 | -0.092125 | 0.092595 | 1.9394 | 0.093903 | 0.050265 | -1.8258 | 10.3873 | -157.1042 | 24.4491 | -169.6127 | 22.8958 | -155.5509 | 1.0209 | 0.73405 | 0.43713 | 1.0166 | 0.69137 | 0.43802 | 2.2033 | -155.8321 | 143.2941 | 2.0088 | -157.8373 | 149.0637

## LL_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.064934 | 1.0328 | 1.0852 | 0.064934 | 1.0328 | 1.0852 | 0.7498 | 11.9253 | 12.5306 | 0.7498 | 11.9253 | 12.5306 | -0.74591 | 11.3062 | 2.3283 | 0.75012 | -10.2413 | -1.1526 | 0.070648 | 0.82643 | 9.4403 | -0.06816 | -0.19713 | -8.7455 | -173.8109 | -136.5841 | 41.3413 | 6.1891 | 43.4159 | -138.6587 | 0.99927 | 0.95061 | 0.77596 | 1.0046 | 0.85895 | 0.70397 | 0.77863 | -132.4035 | 117.4865 | 0.99722 | -135.4814 | 123.8333
Line_1 | 0.040852 | 1.2568 | 1.2864 | 0.040852 | 1.2568 | 1.2864 | 0.47172 | 14.512 | 14.8543 | 0.47172 | 14.512 | 14.8543 | 0.47461 | -10.8711 | 0.48087 | -0.47294 | 12.4481 | 1.1714 | 0.030585 | 0.28236 | -9.4148 | -0.0296 | 0.64954 | 10.3912 | -2.5841 | 41.5316 | -139.7351 | 177.4159 | -138.4684 | 40.2649 | 1.0082 | 0.74937 | 0.63463 | 1.0046 | 0.85895 | 0.70397 | 1.1031 | -139.9562 | 133.1889 | 0.99722 | -135.4814 | 123.8333
Line_2 | 0.025339 | 0.22712 | 0.20246 | 0.025339 | 0.22712 | 0.20246 | 0.29259 | 2.6226 | 2.3378 | 0.29259 | 2.6226 | 2.3378 | 0.27783 | 2.2583 | 0.059675 | -0.27718 | -2.2068 | -0.018751 | -0.097381 | 0.48284 | 1.6698 | 0.09776 | -0.45241 | -1.6456 | 20.4244 | -147.0671 | 34.4862 | -159.5756 | 32.9329 | -145.5138 | 1.0062 | 0.88055 | 0.71472 | 1.0046 | 0.85895 | 0.70397 | 1.1082 | -134.9983 | 122.4394 | 0.99722 | -135.4814 | 123.8333

## LL_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.064934 | 1.0328 | 1.0852 | 0.064934 | 1.0328 | 1.0852 | 0.7498 | 11.9253 | 12.5306 | 0.7498 | 11.9253 | 12.5306 | -0.74591 | 11.3062 | 2.3283 | 0.75012 | -10.2413 | -1.1526 | 0.070648 | 0.82643 | 9.4403 | -0.06816 | -0.19713 | -8.7455 | -173.8109 | -136.5841 | 41.3413 | 6.1891 | 43.4159 | -138.6587 | 0.99927 | 0.95061 | 0.77596 | 1.0046 | 0.85895 | 0.70397 | 0.77863 | -132.4035 | 117.4865 | 0.99722 | -135.4814 | 123.8333
Line_1 | 0.040852 | 1.2568 | 1.2864 | 0.040852 | 1.2568 | 1.2864 | 0.47172 | 14.512 | 14.8543 | 0.47172 | 14.512 | 14.8543 | 0.47461 | -10.8711 | 0.48087 | -0.47294 | 12.4481 | 1.1714 | 0.030585 | 0.28236 | -9.4148 | -0.0296 | 0.64954 | 10.3912 | -2.5841 | 41.5316 | -139.7351 | 177.4159 | -138.4684 | 40.2649 | 1.0082 | 0.74937 | 0.63463 | 1.0046 | 0.85895 | 0.70397 | 1.1031 | -139.9562 | 133.1889 | 0.99722 | -135.4814 | 123.8333
Line_2 | 0.025339 | 0.22712 | 0.20246 | 0.025339 | 0.22712 | 0.20246 | 0.29259 | 2.6226 | 2.3378 | 0.29259 | 2.6226 | 2.3378 | 0.27783 | 2.2583 | 0.059675 | -0.27718 | -2.2068 | -0.018751 | -0.097381 | 0.48284 | 1.6698 | 0.09776 | -0.45241 | -1.6456 | 20.4244 | -147.0671 | 34.4862 | -159.5756 | 32.9329 | -145.5138 | 1.0062 | 0.88055 | 0.71472 | 1.0046 | 0.85895 | 0.70397 | 1.1082 | -134.9983 | 122.4394 | 0.99722 | -135.4814 | 123.8333

## LG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.6434 | 0.78618 | 0.67182 | 1.6413 | 0.78817 | 0.67381 | 18.9767 | 9.0781 | 7.7576 | 18.9523 | 9.101 | 7.7805 | 6.4233 | -10.1593 | 9.4098 | -4.5874 | 10.3588 | -9.4017 | 5.9542 | 6.6018 | 0.86153 | -4.0836 | -6.4579 | -0.65997 | -70.864 | 87.759 | 126.8247 | 109.1385 | -92.1901 | -53.2356 |  | 0.46154 | 1.3346 | 1.2181 | 0.32406 | 1.3413 | 1.2113 | -28.0345 | -125.2579 | 132.0559 | -29.1867 | -124.1303 | 130.7798
Line_1 | 2.5106 | 0.59382 | 0.43086 | 2.513 | 0.59149 | 0.42837 | 28.9901 | 6.8568 | 4.9751 | 29.0181 | 6.8299 | 4.9464 | 9.6622e-11 | 8.325 | -5.7347 | 7.2389 | -8.5766 | 5.2026 | -9.0032e-11 | -4.0112 | -3.3859 | 6.002 | 3.219 | 2.9722 | 111.1634 | -103.4718 | -78.9801 | -68.8501 | 76.4417 | 101.0405 |  | 0 | 1.3477 | 1.3386 | 0.32406 | 1.3413 | 1.2113 | 0 | -129.1977 | 131.5782 | -29.1867 | -124.1303 | 130.7798
Line_2 | 0.87655 | 0.24062 | 0.34407 | 0.87463 | 0.2387 | 0.34271 | 10.1215 | 2.7784 | 3.973 | 10.0993 | 2.7563 | 3.9573 | 4.254 | 2.1621 | -3.6684 | -2.6515 | -1.7822 | 4.1991 | 2.9565 | -3.083 | 2.208 | -1.9184 | 3.2389 | -2.3123 | -65.0747 | -62.9734 | -20.6078 | 114.9265 | 117.048 | 159.6195 |  | 0.51183 | 1.3553 | 1.0777 | 0.32406 | 1.3413 | 1.2113 | -30.2756 | -117.9307 | 128.3488 | -29.1867 | -124.1303 | 130.7798

## LG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.6434 | 0.78618 | 0.67182 | 1.6413 | 0.78817 | 0.67381 | 18.9767 | 9.0781 | 7.7576 | 18.9523 | 9.101 | 7.7805 | 6.4233 | -10.1593 | 9.4098 | -4.5874 | 10.3588 | -9.4017 | 5.9542 | 6.6018 | 0.86153 | -4.0836 | -6.4579 | -0.65997 | -70.864 | 87.759 | 126.8247 | 109.1385 | -92.1901 | -53.2356 |  | 0.46154 | 1.3346 | 1.2181 | 0.32406 | 1.3413 | 1.2113 | -28.0345 | -125.2579 | 132.0559 | -29.1867 | -124.1303 | 130.7798
Line_1 | 2.5106 | 0.59382 | 0.43086 | 2.513 | 0.59149 | 0.42837 | 28.9901 | 6.8568 | 4.9751 | 29.0181 | 6.8299 | 4.9464 | 9.6622e-11 | 8.325 | -5.7347 | 7.2389 | -8.5766 | 5.2026 | -9.0032e-11 | -4.0112 | -3.3859 | 6.002 | 3.219 | 2.9722 | 111.1634 | -103.4718 | -78.9801 | -68.8501 | 76.4417 | 101.0405 |  | 0 | 1.3477 | 1.3386 | 0.32406 | 1.3413 | 1.2113 | 0 | -129.1977 | 131.5782 | -29.1867 | -124.1303 | 130.7798
Line_2 | 0.87655 | 0.24062 | 0.34407 | 0.87463 | 0.2387 | 0.34271 | 10.1215 | 2.7784 | 3.973 | 10.0993 | 2.7563 | 3.9573 | 4.254 | 2.1621 | -3.6684 | -2.6515 | -1.7822 | 4.1991 | 2.9565 | -3.083 | 2.208 | -1.9184 | 3.2389 | -2.3123 | -65.0747 | -62.9734 | -20.6078 | 114.9265 | 117.048 | 159.6195 |  | 0.51183 | 1.3553 | 1.0777 | 0.32406 | 1.3413 | 1.2113 | -30.2756 | -117.9307 | 128.3488 | -29.1867 | -124.1303 | 130.7798

## LG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.4414 | 0.20298 | 0.3306 | 0.4407 | 0.20338 | 0.33109 | 5.0969 | 2.3438 | 3.8174 | 5.0887 | 2.3485 | 3.8231 | 4.1536 | -2.8145 | 2.8295 | -4.0027 | 2.8404 | -2.8167 | 2.4269 | 0.53201 | -3.293 | -2.2901 | -0.53888 | 3.3658 | -39.4221 | 70.1431 | 174.1276 | 140.6007 | -109.6852 | -5.9654 |  | 0.94383 | 1.2221 | 1.1373 | 0.90623 | 1.231 | 1.148 | -9.125 | -120.5608 | 124.7986 | -9.6242 | -120.4279 | 123.9588
Line_1 | 0.79983 | 0.18585 | 0.1577 | 0.80066 | 0.18523 | 0.15699 | 9.2357 | 2.146 | 1.821 | 9.2452 | 2.1389 | 1.8128 | -5.9284 | 2.5905 | -1.936 | 6.7158 | -2.5695 | 1.8394 | -4.3965 | -0.68183 | 0.97119 | 5.0094 | 0.57479 | -0.97335 | 133.6736 | -107.6306 | -28.334 | -46.3442 | 72.1813 | 151.8457 |  | 0.79915 | 1.2482 | 1.1894 | 0.90623 | 1.231 | 1.148 | -9.766 | -122.3765 | 125.0251 | -9.6242 | -120.4279 | 123.9588
Line_2 | 0.36775 | 0.019326 | 0.19532 | 0.36709 | 0.01922 | 0.19496 | 4.2464 | 0.22315 | 2.2553 | 4.2388 | 0.22194 | 2.2512 | 2.9475 | 0.27073 | -0.87832 | -2.7131 | -0.27084 | 0.97732 | 2.9143 | 0.036766 | 2.3632 | -2.7194 | -0.035907 | -2.3925 | -54.6752 | -126.024 | 11.5734 | 125.3093 | 52.02 | -168.2611 |  | 0.97612 | 1.2243 | 1.1178 | 0.90623 | 1.231 | 1.148 | -9.9998 | -118.2903 | 121.9619 | -9.6242 | -120.4279 | 123.9588

## LG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.4414 | 0.20298 | 0.3306 | 0.4407 | 0.20338 | 0.33109 | 5.0969 | 2.3438 | 3.8174 | 5.0887 | 2.3485 | 3.8231 | 4.1536 | -2.8145 | 2.8295 | -4.0027 | 2.8404 | -2.8167 | 2.4269 | 0.53201 | -3.293 | -2.2901 | -0.53888 | 3.3658 | -39.4221 | 70.1431 | 174.1276 | 140.6007 | -109.6852 | -5.9654 |  | 0.94383 | 1.2221 | 1.1373 | 0.90623 | 1.231 | 1.148 | -9.125 | -120.5608 | 124.7986 | -9.6242 | -120.4279 | 123.9588
Line_1 | 0.79983 | 0.18585 | 0.1577 | 0.80066 | 0.18523 | 0.15699 | 9.2357 | 2.146 | 1.821 | 9.2452 | 2.1389 | 1.8128 | -5.9284 | 2.5905 | -1.936 | 6.7158 | -2.5695 | 1.8394 | -4.3965 | -0.68183 | 0.97119 | 5.0094 | 0.57479 | -0.97335 | 133.6736 | -107.6306 | -28.334 | -46.3442 | 72.1813 | 151.8457 |  | 0.79915 | 1.2482 | 1.1894 | 0.90623 | 1.231 | 1.148 | -9.766 | -122.3765 | 125.0251 | -9.6242 | -120.4279 | 123.9588
Line_2 | 0.36775 | 0.019326 | 0.19532 | 0.36709 | 0.01922 | 0.19496 | 4.2464 | 0.22315 | 2.2553 | 4.2388 | 0.22194 | 2.2512 | 2.9475 | 0.27073 | -0.87832 | -2.7131 | -0.27084 | 0.97732 | 2.9143 | 0.036766 | 2.3632 | -2.7194 | -0.035907 | -2.3925 | -54.6752 | -126.024 | 11.5734 | 125.3093 | 52.02 | -168.2611 |  | 0.97612 | 1.2243 | 1.1178 | 0.90623 | 1.231 | 1.148 | -9.9998 | -118.2903 | 121.9619 | -9.6242 | -120.4279 | 123.9588

## LG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.3958 | 0.65716 | 0.55576 | 1.3943 | 0.65863 | 0.55723 | 16.117 | 7.5882 | 6.4173 | 16.1 | 7.6052 | 6.4343 | 7.4994 | -4.8865 | 6.3891 | -5.0527 | 5.1077 | -6.296 | 5.0324 | 7.054 | 1.1085 | -3.6296 | -6.9563 | -1.027 | -61.4799 | 112.6029 | 119.1566 | 118.5226 | -67.389 | -60.8513 |  | 0.56036 | 1.1309 | 1.0105 | 0.38641 | 1.1348 | 0.99143 | -27.6166 | -122.6857 | 128.9996 | -25.7862 | -121.101 | 128.4129
Line_1 | 1.9195 | 0.56419 | 0.49281 | 1.9213 | 0.56223 | 0.49084 | 22.1641 | 6.5147 | 5.6905 | 22.1855 | 6.4921 | 5.6677 | -4.3685e-11 | 5.8163 | -5.1222 | 7.2417 | -6.0639 | 4.7804 | 6.3564e-12 | -5.1327 | -3.7681 | 4.588 | 4.1836 | 2.9535 | 121.8775 | -86.4693 | -83.2764 | -58.1429 | 93.5021 | 96.7036 |  | 0 | 1.1907 | 1.1175 | 0.38641 | 1.1348 | 0.99143 | 0 | -127.8969 | 133.0629 | -25.7862 | -121.101 | 128.4129
Line_2 | 0.53678 | 0.22477 | 0.21486 | 0.53556 | 0.22383 | 0.21412 | 6.1982 | 2.5954 | 2.481 | 6.1841 | 2.5846 | 2.4724 | 3.3661 | -0.48849 | -1.1134 | -2.189 | 0.95616 | 1.5156 | 1.5906 | -2.8281 | 1.8045 | -0.95846 | 2.7727 | -1.9265 | -49.4394 | -12.2748 | -0.03819 | 130.567 | 167.9259 | -179.78 |  | 0.60066 | 1.1058 | 0.85461 | 0.38641 | 1.1348 | 0.99143 | -24.1463 | -112.0745 | 121.636 | -25.7862 | -121.101 | 128.4129

## LG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.3958 | 0.65716 | 0.55576 | 1.3943 | 0.65863 | 0.55723 | 16.117 | 7.5882 | 6.4173 | 16.1 | 7.6052 | 6.4343 | 7.4994 | -4.8865 | 6.3891 | -5.0527 | 5.1077 | -6.296 | 5.0324 | 7.054 | 1.1085 | -3.6296 | -6.9563 | -1.027 | -61.4799 | 112.6029 | 119.1566 | 118.5226 | -67.389 | -60.8513 |  | 0.56036 | 1.1309 | 1.0105 | 0.38641 | 1.1348 | 0.99143 | -27.6166 | -122.6857 | 128.9996 | -25.7862 | -121.101 | 128.4129
Line_1 | 1.9195 | 0.56419 | 0.49281 | 1.9213 | 0.56223 | 0.49084 | 22.1641 | 6.5147 | 5.6905 | 22.1855 | 6.4921 | 5.6677 | -4.3685e-11 | 5.8163 | -5.1222 | 7.2417 | -6.0639 | 4.7804 | 6.3564e-12 | -5.1327 | -3.7681 | 4.588 | 4.1836 | 2.9535 | 121.8775 | -86.4693 | -83.2764 | -58.1429 | 93.5021 | 96.7036 |  | 0 | 1.1907 | 1.1175 | 0.38641 | 1.1348 | 0.99143 | 0 | -127.8969 | 133.0629 | -25.7862 | -121.101 | 128.4129
Line_2 | 0.53678 | 0.22477 | 0.21486 | 0.53556 | 0.22383 | 0.21412 | 6.1982 | 2.5954 | 2.481 | 6.1841 | 2.5846 | 2.4724 | 3.3661 | -0.48849 | -1.1134 | -2.189 | 0.95616 | 1.5156 | 1.5906 | -2.8281 | 1.8045 | -0.95846 | 2.7727 | -1.9265 | -49.4394 | -12.2748 | -0.03819 | 130.567 | 167.9259 | -179.78 |  | 0.60066 | 1.1058 | 0.85461 | 0.38641 | 1.1348 | 0.99143 | -24.1463 | -112.0745 | 121.636 | -25.7862 | -121.101 | 128.4129

## LG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.50708 | 0.23874 | 0.2019 | 0.50654 | 0.23928 | 0.20244 | 5.8553 | 2.7568 | 2.3314 | 5.8491 | 2.7629 | 2.3376 | 3.9993 | -1.0912 | 2.2579 | -3.6733 | 1.1211 | -2.2494 | 3.0475 | 2.6825 | -0.43271 | -2.8597 | -2.6736 | 0.44481 | -46.5722 | 127.5106 | 134.0642 | 133.4302 | -52.4814 | -45.9436 |  | 0.85872 | 1.0505 | 0.98609 | 0.79588 | 1.0493 | 0.98092 | -9.2646 | -120.3539 | 123.2153 | -8.6687 | -119.7313 | 122.8706
Line_1 | 0.69733 | 0.20497 | 0.17904 | 0.69801 | 0.20426 | 0.17832 | 8.0521 | 2.3668 | 2.0673 | 8.0599 | 2.3586 | 2.0591 | -4.3234 | 1.6211 | -2.0314 | 5.2823 | -1.6514 | 1.9809 | -3.0295 | -1.9734 | -0.50142 | 3.6395 | 1.8432 | 0.39436 | 136.7851 | -71.5617 | -68.3687 | -43.2352 | 108.4097 | 111.6113 |  | 0.65563 | 1.079 | 1.0121 | 0.79588 | 1.0493 | 0.98092 | -8.1957 | -122.1597 | 125.4964 | -8.6687 | -119.7313 | 122.8706
Line_2 | 0.19501 | 0.081657 | 0.078059 | 0.19457 | 0.081317 | 0.077788 | 2.2518 | 0.94289 | 0.90135 | 2.2467 | 0.93897 | 0.89822 | 1.7674 | -0.46864 | -0.2183 | -1.6091 | 0.53032 | 0.26851 | 0.86489 | -0.84103 | 0.82479 | -0.77981 | 0.83035 | -0.83918 | -34.5317 | 2.6328 | 14.8694 | 145.4747 | -177.1664 | -164.8724 |  | 0.87382 | 1.0211 | 0.94657 | 0.79588 | 1.0493 | 0.98092 | -8.4561 | -116.4947 | 119.694 | -8.6687 | -119.7313 | 122.8706

## LG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.50708 | 0.23874 | 0.2019 | 0.50654 | 0.23928 | 0.20244 | 5.8553 | 2.7568 | 2.3314 | 5.8491 | 2.7629 | 2.3376 | 3.9993 | -1.0912 | 2.2579 | -3.6733 | 1.1211 | -2.2494 | 3.0475 | 2.6825 | -0.43271 | -2.8597 | -2.6736 | 0.44481 | -46.5722 | 127.5106 | 134.0642 | 133.4302 | -52.4814 | -45.9436 |  | 0.85872 | 1.0505 | 0.98609 | 0.79588 | 1.0493 | 0.98092 | -9.2646 | -120.3539 | 123.2153 | -8.6687 | -119.7313 | 122.8706
Line_1 | 0.69733 | 0.20497 | 0.17904 | 0.69801 | 0.20426 | 0.17832 | 8.0521 | 2.3668 | 2.0673 | 8.0599 | 2.3586 | 2.0591 | -4.3234 | 1.6211 | -2.0314 | 5.2823 | -1.6514 | 1.9809 | -3.0295 | -1.9734 | -0.50142 | 3.6395 | 1.8432 | 0.39436 | 136.7851 | -71.5617 | -68.3687 | -43.2352 | 108.4097 | 111.6113 |  | 0.65563 | 1.079 | 1.0121 | 0.79588 | 1.0493 | 0.98092 | -8.1957 | -122.1597 | 125.4964 | -8.6687 | -119.7313 | 122.8706
Line_2 | 0.19501 | 0.081657 | 0.078059 | 0.19457 | 0.081317 | 0.077788 | 2.2518 | 0.94289 | 0.90135 | 2.2467 | 0.93897 | 0.89822 | 1.7674 | -0.46864 | -0.2183 | -1.6091 | 0.53032 | 0.26851 | 0.86489 | -0.84103 | 0.82479 | -0.77981 | 0.83035 | -0.83918 | -34.5317 | 2.6328 | 14.8694 | 145.4747 | -177.1664 | -164.8724 |  | 0.87382 | 1.0211 | 0.94657 | 0.79588 | 1.0493 | 0.98092 | -8.4561 | -116.4947 | 119.694 | -8.6687 | -119.7313 | 122.8706

## LLG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.37358 | 2.8433 | 2.9256 | 0.37516 | 2.8431 | 2.9254 | 4.3137 | 32.8311 | 33.7818 | 4.332 | 32.8295 | 33.7795 | -1.0089 | 13.4488 | 6.6766 | 1.0255 | -8.7935 | -2.5657 | 5.6822 | 6.3984 | 16.2021 | -5.7055 | -2.1781 | -10.5029 | -95.0158 | -166.3187 | 24.8508 | 85.0888 | 13.716 | -155.1827 |  | 1.3379 | 0.45363 | 0.51874 | 1.3382 | 0.27595 | 0.32007 | 5.0524 | -140.8753 | 92.455 | 5.2779 | -152.3724 | 101.0894
Line_1 | 0.3448 | 3.6878 | 3.5042 | 0.34305 | 3.6879 | 3.505 | 3.9814 | 42.5835 | 40.4625 | 3.9612 | 42.5843 | 40.4717 | 2.4264 | 8.8808e-11 | 1.0661e-10 | -2.4996 | 10.983 | 4.5533 | -5.1316 | -7.354e-11 | -9.5934e-12 | 4.6744 | 4.1787 | 12.1271 | 67.3202 | 6.8292 | -148.362 | -112.8576 | -173.2025 | 31.6687 |  | 1.4257 | 0 | 0 | 1.3382 | 0.27595 | 0.32007 | 2.6265 | 0 | 0 | 5.2779 | -152.3724 | 101.0894
Line_2 | 0.11772 | 0.93181 | 0.69544 | 0.11643 | 0.93079 | 0.6945 | 1.3593 | 10.7596 | 8.0302 | 1.3444 | 10.7478 | 8.0194 | -1.3304 | 3.7062 | 2.3939 | 1.4742 | -2.1895 | -1.9875 | -1.0658 | 2.0627 | 2.7597 | 1.0311 | -2.0006 | -1.6242 | 149.87 | 165.135 | 61.939 | -29.6935 | -14.7913 | -118.1656 |  | 1.254 | 0.39421 | 0.45495 | 1.3382 | 0.27595 | 0.32007 | 8.5684 | -165.7662 | 110.9995 | 5.2779 | -152.3724 | 101.0894

## LLG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.37358 | 2.8433 | 2.9256 | 0.37516 | 2.8431 | 2.9254 | 4.3137 | 32.8311 | 33.7818 | 4.332 | 32.8295 | 33.7795 | -1.0089 | 13.4488 | 6.6766 | 1.0255 | -8.7935 | -2.5657 | 5.6822 | 6.3984 | 16.2021 | -5.7055 | -2.1781 | -10.5029 | -95.0158 | -166.3187 | 24.8508 | 85.0888 | 13.716 | -155.1827 |  | 1.3379 | 0.45363 | 0.51874 | 1.3382 | 0.27595 | 0.32007 | 5.0524 | -140.8753 | 92.455 | 5.2779 | -152.3724 | 101.0894
Line_1 | 0.3448 | 3.6878 | 3.5042 | 0.34305 | 3.6879 | 3.505 | 3.9814 | 42.5835 | 40.4625 | 3.9612 | 42.5843 | 40.4717 | 2.4264 | 8.8808e-11 | 1.0661e-10 | -2.4996 | 10.983 | 4.5533 | -5.1316 | -7.354e-11 | -9.5934e-12 | 4.6744 | 4.1787 | 12.1271 | 67.3202 | 6.8292 | -148.362 | -112.8576 | -173.2025 | 31.6687 |  | 1.4257 | 0 | 0 | 1.3382 | 0.27595 | 0.32007 | 2.6265 | 0 | 0 | 5.2779 | -152.3724 | 101.0894
Line_2 | 0.11772 | 0.93181 | 0.69544 | 0.11643 | 0.93079 | 0.6945 | 1.3593 | 10.7596 | 8.0302 | 1.3444 | 10.7478 | 8.0194 | -1.3304 | 3.7062 | 2.3939 | 1.4742 | -2.1895 | -1.9875 | -1.0658 | 2.0627 | 2.7597 | 1.0311 | -2.0006 | -1.6242 | 149.87 | 165.135 | 61.939 | -29.6935 | -14.7913 | -118.1656 |  | 1.254 | 0.39421 | 0.45495 | 1.3382 | 0.27595 | 0.32007 | 8.5684 | -165.7662 | 110.9995 | 5.2779 | -152.3724 | 101.0894

## LLG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.038444 | 0.70889 | 0.66306 | 0.038695 | 0.70896 | 0.66288 | 0.44392 | 8.1856 | 7.6564 | 0.44681 | 8.1864 | 7.6543 | 0.52548 | 7.4462 | 3.8952 | -0.53296 | -7.1536 | -3.681 | -0.10292 | 1.778 | 6.6151 | 0.097933 | -1.5365 | -6.2957 | 14.3395 | -138.4256 | 50.8262 | -166.597 | 41.6289 | -129.2303 |  | 1.2062 | 0.93525 | 1.0027 | 1.2128 | 0.89377 | 0.95277 | 3.2573 | -124.996 | 110.3349 | 2.9909 | -126.2487 | 110.4553
Line_1 | 0.0619 | 0.99759 | 0.93123 | 0.061287 | 0.99761 | 0.93166 | 0.71476 | 11.5192 | 10.7529 | 0.70768 | 11.5194 | 10.7579 | 0.25502 | -8.0887 | -5.9326 | -0.26137 | 9.012 | 6.2865 | -0.86162 | -4.7999 | -7.0502 | 0.8175 | 4.9784 | 8.0957 | 75.7448 | 24.8803 | -121.7562 | -104.7394 | -155.1659 | 58.2855 |  | 1.2572 | 0.81652 | 0.8569 | 1.2128 | 0.89377 | 0.95277 | 2.232 | -124.4344 | 108.164 | 2.9909 | -126.2487 | 110.4553
Line_2 | 0.086449 | 0.37949 | 0.28818 | 0.086547 | 0.37901 | 0.28784 | 0.99823 | 4.382 | 3.3276 | 0.99936 | 4.3765 | 3.3237 | -0.78327 | 2.1128 | 2.6715 | 0.79433 | -1.8584 | -2.6055 | 0.87289 | 3.4917 | 1.9863 | -0.91543 | -3.4419 | -1.8 | -128.3625 | 172.0579 | 75.9198 | 52.0423 | -7.8828 | -104.1833 |  | 1.1749 | 0.93136 | 1.0004 | 1.2128 | 0.89377 | 0.95277 | 3.5401 | -129.1202 | 112.5504 | 2.9909 | -126.2487 | 110.4553

## LLG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.038444 | 0.70889 | 0.66306 | 0.038695 | 0.70896 | 0.66288 | 0.44392 | 8.1856 | 7.6564 | 0.44681 | 8.1864 | 7.6543 | 0.52548 | 7.4462 | 3.8952 | -0.53296 | -7.1536 | -3.681 | -0.10292 | 1.778 | 6.6151 | 0.097933 | -1.5365 | -6.2957 | 14.3395 | -138.4256 | 50.8262 | -166.597 | 41.6289 | -129.2303 |  | 1.2062 | 0.93525 | 1.0027 | 1.2128 | 0.89377 | 0.95277 | 3.2573 | -124.996 | 110.3349 | 2.9909 | -126.2487 | 110.4553
Line_1 | 0.0619 | 0.99759 | 0.93123 | 0.061287 | 0.99761 | 0.93166 | 0.71476 | 11.5192 | 10.7529 | 0.70768 | 11.5194 | 10.7579 | 0.25502 | -8.0887 | -5.9326 | -0.26137 | 9.012 | 6.2865 | -0.86162 | -4.7999 | -7.0502 | 0.8175 | 4.9784 | 8.0957 | 75.7448 | 24.8803 | -121.7562 | -104.7394 | -155.1659 | 58.2855 |  | 1.2572 | 0.81652 | 0.8569 | 1.2128 | 0.89377 | 0.95277 | 2.232 | -124.4344 | 108.164 | 2.9909 | -126.2487 | 110.4553
Line_2 | 0.086449 | 0.37949 | 0.28818 | 0.086547 | 0.37901 | 0.28784 | 0.99823 | 4.382 | 3.3276 | 0.99936 | 4.3765 | 3.3237 | -0.78327 | 2.1128 | 2.6715 | 0.79433 | -1.8584 | -2.6055 | 0.87289 | 3.4917 | 1.9863 | -0.91543 | -3.4419 | -1.8 | -128.3625 | 172.0579 | 75.9198 | 52.0423 | -7.8828 | -104.1833 |  | 1.1749 | 0.93136 | 1.0004 | 1.2128 | 0.89377 | 0.95277 | 3.5401 | -129.1202 | 112.5504 | 2.9909 | -126.2487 | 110.4553

## LLG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.44745 | 2.2387 | 2.3773 | 0.44861 | 2.2387 | 2.377 | 5.1667 | 25.8501 | 27.4504 | 5.1801 | 25.85 | 27.4471 | 0.37921 | 14.7845 | 9.7681 | -0.28652 | -9.4202 | -4.3276 | 5.7194 | 2.3891 | 12.2803 | -5.7205 | -0.06353 | -8.1984 | -81.2094 | -155.003 | 39.1175 | 98.8351 | 25.028 | -140.9109 |  | 1.1094 | 0.57935 | 0.57163 | 1.1057 | 0.36443 | 0.33776 | 4.9973 | -145.8235 | 90.6177 | 5.9678 | -154.5856 | 101.2612
Line_1 | 0.41712 | 2.8816 | 2.75 | 0.41558 | 2.8814 | 2.7509 | 4.8165 | 33.2741 | 31.7544 | 4.7987 | 33.2713 | 31.7643 | 1.1817 | -1.0169e-10 | -4.2563e-11 | -1.2371 | 12.0658 | 5.6306 | -5.8095 | -6.5326e-11 | -1.0843e-10 | 5.1597 | 1.1965 | 9.1324 | 82.556 | 19.7831 | -137.1115 | -97.515 | -160.2488 | 42.9172 |  | 1.2309 | 0 | 0 | 1.1057 | 0.36443 | 0.33776 | 4.0532 | 0 | 0 | 5.9678 | -154.5856 | 101.2612
Line_2 | 0.12794 | 0.68449 | 0.41153 | 0.12716 | 0.68392 | 0.41105 | 1.4774 | 7.9038 | 4.752 | 1.4683 | 7.8972 | 4.7464 | -1.3208 | 4.0615 | 1.4579 | 1.5236 | -2.6456 | -1.303 | -0.58963 | 0.97584 | 1.6594 | 0.5608 | -1.133 | -0.934 | 165.4799 | -177.8375 | 65.75 | -14.2397 | 2.2314 | -114.3725 |  | 0.97904 | 0.52849 | 0.46483 | 1.1057 | 0.36443 | 0.33776 | 9.5374 | -164.3273 | 114.4478 | 5.9678 | -154.5856 | 101.2612

## LLG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.44745 | 2.2387 | 2.3773 | 0.44861 | 2.2387 | 2.377 | 5.1667 | 25.8501 | 27.4504 | 5.1801 | 25.85 | 27.4471 | 0.37921 | 14.7845 | 9.7681 | -0.28652 | -9.4202 | -4.3276 | 5.7194 | 2.3891 | 12.2803 | -5.7205 | -0.06353 | -8.1984 | -81.2094 | -155.003 | 39.1175 | 98.8351 | 25.028 | -140.9109 |  | 1.1094 | 0.57935 | 0.57163 | 1.1057 | 0.36443 | 0.33776 | 4.9973 | -145.8235 | 90.6177 | 5.9678 | -154.5856 | 101.2612
Line_1 | 0.41712 | 2.8816 | 2.75 | 0.41558 | 2.8814 | 2.7509 | 4.8165 | 33.2741 | 31.7544 | 4.7987 | 33.2713 | 31.7643 | 1.1817 | -1.0169e-10 | -4.2563e-11 | -1.2371 | 12.0658 | 5.6306 | -5.8095 | -6.5326e-11 | -1.0843e-10 | 5.1597 | 1.1965 | 9.1324 | 82.556 | 19.7831 | -137.1115 | -97.515 | -160.2488 | 42.9172 |  | 1.2309 | 0 | 0 | 1.1057 | 0.36443 | 0.33776 | 4.0532 | 0 | 0 | 5.9678 | -154.5856 | 101.2612
Line_2 | 0.12794 | 0.68449 | 0.41153 | 0.12716 | 0.68392 | 0.41105 | 1.4774 | 7.9038 | 4.752 | 1.4683 | 7.8972 | 4.7464 | -1.3208 | 4.0615 | 1.4579 | 1.5236 | -2.6456 | -1.303 | -0.58963 | 0.97584 | 1.6594 | 0.5608 | -1.133 | -0.934 | 165.4799 | -177.8375 | 65.75 | -14.2397 | 2.2314 | -114.3725 |  | 0.97904 | 0.52849 | 0.46483 | 1.1057 | 0.36443 | 0.33776 | 9.5374 | -164.3273 | 114.4478 | 5.9678 | -154.5856 | 101.2612

## LLG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.18715 | 0.67049 | 0.70808 | 0.18763 | 0.67045 | 0.70795 | 2.161 | 7.7421 | 8.1763 | 2.1666 | 7.7416 | 8.1747 | 0.94706 | 6.2232 | 4.102 | -0.93462 | -5.7251 | -3.6195 | 2.0239 | 2.1568 | 6.0497 | -2.0244 | -1.9618 | -5.663 | -62.3943 | -145.5504 | 54.7374 | 117.637 | 34.492 | -125.3015 |  | 1.034 | 0.85072 | 0.89397 | 1.0291 | 0.78173 | 0.82215 | 2.5287 | -126.4358 | 110.598 | 2.8551 | -126.5934 | 112.1138
Line_1 | 0.17202 | 0.88605 | 0.81591 | 0.17138 | 0.88601 | 0.8163 | 1.9863 | 10.2313 | 9.4213 | 1.9789 | 10.2308 | 9.4258 | -0.26588 | -5.9489 | -4.3377 | 0.24666 | 7.2481 | 4.8104 | -2.133 | -3.335 | -5.1001 | 2.0216 | 3.3807 | 6.0756 | 99.8698 | 28.4445 | -119.5541 | -80.1883 | -151.5986 | 60.484 |  | 1.0821 | 0.66658 | 0.71065 | 1.0291 | 0.78173 | 0.82215 | 2.7645 | -122.28 | 110.0639 | 2.8551 | -126.5934 | 112.1138
Line_2 | 0.058201 | 0.23086 | 0.13304 | 0.057893 | 0.2306 | 0.13276 | 0.67205 | 2.6658 | 1.5362 | 0.66849 | 2.6627 | 1.533 | -0.65244 | 1.7128 | 1.2291 | 0.68796 | -1.523 | -1.1909 | -0.01109 | 1.4068 | 0.50281 | 0.0028328 | -1.4189 | -0.41269 | -177.65 | -169.6439 | 93.1321 | 2.6192 | 10.4338 | -86.9997 |  | 0.97096 | 0.83144 | 0.86444 | 1.0291 | 0.78173 | 0.82215 | 3.3238 | -130.2454 | 115.3817 | 2.8551 | -126.5934 | 112.1138

## LLG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.18715 | 0.67049 | 0.70808 | 0.18763 | 0.67045 | 0.70795 | 2.161 | 7.7421 | 8.1763 | 2.1666 | 7.7416 | 8.1747 | 0.94706 | 6.2232 | 4.102 | -0.93462 | -5.7251 | -3.6195 | 2.0239 | 2.1568 | 6.0497 | -2.0244 | -1.9618 | -5.663 | -62.3943 | -145.5504 | 54.7374 | 117.637 | 34.492 | -125.3015 |  | 1.034 | 0.85072 | 0.89397 | 1.0291 | 0.78173 | 0.82215 | 2.5287 | -126.4358 | 110.598 | 2.8551 | -126.5934 | 112.1138
Line_1 | 0.17202 | 0.88605 | 0.81591 | 0.17138 | 0.88601 | 0.8163 | 1.9863 | 10.2313 | 9.4213 | 1.9789 | 10.2308 | 9.4258 | -0.26588 | -5.9489 | -4.3377 | 0.24666 | 7.2481 | 4.8104 | -2.133 | -3.335 | -5.1001 | 2.0216 | 3.3807 | 6.0756 | 99.8698 | 28.4445 | -119.5541 | -80.1883 | -151.5986 | 60.484 |  | 1.0821 | 0.66658 | 0.71065 | 1.0291 | 0.78173 | 0.82215 | 2.7645 | -122.28 | 110.0639 | 2.8551 | -126.5934 | 112.1138
Line_2 | 0.058201 | 0.23086 | 0.13304 | 0.057893 | 0.2306 | 0.13276 | 0.67205 | 2.6658 | 1.5362 | 0.66849 | 2.6627 | 1.533 | -0.65244 | 1.7128 | 1.2291 | 0.68796 | -1.523 | -1.1909 | -0.01109 | 1.4068 | 0.50281 | 0.0028328 | -1.4189 | -0.41269 | -177.65 | -169.6439 | 93.1321 | 2.6192 | 10.4338 | -86.9997 |  | 0.97096 | 0.83144 | 0.86444 | 1.0291 | 0.78173 | 0.82215 | 3.3238 | -130.2454 | 115.3817 | 2.8551 | -126.5934 | 112.1138