## LLL_max_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 4.283 | 4.283 | 0 | 9.2778 | 148.3662 | 148.3662 | 28.6163 | -1e-07 | 32.4685 | -1e-07 | -77.7798 | 102.2202 | 0.29171 | 0 | -29.1714 | 0
Line_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6021e-19 | 0 | -1.2515e-19 | 0 | 0 | 0 | 0 | 0 | 0
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6021e-19 | 0 | -1.2515e-19 | 0 | 0 | 0 | 0 | 0 | 0
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## LLL_max_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 4.283 | 4.283 | 0 | 9.2778 | 148.3662 | 148.3662 | 28.6163 | -1e-07 | 32.4685 | -1e-07 | -77.7798 | 102.2202 | 0.29171 | 0 | -29.1714 | 0
Line_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6021e-19 | 0 | -1.2515e-19 | 0 | 0 | 0 | 0 | 0 | 0
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6021e-19 | 0 | -1.2515e-19 | 0 | 0 | 0 | 0 | 0 | 0
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## LLL_max_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 1.3097 | 1.3097 | 0 | 2.8371 | 45.3689 | 45.3689 | 28.405 | -25.7292 | 28.7652 | -25.7292 | -54.5297 | 125.4703 | 0.89106 | 0.80202 | -9.1687 | -9.5297
Line_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.495e-09 | 0 | 1.6067e-09 | 0 | 0 | 0.80202 | 0.80202 | -9.5297 | -9.5297
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.495e-09 | 0 | 1.6067e-09 | 0 | 0 | 0.80202 | 0.80202 | -9.5297 | -9.5297
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80202 | 0.80202 | -9.5297 | -9.5297

## LLL_max_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 1.3097 | 1.3097 | 0 | 2.8371 | 45.3689 | 45.3689 | 28.405 | -25.7292 | 28.7652 | -25.7292 | -54.5297 | 125.4703 | 0.89106 | 0.80202 | -9.1687 | -9.5297
Line_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.495e-09 | 0 | 1.6067e-09 | 0 | 0 | 0.80202 | 0.80202 | -9.5297 | -9.5297
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.495e-09 | 0 | 1.6067e-09 | 0 | 0 | 0.80202 | 0.80202 | -9.5297 | -9.5297
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80202 | 0.80202 | -9.5297 | -9.5297

## LLL_min_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 3.6016 | 3.6016 | 0 | 6.8381 | 124.7634 | 124.7634 | 38.8525 | -1e-07 | 22.9597 | -1e-07 | -69.6723 | 110.3277 | 0.36172 | 0 | -39.0915 | 0
Line_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.731e-20 | 0 | 6.3235e-20 | 0 | 0 | 0 | 0 | 0 | 0
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.731e-20 | 0 | 6.3235e-20 | 0 | 0 | 0 | 0 | 0 | 0
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## LLL_min_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 3.6016 | 3.6016 | 0 | 6.8381 | 124.7634 | 124.7634 | 38.8525 | -1e-07 | 22.9597 | -1e-07 | -69.6723 | 110.3277 | 0.36172 | 0 | -39.0915 | 0
Line_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.731e-20 | 0 | 6.3235e-20 | 0 | 0 | 0 | 0 | 0 | 0
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.731e-20 | 0 | 6.3235e-20 | 0 | 0 | 0 | 0 | 0 | 0
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## LLL_min_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 1.1462 | 1.1462 | 0 | 2.1763 | 39.7072 | 39.7072 | 23.6436 | -19.7082 | 22.0338 | -19.7082 | -52.6343 | 127.3657 | 0.81393 | 0.70193 | -9.6527 | -7.6343
Line_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.233e-09 | 0 | 1.0258e-09 | 0 | 0 | 0.70193 | 0.70193 | -7.6343 | -7.6343
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.233e-09 | 0 | 1.0258e-09 | 0 | 0 | 0.70193 | 0.70193 | -7.6343 | -7.6343
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.70193 | 0.70193 | -7.6343 | -7.6343

## LLL_min_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 1.1462 | 1.1462 | 0 | 2.1763 | 39.7072 | 39.7072 | 23.6436 | -19.7082 | 22.0338 | -19.7082 | -52.6343 | 127.3657 | 0.81393 | 0.70193 | -9.6527 | -7.6343
Line_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.233e-09 | 0 | 1.0258e-09 | 0 | 0 | 0.70193 | 0.70193 | -7.6343 | -7.6343
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.233e-09 | 0 | 1.0258e-09 | 0 | 0 | 0.70193 | 0.70193 | -7.6343 | -7.6343
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.70193 | 0.70193 | -7.6343 | -7.6343

## LL_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 3.7092 | 3.7092 | 0 | 3.7092 | 3.7092 | 0 | 42.8296 | 42.8296 | 0 | 42.8296 | 42.8296 | -2.0843e-14 | 30.1766 | -15.8685 | 5.2106e-15 | -23.0225 | 23.0225 | -3.1264e-14 | 3.131 | 13.1032 | 5.2106e-14 | 4.9861 | -4.9861 | 0 | -167.7798 | 12.2202 | 0 | 12.2202 | -167.7798 | 1.1 | 0.70836 | 0.48049 | 1.1 | 0.55 | 0.55 | 1.1634e-12 | -161.8563 | 152.6723 | 1.1544e-12 | 180 | -180
Line_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.2106e-14 | -1.8237e-14 | 5.2107e-15 | 4.1685e-14 | 3.3869e-14 | -1.5632e-14 | 5.2106e-14 | -1.9212e-09 | 1.9211e-09 | -3.1264e-14 | 1.9212e-09 | -1.9211e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.55 | 0.55 | 1.1 | 0.55 | 0.55 | 1.1033e-12 | -180 | 180 | 1.1544e-12 | 180 | -180
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.1685e-14 | -2.8659e-14 | 1.5632e-14 | 3.1264e-14 | 3.3869e-14 | -1.5632e-14 | 4.6896e-14 | -1.9212e-09 | 1.9211e-09 | -2.6053e-14 | 1.9212e-09 | -1.9211e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.55 | 0.55 | 1.1 | 0.55 | 0.55 | 1.1084e-12 | -180 | 180 | 1.1544e-12 | 180 | -180
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.0421e-14 | 1.3027e-14 | -1.0421e-14 | -1.008e-28 | 0 | -5.2106e-15 | 1.5632e-14 | -7.816e-15 | -1.0421e-14 | 5.2106e-15 | 0 | -1.0421e-14 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.55 | 0.55 | 1.1 | 0.55 | 0.55 | 1.1033e-12 | -180 | 180 | 1.1084e-12 | -180 | 180

## LL_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 3.7092 | 3.7092 | 0 | 3.7092 | 3.7092 | 0 | 42.8296 | 42.8296 | 0 | 42.8296 | 42.8296 | -2.0843e-14 | 30.1766 | -15.8685 | 5.2106e-15 | -23.0225 | 23.0225 | -3.1264e-14 | 3.131 | 13.1032 | 5.2106e-14 | 4.9861 | -4.9861 | 0 | -167.7798 | 12.2202 | 0 | 12.2202 | -167.7798 | 1.1 | 0.70836 | 0.48049 | 1.1 | 0.55 | 0.55 | 1.1634e-12 | -161.8563 | 152.6723 | 1.1544e-12 | 180 | -180
Line_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.2106e-14 | -1.8237e-14 | 5.2107e-15 | 4.1685e-14 | 3.3869e-14 | -1.5632e-14 | 5.2106e-14 | -1.9212e-09 | 1.9211e-09 | -3.1264e-14 | 1.9212e-09 | -1.9211e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.55 | 0.55 | 1.1 | 0.55 | 0.55 | 1.1033e-12 | -180 | 180 | 1.1544e-12 | 180 | -180
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.1685e-14 | -2.8659e-14 | 1.5632e-14 | 3.1264e-14 | 3.3869e-14 | -1.5632e-14 | 4.6896e-14 | -1.9212e-09 | 1.9211e-09 | -2.6053e-14 | 1.9212e-09 | -1.9211e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.55 | 0.55 | 1.1 | 0.55 | 0.55 | 1.1084e-12 | -180 | 180 | 1.1544e-12 | 180 | -180
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.0421e-14 | 1.3027e-14 | -1.0421e-14 | -1.008e-28 | 0 | -5.2106e-15 | 1.5632e-14 | -7.816e-15 | -1.0421e-14 | 5.2106e-15 | 0 | -1.0421e-14 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.55 | 0.55 | 1.1 | 0.55 | 0.55 | 1.1033e-12 | -180 | 180 | 1.1084e-12 | -180 | 180

## LL_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 1.7631 | 1.7631 | 0 | 1.7631 | 1.7631 | 0 | 20.3584 | 20.3584 | 0 | 20.3584 | 20.3584 | -1.5632e-14 | 19.0761 | -0.30087 | 1.3027e-14 | -17.4596 | 1.9173 | -1.5632e-14 | 3.9919 | 15.2185 | 2.0843e-14 | -2.1579 | -13.3845 | 0 | -149.913 | 30.087 | 0 | 30.087 | -149.913 | 1.1 | 0.95731 | 0.74767 | 1.1 | 0.86414 | 0.66415 | -2.4055e-12 | -138.0936 | 121.2196 | -2.4107e-12 | -142.8673 | 128.239
Line_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.8623e-28 | 4.7339e-10 | 1.0337e-09 | -5.2106e-15 | -4.7338e-10 | -1.0337e-09 | 2.0843e-14 | -1.3544e-09 | 3.8384e-10 | -1.5632e-14 | 1.3544e-09 | -3.8385e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.86414 | 0.66415 | 1.1 | 0.86414 | 0.66415 | -2.4362e-12 | -142.8673 | 128.239 | -2.4107e-12 | -142.8673 | 128.239
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.816e-15 | 4.734e-10 | 1.0337e-09 | -1.3027e-14 | -4.7339e-10 | -1.0337e-09 | 2.0843e-14 | -1.3544e-09 | 3.8385e-10 | -1.3027e-14 | 1.3544e-09 | -3.8385e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.86414 | 0.66415 | 1.1 | 0.86414 | 0.66415 | -2.433e-12 | -142.8673 | 128.239 | -2.4107e-12 | -142.8673 | 128.239
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.816e-15 | 7.9238e-16 | -4.9421e-15 | 2.6053e-15 | 2.8672e-15 | -1.9472e-15 | 5.2106e-15 | 5.7344e-15 | -3.8945e-15 | 2.6053e-15 | -3.9619e-16 | 2.471e-15 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.86414 | 0.66415 | 1.1 | 0.86414 | 0.66415 | -2.4362e-12 | -142.8673 | 128.239 | -2.433e-12 | -142.8673 | 128.239

## LL_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 1.7631 | 1.7631 | 0 | 1.7631 | 1.7631 | 0 | 20.3584 | 20.3584 | 0 | 20.3584 | 20.3584 | -1.5632e-14 | 19.0761 | -0.30087 | 1.3027e-14 | -17.4596 | 1.9173 | -1.5632e-14 | 3.9919 | 15.2185 | 2.0843e-14 | -2.1579 | -13.3845 | 0 | -149.913 | 30.087 | 0 | 30.087 | -149.913 | 1.1 | 0.95731 | 0.74767 | 1.1 | 0.86414 | 0.66415 | -2.4055e-12 | -138.0936 | 121.2196 | -2.4107e-12 | -142.8673 | 128.239
Line_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.8623e-28 | 4.7339e-10 | 1.0337e-09 | -5.2106e-15 | -4.7338e-10 | -1.0337e-09 | 2.0843e-14 | -1.3544e-09 | 3.8384e-10 | -1.5632e-14 | 1.3544e-09 | -3.8385e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.86414 | 0.66415 | 1.1 | 0.86414 | 0.66415 | -2.4362e-12 | -142.8673 | 128.239 | -2.4107e-12 | -142.8673 | 128.239
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.816e-15 | 4.734e-10 | 1.0337e-09 | -1.3027e-14 | -4.7339e-10 | -1.0337e-09 | 2.0843e-14 | -1.3544e-09 | 3.8385e-10 | -1.3027e-14 | 1.3544e-09 | -3.8385e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.86414 | 0.66415 | 1.1 | 0.86414 | 0.66415 | -2.433e-12 | -142.8673 | 128.239 | -2.4107e-12 | -142.8673 | 128.239
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.816e-15 | 7.9238e-16 | -4.9421e-15 | 2.6053e-15 | 2.8672e-15 | -1.9472e-15 | 5.2106e-15 | 5.7344e-15 | -3.8945e-15 | 2.6053e-15 | -3.9619e-16 | 2.471e-15 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.86414 | 0.66415 | 1.1 | 0.86414 | 0.66415 | -2.4362e-12 | -142.8673 | 128.239 | -2.433e-12 | -142.8673 | 128.239

## LL_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 3.1191 | 3.1191 | 0 | 3.1191 | 3.1191 | 0 | 36.0161 | 36.0161 | 0 | 36.0161 | 36.0161 | 2.3685e-14 | 26.5997 | -7.1734 | -3.5527e-14 | -16.8865 | 16.8865 | 4.6316e-27 | -0.51586 | 11.9957 | -4.737e-15 | 6.2558 | -6.2558 | 0 | -159.6723 | 20.3277 | 0 | 20.3277 | -159.6723 | 1 | 0.73869 | 0.38808 | 1 | 0.5 | 0.5 | 1.1204e-11 | -160.7833 | 141.207 | 1.123e-11 | -180 | 180
Line_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.3159e-14 | 8.2898e-15 | 1.1842e-14 | 2.1316e-14 | -2.3685e-15 | -4.737e-15 | -1.8948e-14 | -1.5877e-09 | 1.5877e-09 | 1.4211e-14 | 1.5877e-09 | -1.5877e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 1.1227e-11 | -180 | 180 | 1.123e-11 | -180 | 180
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.5527e-14 | 3.5528e-15 | 2.3686e-15 | 2.3685e-14 | 2.3685e-15 | 4.7369e-15 | -1.8948e-14 | -1.5877e-09 | 1.5877e-09 | 1.4211e-14 | 1.5877e-09 | -1.5877e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 1.1244e-11 | -180 | 180 | 1.123e-11 | -180 | 180
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.3685e-15 | 1.3027e-14 | 1.1842e-14 | -9.4739e-15 | -2.6628e-25 | 2.3685e-15 | -4.737e-15 | 7.1054e-15 | -4.737e-15 | -4.737e-15 | 4.737e-15 | 1.4211e-14 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 1.1227e-11 | -180 | 180 | 1.1244e-11 | -180 | 180

## LL_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 3.1191 | 3.1191 | 0 | 3.1191 | 3.1191 | 0 | 36.0161 | 36.0161 | 0 | 36.0161 | 36.0161 | 2.3685e-14 | 26.5997 | -7.1734 | -3.5527e-14 | -16.8865 | 16.8865 | 4.6316e-27 | -0.51586 | 11.9957 | -4.737e-15 | 6.2558 | -6.2558 | 0 | -159.6723 | 20.3277 | 0 | 20.3277 | -159.6723 | 1 | 0.73869 | 0.38808 | 1 | 0.5 | 0.5 | 1.1204e-11 | -160.7833 | 141.207 | 1.123e-11 | -180 | 180
Line_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.3159e-14 | 8.2898e-15 | 1.1842e-14 | 2.1316e-14 | -2.3685e-15 | -4.737e-15 | -1.8948e-14 | -1.5877e-09 | 1.5877e-09 | 1.4211e-14 | 1.5877e-09 | -1.5877e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 1.1227e-11 | -180 | 180 | 1.123e-11 | -180 | 180
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.5527e-14 | 3.5528e-15 | 2.3686e-15 | 2.3685e-14 | 2.3685e-15 | 4.7369e-15 | -1.8948e-14 | -1.5877e-09 | 1.5877e-09 | 1.4211e-14 | 1.5877e-09 | -1.5877e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 1.1244e-11 | -180 | 180 | 1.123e-11 | -180 | 180
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.3685e-15 | 1.3027e-14 | 1.1842e-14 | -9.4739e-15 | -2.6628e-25 | 2.3685e-15 | -4.737e-15 | 7.1054e-15 | -4.737e-15 | -4.737e-15 | 4.737e-15 | 1.4211e-14 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 1.1227e-11 | -180 | 180 | 1.1244e-11 | -180 | 180

## LL_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 1.5183 | 1.5183 | 0 | 1.5183 | 1.5183 | 0 | 17.5318 | 17.5318 | 0 | 17.5318 | 17.5318 | 5.9212e-15 | 15.3932 | 0.73601 | -1.125e-14 | -13.0917 | 1.5655 | 2.3685e-15 | 2.3135 | 11.9328 | -7.1054e-15 | -0.95344 | -10.5727 | 0 | -146.7238 | 33.2762 | 0 | 33.2762 | -146.7238 | 1 | 0.88788 | 0.68193 | 1 | 0.74872 | 0.60963 | 3.7757e-12 | -138.1765 | 119.7467 | 3.7851e-12 | -142.5584 | 131.6989
Line_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.4211e-14 | 4.798e-10 | 8.2616e-10 | 9.4739e-15 | -4.798e-10 | -8.2616e-10 | -4.737e-15 | -1.0532e-09 | 4.5325e-10 | 6.2587e-28 | 1.0532e-09 | -4.5325e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.74872 | 0.60963 | 1 | 0.74872 | 0.60963 | 3.784e-12 | -142.5584 | 131.6989 | 3.7851e-12 | -142.5584 | 131.6989
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -9.4739e-15 | 4.798e-10 | 8.2616e-10 | 4.737e-15 | -4.7979e-10 | -8.2615e-10 | -1.1842e-14 | -1.0532e-09 | 4.5325e-10 | 7.1054e-15 | 1.0532e-09 | -4.5325e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.74872 | 0.60963 | 1 | 0.74872 | 0.60963 | 3.7922e-12 | -142.5584 | 131.6989 | 3.7851e-12 | -142.5584 | 131.6989
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.5133e-15 | 4.5538e-15 | 6.9488e-15 | 2.9606e-15 | -3.5642e-15 | 3.1167e-15 | 7.1054e-15 | 5.7203e-15 | 5.224e-15 | -9.4739e-15 | 1.7378e-15 | 8.4292e-16 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.74872 | 0.60963 | 1 | 0.74872 | 0.60963 | 3.784e-12 | -142.5584 | 131.6989 | 3.7922e-12 | -142.5584 | 131.6989

## LL_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 1.5183 | 1.5183 | 0 | 1.5183 | 1.5183 | 0 | 17.5318 | 17.5318 | 0 | 17.5318 | 17.5318 | 5.9212e-15 | 15.3932 | 0.73601 | -1.125e-14 | -13.0917 | 1.5655 | 2.3685e-15 | 2.3135 | 11.9328 | -7.1054e-15 | -0.95344 | -10.5727 | 0 | -146.7238 | 33.2762 | 0 | 33.2762 | -146.7238 | 1 | 0.88788 | 0.68193 | 1 | 0.74872 | 0.60963 | 3.7757e-12 | -138.1765 | 119.7467 | 3.7851e-12 | -142.5584 | 131.6989
Line_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.4211e-14 | 4.798e-10 | 8.2616e-10 | 9.4739e-15 | -4.798e-10 | -8.2616e-10 | -4.737e-15 | -1.0532e-09 | 4.5325e-10 | 6.2587e-28 | 1.0532e-09 | -4.5325e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.74872 | 0.60963 | 1 | 0.74872 | 0.60963 | 3.784e-12 | -142.5584 | 131.6989 | 3.7851e-12 | -142.5584 | 131.6989
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -9.4739e-15 | 4.798e-10 | 8.2616e-10 | 4.737e-15 | -4.7979e-10 | -8.2615e-10 | -1.1842e-14 | -1.0532e-09 | 4.5325e-10 | 7.1054e-15 | 1.0532e-09 | -4.5325e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.74872 | 0.60963 | 1 | 0.74872 | 0.60963 | 3.7922e-12 | -142.5584 | 131.6989 | 3.7851e-12 | -142.5584 | 131.6989
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.5133e-15 | 4.5538e-15 | 6.9488e-15 | 2.9606e-15 | -3.5642e-15 | 3.1167e-15 | 7.1054e-15 | 5.7203e-15 | 5.224e-15 | -9.4739e-15 | 1.7378e-15 | 8.4292e-16 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.74872 | 0.60963 | 1 | 0.74872 | 0.60963 | 3.784e-12 | -142.5584 | 131.6989 | 3.7922e-12 | -142.5584 | 131.6989

## LG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.021665 | 0.010833 | 0.010833 | 0.016247 | 0.016251 | 0.016251 | 0.25017 | 0.12508 | 0.12508 | 0.1876 | 0.18765 | 0.18765 | 2.6525e-05 | -0.11764 | 0.12067 | 9.0394e-15 | 0.17746 | -0.18006 | 0.00019223 | 0.20638 | 0.20457 | 6.4938e-14 | -0.30903 | -0.30715 | -89.566 | 90.4339 | 90.4339 | 90.5664 | -89.6985 | -89.6985 |  | 0.00077567 | 1.8991 | 1.8988 | 0 | 1.899 | 1.8973 | -7.4225 | -149.8811 | 149.8996 | 0 | -149.8322 | 149.9212
Line_1 | 0.01354 | 0.01354 | 0.01354 | 0.0081256 | 0.0081256 | 0.0081256 | 0.15635 | 0.15635 | 0.15635 | 0.093827 | 0.093827 | 0.093827 | 0.00054206 | 0.14867 | -0.14921 | 4.3707e-15 | -0.08873 | 0.090031 | 0.00021565 | -0.25711 | -0.25585 | 3.2499e-14 | 0.15452 | 0.15358 | -89.759 | -89.759 | -89.759 | 90.3015 | 90.3015 | 90.3015 |  | 0.0037313 | 1.8996 | 1.8944 | 0 | 1.899 | 1.8973 | -68.0646 | -149.7208 | 149.9907 | 0 | -149.8322 | 149.9212
Line_2 | 0.01354 | 0.01354 | 0.01354 | 0.0081256 | 0.0081256 | 0.0081256 | 0.15635 | 0.15635 | 0.15635 | 0.093827 | 0.093827 | 0.093827 | 0.00054206 | 0.14867 | -0.14921 | 4.3707e-15 | -0.08873 | 0.090031 | 0.00021565 | -0.25711 | -0.25585 | 3.2499e-14 | 0.15452 | 0.15358 | -89.759 | -89.759 | -89.759 | 90.3015 | 90.3015 | 90.3015 |  | 0.0037313 | 1.8996 | 1.8944 | 0 | 1.899 | 1.8973 | -68.0646 | -149.7208 | 149.9907 | 0 | -149.8322 | 149.9212
Line_3 | 0.0027055 | 0.0027055 | 0.0027055 | 0.0027055 | 0.0027055 | 0.0027055 | 0.031241 | 0.031241 | 0.031241 | 0.031241 | 0.031241 | 0.031241 | 0.00010831 | 0.029706 | -0.029815 | 0.00010831 | 0.029706 | -0.029815 | 4.309e-05 | -0.051374 | -0.051123 | 4.309e-05 | -0.051374 | -0.051123 | -89.759 | -89.759 | -89.759 | -89.759 | -89.759 | -89.759 |  | 0.0037313 | 1.8996 | 1.8944 | 0.0037313 | 1.8996 | 1.8944 | -68.0646 | -149.7208 | 149.9907 | -68.0646 | -149.7208 | 149.9907

## LG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.021665 | 0.010833 | 0.010833 | 0.016247 | 0.016251 | 0.016251 | 0.25017 | 0.12508 | 0.12508 | 0.1876 | 0.18765 | 0.18765 | 2.6525e-05 | -0.11764 | 0.12067 | 9.0394e-15 | 0.17746 | -0.18006 | 0.00019223 | 0.20638 | 0.20457 | 6.4938e-14 | -0.30903 | -0.30715 | -89.566 | 90.4339 | 90.4339 | 90.5664 | -89.6985 | -89.6985 |  | 0.00077567 | 1.8991 | 1.8988 | 0 | 1.899 | 1.8973 | -7.4225 | -149.8811 | 149.8996 | 0 | -149.8322 | 149.9212
Line_1 | 0.01354 | 0.01354 | 0.01354 | 0.0081256 | 0.0081256 | 0.0081256 | 0.15635 | 0.15635 | 0.15635 | 0.093827 | 0.093827 | 0.093827 | 0.00054206 | 0.14867 | -0.14921 | 4.3707e-15 | -0.08873 | 0.090031 | 0.00021565 | -0.25711 | -0.25585 | 3.2499e-14 | 0.15452 | 0.15358 | -89.759 | -89.759 | -89.759 | 90.3015 | 90.3015 | 90.3015 |  | 0.0037313 | 1.8996 | 1.8944 | 0 | 1.899 | 1.8973 | -68.0646 | -149.7208 | 149.9907 | 0 | -149.8322 | 149.9212
Line_2 | 0.01354 | 0.01354 | 0.01354 | 0.0081256 | 0.0081256 | 0.0081256 | 0.15635 | 0.15635 | 0.15635 | 0.093827 | 0.093827 | 0.093827 | 0.00054206 | 0.14867 | -0.14921 | 4.3707e-15 | -0.08873 | 0.090031 | 0.00021565 | -0.25711 | -0.25585 | 3.2499e-14 | 0.15452 | 0.15358 | -89.759 | -89.759 | -89.759 | 90.3015 | 90.3015 | 90.3015 |  | 0.0037313 | 1.8996 | 1.8944 | 0 | 1.899 | 1.8973 | -68.0646 | -149.7208 | 149.9907 | 0 | -149.8322 | 149.9212
Line_3 | 0.0027055 | 0.0027055 | 0.0027055 | 0.0027055 | 0.0027055 | 0.0027055 | 0.031241 | 0.031241 | 0.031241 | 0.031241 | 0.031241 | 0.031241 | 0.00010831 | 0.029706 | -0.029815 | 0.00010831 | 0.029706 | -0.029815 | 4.309e-05 | -0.051374 | -0.051123 | 4.309e-05 | -0.051374 | -0.051123 | -89.759 | -89.759 | -89.759 | -89.759 | -89.759 | -89.759 |  | 0.0037313 | 1.8996 | 1.8944 | 0.0037313 | 1.8996 | 1.8944 | -68.0646 | -149.7208 | 149.9907 | -68.0646 | -149.7208 | 149.9907

## LG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.021388 | 0.010694 | 0.010694 | 0.016039 | 0.016043 | 0.016043 | 0.24697 | 0.12348 | 0.12348 | 0.1852 | 0.18525 | 0.18525 | 0.0034567 | -0.11528 | 0.11994 | -0.0025787 | 0.1739 | -0.179 | 0.0036181 | 0.20347 | 0.19874 | -0.0025668 | -0.30468 | -0.2984 | -88.8479 | 91.152 | 91.152 | 91.2845 | -88.9804 | -88.9804 |  | 0.020262 | 1.8938 | 1.8798 | 0.019646 | 1.8937 | 1.8784 | -42.5404 | -149.3137 | 150.0408 | -43.848 | -149.2653 | 150.0619
Line_1 | 0.013367 | 0.013367 | 0.013367 | 0.0080216 | 0.0080216 | 0.0080216 | 0.15435 | 0.15435 | 0.15435 | 0.092626 | 0.092626 | 0.092626 | 0.0026652 | 0.14568 | -0.14835 | -0.0012838 | -0.086948 | 0.0895 | 0.0023615 | -0.25349 | -0.24857 | -0.0012897 | 0.15234 | 0.1492 | -89.0409 | -89.0409 | -89.0409 | 91.0196 | 91.0196 | 91.0196 |  | 0.023071 | 1.8943 | 1.8755 | 0.019646 | 1.8937 | 1.8784 | -47.498 | -149.155 | 150.1302 | -43.848 | -149.2653 | 150.0619
Line_2 | 0.013367 | 0.013367 | 0.013367 | 0.0080216 | 0.0080216 | 0.0080216 | 0.15435 | 0.15435 | 0.15435 | 0.092626 | 0.092626 | 0.092626 | 0.0026652 | 0.14568 | -0.14835 | -0.0012838 | -0.086948 | 0.0895 | 0.0023615 | -0.25349 | -0.24857 | -0.0012897 | 0.15234 | 0.1492 | -89.0409 | -89.0409 | -89.0409 | 91.0196 | 91.0196 | 91.0196 |  | 0.023071 | 1.8943 | 1.8755 | 0.019646 | 1.8937 | 1.8784 | -47.498 | -149.155 | 150.1302 | -43.848 | -149.2653 | 150.0619
Line_3 | 0.0026709 | 0.0026709 | 0.0026709 | 0.0026709 | 0.0026709 | 0.0026709 | 0.030841 | 0.030841 | 0.030841 | 0.030841 | 0.030841 | 0.030841 | 0.00053254 | 0.029109 | -0.029642 | 0.00053254 | 0.029109 | -0.029642 | 0.00047187 | -0.050651 | -0.049668 | 0.00047187 | -0.050651 | -0.049668 | -89.0409 | -89.0409 | -89.0409 | -89.0409 | -89.0409 | -89.0409 |  | 0.023071 | 1.8943 | 1.8755 | 0.023071 | 1.8943 | 1.8755 | -47.498 | -149.155 | 150.1302 | -47.498 | -149.155 | 150.1302

## LG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.021388 | 0.010694 | 0.010694 | 0.016039 | 0.016043 | 0.016043 | 0.24697 | 0.12348 | 0.12348 | 0.1852 | 0.18525 | 0.18525 | 0.0034567 | -0.11528 | 0.11994 | -0.0025787 | 0.1739 | -0.179 | 0.0036181 | 0.20347 | 0.19874 | -0.0025668 | -0.30468 | -0.2984 | -88.8479 | 91.152 | 91.152 | 91.2845 | -88.9804 | -88.9804 |  | 0.020262 | 1.8938 | 1.8798 | 0.019646 | 1.8937 | 1.8784 | -42.5404 | -149.3137 | 150.0408 | -43.848 | -149.2653 | 150.0619
Line_1 | 0.013367 | 0.013367 | 0.013367 | 0.0080216 | 0.0080216 | 0.0080216 | 0.15435 | 0.15435 | 0.15435 | 0.092626 | 0.092626 | 0.092626 | 0.0026652 | 0.14568 | -0.14835 | -0.0012838 | -0.086948 | 0.0895 | 0.0023615 | -0.25349 | -0.24857 | -0.0012897 | 0.15234 | 0.1492 | -89.0409 | -89.0409 | -89.0409 | 91.0196 | 91.0196 | 91.0196 |  | 0.023071 | 1.8943 | 1.8755 | 0.019646 | 1.8937 | 1.8784 | -47.498 | -149.155 | 150.1302 | -43.848 | -149.2653 | 150.0619
Line_2 | 0.013367 | 0.013367 | 0.013367 | 0.0080216 | 0.0080216 | 0.0080216 | 0.15435 | 0.15435 | 0.15435 | 0.092626 | 0.092626 | 0.092626 | 0.0026652 | 0.14568 | -0.14835 | -0.0012838 | -0.086948 | 0.0895 | 0.0023615 | -0.25349 | -0.24857 | -0.0012897 | 0.15234 | 0.1492 | -89.0409 | -89.0409 | -89.0409 | 91.0196 | 91.0196 | 91.0196 |  | 0.023071 | 1.8943 | 1.8755 | 0.019646 | 1.8937 | 1.8784 | -47.498 | -149.155 | 150.1302 | -43.848 | -149.2653 | 150.0619
Line_3 | 0.0026709 | 0.0026709 | 0.0026709 | 0.0026709 | 0.0026709 | 0.0026709 | 0.030841 | 0.030841 | 0.030841 | 0.030841 | 0.030841 | 0.030841 | 0.00053254 | 0.029109 | -0.029642 | 0.00053254 | 0.029109 | -0.029642 | 0.00047187 | -0.050651 | -0.049668 | 0.00047187 | -0.050651 | -0.049668 | -89.0409 | -89.0409 | -89.0409 | -89.0409 | -89.0409 | -89.0409 |  | 0.023071 | 1.8943 | 1.8755 | 0.023071 | 1.8943 | 1.8755 | -47.498 | -149.155 | 150.1302 | -47.498 | -149.155 | 150.1302

## LG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.019692 | 0.0098459 | 0.0098459 | 0.014767 | 0.014771 | 0.014771 | 0.22738 | 0.11369 | 0.11369 | 0.17052 | 0.17056 | 0.17056 | 4.2099e-05 | -0.096051 | 0.10085 | 1.7196e-15 | 0.14564 | -0.14976 | 0.00016234 | 0.17115 | 0.16832 | -2.1012e-14 | -0.25598 | -0.25304 | -89.176 | 90.824 | 90.824 | 91.0783 | -89.4302 | -89.4302 |  | 0.00073755 | 1.7263 | 1.7259 | 0 | 1.7267 | 1.724 | -13.7144 | -149.8745 | 149.8964 | 0 | -149.7931 | 149.9503
Line_1 | 0.012307 | 0.012307 | 0.012307 | 0.0073854 | 0.0073854 | 0.0073854 | 0.1421 | 0.1421 | 0.1421 | 0.085279 | 0.085279 | 0.085279 | 0.00085976 | 0.12263 | -0.12349 | 9.5326e-16 | -0.072818 | 0.074882 | 0.00017815 | -0.21285 | -0.2109 | -1.05e-14 | 0.12799 | 0.12652 | -89.5464 | -89.5464 | -89.5464 | 90.5698 | 90.5698 | 90.5698 |  | 0.0061787 | 1.7287 | 1.7198 | 0 | 1.7267 | 1.724 | -77.8401 | -149.5983 | 150.1028 | 0 | -149.7931 | 149.9503
Line_2 | 0.012307 | 0.012307 | 0.012307 | 0.0073854 | 0.0073854 | 0.0073854 | 0.1421 | 0.1421 | 0.1421 | 0.085279 | 0.085279 | 0.085279 | 0.00085976 | 0.12263 | -0.12349 | 9.5326e-16 | -0.072818 | 0.074882 | 0.00017815 | -0.21285 | -0.2109 | -1.05e-14 | 0.12799 | 0.12652 | -89.5464 | -89.5464 | -89.5464 | 90.5698 | 90.5698 | 90.5698 |  | 0.0061787 | 1.7287 | 1.7198 | 0 | 1.7267 | 1.724 | -77.8401 | -149.5983 | 150.1028 | 0 | -149.7931 | 149.9503
Line_3 | 0.002459 | 0.002459 | 0.002459 | 0.002459 | 0.002459 | 0.002459 | 0.028394 | 0.028394 | 0.028394 | 0.028394 | 0.028394 | 0.028394 | 0.00017179 | 0.024504 | -0.024675 | 0.00017179 | 0.024504 | -0.024675 | 3.5596e-05 | -0.04253 | -0.042141 | 3.5596e-05 | -0.04253 | -0.042141 | -89.5464 | -89.5464 | -89.5464 | -89.5464 | -89.5464 | -89.5464 |  | 0.0061787 | 1.7287 | 1.7198 | 0.0061787 | 1.7287 | 1.7198 | -77.8401 | -149.5983 | 150.1028 | -77.8401 | -149.5983 | 150.1028

## LG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.019692 | 0.0098459 | 0.0098459 | 0.014767 | 0.014771 | 0.014771 | 0.22738 | 0.11369 | 0.11369 | 0.17052 | 0.17056 | 0.17056 | 4.2099e-05 | -0.096051 | 0.10085 | 1.7196e-15 | 0.14564 | -0.14976 | 0.00016234 | 0.17115 | 0.16832 | -2.1012e-14 | -0.25598 | -0.25304 | -89.176 | 90.824 | 90.824 | 91.0783 | -89.4302 | -89.4302 |  | 0.00073755 | 1.7263 | 1.7259 | 0 | 1.7267 | 1.724 | -13.7144 | -149.8745 | 149.8964 | 0 | -149.7931 | 149.9503
Line_1 | 0.012307 | 0.012307 | 0.012307 | 0.0073854 | 0.0073854 | 0.0073854 | 0.1421 | 0.1421 | 0.1421 | 0.085279 | 0.085279 | 0.085279 | 0.00085976 | 0.12263 | -0.12349 | 9.5326e-16 | -0.072818 | 0.074882 | 0.00017815 | -0.21285 | -0.2109 | -1.05e-14 | 0.12799 | 0.12652 | -89.5464 | -89.5464 | -89.5464 | 90.5698 | 90.5698 | 90.5698 |  | 0.0061787 | 1.7287 | 1.7198 | 0 | 1.7267 | 1.724 | -77.8401 | -149.5983 | 150.1028 | 0 | -149.7931 | 149.9503
Line_2 | 0.012307 | 0.012307 | 0.012307 | 0.0073854 | 0.0073854 | 0.0073854 | 0.1421 | 0.1421 | 0.1421 | 0.085279 | 0.085279 | 0.085279 | 0.00085976 | 0.12263 | -0.12349 | 9.5326e-16 | -0.072818 | 0.074882 | 0.00017815 | -0.21285 | -0.2109 | -1.05e-14 | 0.12799 | 0.12652 | -89.5464 | -89.5464 | -89.5464 | 90.5698 | 90.5698 | 90.5698 |  | 0.0061787 | 1.7287 | 1.7198 | 0 | 1.7267 | 1.724 | -77.8401 | -149.5983 | 150.1028 | 0 | -149.7931 | 149.9503
Line_3 | 0.002459 | 0.002459 | 0.002459 | 0.002459 | 0.002459 | 0.002459 | 0.028394 | 0.028394 | 0.028394 | 0.028394 | 0.028394 | 0.028394 | 0.00017179 | 0.024504 | -0.024675 | 0.00017179 | 0.024504 | -0.024675 | 3.5596e-05 | -0.04253 | -0.042141 | 3.5596e-05 | -0.04253 | -0.042141 | -89.5464 | -89.5464 | -89.5464 | -89.5464 | -89.5464 | -89.5464 |  | 0.0061787 | 1.7287 | 1.7198 | 0.0061787 | 1.7287 | 1.7198 | -77.8401 | -149.5983 | 150.1028 | -77.8401 | -149.5983 | 150.1028

## LG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.019438 | 0.009719 | 0.009719 | 0.014577 | 0.01458 | 0.01458 | 0.22445 | 0.11223 | 0.11223 | 0.16832 | 0.16836 | 0.16836 | 0.0028748 | -0.094111 | 0.1002 | -0.0021345 | 0.1427 | -0.14884 | 0.002992 | 0.1687 | 0.16349 | -0.0021157 | -0.25233 | -0.2458 | -88.463 | 91.5369 | 91.5369 | 91.7913 | -88.7173 | -88.7173 |  | 0.018486 | 1.7213 | 1.7086 | 0.017855 | 1.7218 | 1.7067 | -42.319 | -149.3084 | 150.0336 | -43.4631 | -149.2277 | 150.0867
Line_1 | 0.012148 | 0.012148 | 0.012148 | 0.0072902 | 0.0072902 | 0.0072902 | 0.14027 | 0.14027 | 0.14027 | 0.08418 | 0.08418 | 0.08418 | 0.0025973 | 0.12016 | -0.12275 | -0.0010581 | -0.071349 | 0.074418 | 0.001956 | -0.20982 | -0.20487 | -0.0010675 | 0.12616 | 0.1229 | -88.8335 | -88.8335 | -88.8335 | 91.2827 | 91.2827 | 91.2827 |  | 0.023179 | 1.7237 | 1.7026 | 0.017855 | 1.7218 | 1.7067 | -51.8501 | -149.0348 | 150.2373 | -43.4631 | -149.2277 | 150.0867
Line_2 | 0.012148 | 0.012148 | 0.012148 | 0.0072902 | 0.0072902 | 0.0072902 | 0.14027 | 0.14027 | 0.14027 | 0.08418 | 0.08418 | 0.08418 | 0.0025973 | 0.12016 | -0.12275 | -0.0010581 | -0.071349 | 0.074418 | 0.001956 | -0.20982 | -0.20487 | -0.0010675 | 0.12616 | 0.1229 | -88.8335 | -88.8335 | -88.8335 | 91.2827 | 91.2827 | 91.2827 |  | 0.023179 | 1.7237 | 1.7026 | 0.017855 | 1.7218 | 1.7067 | -51.8501 | -149.0348 | 150.2373 | -43.4631 | -149.2277 | 150.0867
Line_3 | 0.0024274 | 0.0024274 | 0.0024274 | 0.0024274 | 0.0024274 | 0.0024274 | 0.028029 | 0.028029 | 0.028029 | 0.028029 | 0.028029 | 0.028029 | 0.00051897 | 0.024009 | -0.024528 | 0.00051897 | 0.024009 | -0.024528 | 0.00039084 | -0.041924 | -0.040936 | 0.00039084 | -0.041924 | -0.040936 | -88.8335 | -88.8335 | -88.8335 | -88.8335 | -88.8335 | -88.8335 |  | 0.023179 | 1.7237 | 1.7026 | 0.023179 | 1.7237 | 1.7026 | -51.8501 | -149.0348 | 150.2373 | -51.8501 | -149.0348 | 150.2373

## LG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.019438 | 0.009719 | 0.009719 | 0.014577 | 0.01458 | 0.01458 | 0.22445 | 0.11223 | 0.11223 | 0.16832 | 0.16836 | 0.16836 | 0.0028748 | -0.094111 | 0.1002 | -0.0021345 | 0.1427 | -0.14884 | 0.002992 | 0.1687 | 0.16349 | -0.0021157 | -0.25233 | -0.2458 | -88.463 | 91.5369 | 91.5369 | 91.7913 | -88.7173 | -88.7173 |  | 0.018486 | 1.7213 | 1.7086 | 0.017855 | 1.7218 | 1.7067 | -42.319 | -149.3084 | 150.0336 | -43.4631 | -149.2277 | 150.0867
Line_1 | 0.012148 | 0.012148 | 0.012148 | 0.0072902 | 0.0072902 | 0.0072902 | 0.14027 | 0.14027 | 0.14027 | 0.08418 | 0.08418 | 0.08418 | 0.0025973 | 0.12016 | -0.12275 | -0.0010581 | -0.071349 | 0.074418 | 0.001956 | -0.20982 | -0.20487 | -0.0010675 | 0.12616 | 0.1229 | -88.8335 | -88.8335 | -88.8335 | 91.2827 | 91.2827 | 91.2827 |  | 0.023179 | 1.7237 | 1.7026 | 0.017855 | 1.7218 | 1.7067 | -51.8501 | -149.0348 | 150.2373 | -43.4631 | -149.2277 | 150.0867
Line_2 | 0.012148 | 0.012148 | 0.012148 | 0.0072902 | 0.0072902 | 0.0072902 | 0.14027 | 0.14027 | 0.14027 | 0.08418 | 0.08418 | 0.08418 | 0.0025973 | 0.12016 | -0.12275 | -0.0010581 | -0.071349 | 0.074418 | 0.001956 | -0.20982 | -0.20487 | -0.0010675 | 0.12616 | 0.1229 | -88.8335 | -88.8335 | -88.8335 | 91.2827 | 91.2827 | 91.2827 |  | 0.023179 | 1.7237 | 1.7026 | 0.017855 | 1.7218 | 1.7067 | -51.8501 | -149.0348 | 150.2373 | -43.4631 | -149.2277 | 150.0867
Line_3 | 0.0024274 | 0.0024274 | 0.0024274 | 0.0024274 | 0.0024274 | 0.0024274 | 0.028029 | 0.028029 | 0.028029 | 0.028029 | 0.028029 | 0.028029 | 0.00051897 | 0.024009 | -0.024528 | 0.00051897 | 0.024009 | -0.024528 | 0.00039084 | -0.041924 | -0.040936 | 0.00039084 | -0.041924 | -0.040936 | -88.8335 | -88.8335 | -88.8335 | -88.8335 | -88.8335 | -88.8335 |  | 0.023179 | 1.7237 | 1.7026 | 0.023179 | 1.7237 | 1.7026 | -51.8501 | -149.0348 | 150.2373 | -51.8501 | -149.0348 | 150.2373

## LLG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.0054365 | 3.7086 | 3.7097 | 0.0081559 | 3.7092 | 3.7091 | 0.062775 | 42.8232 | 42.8361 | 0.094177 | 42.8298 | 42.8294 | 0.00071876 | 7.1486 | 7.1595 | -0.00065549 | 6.8658e-11 | 5.7332e-11 | 0.10348 | 8.1345 | 8.0998 | -0.1552 | -3.8734e-11 | 4.403e-11 | -89.6107 | -167.8209 | 12.2612 | 90.2569 | 12.2201 | -167.7798 |  | 1.6484 | 0.25288 | 0.25237 | 1.648 | 0 | 0 | -0.008648 | -119.1302 | 60.7873 | 0.014929 | 0 | 0
Line_1 | 0.0067953 | 0.0067953 | 0.0067953 | 0.004078 | 0.004078 | 0.004078 | 0.078465 | 0.078465 | 0.078465 | 0.047088 | 0.047088 | 0.047088 | -0.00027306 | 0.00013653 | 0.00013653 | 0.00032774 | 2.6014e-14 | 6.0423e-14 | -0.12925 | 5.4315e-05 | 5.4315e-05 | 0.077598 | 8.2672e-14 | -5.163e-14 | 90.1964 | 90.1964 | 90.1964 | -89.7431 | -89.7431 | -89.7431 |  | 1.6473 | 0.0018726 | 0.0018726 | 1.648 | 0 | 0 | 0.075373 | 111.8908 | 111.8908 | 0.014929 | 0 | 0
Line_2 | 0.0067953 | 0.0067953 | 0.0067953 | 0.004078 | 0.004078 | 0.004078 | 0.078465 | 0.078465 | 0.078465 | 0.047088 | 0.047088 | 0.047088 | -0.00027306 | 0.00013653 | 0.00013653 | 0.00032774 | 2.6014e-14 | 6.0423e-14 | -0.12925 | 5.4315e-05 | 5.4315e-05 | 0.077598 | 8.2672e-14 | -5.163e-14 | 90.1964 | 90.1964 | 90.1964 | -89.7431 | -89.7431 | -89.7431 |  | 1.6473 | 0.0018726 | 0.0018726 | 1.648 | 0 | 0 | 0.075373 | 111.8908 | 111.8908 | 0.014929 | 0 | 0
Line_3 | 0.0013578 | 0.0013578 | 0.0013578 | 0.0013578 | 0.0013578 | 0.0013578 | 0.015679 | 0.015679 | 0.015679 | 0.015679 | 0.015679 | 0.015679 | -5.456e-05 | 2.728e-05 | 2.728e-05 | -5.456e-05 | 2.728e-05 | 2.728e-05 | -0.025826 | 1.0853e-05 | 1.0853e-05 | -0.025826 | 1.0853e-05 | 1.0853e-05 | 90.1964 | 90.1964 | 90.1964 | 90.1964 | 90.1964 | 90.1964 |  | 1.6473 | 0.0018726 | 0.0018726 | 1.6473 | 0.0018726 | 0.0018726 | 0.075373 | 111.8908 | 111.8908 | 0.075373 | 111.8908 | 111.8908

## LLG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.0054365 | 3.7086 | 3.7097 | 0.0081559 | 3.7092 | 3.7091 | 0.062775 | 42.8232 | 42.8361 | 0.094177 | 42.8298 | 42.8294 | 0.00071876 | 7.1486 | 7.1595 | -0.00065549 | 6.8658e-11 | 5.7332e-11 | 0.10348 | 8.1345 | 8.0998 | -0.1552 | -3.8734e-11 | 4.403e-11 | -89.6107 | -167.8209 | 12.2612 | 90.2569 | 12.2201 | -167.7798 |  | 1.6484 | 0.25288 | 0.25237 | 1.648 | 0 | 0 | -0.008648 | -119.1302 | 60.7873 | 0.014929 | 0 | 0
Line_1 | 0.0067953 | 0.0067953 | 0.0067953 | 0.004078 | 0.004078 | 0.004078 | 0.078465 | 0.078465 | 0.078465 | 0.047088 | 0.047088 | 0.047088 | -0.00027306 | 0.00013653 | 0.00013653 | 0.00032774 | 2.6014e-14 | 6.0423e-14 | -0.12925 | 5.4315e-05 | 5.4315e-05 | 0.077598 | 8.2672e-14 | -5.163e-14 | 90.1964 | 90.1964 | 90.1964 | -89.7431 | -89.7431 | -89.7431 |  | 1.6473 | 0.0018726 | 0.0018726 | 1.648 | 0 | 0 | 0.075373 | 111.8908 | 111.8908 | 0.014929 | 0 | 0
Line_2 | 0.0067953 | 0.0067953 | 0.0067953 | 0.004078 | 0.004078 | 0.004078 | 0.078465 | 0.078465 | 0.078465 | 0.047088 | 0.047088 | 0.047088 | -0.00027306 | 0.00013653 | 0.00013653 | 0.00032774 | 2.6014e-14 | 6.0423e-14 | -0.12925 | 5.4315e-05 | 5.4315e-05 | 0.077598 | 8.2672e-14 | -5.163e-14 | 90.1964 | 90.1964 | 90.1964 | -89.7431 | -89.7431 | -89.7431 |  | 1.6473 | 0.0018726 | 0.0018726 | 1.648 | 0 | 0 | 0.075373 | 111.8908 | 111.8908 | 0.014929 | 0 | 0
Line_3 | 0.0013578 | 0.0013578 | 0.0013578 | 0.0013578 | 0.0013578 | 0.0013578 | 0.015679 | 0.015679 | 0.015679 | 0.015679 | 0.015679 | 0.015679 | -5.456e-05 | 2.728e-05 | 2.728e-05 | -5.456e-05 | 2.728e-05 | 2.728e-05 | -0.025826 | 1.0853e-05 | 1.0853e-05 | -0.025826 | 1.0853e-05 | 1.0853e-05 | 90.1964 | 90.1964 | 90.1964 | 90.1964 | 90.1964 | 90.1964 |  | 1.6473 | 0.0018726 | 0.0018726 | 1.6473 | 0.0018726 | 0.0018726 | 0.075373 | 111.8908 | 111.8908 | 0.075373 | 111.8908 | 111.8908

## LLG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.0054015 | 1.1327 | 1.1358 | 0.0081034 | 1.1342 | 1.1342 | 0.062371 | 13.0791 | 13.1146 | 0.09357 | 13.097 | 13.0967 | 0.0011472 | 7.0912 | 7.1115 | -0.0013021 | -6.4439 | -6.4207 | 0.10259 | 7.1352 | 7.2476 | -0.15386 | -6.3685 | -6.4961 | -89.2477 | -144.642 | 35.5823 | 90.6199 | 35.4698 | -144.5292 |  | 1.6449 | 0.76914 | 0.77424 | 1.6444 | 0.69175 | 0.6974 | 0.11163 | -99.4649 | 81.1256 | 0.13504 | -99.8675 | 80.8054
Line_1 | 0.0067515 | 0.0067515 | 0.0067515 | 0.0040517 | 0.0040517 | 0.0040517 | 0.07796 | 0.07796 | 0.07796 | 0.046785 | 0.046785 | 0.046785 | -0.00081473 | -0.052903 | 0.053718 | 0.00065105 | 0.031823 | -0.03215 | -0.12814 | 0.0098137 | -0.0091576 | 0.076931 | -0.0058908 | 0.0055617 | 90.5594 | 90.5594 | 90.5594 | -89.3801 | -89.3801 | -89.3801 |  | 1.6437 | 0.69018 | 0.69899 | 1.6444 | 0.69175 | 0.6974 | 0.19512 | -99.9496 | 80.8849 | 0.13504 | -99.8675 | 80.8054
Line_2 | 0.0067515 | 0.0067515 | 0.0067515 | 0.0040517 | 0.0040517 | 0.0040517 | 0.07796 | 0.07796 | 0.07796 | 0.046785 | 0.046785 | 0.046785 | -0.00081473 | -0.052903 | 0.053718 | 0.00065105 | 0.031823 | -0.03215 | -0.12814 | 0.0098137 | -0.0091576 | 0.076931 | -0.0058908 | 0.0055617 | 90.5594 | 90.5594 | 90.5594 | -89.3801 | -89.3801 | -89.3801 |  | 1.6437 | 0.69018 | 0.69899 | 1.6444 | 0.69175 | 0.6974 | 0.19512 | -99.9496 | 80.8849 | 0.13504 | -99.8675 | 80.8054
Line_3 | 0.0013491 | 0.0013491 | 0.0013491 | 0.0013491 | 0.0013491 | 0.0013491 | 0.015578 | 0.015578 | 0.015578 | 0.015578 | 0.015578 | 0.015578 | -0.00016279 | -0.010571 | 0.010734 | -0.00016279 | -0.010571 | 0.010734 | -0.025604 | 0.0019609 | -0.0018298 | -0.025604 | 0.0019609 | -0.0018298 | 90.5594 | 90.5594 | 90.5594 | 90.5594 | 90.5594 | 90.5594 |  | 1.6437 | 0.69018 | 0.69899 | 1.6437 | 0.69018 | 0.69899 | 0.19512 | -99.9496 | 80.8849 | 0.19512 | -99.9496 | 80.8849

## LLG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.0054015 | 1.1327 | 1.1358 | 0.0081034 | 1.1342 | 1.1342 | 0.062371 | 13.0791 | 13.1146 | 0.09357 | 13.097 | 13.0967 | 0.0011472 | 7.0912 | 7.1115 | -0.0013021 | -6.4439 | -6.4207 | 0.10259 | 7.1352 | 7.2476 | -0.15386 | -6.3685 | -6.4961 | -89.2477 | -144.642 | 35.5823 | 90.6199 | 35.4698 | -144.5292 |  | 1.6449 | 0.76914 | 0.77424 | 1.6444 | 0.69175 | 0.6974 | 0.11163 | -99.4649 | 81.1256 | 0.13504 | -99.8675 | 80.8054
Line_1 | 0.0067515 | 0.0067515 | 0.0067515 | 0.0040517 | 0.0040517 | 0.0040517 | 0.07796 | 0.07796 | 0.07796 | 0.046785 | 0.046785 | 0.046785 | -0.00081473 | -0.052903 | 0.053718 | 0.00065105 | 0.031823 | -0.03215 | -0.12814 | 0.0098137 | -0.0091576 | 0.076931 | -0.0058908 | 0.0055617 | 90.5594 | 90.5594 | 90.5594 | -89.3801 | -89.3801 | -89.3801 |  | 1.6437 | 0.69018 | 0.69899 | 1.6444 | 0.69175 | 0.6974 | 0.19512 | -99.9496 | 80.8849 | 0.13504 | -99.8675 | 80.8054
Line_2 | 0.0067515 | 0.0067515 | 0.0067515 | 0.0040517 | 0.0040517 | 0.0040517 | 0.07796 | 0.07796 | 0.07796 | 0.046785 | 0.046785 | 0.046785 | -0.00081473 | -0.052903 | 0.053718 | 0.00065105 | 0.031823 | -0.03215 | -0.12814 | 0.0098137 | -0.0091576 | 0.076931 | -0.0058908 | 0.0055617 | 90.5594 | 90.5594 | 90.5594 | -89.3801 | -89.3801 | -89.3801 |  | 1.6437 | 0.69018 | 0.69899 | 1.6444 | 0.69175 | 0.6974 | 0.19512 | -99.9496 | 80.8849 | 0.13504 | -99.8675 | 80.8054
Line_3 | 0.0013491 | 0.0013491 | 0.0013491 | 0.0013491 | 0.0013491 | 0.0013491 | 0.015578 | 0.015578 | 0.015578 | 0.015578 | 0.015578 | 0.015578 | -0.00016279 | -0.010571 | 0.010734 | -0.00016279 | -0.010571 | 0.010734 | -0.025604 | 0.0019609 | -0.0018298 | -0.025604 | 0.0019609 | -0.0018298 | 90.5594 | 90.5594 | 90.5594 | 90.5594 | 90.5594 | 90.5594 |  | 1.6437 | 0.69018 | 0.69899 | 1.6437 | 0.69018 | 0.69899 | 0.19512 | -99.9496 | 80.8849 | 0.19512 | -99.9496 | 80.8849

## LLG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.004942 | 3.1183 | 3.1199 | 0.007414 | 3.1191 | 3.1191 | 0.057066 | 36.0065 | 36.0257 | 0.08561 | 36.0165 | 36.0157 | 0.0011404 | 9.7122 | 9.7141 | -0.00104 | -1.3504e-10 | 4.4958e-11 | 0.085504 | 5.7645 | 5.7154 | -0.12824 | -1.3588e-10 | -1.8127e-10 | -89.2548 | -159.7151 | 20.3704 | 90.491 | 20.3275 | -159.6721 |  | 1.4985 | 0.31367 | 0.31285 | 1.4981 | 0 | 0 | -0.018883 | -129.0246 | 50.8413 | 0.026385 | 0 | 0
Line_1 | 0.0061771 | 0.0061771 | 0.0061771 | 0.003707 | 0.003707 | 0.003707 | 0.071327 | 0.071327 | 0.071327 | 0.042805 | 0.042805 | 0.042805 | -0.00043322 | 0.00021661 | 0.00021661 | 0.00051999 | 2.0637e-13 | -1.8453e-13 | -0.10681 | 4.4883e-05 | 4.4883e-05 | 0.064122 | -9.6167e-14 | -1.2337e-13 | 90.3748 | 90.3748 | 90.3748 | -89.509 | -89.509 | -89.509 |  | 1.4974 | 0.0031014 | 0.0031014 | 1.4981 | 0 | 0 | 0.14244 | 102.0812 | 102.0812 | 0.026385 | 0 | 0
Line_2 | 0.0061771 | 0.0061771 | 0.0061771 | 0.003707 | 0.003707 | 0.003707 | 0.071327 | 0.071327 | 0.071327 | 0.042805 | 0.042805 | 0.042805 | -0.00043322 | 0.00021661 | 0.00021661 | 0.00051999 | 2.0637e-13 | -1.8453e-13 | -0.10681 | 4.4883e-05 | 4.4883e-05 | 0.064122 | -9.6167e-14 | -1.2337e-13 | 90.3748 | 90.3748 | 90.3748 | -89.509 | -89.509 | -89.509 |  | 1.4974 | 0.0031014 | 0.0031014 | 1.4981 | 0 | 0 | 0.14244 | 102.0812 | 102.0812 | 0.026385 | 0 | 0
Line_3 | 0.0012343 | 0.0012343 | 0.0012343 | 0.0012343 | 0.0012343 | 0.0012343 | 0.014252 | 0.014252 | 0.014252 | 0.014252 | 0.014252 | 0.014252 | -8.6564e-05 | 4.3282e-05 | 4.3282e-05 | -8.6564e-05 | 4.3282e-05 | 4.3282e-05 | -0.021341 | 8.9683e-06 | 8.9683e-06 | -0.021341 | 8.9683e-06 | 8.9683e-06 | 90.3748 | 90.3748 | 90.3748 | 90.3748 | 90.3748 | 90.3748 |  | 1.4974 | 0.0031014 | 0.0031014 | 1.4974 | 0.0031014 | 0.0031014 | 0.14244 | 102.0812 | 102.0812 | 0.14244 | 102.0812 | 102.0812

## LLG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.004942 | 3.1183 | 3.1199 | 0.007414 | 3.1191 | 3.1191 | 0.057066 | 36.0065 | 36.0257 | 0.08561 | 36.0165 | 36.0157 | 0.0011404 | 9.7122 | 9.7141 | -0.00104 | -1.3504e-10 | 4.4958e-11 | 0.085504 | 5.7645 | 5.7154 | -0.12824 | -1.3588e-10 | -1.8127e-10 | -89.2548 | -159.7151 | 20.3704 | 90.491 | 20.3275 | -159.6721 |  | 1.4985 | 0.31367 | 0.31285 | 1.4981 | 0 | 0 | -0.018883 | -129.0246 | 50.8413 | 0.026385 | 0 | 0
Line_1 | 0.0061771 | 0.0061771 | 0.0061771 | 0.003707 | 0.003707 | 0.003707 | 0.071327 | 0.071327 | 0.071327 | 0.042805 | 0.042805 | 0.042805 | -0.00043322 | 0.00021661 | 0.00021661 | 0.00051999 | 2.0637e-13 | -1.8453e-13 | -0.10681 | 4.4883e-05 | 4.4883e-05 | 0.064122 | -9.6167e-14 | -1.2337e-13 | 90.3748 | 90.3748 | 90.3748 | -89.509 | -89.509 | -89.509 |  | 1.4974 | 0.0031014 | 0.0031014 | 1.4981 | 0 | 0 | 0.14244 | 102.0812 | 102.0812 | 0.026385 | 0 | 0
Line_2 | 0.0061771 | 0.0061771 | 0.0061771 | 0.003707 | 0.003707 | 0.003707 | 0.071327 | 0.071327 | 0.071327 | 0.042805 | 0.042805 | 0.042805 | -0.00043322 | 0.00021661 | 0.00021661 | 0.00051999 | 2.0637e-13 | -1.8453e-13 | -0.10681 | 4.4883e-05 | 4.4883e-05 | 0.064122 | -9.6167e-14 | -1.2337e-13 | 90.3748 | 90.3748 | 90.3748 | -89.509 | -89.509 | -89.509 |  | 1.4974 | 0.0031014 | 0.0031014 | 1.4981 | 0 | 0 | 0.14244 | 102.0812 | 102.0812 | 0.026385 | 0 | 0
Line_3 | 0.0012343 | 0.0012343 | 0.0012343 | 0.0012343 | 0.0012343 | 0.0012343 | 0.014252 | 0.014252 | 0.014252 | 0.014252 | 0.014252 | 0.014252 | -8.6564e-05 | 4.3282e-05 | 4.3282e-05 | -8.6564e-05 | 4.3282e-05 | 4.3282e-05 | -0.021341 | 8.9683e-06 | 8.9683e-06 | -0.021341 | 8.9683e-06 | 8.9683e-06 | 90.3748 | 90.3748 | 90.3748 | 90.3748 | 90.3748 | 90.3748 |  | 1.4974 | 0.0031014 | 0.0031014 | 1.4974 | 0.0031014 | 0.0031014 | 0.14244 | 102.0812 | 102.0812 | 0.14244 | 102.0812 | 102.0812

## LLG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.00491 | 0.99123 | 0.99413 | 0.007366 | 0.99271 | 0.99265 | 0.056696 | 11.4457 | 11.4793 | 0.085055 | 11.4628 | 11.4622 | 0.0014872 | 5.9027 | 5.9192 | -0.0015666 | -4.935 | -4.9192 | 0.084761 | 5.4663 | 5.5507 | -0.12713 | -4.8762 | -4.9779 | -88.8941 | -142.7488 | 37.4797 | 90.8517 | 37.3646 | -142.6333 |  | 1.4952 | 0.70289 | 0.7069 | 1.4948 | 0.60523 | 0.61057 | 0.10066 | -99.9467 | 80.6396 | 0.14566 | -97.9786 | 82.7069
Line_1 | 0.0061371 | 0.0061371 | 0.0061371 | 0.003683 | 0.003683 | 0.003683 | 0.070865 | 0.070865 | 0.070865 | 0.042527 | 0.042527 | 0.042527 | -0.00087669 | -0.042181 | 0.043058 | 0.00078332 | 0.025434 | -0.025704 | -0.10588 | 0.0065423 | -0.0059988 | 0.063566 | -0.0039512 | 0.0036787 | 90.7355 | 90.7355 | 90.7355 | -89.1483 | -89.1483 | -89.1483 |  | 1.4942 | 0.60235 | 0.61347 | 1.4948 | 0.60523 | 0.61057 | 0.26111 | -98.0809 | 82.8041 | 0.14566 | -97.9786 | 82.7069
Line_2 | 0.0061371 | 0.0061371 | 0.0061371 | 0.003683 | 0.003683 | 0.003683 | 0.070865 | 0.070865 | 0.070865 | 0.042527 | 0.042527 | 0.042527 | -0.00087669 | -0.042181 | 0.043058 | 0.00078332 | 0.025434 | -0.025704 | -0.10588 | 0.0065423 | -0.0059988 | 0.063566 | -0.0039512 | 0.0036787 | 90.7355 | 90.7355 | 90.7355 | -89.1483 | -89.1483 | -89.1483 |  | 1.4942 | 0.60235 | 0.61347 | 1.4948 | 0.60523 | 0.61057 | 0.26111 | -98.0809 | 82.8041 | 0.14566 | -97.9786 | 82.7069
Line_3 | 0.0012263 | 0.0012263 | 0.0012263 | 0.0012263 | 0.0012263 | 0.0012263 | 0.01416 | 0.01416 | 0.01416 | 0.01416 | 0.01416 | 0.01416 | -0.00017518 | -0.0084284 | 0.0086036 | -0.00017518 | -0.0084284 | 0.0086036 | -0.021157 | 0.0013073 | -0.0011987 | -0.021157 | 0.0013073 | -0.0011987 | 90.7355 | 90.7355 | 90.7355 | 90.7355 | 90.7355 | 90.7355 |  | 1.4942 | 0.60235 | 0.61347 | 1.4942 | 0.60235 | 0.61347 | 0.26111 | -98.0809 | 82.8041 | 0.26111 | -98.0809 | 82.8041

## LLG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.00491 | 0.99123 | 0.99413 | 0.007366 | 0.99271 | 0.99265 | 0.056696 | 11.4457 | 11.4793 | 0.085055 | 11.4628 | 11.4622 | 0.0014872 | 5.9027 | 5.9192 | -0.0015666 | -4.935 | -4.9192 | 0.084761 | 5.4663 | 5.5507 | -0.12713 | -4.8762 | -4.9779 | -88.8941 | -142.7488 | 37.4797 | 90.8517 | 37.3646 | -142.6333 |  | 1.4952 | 0.70289 | 0.7069 | 1.4948 | 0.60523 | 0.61057 | 0.10066 | -99.9467 | 80.6396 | 0.14566 | -97.9786 | 82.7069
Line_1 | 0.0061371 | 0.0061371 | 0.0061371 | 0.003683 | 0.003683 | 0.003683 | 0.070865 | 0.070865 | 0.070865 | 0.042527 | 0.042527 | 0.042527 | -0.00087669 | -0.042181 | 0.043058 | 0.00078332 | 0.025434 | -0.025704 | -0.10588 | 0.0065423 | -0.0059988 | 0.063566 | -0.0039512 | 0.0036787 | 90.7355 | 90.7355 | 90.7355 | -89.1483 | -89.1483 | -89.1483 |  | 1.4942 | 0.60235 | 0.61347 | 1.4948 | 0.60523 | 0.61057 | 0.26111 | -98.0809 | 82.8041 | 0.14566 | -97.9786 | 82.7069
Line_2 | 0.0061371 | 0.0061371 | 0.0061371 | 0.003683 | 0.003683 | 0.003683 | 0.070865 | 0.070865 | 0.070865 | 0.042527 | 0.042527 | 0.042527 | -0.00087669 | -0.042181 | 0.043058 | 0.00078332 | 0.025434 | -0.025704 | -0.10588 | 0.0065423 | -0.0059988 | 0.063566 | -0.0039512 | 0.0036787 | 90.7355 | 90.7355 | 90.7355 | -89.1483 | -89.1483 | -89.1483 |  | 1.4942 | 0.60235 | 0.61347 | 1.4948 | 0.60523 | 0.61057 | 0.26111 | -98.0809 | 82.8041 | 0.14566 | -97.9786 | 82.7069
Line_3 | 0.0012263 | 0.0012263 | 0.0012263 | 0.0012263 | 0.0012263 | 0.0012263 | 0.01416 | 0.01416 | 0.01416 | 0.01416 | 0.01416 | 0.01416 | -0.00017518 | -0.0084284 | 0.0086036 | -0.00017518 | -0.0084284 | 0.0086036 | -0.021157 | 0.0013073 | -0.0011987 | -0.021157 | 0.0013073 | -0.0011987 | 90.7355 | 90.7355 | 90.7355 | 90.7355 | 90.7355 | 90.7355 |  | 1.4942 | 0.60235 | 0.61347 | 1.4942 | 0.60235 | 0.61347 | 0.26111 | -98.0809 | 82.8041 | 0.26111 | -98.0809 | 82.8041