## LLL_max_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 3.6358 | 3.6358 | 0 | 0 | 125.9486 | 125.9486 | 36.0342 | -15.4122 | 41.0034 | -17.6054 | -73.0863 | 106.9137 | 0.43341 | 0.18578 | -24.3956 | -24.2861
Line_1 | 2.7277 | 2.7277 | 5.405 | 0 | 94.4895 | 94.4895 | -1e-07 | 11.6068 | -1e-07 | 13.1692 | 107.1055 | -72.8945 | 0 | 0.18578 | 0 | -24.2861
Line_2 | 0.90821 | 0.90821 | 0 | 0 | 31.4612 | 31.4612 | -2.5187 | 3.8055 | -2.9762 | 4.4362 | 106.3378 | -73.6622 | 0.12393 | 0.18578 | -23.9029 | -24.2861
Line_3 | 1.8196 | 1.8196 | 3.5617 | 0 | 63.0325 | 63.0325 | -1e-07 | 5.165 | -1e-07 | 5.8603 | 107.4886 | -72.5114 | 0 | 0.12393 | 0 | -23.9029

## LLL_max_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 3.6358 | 3.6358 | 0 | 0 | 125.9486 | 125.9486 | 36.0342 | -15.4122 | 41.0034 | -17.6054 | -73.0863 | 106.9137 | 0.43341 | 0.18578 | -24.3956 | -24.2861
Line_1 | 2.7277 | 2.7277 | 5.405 | 0 | 94.4895 | 94.4895 | -1e-07 | 11.6068 | -1e-07 | 13.1692 | 107.1055 | -72.8945 | 0 | 0.18578 | 0 | -24.2861
Line_2 | 0.90821 | 0.90821 | 0 | 0 | 31.4612 | 31.4612 | -2.5187 | 3.8055 | -2.9762 | 4.4362 | 106.3378 | -73.6622 | 0.12393 | 0.18578 | -23.9029 | -24.2861
Line_3 | 1.8196 | 1.8196 | 3.5617 | 0 | 63.0325 | 63.0325 | -1e-07 | 5.165 | -1e-07 | 5.8603 | 107.4886 | -72.5114 | 0 | 0.12393 | 0 | -23.9029

## LLL_max_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.79728 | 0.79728 | 0 | 0 | 27.6185 | 27.6185 | 20.9759 | -19.9843 | 17.3767 | -16.2516 | -45.7967 | 134.2033 | 0.98624 | 0.93264 | -6.158 | -6.6781
Line_1 | 0.63574 | 0.63574 | 1.3036 | 0 | 22.0228 | 22.0228 | -14.7741 | 15.4046 | -12.8701 | 13.5855 | 131.9124 | -48.0876 | 0.8897 | 0.93264 | -7.0275 | -6.6781
Line_2 | 0.16402 | 0.16402 | 0 | 0 | 5.6819 | 5.6819 | -4.5378 | 4.5797 | -2.6184 | 2.6661 | 143.1163 | -36.8837 | 0.92205 | 0.93264 | -6.8973 | -6.6781
Line_3 | 0.47591 | 0.47591 | 0.9321 | 0 | 16.4861 | 16.4861 | -10.3898 | 10.7431 | -10.3535 | 10.7544 | 128.0726 | -51.9274 | 0.8897 | 0.92205 | -7.0275 | -6.8973

## LLL_max_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.79728 | 0.79728 | 0 | 0 | 27.6185 | 27.6185 | 20.9759 | -19.9843 | 17.3767 | -16.2516 | -45.7967 | 134.2033 | 0.98624 | 0.93264 | -6.158 | -6.6781
Line_1 | 0.63574 | 0.63574 | 1.3036 | 0 | 22.0228 | 22.0228 | -14.7741 | 15.4046 | -12.8701 | 13.5855 | 131.9124 | -48.0876 | 0.8897 | 0.93264 | -7.0275 | -6.6781
Line_2 | 0.16402 | 0.16402 | 0 | 0 | 5.6819 | 5.6819 | -4.5378 | 4.5797 | -2.6184 | 2.6661 | 143.1163 | -36.8837 | 0.92205 | 0.93264 | -6.8973 | -6.6781
Line_3 | 0.47591 | 0.47591 | 0.9321 | 0 | 16.4861 | 16.4861 | -10.3898 | 10.7431 | -10.3535 | 10.7544 | 128.0726 | -51.9274 | 0.8897 | 0.92205 | -7.0275 | -6.8973

## LLL_min_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 2.9516 | 2.9516 | 0 | 0 | 102.2474 | 102.2474 | 45.756 | -19.6615 | 26.7104 | -11.29 | -61.5111 | 118.4889 | 0.51817 | 0.22174 | -31.2365 | -31.6459
Line_1 | 2.2078 | 2.2078 | 3.9682 | 0 | 76.4821 | 76.4821 | -1e-07 | 14.6004 | -1e-07 | 8.628 | 117.7734 | -62.2266 | 0 | 0.22174 | 0 | -31.6459
Line_2 | 0.74446 | 0.74446 | 0 | 0 | 25.7889 | 25.7889 | -3.4011 | 5.0611 | -1.681 | 2.6619 | 120.6115 | -59.3885 | 0.14711 | 0.22174 | -33.0879 | -31.6459
Line_3 | 1.4648 | 1.4648 | 2.6326 | 0 | 50.7409 | 50.7409 | -1e-07 | 6.4263 | -1e-07 | 3.7976 | 116.3313 | -63.6687 | 0 | 0.14711 | 0 | -33.0879

## LLL_min_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 2.9516 | 2.9516 | 0 | 0 | 102.2474 | 102.2474 | 45.756 | -19.6615 | 26.7104 | -11.29 | -61.5111 | 118.4889 | 0.51817 | 0.22174 | -31.2365 | -31.6459
Line_1 | 2.2078 | 2.2078 | 3.9682 | 0 | 76.4821 | 76.4821 | -1e-07 | 14.6004 | -1e-07 | 8.628 | 117.7734 | -62.2266 | 0 | 0.22174 | 0 | -31.6459
Line_2 | 0.74446 | 0.74446 | 0 | 0 | 25.7889 | 25.7889 | -3.4011 | 5.0611 | -1.681 | 2.6619 | 120.6115 | -59.3885 | 0.14711 | 0.22174 | -33.0879 | -31.6459
Line_3 | 1.4648 | 1.4648 | 2.6326 | 0 | 50.7409 | 50.7409 | -1e-07 | 6.4263 | -1e-07 | 3.7976 | 116.3313 | -63.6687 | 0 | 0.14711 | 0 | -33.0879

## LLL_min_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.79717 | 0.79717 | 0 | 0 | 27.6148 | 27.6148 | 18.6059 | -16.7025 | 15.5964 | -14.4716 | -47.0211 | 132.9789 | 0.87917 | 0.80029 | -7.0497 | -6.1144
Line_1 | 0.59629 | 0.59629 | 1.0717 | 0 | 20.6561 | 20.6561 | -11.2925 | 12.3575 | -10.3507 | 10.9801 | 132.2633 | -47.7367 | 0.7416 | 0.80029 | -5.2282 | -6.1144
Line_2 | 0.20106 | 0.20106 | 0 | 0 | 6.965 | 6.965 | -4.2239 | 4.345 | -3.4199 | 3.4915 | 135.1015 | -44.8985 | 0.78031 | 0.80029 | -5.9028 | -6.1144
Line_3 | 0.3956 | 0.3956 | 0.71101 | 0 | 13.704 | 13.704 | -7.3166 | 7.7854 | -7.0534 | 7.3304 | 130.8213 | -49.1787 | 0.7416 | 0.78031 | -5.2282 | -5.9028

## LLL_min_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.79717 | 0.79717 | 0 | 0 | 27.6148 | 27.6148 | 18.6059 | -16.7025 | 15.5964 | -14.4716 | -47.0211 | 132.9789 | 0.87917 | 0.80029 | -7.0497 | -6.1144
Line_1 | 0.59629 | 0.59629 | 1.0717 | 0 | 20.6561 | 20.6561 | -11.2925 | 12.3575 | -10.3507 | 10.9801 | 132.2633 | -47.7367 | 0.7416 | 0.80029 | -5.2282 | -6.1144
Line_2 | 0.20106 | 0.20106 | 0 | 0 | 6.965 | 6.965 | -4.2239 | 4.345 | -3.4199 | 3.4915 | 135.1015 | -44.8985 | 0.78031 | 0.80029 | -5.9028 | -6.1144
Line_3 | 0.3956 | 0.3956 | 0.71101 | 0 | 13.704 | 13.704 | -7.3166 | 7.7854 | -7.0534 | 7.3304 | 130.8213 | -49.1787 | 0.7416 | 0.78031 | -5.2282 | -5.9028

## LL_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.36184 | 3.0849 | 3.2334 | 0.36184 | 3.0849 | 3.2334 | 4.1781 | 35.621 | 37.3363 | 4.1781 | 35.621 | 37.3363 | -3.0459 | 29.02 | -12.393 | 3.114 | -24.0714 | 17.8296 | -3.7564 | 3.1835 | 15.3596 | 3.8336 | 2.4312 | -9.1912 | 131.2748 | -159.9336 | 14.078 | -48.7252 | 20.0664 | -165.922 | 1.1575 | 0.81957 | 0.5286 | 1.1821 | 0.6792 | 0.53726 | 2.2371 | -153.6732 | 142.9765 | 2.188 | -165.7008 | 166.8068
Line_1 | 0.18371 | 2.3133 | 2.3918 | 0.18371 | 2.3133 | 2.3918 | 2.1213 | 26.7118 | 27.6179 | 2.1213 | 26.7118 | 27.6179 | 1.6145 | -15.3112 | 16.1185 | -1.597 | 18.0939 | -13.1438 | 1.9532 | 4.4866 | -3.51 | -1.9333 | -1.3293 | 6.8851 | -48.254 | 18.5008 | -165.5462 | 131.746 | -161.4992 | 14.4538 | 1.1946 | 0.5973 | 0.5973 | 1.1821 | 0.6792 | 0.53726 | 2.1688 | -177.8312 | -177.8312 | 2.188 | -165.7008 | 166.8068
Line_2 | 0.17814 | 0.77501 | 0.84184 | 0.17814 | 0.77501 | 0.84184 | 2.057 | 8.949 | 9.7207 | 2.057 | 8.949 | 9.7207 | 1.5335 | -5.6651 | 5.0543 | -1.517 | 5.9775 | -4.6858 | 1.919 | 1.4563 | -1.8879 | -1.9003 | -1.1019 | 2.306 | -49.2111 | 24.7439 | -166.9899 | 130.7889 | -155.2561 | 13.0101 | 1.1942 | 0.65363 | 0.55504 | 1.1821 | 0.6792 | 0.53726 | 2.1597 | -169.6723 | 172.5282 | 2.188 | -165.7008 | 166.8068
Line_3 | 0.006339 | 1.5452 | 1.5504 | 0.006339 | 1.5452 | 1.5504 | 0.073197 | 17.8424 | 17.902 | 0.073197 | 17.8424 | 17.902 | 0.080827 | -10.3755 | 10.4159 | -0.080806 | 11.6171 | -9.166 | 0.03336 | 2.4346 | -2.4179 | -0.033337 | -1.0259 | 3.836 | -20.2589 | 15.3742 | -164.7623 | 159.7411 | -164.6258 | 15.2377 | 1.1946 | 0.5973 | 0.5973 | 1.1942 | 0.65363 | 0.55504 | 2.1688 | -177.8312 | -177.8312 | 2.1597 | -169.6723 | 172.5282

## LL_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.36184 | 3.0849 | 3.2334 | 0.36184 | 3.0849 | 3.2334 | 4.1781 | 35.621 | 37.3363 | 4.1781 | 35.621 | 37.3363 | -3.0459 | 29.02 | -12.393 | 3.114 | -24.0714 | 17.8296 | -3.7564 | 3.1835 | 15.3596 | 3.8336 | 2.4312 | -9.1912 | 131.2748 | -159.9336 | 14.078 | -48.7252 | 20.0664 | -165.922 | 1.1575 | 0.81957 | 0.5286 | 1.1821 | 0.6792 | 0.53726 | 2.2371 | -153.6732 | 142.9765 | 2.188 | -165.7008 | 166.8068
Line_1 | 0.18371 | 2.3133 | 2.3918 | 0.18371 | 2.3133 | 2.3918 | 2.1213 | 26.7118 | 27.6179 | 2.1213 | 26.7118 | 27.6179 | 1.6145 | -15.3112 | 16.1185 | -1.597 | 18.0939 | -13.1438 | 1.9532 | 4.4866 | -3.51 | -1.9333 | -1.3293 | 6.8851 | -48.254 | 18.5008 | -165.5462 | 131.746 | -161.4992 | 14.4538 | 1.1946 | 0.5973 | 0.5973 | 1.1821 | 0.6792 | 0.53726 | 2.1688 | -177.8312 | -177.8312 | 2.188 | -165.7008 | 166.8068
Line_2 | 0.17814 | 0.77501 | 0.84184 | 0.17814 | 0.77501 | 0.84184 | 2.057 | 8.949 | 9.7207 | 2.057 | 8.949 | 9.7207 | 1.5335 | -5.6651 | 5.0543 | -1.517 | 5.9775 | -4.6858 | 1.919 | 1.4563 | -1.8879 | -1.9003 | -1.1019 | 2.306 | -49.2111 | 24.7439 | -166.9899 | 130.7889 | -155.2561 | 13.0101 | 1.1942 | 0.65363 | 0.55504 | 1.1821 | 0.6792 | 0.53726 | 2.1597 | -169.6723 | 172.5282 | 2.188 | -165.7008 | 166.8068
Line_3 | 0.006339 | 1.5452 | 1.5504 | 0.006339 | 1.5452 | 1.5504 | 0.073197 | 17.8424 | 17.902 | 0.073197 | 17.8424 | 17.902 | 0.080827 | -10.3755 | 10.4159 | -0.080806 | 11.6171 | -9.166 | 0.03336 | 2.4346 | -2.4179 | -0.033337 | -1.0259 | 3.836 | -20.2589 | 15.3742 | -164.7623 | 159.7411 | -164.6258 | 15.2377 | 1.1946 | 0.5973 | 0.5973 | 1.1942 | 0.65363 | 0.55504 | 2.1688 | -177.8312 | -177.8312 | 2.1597 | -169.6723 | 172.5282

## LL_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.26649 | 1.2614 | 1.2336 | 0.26649 | 1.2614 | 1.2336 | 3.0772 | 14.5653 | 14.2444 | 3.0772 | 14.5653 | 14.2444 | -1.7911 | 15.2178 | 0.28699 | 1.8281 | -14.3904 | 0.50433 | -3.0409 | 0.78464 | 12.1494 | 3.0828 | 0.15412 | -11.2516 | 121.7957 | -136.1541 | 31.6491 | -58.2043 | 43.8459 | -148.3509 | 1.1469 | 1.0462 | 0.85317 | 1.1647 | 0.98805 | 0.79069 | 1.2969 | -133.2025 | 120.296 | 1.1282 | -136.7676 | 124.2156
Line_1 | 0.13441 | 0.95605 | 0.94778 | 0.13441 | 0.95605 | 0.94778 | 1.552 | 11.0395 | 10.944 | 1.552 | 11.0395 | 10.944 | 0.95258 | -10.4164 | 0.79274 | -0.94319 | 10.8917 | -0.32563 | 1.5527 | -0.049073 | -8.1172 | -1.542 | 0.58835 | 8.6472 | -57.42 | 40.1404 | -147.941 | 122.58 | -139.8596 | 32.059 | 1.1737 | 0.94357 | 0.74523 | 1.1647 | 0.98805 | 0.79069 | 1.051 | -139.5897 | 127.6369 | 1.1282 | -136.7676 | 124.2156
Line_2 | 0.13211 | 0.31349 | 0.28593 | 0.13211 | 0.31349 | 0.28593 | 1.5255 | 3.6199 | 3.3016 | 1.5255 | 3.6199 | 3.3016 | 0.89397 | -3.4476 | 0.22121 | -0.88489 | 3.4987 | -0.1787 | 1.5511 | 0.80045 | -2.5562 | -1.5408 | -0.74246 | 2.6044 | -59.0022 | 55.2134 | -149.7095 | 120.9978 | -124.7866 | 30.2905 | 1.1735 | 0.97774 | 0.77712 | 1.1647 | 0.98805 | 0.79069 | 1.0404 | -137.8576 | 125.2365 | 1.1282 | -136.7676 | 124.2156
Line_3 | 0.0043354 | 0.65841 | 0.66204 | 0.0043354 | 0.65841 | 0.66204 | 0.050061 | 7.6027 | 7.6446 | 0.050061 | 7.6027 | 7.6446 | 0.058746 | -7.1142 | 0.47813 | -0.058736 | 7.3396 | -0.25021 | 0.0012086 | -0.92175 | -5.6769 | -0.0011976 | 1.1775 | 5.9355 | -0.1276 | 33.0278 | -147.1774 | 179.8724 | -146.9722 | 32.8226 | 1.1737 | 0.94357 | 0.74523 | 1.1735 | 0.97774 | 0.77712 | 1.051 | -139.5897 | 127.6369 | 1.0404 | -137.8576 | 125.2365

## LL_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.26649 | 1.2614 | 1.2336 | 0.26649 | 1.2614 | 1.2336 | 3.0772 | 14.5653 | 14.2444 | 3.0772 | 14.5653 | 14.2444 | -1.7911 | 15.2178 | 0.28699 | 1.8281 | -14.3904 | 0.50433 | -3.0409 | 0.78464 | 12.1494 | 3.0828 | 0.15412 | -11.2516 | 121.7957 | -136.1541 | 31.6491 | -58.2043 | 43.8459 | -148.3509 | 1.1469 | 1.0462 | 0.85317 | 1.1647 | 0.98805 | 0.79069 | 1.2969 | -133.2025 | 120.296 | 1.1282 | -136.7676 | 124.2156
Line_1 | 0.13441 | 0.95605 | 0.94778 | 0.13441 | 0.95605 | 0.94778 | 1.552 | 11.0395 | 10.944 | 1.552 | 11.0395 | 10.944 | 0.95258 | -10.4164 | 0.79274 | -0.94319 | 10.8917 | -0.32563 | 1.5527 | -0.049073 | -8.1172 | -1.542 | 0.58835 | 8.6472 | -57.42 | 40.1404 | -147.941 | 122.58 | -139.8596 | 32.059 | 1.1737 | 0.94357 | 0.74523 | 1.1647 | 0.98805 | 0.79069 | 1.051 | -139.5897 | 127.6369 | 1.1282 | -136.7676 | 124.2156
Line_2 | 0.13211 | 0.31349 | 0.28593 | 0.13211 | 0.31349 | 0.28593 | 1.5255 | 3.6199 | 3.3016 | 1.5255 | 3.6199 | 3.3016 | 0.89397 | -3.4476 | 0.22121 | -0.88489 | 3.4987 | -0.1787 | 1.5511 | 0.80045 | -2.5562 | -1.5408 | -0.74246 | 2.6044 | -59.0022 | 55.2134 | -149.7095 | 120.9978 | -124.7866 | 30.2905 | 1.1735 | 0.97774 | 0.77712 | 1.1647 | 0.98805 | 0.79069 | 1.0404 | -137.8576 | 125.2365 | 1.1282 | -136.7676 | 124.2156
Line_3 | 0.0043354 | 0.65841 | 0.66204 | 0.0043354 | 0.65841 | 0.66204 | 0.050061 | 7.6027 | 7.6446 | 0.050061 | 7.6027 | 7.6446 | 0.058746 | -7.1142 | 0.47813 | -0.058736 | 7.3396 | -0.25021 | 0.0012086 | -0.92175 | -5.6769 | -0.0011976 | 1.1775 | 5.9355 | -0.1276 | 33.0278 | -147.1774 | 179.8724 | -146.9722 | 32.8226 | 1.1737 | 0.94357 | 0.74523 | 1.1735 | 0.97774 | 0.77712 | 1.051 | -139.5897 | 127.6369 | 1.0404 | -137.8576 | 125.2365

## LL_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.1573 | 2.5018 | 2.6288 | 0.1573 | 2.5018 | 2.6288 | 1.8163 | 28.8882 | 30.3543 | 1.8163 | 28.8882 | 30.3543 | -1.8033 | 24.2039 | -2.0881 | 1.828 | -17.955 | 8.9874 | -0.29968 | -0.52181 | 13.6286 | 0.31428 | 4.2146 | -9.5515 | 172.4103 | -150.363 | 27.5625 | -7.5897 | 29.637 | -152.4375 | 1.0064 | 0.83804 | 0.45422 | 1.0212 | 0.63843 | 0.43207 | 1.8461 | -151.598 | 126.2732 | 2.1658 | -163.5729 | 160.8196
Line_1 | 0.080807 | 1.868 | 1.9334 | 0.080807 | 1.868 | 1.9334 | 0.93307 | 21.5701 | 22.3245 | 0.93307 | 21.5701 | 22.3245 | 0.9414 | -10.0168 | 10.4875 | -0.93488 | 13.5007 | -6.7556 | 0.18797 | 4.7735 | -4.6795 | -0.18412 | -2.7146 | 6.8848 | -8.9755 | 27.7962 | -153.6375 | 171.0245 | -152.2038 | 26.3625 | 1.0288 | 0.51442 | 0.51442 | 1.0212 | 0.63843 | 0.43207 | 2.3162 | -177.6838 | -177.6838 | 2.1658 | -163.5729 | 160.8196
Line_2 | 0.07654 | 0.63756 | 0.697 | 0.07654 | 0.63756 | 0.697 | 0.88381 | 7.3619 | 8.0483 | 0.88381 | 7.3619 | 8.0483 | 0.89894 | -4.0484 | 2.7169 | -0.89309 | 4.4543 | -2.2318 | 0.13362 | 1.7398 | -2.3801 | -0.13017 | -1.4999 | 2.6667 | -6.1266 | 35.0378 | -149.1073 | 173.8734 | -144.9622 | 30.8927 | 1.0283 | 0.59855 | 0.44878 | 1.0212 | 0.63843 | 0.43207 | 2.3283 | -168.2174 | 169.6733 | 2.1658 | -163.5729 | 160.8196
Line_3 | 0.0057872 | 1.2382 | 1.2398 | 0.0057872 | 1.2382 | 1.2398 | 0.066825 | 14.2971 | 14.3155 | 0.066825 | 14.2971 | 14.3155 | 0.041958 | -6.8307 | 6.8517 | -0.041925 | 8.3613 | -5.3171 | 0.054463 | 2.7263 | -2.6991 | -0.054444 | -1.8218 | 3.6059 | -50.0733 | 24.0746 | -156.1827 | 129.9267 | -155.9254 | 23.8173 | 1.0288 | 0.51442 | 0.51442 | 1.0283 | 0.59855 | 0.44878 | 2.3162 | -177.6838 | -177.6838 | 2.3283 | -168.2174 | 169.6733

## LL_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.1573 | 2.5018 | 2.6288 | 0.1573 | 2.5018 | 2.6288 | 1.8163 | 28.8882 | 30.3543 | 1.8163 | 28.8882 | 30.3543 | -1.8033 | 24.2039 | -2.0881 | 1.828 | -17.955 | 8.9874 | -0.29968 | -0.52181 | 13.6286 | 0.31428 | 4.2146 | -9.5515 | 172.4103 | -150.363 | 27.5625 | -7.5897 | 29.637 | -152.4375 | 1.0064 | 0.83804 | 0.45422 | 1.0212 | 0.63843 | 0.43207 | 1.8461 | -151.598 | 126.2732 | 2.1658 | -163.5729 | 160.8196
Line_1 | 0.080807 | 1.868 | 1.9334 | 0.080807 | 1.868 | 1.9334 | 0.93307 | 21.5701 | 22.3245 | 0.93307 | 21.5701 | 22.3245 | 0.9414 | -10.0168 | 10.4875 | -0.93488 | 13.5007 | -6.7556 | 0.18797 | 4.7735 | -4.6795 | -0.18412 | -2.7146 | 6.8848 | -8.9755 | 27.7962 | -153.6375 | 171.0245 | -152.2038 | 26.3625 | 1.0288 | 0.51442 | 0.51442 | 1.0212 | 0.63843 | 0.43207 | 2.3162 | -177.6838 | -177.6838 | 2.1658 | -163.5729 | 160.8196
Line_2 | 0.07654 | 0.63756 | 0.697 | 0.07654 | 0.63756 | 0.697 | 0.88381 | 7.3619 | 8.0483 | 0.88381 | 7.3619 | 8.0483 | 0.89894 | -4.0484 | 2.7169 | -0.89309 | 4.4543 | -2.2318 | 0.13362 | 1.7398 | -2.3801 | -0.13017 | -1.4999 | 2.6667 | -6.1266 | 35.0378 | -149.1073 | 173.8734 | -144.9622 | 30.8927 | 1.0283 | 0.59855 | 0.44878 | 1.0212 | 0.63843 | 0.43207 | 2.3283 | -168.2174 | 169.6733 | 2.1658 | -163.5729 | 160.8196
Line_3 | 0.0057872 | 1.2382 | 1.2398 | 0.0057872 | 1.2382 | 1.2398 | 0.066825 | 14.2971 | 14.3155 | 0.066825 | 14.2971 | 14.3155 | 0.041958 | -6.8307 | 6.8517 | -0.041925 | 8.3613 | -5.3171 | 0.054463 | 2.7263 | -2.6991 | -0.054444 | -1.8218 | 3.6059 | -50.0733 | 24.0746 | -156.1827 | 129.9267 | -155.9254 | 23.8173 | 1.0288 | 0.51442 | 0.51442 | 1.0283 | 0.59855 | 0.44878 | 2.3162 | -177.6838 | -177.6838 | 2.3283 | -168.2174 | 169.6733

## LL_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.068597 | 1.091 | 1.1464 | 0.068597 | 1.091 | 1.1464 | 0.79209 | 12.5981 | 13.2375 | 0.79209 | 12.5981 | 13.2375 | -0.78949 | 11.8666 | 2.206 | 0.79419 | -10.6782 | -0.89388 | 0.059138 | 0.94684 | 9.8501 | -0.056362 | -0.24454 | -9.0747 | -174.893 | -137.6663 | 40.2592 | 5.107 | 42.3337 | -139.7408 | 0.99951 | 0.94493 | 0.76254 | 1.0052 | 0.84783 | 0.68885 | 0.82315 | -133.1043 | 117.6357 | 1.0476 | -136.3544 | 124.6336
Line_1 | 0.03524 | 0.81464 | 0.84313 | 0.03524 | 0.81464 | 0.84313 | 0.40691 | 9.4067 | 9.7357 | 0.40691 | 9.4067 | 9.7357 | 0.40981 | -7.3006 | 0.19224 | -0.40857 | 7.9632 | 0.5175 | -0.018346 | -0.047078 | -6.267 | 0.019079 | 0.43863 | 6.6864 | 3.7212 | 40.4929 | -140.9408 | -176.2788 | -139.5071 | 39.0592 | 1.0081 | 0.77612 | 0.64402 | 1.0052 | 0.84783 | 0.68885 | 1.1579 | -139.1377 | 130.8161 | 1.0476 | -136.3544 | 124.6336
Line_2 | 0.033379 | 0.27804 | 0.30396 | 0.033379 | 0.27804 | 0.30396 | 0.38543 | 3.2105 | 3.5098 | 0.38543 | 3.2105 | 3.5098 | 0.38673 | -2.6378 | -0.28414 | -0.38562 | 2.715 | 0.37638 | -0.036626 | 0.23969 | -2.3338 | 0.037283 | -0.19408 | 2.3883 | 6.5701 | 47.7344 | -136.4106 | -173.4299 | -132.2656 | 43.5894 | 1.0079 | 0.82502 | 0.66983 | 1.0052 | 0.84783 | 0.68885 | 1.1599 | -137.4576 | 126.6478 | 1.0476 | -136.3544 | 124.6336
Line_3 | 0.0025238 | 0.53996 | 0.54066 | 0.0025238 | 0.53996 | 0.54066 | 0.029142 | 6.2349 | 6.243 | 0.029142 | 6.2349 | 6.243 | 0.022981 | -4.8268 | 0.30161 | -0.022975 | 5.1178 | -0.0097645 | 0.018303 | -0.34522 | -4.0093 | -0.018299 | 0.51724 | 4.1817 | -37.3766 | 36.7713 | -143.486 | 142.6234 | -143.2287 | 36.514 | 1.0081 | 0.77612 | 0.64402 | 1.0079 | 0.82502 | 0.66983 | 1.1579 | -139.1377 | 130.8161 | 1.1599 | -137.4576 | 126.6478

## LL_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.068597 | 1.091 | 1.1464 | 0.068597 | 1.091 | 1.1464 | 0.79209 | 12.5981 | 13.2375 | 0.79209 | 12.5981 | 13.2375 | -0.78949 | 11.8666 | 2.206 | 0.79419 | -10.6782 | -0.89388 | 0.059138 | 0.94684 | 9.8501 | -0.056362 | -0.24454 | -9.0747 | -174.893 | -137.6663 | 40.2592 | 5.107 | 42.3337 | -139.7408 | 0.99951 | 0.94493 | 0.76254 | 1.0052 | 0.84783 | 0.68885 | 0.82315 | -133.1043 | 117.6357 | 1.0476 | -136.3544 | 124.6336
Line_1 | 0.03524 | 0.81464 | 0.84313 | 0.03524 | 0.81464 | 0.84313 | 0.40691 | 9.4067 | 9.7357 | 0.40691 | 9.4067 | 9.7357 | 0.40981 | -7.3006 | 0.19224 | -0.40857 | 7.9632 | 0.5175 | -0.018346 | -0.047078 | -6.267 | 0.019079 | 0.43863 | 6.6864 | 3.7212 | 40.4929 | -140.9408 | -176.2788 | -139.5071 | 39.0592 | 1.0081 | 0.77612 | 0.64402 | 1.0052 | 0.84783 | 0.68885 | 1.1579 | -139.1377 | 130.8161 | 1.0476 | -136.3544 | 124.6336
Line_2 | 0.033379 | 0.27804 | 0.30396 | 0.033379 | 0.27804 | 0.30396 | 0.38543 | 3.2105 | 3.5098 | 0.38543 | 3.2105 | 3.5098 | 0.38673 | -2.6378 | -0.28414 | -0.38562 | 2.715 | 0.37638 | -0.036626 | 0.23969 | -2.3338 | 0.037283 | -0.19408 | 2.3883 | 6.5701 | 47.7344 | -136.4106 | -173.4299 | -132.2656 | 43.5894 | 1.0079 | 0.82502 | 0.66983 | 1.0052 | 0.84783 | 0.68885 | 1.1599 | -137.4576 | 126.6478 | 1.0476 | -136.3544 | 124.6336
Line_3 | 0.0025238 | 0.53996 | 0.54066 | 0.0025238 | 0.53996 | 0.54066 | 0.029142 | 6.2349 | 6.243 | 0.029142 | 6.2349 | 6.243 | 0.022981 | -4.8268 | 0.30161 | -0.022975 | 5.1178 | -0.0097645 | 0.018303 | -0.34522 | -4.0093 | -0.018299 | 0.51724 | 4.1817 | -37.3766 | 36.7713 | -143.486 | 142.6234 | -143.2287 | 36.514 | 1.0081 | 0.77612 | 0.64402 | 1.0079 | 0.82502 | 0.66983 | 1.1579 | -139.1377 | 130.8161 | 1.1599 | -137.4576 | 126.6478

## LG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.896 | 0.97822 | 0.71693 | 1.8941 | 0.98022 | 0.71892 | 21.8927 | 11.2955 | 8.2784 | 21.871 | 11.3186 | 8.3014 | 5.5797 | -12.2495 | 10.2148 | -3.2551 | 13.1534 | -10.0397 | 6.7233 | 5.5701 | 3.529 | -2.8823 | -5.8563 | -3.9122 | -63.5864 | 76.9157 | 107.3835 | 116.4401 | -103.054 | -72.6618 |  | 0.39908 | 1.1913 | 1.3055 | 0.19879 | 1.2721 | 1.298 | -13.2759 | -127.5366 | 126.4424 | -22.0361 | -127.0544 | 128.6274
Line_1 | 1.6225 | 0.51958 | 0.37366 | 1.6248 | 0.51713 | 0.37117 | 18.7346 | 5.9996 | 4.3146 | 18.7618 | 5.9713 | 4.2859 | 7.5453e-11 | 7.0999 | -5.2267 | 2.649 | -7.0404 | 5.0229 | -6.9476e-11 | -3.2367 | -2.626 | 2.6256 | 2.8515 | 2.3911 | 113.2528 | -104.9291 | -76.9131 | -66.7817 | 74.9949 | 103.1712 |  | 0 | 1.3006 | 1.3557 | 0.19879 | 1.2721 | 1.298 | 0 | -129.4366 | 129.7627 | -22.0361 | -127.0544 | 128.6274
Line_2 | 0.28495 | 0.46591 | 0.352 | 0.28677 | 0.46373 | 0.34977 | 3.2903 | 5.3799 | 4.0645 | 3.3113 | 5.3547 | 4.0388 | -0.69388 | 6.5527 | -4.7655 | 0.60613 | -6.113 | 5.0168 | -0.070249 | -2.8428 | -1.5518 | 0.25674 | 3.0048 | 1.521 | 135.29 | -100.7896 | -68.3323 | -44.9921 | 79.1219 | 111.7606 |  | 0.21196 | 1.3277 | 1.233 | 0.19879 | 1.2721 | 1.298 | -38.929 | -124.2423 | 129.7051 | -22.0361 | -127.0544 | 128.6274
Line_3 | 1.3614 | 0.064988 | 0.058966 | 1.3638 | 0.063393 | 0.057531 | 15.72 | 0.75042 | 0.68088 | 15.7483 | 0.73199 | 0.66431 | 6.7685e-11 | 0.9704 | -0.0048785 | 2.8203 | -0.94664 | -0.024234 | -5.3156e-11 | 0.10417 | -0.92306 | 1.7856 | -0.21995 | 0.81877 | 108.7582 | -135.5638 | -139.9345 | -71.2679 | 42.6775 | 38.0098 |  | 0 | 1.3006 | 1.3557 | 0.21196 | 1.3277 | 1.233 | 0 | -129.4366 | 129.7627 | -38.929 | -124.2423 | 129.7051

## LG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.896 | 0.97822 | 0.71693 | 1.8941 | 0.98022 | 0.71892 | 21.8927 | 11.2955 | 8.2784 | 21.871 | 11.3186 | 8.3014 | 5.5797 | -12.2495 | 10.2148 | -3.2551 | 13.1534 | -10.0397 | 6.7233 | 5.5701 | 3.529 | -2.8823 | -5.8563 | -3.9122 | -63.5864 | 76.9157 | 107.3835 | 116.4401 | -103.054 | -72.6618 |  | 0.39908 | 1.1913 | 1.3055 | 0.19879 | 1.2721 | 1.298 | -13.2759 | -127.5366 | 126.4424 | -22.0361 | -127.0544 | 128.6274
Line_1 | 1.6225 | 0.51958 | 0.37366 | 1.6248 | 0.51713 | 0.37117 | 18.7346 | 5.9996 | 4.3146 | 18.7618 | 5.9713 | 4.2859 | 7.5453e-11 | 7.0999 | -5.2267 | 2.649 | -7.0404 | 5.0229 | -6.9476e-11 | -3.2367 | -2.626 | 2.6256 | 2.8515 | 2.3911 | 113.2528 | -104.9291 | -76.9131 | -66.7817 | 74.9949 | 103.1712 |  | 0 | 1.3006 | 1.3557 | 0.19879 | 1.2721 | 1.298 | 0 | -129.4366 | 129.7627 | -22.0361 | -127.0544 | 128.6274
Line_2 | 0.28495 | 0.46591 | 0.352 | 0.28677 | 0.46373 | 0.34977 | 3.2903 | 5.3799 | 4.0645 | 3.3113 | 5.3547 | 4.0388 | -0.69388 | 6.5527 | -4.7655 | 0.60613 | -6.113 | 5.0168 | -0.070249 | -2.8428 | -1.5518 | 0.25674 | 3.0048 | 1.521 | 135.29 | -100.7896 | -68.3323 | -44.9921 | 79.1219 | 111.7606 |  | 0.21196 | 1.3277 | 1.233 | 0.19879 | 1.2721 | 1.298 | -38.929 | -124.2423 | 129.7051 | -22.0361 | -127.0544 | 128.6274
Line_3 | 1.3614 | 0.064988 | 0.058966 | 1.3638 | 0.063393 | 0.057531 | 15.72 | 0.75042 | 0.68088 | 15.7483 | 0.73199 | 0.66431 | 6.7685e-11 | 0.9704 | -0.0048785 | 2.8203 | -0.94664 | -0.024234 | -5.3156e-11 | 0.10417 | -0.92306 | 1.7856 | -0.21995 | 0.81877 | 108.7582 | -135.5638 | -139.9345 | -71.2679 | 42.6775 | 38.0098 |  | 0 | 1.3006 | 1.3557 | 0.21196 | 1.3277 | 1.233 | 0 | -129.4366 | 129.7627 | -38.929 | -124.2423 | 129.7051

## LG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.48833 | 0.27077 | 0.28854 | 0.4878 | 0.27121 | 0.28894 | 5.6387 | 3.1265 | 3.3318 | 5.6327 | 3.1317 | 3.3364 | 4.8102 | -3.6605 | 2.9879 | -4.6145 | 3.7729 | -3.0116 | 2.1684 | 0.35516 | -2.5527 | -1.8923 | -0.36256 | 2.5358 | -30.5977 | 63.7957 | 163.815 | 149.4502 | -116.1009 | -16.2891 |  | 0.93574 | 1.1763 | 1.1795 | 0.88545 | 1.2103 | 1.18 | -6.3323 | -121.7461 | 123.3064 | -8.2528 | -121.59 | 123.6127
Line_1 | 0.45332 | 0.14737 | 0.14213 | 0.45404 | 0.14681 | 0.1416 | 5.2345 | 1.7017 | 1.6412 | 5.2428 | 1.6952 | 1.635 | -3.6945 | 2.0763 | -1.5931 | 3.9297 | -2.0423 | 1.5472 | -2.2606 | -0.2382 | 1.1515 | 2.4713 | 0.19619 | -1.1526 | 139.6318 | -115.8717 | -19.9526 | -40.418 | 63.8972 | 160.2977 |  | 0.82744 | 1.2282 | 1.1977 | 0.88545 | 1.2103 | 1.18 | -8.9066 | -122.4163 | 124.1869 | -8.2528 | -121.59 | 123.6127
Line_2 | 0.087778 | 0.12485 | 0.14831 | 0.087716 | 0.12441 | 0.14784 | 1.0136 | 1.4416 | 1.7126 | 1.0129 | 1.4365 | 1.7071 | -0.67244 | 1.7625 | -1.4457 | 0.68485 | -1.7306 | 1.4644 | 0.60788 | -0.14703 | 1.3688 | -0.57905 | 0.16638 | -1.3832 | -147.5586 | -115.8271 | -13.2367 | 31.9623 | 63.9014 | 166.98 |  | 0.89433 | 1.2268 | 1.1625 | 0.88545 | 1.2103 | 1.18 | -9.6719 | -120.5958 | 123.3284 | -8.2528 | -121.59 | 123.6127
Line_3 | 0.43516 | 0.022723 | 0.018239 | 0.43595 | 0.022208 | 0.017848 | 5.0248 | 0.26238 | 0.21061 | 5.0339 | 0.25644 | 0.20609 | -3.0626 | 0.31978 | -0.087703 | 3.3552 | -0.31396 | 0.077779 | -2.812 | -0.039753 | -0.23652 | 3.0017 | 0.0201 | 0.2266 | 128.5365 | -115.3301 | -125.4679 | -51.4893 | 63.0672 | 52.273 |  | 0.82744 | 1.2282 | 1.1977 | 0.89433 | 1.2268 | 1.1625 | -8.9066 | -122.4163 | 124.1869 | -9.6719 | -120.5958 | 123.3284

## LG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.48833 | 0.27077 | 0.28854 | 0.4878 | 0.27121 | 0.28894 | 5.6387 | 3.1265 | 3.3318 | 5.6327 | 3.1317 | 3.3364 | 4.8102 | -3.6605 | 2.9879 | -4.6145 | 3.7729 | -3.0116 | 2.1684 | 0.35516 | -2.5527 | -1.8923 | -0.36256 | 2.5358 | -30.5977 | 63.7957 | 163.815 | 149.4502 | -116.1009 | -16.2891 |  | 0.93574 | 1.1763 | 1.1795 | 0.88545 | 1.2103 | 1.18 | -6.3323 | -121.7461 | 123.3064 | -8.2528 | -121.59 | 123.6127
Line_1 | 0.45332 | 0.14737 | 0.14213 | 0.45404 | 0.14681 | 0.1416 | 5.2345 | 1.7017 | 1.6412 | 5.2428 | 1.6952 | 1.635 | -3.6945 | 2.0763 | -1.5931 | 3.9297 | -2.0423 | 1.5472 | -2.2606 | -0.2382 | 1.1515 | 2.4713 | 0.19619 | -1.1526 | 139.6318 | -115.8717 | -19.9526 | -40.418 | 63.8972 | 160.2977 |  | 0.82744 | 1.2282 | 1.1977 | 0.88545 | 1.2103 | 1.18 | -8.9066 | -122.4163 | 124.1869 | -8.2528 | -121.59 | 123.6127
Line_2 | 0.087778 | 0.12485 | 0.14831 | 0.087716 | 0.12441 | 0.14784 | 1.0136 | 1.4416 | 1.7126 | 1.0129 | 1.4365 | 1.7071 | -0.67244 | 1.7625 | -1.4457 | 0.68485 | -1.7306 | 1.4644 | 0.60788 | -0.14703 | 1.3688 | -0.57905 | 0.16638 | -1.3832 | -147.5586 | -115.8271 | -13.2367 | 31.9623 | 63.9014 | 166.98 |  | 0.89433 | 1.2268 | 1.1625 | 0.88545 | 1.2103 | 1.18 | -9.6719 | -120.5958 | 123.3284 | -8.2528 | -121.59 | 123.6127
Line_3 | 0.43516 | 0.022723 | 0.018239 | 0.43595 | 0.022208 | 0.017848 | 5.0248 | 0.26238 | 0.21061 | 5.0339 | 0.25644 | 0.20609 | -3.0626 | 0.31978 | -0.087703 | 3.3552 | -0.31396 | 0.077779 | -2.812 | -0.039753 | -0.23652 | 3.0017 | 0.0201 | 0.2266 | 128.5365 | -115.3301 | -125.4679 | -51.4893 | 63.0672 | 52.273 |  | 0.82744 | 1.2282 | 1.1977 | 0.89433 | 1.2268 | 1.1625 | -8.9066 | -122.4163 | 124.1869 | -9.6719 | -120.5958 | 123.3284

## LG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.6529 | 0.81092 | 0.67769 | 1.6516 | 0.81233 | 0.67909 | 19.0862 | 9.3637 | 7.8253 | 19.0712 | 9.38 | 7.8414 | 7.6568 | -6.5346 | 8.0868 | -4.3504 | 7.2284 | -7.6805 | 5.786 | 6.8082 | 2.3765 | -2.4792 | -7.3088 | -2.8447 | -57.227 | 102.372 | 106.8678 | 122.7912 | -77.6307 | -73.1448 |  | 0.50283 | 1.0078 | 1.0771 | 0.26256 | 1.0959 | 1.0445 | -20.15 | -123.8027 | 123.2443 | -27.5308 | -122.9478 | 127.1789
Line_1 | 1.3763 | 0.43824 | 0.36768 | 1.3781 | 0.43626 | 0.3657 | 15.8926 | 5.0604 | 4.2456 | 15.9135 | 5.0375 | 4.2228 | -3.8007e-11 | 4.1005 | -4.1412 | 3.5433 | -4.232 | 3.9417 | 8.4249e-13 | -3.9755 | -2.3366 | 2.214 | 3.545 | 1.9793 | 120.5051 | -83.0005 | -79.5093 | -59.5292 | 97.0042 | 100.5153 |  | 0 | 1.1286 | 1.12 | 0.26256 | 1.0959 | 1.0445 | 0 | -127.1142 | 129.9241 | -27.5308 | -122.9478 | 127.1789
Line_2 | 0.27869 | 0.38184 | 0.31985 | 0.2802 | 0.38018 | 0.31819 | 3.218 | 4.4091 | 3.6934 | 3.2355 | 4.3899 | 3.6742 | -0.95339 | 3.5114 | -3.3602 | 0.80704 | -2.9964 | 3.7389 | -0.088718 | -3.7153 | -0.85738 | 0.26521 | 3.7638 | 0.86541 | 134.4188 | -71.4652 | -65.8753 | -45.7221 | 108.5286 | 114.1466 |  | 0.29755 | 1.1594 | 0.93895 | 0.26256 | 1.0959 | 1.0445 | -40.2648 | -118.0818 | 128.4386 | -27.5308 | -122.9478 | 127.1789
Line_3 | 1.107 | 0.099985 | 0.094706 | 1.1089 | 0.098888 | 0.093596 | 12.7827 | 1.1545 | 1.0936 | 12.8045 | 1.1419 | 1.0808 | -3.0555e-11 | 1.2972 | -0.17172 | 3.5142 | -1.2766 | 0.15125 | -1.1732e-12 | 0.12283 | -1.2127 | 1.4717 | -0.35088 | 1.0034 | 117.0364 | -132.5234 | -132.016 | -62.9884 | 46.5493 | 47.0103 |  | 0 | 1.1286 | 1.12 | 0.29755 | 1.1594 | 0.93895 | 0 | -127.1142 | 129.9241 | -40.2648 | -118.0818 | 128.4386

## LG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.6529 | 0.81092 | 0.67769 | 1.6516 | 0.81233 | 0.67909 | 19.0862 | 9.3637 | 7.8253 | 19.0712 | 9.38 | 7.8414 | 7.6568 | -6.5346 | 8.0868 | -4.3504 | 7.2284 | -7.6805 | 5.786 | 6.8082 | 2.3765 | -2.4792 | -7.3088 | -2.8447 | -57.227 | 102.372 | 106.8678 | 122.7912 | -77.6307 | -73.1448 |  | 0.50283 | 1.0078 | 1.0771 | 0.26256 | 1.0959 | 1.0445 | -20.15 | -123.8027 | 123.2443 | -27.5308 | -122.9478 | 127.1789
Line_1 | 1.3763 | 0.43824 | 0.36768 | 1.3781 | 0.43626 | 0.3657 | 15.8926 | 5.0604 | 4.2456 | 15.9135 | 5.0375 | 4.2228 | -3.8007e-11 | 4.1005 | -4.1412 | 3.5433 | -4.232 | 3.9417 | 8.4249e-13 | -3.9755 | -2.3366 | 2.214 | 3.545 | 1.9793 | 120.5051 | -83.0005 | -79.5093 | -59.5292 | 97.0042 | 100.5153 |  | 0 | 1.1286 | 1.12 | 0.26256 | 1.0959 | 1.0445 | 0 | -127.1142 | 129.9241 | -27.5308 | -122.9478 | 127.1789
Line_2 | 0.27869 | 0.38184 | 0.31985 | 0.2802 | 0.38018 | 0.31819 | 3.218 | 4.4091 | 3.6934 | 3.2355 | 4.3899 | 3.6742 | -0.95339 | 3.5114 | -3.3602 | 0.80704 | -2.9964 | 3.7389 | -0.088718 | -3.7153 | -0.85738 | 0.26521 | 3.7638 | 0.86541 | 134.4188 | -71.4652 | -65.8753 | -45.7221 | 108.5286 | 114.1466 |  | 0.29755 | 1.1594 | 0.93895 | 0.26256 | 1.0959 | 1.0445 | -40.2648 | -118.0818 | 128.4386 | -27.5308 | -122.9478 | 127.1789
Line_3 | 1.107 | 0.099985 | 0.094706 | 1.1089 | 0.098888 | 0.093596 | 12.7827 | 1.1545 | 1.0936 | 12.8045 | 1.1419 | 1.0808 | -3.0555e-11 | 1.2972 | -0.17172 | 3.5142 | -1.2766 | 0.15125 | -1.1732e-12 | 0.12283 | -1.2127 | 1.4717 | -0.35088 | 1.0034 | 117.0364 | -132.5234 | -132.016 | -62.9884 | 46.5493 | 47.0103 |  | 0 | 1.1286 | 1.12 | 0.29755 | 1.1594 | 0.93895 | 0 | -127.1142 | 129.9241 | -40.2648 | -118.0818 | 128.4386

## LG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.53658 | 0.26325 | 0.22 | 0.53616 | 0.2637 | 0.22045 | 6.1959 | 3.0397 | 2.5403 | 6.191 | 3.045 | 2.5455 | 4.3895 | -1.5464 | 2.5859 | -4.0389 | 1.6211 | -2.5467 | 2.9889 | 2.6451 | -0.071085 | -2.6374 | -2.7012 | 0.02202 | -41.0674 | 118.5317 | 123.0275 | 138.9509 | -61.4711 | -56.9851 |  | 0.85709 | 1.008 | 1.0183 | 0.77916 | 1.0346 | 1.0005 | -6.8151 | -121.156 | 121.4528 | -7.9046 | -120.5006 | 122.5195
Line_1 | 0.4468 | 0.14227 | 0.11936 | 0.44739 | 0.14162 | 0.11872 | 5.1592 | 1.6428 | 1.3782 | 5.166 | 1.6353 | 1.3708 | -2.9024 | 0.9912 | -1.3906 | 3.2783 | -1.0024 | 1.3644 | -2.0976 | -1.4127 | -0.17735 | 2.3354 | 1.3629 | 0.13966 | 136.6647 | -66.8408 | -63.3496 | -43.3696 | 113.1639 | 116.6749 |  | 0.6941 | 1.0505 | 1.0171 | 0.77916 | 1.0346 | 1.0005 | -7.4792 | -121.7863 | 123.9186 | -7.9046 | -120.5006 | 122.5195
Line_2 | 0.09047 | 0.12396 | 0.10383 | 0.090962 | 0.12342 | 0.10329 | 1.0447 | 1.4313 | 1.199 | 1.0503 | 1.4251 | 1.1927 | -0.77304 | 0.67418 | -1.1466 | 0.76061 | -0.61869 | 1.1823 | -0.2803 | -1.3373 | 0.16354 | 0.30204 | 1.3383 | -0.16168 | 150.5785 | -55.3055 | -49.7156 | -29.5625 | 124.6883 | 130.3062 |  | 0.78714 | 1.0463 | 0.96604 | 0.77916 | 1.0346 | 1.0005 | -9.4913 | -118.5517 | 122.1671 | -7.9046 | -120.5006 | 122.5195
Line_3 | 0.35937 | 0.032458 | 0.030744 | 0.35998 | 0.032102 | 0.030384 | 4.1496 | 0.37479 | 0.355 | 4.1567 | 0.37068 | 0.35084 | -2.2281 | 0.39197 | -0.18177 | 2.6014 | -0.38776 | 0.17458 | -1.8253 | -0.037208 | -0.312 | 1.9844 | 0.0085328 | 0.29051 | 133.1961 | -116.3637 | -115.8564 | -46.8287 | 62.7089 | 63.1699 |  | 0.6941 | 1.0505 | 1.0171 | 0.78714 | 1.0463 | 0.96604 | -7.4792 | -121.7863 | 123.9186 | -9.4913 | -118.5517 | 122.1671

## LG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.53658 | 0.26325 | 0.22 | 0.53616 | 0.2637 | 0.22045 | 6.1959 | 3.0397 | 2.5403 | 6.191 | 3.045 | 2.5455 | 4.3895 | -1.5464 | 2.5859 | -4.0389 | 1.6211 | -2.5467 | 2.9889 | 2.6451 | -0.071085 | -2.6374 | -2.7012 | 0.02202 | -41.0674 | 118.5317 | 123.0275 | 138.9509 | -61.4711 | -56.9851 |  | 0.85709 | 1.008 | 1.0183 | 0.77916 | 1.0346 | 1.0005 | -6.8151 | -121.156 | 121.4528 | -7.9046 | -120.5006 | 122.5195
Line_1 | 0.4468 | 0.14227 | 0.11936 | 0.44739 | 0.14162 | 0.11872 | 5.1592 | 1.6428 | 1.3782 | 5.166 | 1.6353 | 1.3708 | -2.9024 | 0.9912 | -1.3906 | 3.2783 | -1.0024 | 1.3644 | -2.0976 | -1.4127 | -0.17735 | 2.3354 | 1.3629 | 0.13966 | 136.6647 | -66.8408 | -63.3496 | -43.3696 | 113.1639 | 116.6749 |  | 0.6941 | 1.0505 | 1.0171 | 0.77916 | 1.0346 | 1.0005 | -7.4792 | -121.7863 | 123.9186 | -7.9046 | -120.5006 | 122.5195
Line_2 | 0.09047 | 0.12396 | 0.10383 | 0.090962 | 0.12342 | 0.10329 | 1.0447 | 1.4313 | 1.199 | 1.0503 | 1.4251 | 1.1927 | -0.77304 | 0.67418 | -1.1466 | 0.76061 | -0.61869 | 1.1823 | -0.2803 | -1.3373 | 0.16354 | 0.30204 | 1.3383 | -0.16168 | 150.5785 | -55.3055 | -49.7156 | -29.5625 | 124.6883 | 130.3062 |  | 0.78714 | 1.0463 | 0.96604 | 0.77916 | 1.0346 | 1.0005 | -9.4913 | -118.5517 | 122.1671 | -7.9046 | -120.5006 | 122.5195
Line_3 | 0.35937 | 0.032458 | 0.030744 | 0.35998 | 0.032102 | 0.030384 | 4.1496 | 0.37479 | 0.355 | 4.1567 | 0.37068 | 0.35084 | -2.2281 | 0.39197 | -0.18177 | 2.6014 | -0.38776 | 0.17458 | -1.8253 | -0.037208 | -0.312 | 1.9844 | 0.0085328 | 0.29051 | 133.1961 | -116.3637 | -115.8564 | -46.8287 | 62.7089 | 63.1699 |  | 0.6941 | 1.0505 | 1.0171 | 0.78714 | 1.0463 | 0.96604 | -7.4792 | -121.7863 | 123.9186 | -9.4913 | -118.5517 | 122.1671

## LLG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.53701 | 3.3496 | 2.9917 | 0.53859 | 3.3498 | 2.9911 | 6.2008 | 38.6775 | 34.5448 | 6.2191 | 38.6799 | 34.5383 | -2.6778 | 15.5707 | 3.8158 | 3.0592 | -7.1268 | -1.4674 | 7.6448 | 9.7034 | 11.7777 | -7.8507 | -2.9351 | -6.1426 | -109.1052 | -168.6333 | 23.2724 | 70.9678 | 11.396 | -156.7589 |  | 1.3063 | 0.47435 | 0.35839 | 1.3548 | 0.19926 | 0.18285 | 0.19907 | -136.7028 | 95.3209 | 2.2573 | -146.22 | 99.8057
Line_1 | 0.2939 | 2.5186 | 2.2684 | 0.29198 | 2.5185 | 2.2693 | 3.3936 | 29.0821 | 26.1931 | 3.3715 | 29.0809 | 26.2031 | 1.8965 | 5.5329e-11 | 6.7632e-11 | -1.8626 | 5.1529 | 1.4746 | -4.4043 | -5.3435e-11 | -6.8974e-12 | 4.1706 | 2.651 | 4.5587 | 68.3701 | 6.6042 | -152.3181 | -111.8079 | -173.4441 | 27.7309 |  | 1.413 | 0 | 0 | 1.3548 | 0.19926 | 0.18285 | 1.6673 | 0 | 0 | 2.2573 | -146.22 | 99.8057
Line_2 | 0.24908 | 0.86724 | 0.75018 | 0.24736 | 0.86673 | 0.75015 | 2.8762 | 10.014 | 8.6623 | 2.8563 | 10.0082 | 8.662 | 1.355 | -1.3992 | 0.25728 | -1.1966 | 1.9739 | -0.0072573 | -3.6295 | 0.60485 | -1.6632 | 3.68 | 0.28417 | 1.5839 | 74.4386 | 25.7101 | -170.6033 | -105.7552 | -154.4121 | 9.5432 |  | 1.347 | 0.15222 | 0.19429 | 1.3548 | 0.19926 | 0.18285 | 4.9108 | -177.6672 | 108.1901 | 2.2573 | -146.22 | 99.8057
Line_3 | 0.053585 | 1.7224 | 1.5734 | 0.052491 | 1.7228 | 1.5745 | 0.61875 | 19.8883 | 18.1684 | 0.60611 | 19.8927 | 18.1802 | 0.6893 | 4.3326e-11 | 4.5676e-11 | -0.68654 | 3.0154 | 1.099 | -0.53785 | -2.9831e-11 | -1.172e-11 | 0.44186 | 0.27717 | 3.3569 | 39.6319 | -2.8497 | -143.7496 | -142.3235 | 177.0811 | 36.3179 |  | 1.413 | 0 | 0 | 1.347 | 0.15222 | 0.19429 | 1.6673 | 0 | 0 | 4.9108 | -177.6672 | 108.1901

## LLG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.53701 | 3.3496 | 2.9917 | 0.53859 | 3.3498 | 2.9911 | 6.2008 | 38.6775 | 34.5448 | 6.2191 | 38.6799 | 34.5383 | -2.6778 | 15.5707 | 3.8158 | 3.0592 | -7.1268 | -1.4674 | 7.6448 | 9.7034 | 11.7777 | -7.8507 | -2.9351 | -6.1426 | -109.1052 | -168.6333 | 23.2724 | 70.9678 | 11.396 | -156.7589 |  | 1.3063 | 0.47435 | 0.35839 | 1.3548 | 0.19926 | 0.18285 | 0.19907 | -136.7028 | 95.3209 | 2.2573 | -146.22 | 99.8057
Line_1 | 0.2939 | 2.5186 | 2.2684 | 0.29198 | 2.5185 | 2.2693 | 3.3936 | 29.0821 | 26.1931 | 3.3715 | 29.0809 | 26.2031 | 1.8965 | 5.5329e-11 | 6.7632e-11 | -1.8626 | 5.1529 | 1.4746 | -4.4043 | -5.3435e-11 | -6.8974e-12 | 4.1706 | 2.651 | 4.5587 | 68.3701 | 6.6042 | -152.3181 | -111.8079 | -173.4441 | 27.7309 |  | 1.413 | 0 | 0 | 1.3548 | 0.19926 | 0.18285 | 1.6673 | 0 | 0 | 2.2573 | -146.22 | 99.8057
Line_2 | 0.24908 | 0.86724 | 0.75018 | 0.24736 | 0.86673 | 0.75015 | 2.8762 | 10.014 | 8.6623 | 2.8563 | 10.0082 | 8.662 | 1.355 | -1.3992 | 0.25728 | -1.1966 | 1.9739 | -0.0072573 | -3.6295 | 0.60485 | -1.6632 | 3.68 | 0.28417 | 1.5839 | 74.4386 | 25.7101 | -170.6033 | -105.7552 | -154.4121 | 9.5432 |  | 1.347 | 0.15222 | 0.19429 | 1.3548 | 0.19926 | 0.18285 | 4.9108 | -177.6672 | 108.1901 | 2.2573 | -146.22 | 99.8057
Line_3 | 0.053585 | 1.7224 | 1.5734 | 0.052491 | 1.7228 | 1.5745 | 0.61875 | 19.8883 | 18.1684 | 0.60611 | 19.8927 | 18.1802 | 0.6893 | 4.3326e-11 | 4.5676e-11 | -0.68654 | 3.0154 | 1.099 | -0.53785 | -2.9831e-11 | -1.172e-11 | 0.44186 | 0.27717 | 3.3569 | 39.6319 | -2.8497 | -143.7496 | -142.3235 | 177.0811 | 36.3179 |  | 1.413 | 0 | 0 | 1.347 | 0.15222 | 0.19429 | 1.6673 | 0 | 0 | 4.9108 | -177.6672 | 108.1901

## LLG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.037435 | 0.80315 | 0.61528 | 0.037942 | 0.80335 | 0.61496 | 0.43226 | 9.274 | 7.1047 | 0.43812 | 9.2763 | 7.1009 | -0.13779 | 8.6508 | 3.5277 | 0.14313 | -8.0964 | -3.4852 | 0.50102 | 2.4585 | 5.8171 | -0.5158 | -2.1084 | -5.5312 | -104.3487 | -139.6448 | 52.4718 | 76.1934 | 40.3969 | -127.5774 |  | 1.2021 | 0.96974 | 0.95757 | 1.2218 | 0.90191 | 0.92068 | 1.0287 | -123.7799 | 111.2379 | 1.702 | -125.0066 | 110.2075
Line_1 | 0.029121 | 0.61762 | 0.52927 | 0.028551 | 0.61749 | 0.52973 | 0.33626 | 7.1317 | 6.1115 | 0.32968 | 7.1302 | 6.1168 | 0.16046 | -5.491 | -3.3141 | -0.16134 | 5.8356 | 3.3979 | -0.3875 | -2.586 | -4.1787 | 0.36908 | 2.7019 | 4.4911 | 69.0994 | 30.2188 | -122.7478 | -111.9103 | -149.851 | 57.3182 |  | 1.2473 | 0.85105 | 0.87269 | 1.2218 | 0.90191 | 0.92068 | 1.5928 | -124.5626 | 108.8343 | 1.702 | -125.0066 | 110.2075
Line_2 | 0.011136 | 0.2249 | 0.098213 | 0.010479 | 0.22444 | 0.098187 | 0.12859 | 2.597 | 1.1341 | 0.12101 | 2.5916 | 1.1338 | -0.020125 | -2.2035 | -0.076767 | 0.018214 | 2.2607 | 0.087356 | -0.15507 | 0.65824 | -1.0548 | 0.14672 | -0.59352 | 1.0402 | 99.8868 | 69.8325 | -155.3939 | -81.2214 | -110.2965 | 25.008 |  | 1.216 | 0.88554 | 0.93253 | 1.2218 | 0.90191 | 0.92068 | 2.4921 | -126.7996 | 110.4434 | 1.702 | -125.0066 | 110.2075
Line_3 | 0.020498 | 0.46682 | 0.44952 | 0.020134 | 0.46698 | 0.45 | 0.23669 | 5.3904 | 5.1906 | 0.23248 | 5.3922 | 5.1962 | 0.18113 | -3.3516 | -3.2112 | -0.18408 | 3.6082 | 3.3424 | -0.23313 | -3.1324 | -3.1948 | 0.21456 | 3.1275 | 3.5084 | 53.7473 | 12.3737 | -116.019 | -128.1349 | -167.7177 | 64.0554 |  | 1.2473 | 0.85105 | 0.87269 | 1.216 | 0.88554 | 0.93253 | 1.5928 | -124.5626 | 108.8343 | 2.4921 | -126.7996 | 110.4434

## LLG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.037435 | 0.80315 | 0.61528 | 0.037942 | 0.80335 | 0.61496 | 0.43226 | 9.274 | 7.1047 | 0.43812 | 9.2763 | 7.1009 | -0.13779 | 8.6508 | 3.5277 | 0.14313 | -8.0964 | -3.4852 | 0.50102 | 2.4585 | 5.8171 | -0.5158 | -2.1084 | -5.5312 | -104.3487 | -139.6448 | 52.4718 | 76.1934 | 40.3969 | -127.5774 |  | 1.2021 | 0.96974 | 0.95757 | 1.2218 | 0.90191 | 0.92068 | 1.0287 | -123.7799 | 111.2379 | 1.702 | -125.0066 | 110.2075
Line_1 | 0.029121 | 0.61762 | 0.52927 | 0.028551 | 0.61749 | 0.52973 | 0.33626 | 7.1317 | 6.1115 | 0.32968 | 7.1302 | 6.1168 | 0.16046 | -5.491 | -3.3141 | -0.16134 | 5.8356 | 3.3979 | -0.3875 | -2.586 | -4.1787 | 0.36908 | 2.7019 | 4.4911 | 69.0994 | 30.2188 | -122.7478 | -111.9103 | -149.851 | 57.3182 |  | 1.2473 | 0.85105 | 0.87269 | 1.2218 | 0.90191 | 0.92068 | 1.5928 | -124.5626 | 108.8343 | 1.702 | -125.0066 | 110.2075
Line_2 | 0.011136 | 0.2249 | 0.098213 | 0.010479 | 0.22444 | 0.098187 | 0.12859 | 2.597 | 1.1341 | 0.12101 | 2.5916 | 1.1338 | -0.020125 | -2.2035 | -0.076767 | 0.018214 | 2.2607 | 0.087356 | -0.15507 | 0.65824 | -1.0548 | 0.14672 | -0.59352 | 1.0402 | 99.8868 | 69.8325 | -155.3939 | -81.2214 | -110.2965 | 25.008 |  | 1.216 | 0.88554 | 0.93253 | 1.2218 | 0.90191 | 0.92068 | 2.4921 | -126.7996 | 110.4434 | 1.702 | -125.0066 | 110.2075
Line_3 | 0.020498 | 0.46682 | 0.44952 | 0.020134 | 0.46698 | 0.45 | 0.23669 | 5.3904 | 5.1906 | 0.23248 | 5.3922 | 5.1962 | 0.18113 | -3.3516 | -3.2112 | -0.18408 | 3.6082 | 3.3424 | -0.23313 | -3.1324 | -3.1948 | 0.21456 | 3.1275 | 3.5084 | 53.7473 | 12.3737 | -116.019 | -128.1349 | -167.7177 | 64.0554 |  | 1.2473 | 0.85105 | 0.87269 | 1.216 | 0.88554 | 0.93253 | 1.5928 | -124.5626 | 108.8343 | 2.4921 | -126.7996 | 110.4434

## LLG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.59426 | 2.6608 | 2.5121 | 0.59544 | 2.661 | 2.5116 | 6.8619 | 30.7239 | 29.0074 | 6.8755 | 30.726 | 29.0016 | 0.15296 | 17.417 | 7.203 | 0.3284 | -7.896 | -3.0697 | 7.348 | 4.2378 | 10.301 | -7.6899 | -0.30248 | -5.7364 | -88.4295 | -158.9601 | 36.522 | 91.5918 | 21.0655 | -143.503 |  | 1.0711 | 0.58343 | 0.43332 | 1.1195 | 0.25717 | 0.22434 | 0.37794 | -145.2851 | 91.5585 | 4.0371 | -156.7407 | 98.3442
Line_1 | 0.32877 | 2.0094 | 1.8802 | 0.3271 | 2.0091 | 1.8811 | 3.7963 | 23.2025 | 21.7109 | 3.777 | 23.1996 | 21.7214 | 0.52895 | -6.8799e-11 | -2.8907e-11 | -0.56744 | 5.9145 | 2.5232 | -4.526 | -4.4057e-11 | -7.1735e-11 | 4.1899 | 0.78393 | 4.1688 | 86.3812 | 15.7571 | -140.515 | -93.6754 | -164.2909 | 39.5289 |  | 1.2003 | 0 | 0 | 1.1195 | 0.25717 | 0.22434 | 3.047 | 0 | 0 | 4.0371 | -156.7407 | 98.3442
Line_2 | 0.27278 | 0.68707 | 0.64074 | 0.27139 | 0.68669 | 0.64089 | 3.1498 | 7.9336 | 7.3986 | 3.1338 | 7.9292 | 7.4004 | 0.04612 | -1.3177 | -0.22994 | 0.23903 | 1.9815 | 0.54657 | -3.4411 | 1.2805 | -1.8309 | 3.5 | -0.48145 | 1.5676 | 98.0134 | 37.0306 | -152.5609 | -82.0559 | -143.084 | 27.566 |  | 1.0926 | 0.2316 | 0.24941 | 1.1195 | 0.25717 | 0.22434 | 8.7813 | 172.8512 | 110.2809 | 4.0371 | -156.7407 | 98.3442
Line_3 | 0.082767 | 1.3914 | 1.2605 | 0.08192 | 1.3916 | 1.2614 | 0.95571 | 16.066 | 14.555 | 0.94593 | 16.0689 | 14.565 | 0.85182 | -4.1421e-11 | -2.4346e-11 | -0.84331 | 3.6327 | 1.5539 | -0.76838 | -3.8527e-11 | -4.5778e-11 | 0.59746 | -0.80841 | 3.2835 | 45.0988 | 5.4653 | -134.4579 | -135.902 | -174.6027 | 45.6068 |  | 1.2003 | 0 | 0 | 1.0926 | 0.2316 | 0.24941 | 3.047 | 0 | 0 | 8.7813 | 172.8512 | 110.2809

## LLG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.59426 | 2.6608 | 2.5121 | 0.59544 | 2.661 | 2.5116 | 6.8619 | 30.7239 | 29.0074 | 6.8755 | 30.726 | 29.0016 | 0.15296 | 17.417 | 7.203 | 0.3284 | -7.896 | -3.0697 | 7.348 | 4.2378 | 10.301 | -7.6899 | -0.30248 | -5.7364 | -88.4295 | -158.9601 | 36.522 | 91.5918 | 21.0655 | -143.503 |  | 1.0711 | 0.58343 | 0.43332 | 1.1195 | 0.25717 | 0.22434 | 0.37794 | -145.2851 | 91.5585 | 4.0371 | -156.7407 | 98.3442
Line_1 | 0.32877 | 2.0094 | 1.8802 | 0.3271 | 2.0091 | 1.8811 | 3.7963 | 23.2025 | 21.7109 | 3.777 | 23.1996 | 21.7214 | 0.52895 | -6.8799e-11 | -2.8907e-11 | -0.56744 | 5.9145 | 2.5232 | -4.526 | -4.4057e-11 | -7.1735e-11 | 4.1899 | 0.78393 | 4.1688 | 86.3812 | 15.7571 | -140.515 | -93.6754 | -164.2909 | 39.5289 |  | 1.2003 | 0 | 0 | 1.1195 | 0.25717 | 0.22434 | 3.047 | 0 | 0 | 4.0371 | -156.7407 | 98.3442
Line_2 | 0.27278 | 0.68707 | 0.64074 | 0.27139 | 0.68669 | 0.64089 | 3.1498 | 7.9336 | 7.3986 | 3.1338 | 7.9292 | 7.4004 | 0.04612 | -1.3177 | -0.22994 | 0.23903 | 1.9815 | 0.54657 | -3.4411 | 1.2805 | -1.8309 | 3.5 | -0.48145 | 1.5676 | 98.0134 | 37.0306 | -152.5609 | -82.0559 | -143.084 | 27.566 |  | 1.0926 | 0.2316 | 0.24941 | 1.1195 | 0.25717 | 0.22434 | 8.7813 | 172.8512 | 110.2809 | 4.0371 | -156.7407 | 98.3442
Line_3 | 0.082767 | 1.3914 | 1.2605 | 0.08192 | 1.3916 | 1.2614 | 0.95571 | 16.066 | 14.555 | 0.94593 | 16.0689 | 14.565 | 0.85182 | -4.1421e-11 | -2.4346e-11 | -0.84331 | 3.6327 | 1.5539 | -0.76838 | -3.8527e-11 | -4.5778e-11 | 0.59746 | -0.80841 | 3.2835 | 45.0988 | 5.4653 | -134.4579 | -135.902 | -174.6027 | 45.6068 |  | 1.2003 | 0 | 0 | 1.0926 | 0.2316 | 0.24941 | 3.047 | 0 | 0 | 8.7813 | 172.8512 | 110.2809

## LLG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.21667 | 0.74319 | 0.68699 | 0.2171 | 0.74325 | 0.68678 | 2.5019 | 8.5816 | 7.9327 | 2.5069 | 8.5823 | 7.9303 | 0.82905 | 7.0917 | 3.7475 | -0.77138 | -6.296 | -3.4782 | 2.4242 | 2.5937 | 5.6846 | -2.4721 | -2.2843 | -5.3078 | -70.7883 | -145.8077 | 55.1664 | 109.2259 | 34.2252 | -124.8651 |  | 1.024 | 0.87992 | 0.85831 | 1.033 | 0.78039 | 0.80021 | 0.33188 | -125.7186 | 111.7721 | 1.8959 | -125.833 | 111.8984
Line_1 | 0.11928 | 0.56421 | 0.52114 | 0.11867 | 0.56414 | 0.52152 | 1.3773 | 6.5149 | 6.0177 | 1.3703 | 6.5141 | 6.022 | -0.30186 | -4.0488 | -2.7307 | 0.292 | 4.5589 | 2.9275 | -1.4316 | -2.2114 | -3.4517 | 1.3851 | 2.2492 | 3.8277 | 103.8397 | 27.9683 | -120.7454 | -76.1999 | -152.0933 | 59.3076 |  | 1.0623 | 0.70812 | 0.73138 | 1.033 | 0.78039 | 0.80021 | 1.9328 | -123.3885 | 110.9066 | 1.8959 | -125.833 | 111.8984
Line_2 | 0.1001 | 0.19296 | 0.17086 | 0.099593 | 0.1928 | 0.17092 | 1.1558 | 2.2281 | 1.9729 | 1.15 | 2.2263 | 1.9736 | -0.44409 | -1.6802 | -0.52662 | 0.47938 | 1.737 | 0.5507 | -1.0836 | 0.042595 | -1.5122 | 1.0869 | 0.035062 | 1.4801 | 115.7455 | 53.1556 | -137.8636 | -64.3046 | -126.9893 | 42.3068 |  | 1.0132 | 0.75436 | 0.81165 | 1.033 | 0.78039 | 0.80021 | 3.4597 | -128.2966 | 112.9358 | 1.8959 | -125.833 | 111.8984
Line_3 | 0.029766 | 0.39804 | 0.36127 | 0.029454 | 0.39816 | 0.36165 | 0.34371 | 4.5961 | 4.1716 | 0.3401 | 4.5976 | 4.1759 | 0.19174 | -2.4744 | -2.2061 | -0.19365 | 2.8169 | 2.3695 | -0.31071 | -2.1142 | -2.1075 | 0.28501 | 2.0233 | 2.4235 | 60.2538 | 16.0988 | -112.7836 | -120.7345 | -163.9853 | 67.2902 |  | 1.0623 | 0.70812 | 0.73138 | 1.0132 | 0.75436 | 0.81165 | 1.9328 | -123.3885 | 110.9066 | 3.4597 | -128.2966 | 112.9358

## LLG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.21667 | 0.74319 | 0.68699 | 0.2171 | 0.74325 | 0.68678 | 2.5019 | 8.5816 | 7.9327 | 2.5069 | 8.5823 | 7.9303 | 0.82905 | 7.0917 | 3.7475 | -0.77138 | -6.296 | -3.4782 | 2.4242 | 2.5937 | 5.6846 | -2.4721 | -2.2843 | -5.3078 | -70.7883 | -145.8077 | 55.1664 | 109.2259 | 34.2252 | -124.8651 |  | 1.024 | 0.87992 | 0.85831 | 1.033 | 0.78039 | 0.80021 | 0.33188 | -125.7186 | 111.7721 | 1.8959 | -125.833 | 111.8984
Line_1 | 0.11928 | 0.56421 | 0.52114 | 0.11867 | 0.56414 | 0.52152 | 1.3773 | 6.5149 | 6.0177 | 1.3703 | 6.5141 | 6.022 | -0.30186 | -4.0488 | -2.7307 | 0.292 | 4.5589 | 2.9275 | -1.4316 | -2.2114 | -3.4517 | 1.3851 | 2.2492 | 3.8277 | 103.8397 | 27.9683 | -120.7454 | -76.1999 | -152.0933 | 59.3076 |  | 1.0623 | 0.70812 | 0.73138 | 1.033 | 0.78039 | 0.80021 | 1.9328 | -123.3885 | 110.9066 | 1.8959 | -125.833 | 111.8984
Line_2 | 0.1001 | 0.19296 | 0.17086 | 0.099593 | 0.1928 | 0.17092 | 1.1558 | 2.2281 | 1.9729 | 1.15 | 2.2263 | 1.9736 | -0.44409 | -1.6802 | -0.52662 | 0.47938 | 1.737 | 0.5507 | -1.0836 | 0.042595 | -1.5122 | 1.0869 | 0.035062 | 1.4801 | 115.7455 | 53.1556 | -137.8636 | -64.3046 | -126.9893 | 42.3068 |  | 1.0132 | 0.75436 | 0.81165 | 1.033 | 0.78039 | 0.80021 | 3.4597 | -128.2966 | 112.9358 | 1.8959 | -125.833 | 111.8984
Line_3 | 0.029766 | 0.39804 | 0.36127 | 0.029454 | 0.39816 | 0.36165 | 0.34371 | 4.5961 | 4.1716 | 0.3401 | 4.5976 | 4.1759 | 0.19174 | -2.4744 | -2.2061 | -0.19365 | 2.8169 | 2.3695 | -0.31071 | -2.1142 | -2.1075 | 0.28501 | 2.0233 | 2.4235 | 60.2538 | 16.0988 | -112.7836 | -120.7345 | -163.9853 | 67.2902 |  | 1.0623 | 0.70812 | 0.73138 | 1.0132 | 0.75436 | 0.81165 | 1.9328 | -123.3885 | 110.9066 | 3.4597 | -128.2966 | 112.9358