## LLL_max_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 3.6999 | 3.6999 | 0 | 0 | 128.1693 | 128.1693 | 35.5926 | -14.237 | 40.3839 | -16.1536 | -73.5107 | 106.4893 | 0.41999 | 0.168 | -24.9022 | -24.9022
Line_1 | 2.4666 | 2.4666 | 4.9647 | 0 | 85.4462 | 85.4462 | -1e-07 | 9.4914 | -1e-07 | 10.769 | 106.4893 | -73.5107 | 0 | 0.168 | 0 | -24.9022
Line_2 | 1.2333 | 1.2333 | 0 | 0 | 42.7231 | 42.7231 | -2.3728 | 4.7457 | -2.6923 | 5.3845 | 106.4893 | -73.5107 | 0.083999 | 0.168 | -24.9022 | -24.9022
Line_3 | 1.2333 | 1.2333 | 2.4824 | 0 | 42.7231 | 42.7231 | -1e-07 | 2.3728 | -1e-07 | 2.6923 | 106.4893 | -73.5107 | 0 | 0.083999 | 0 | -24.9022

## LLL_max_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 3.6999 | 3.6999 | 0 | 0 | 128.1693 | 128.1693 | 35.5926 | -14.237 | 40.3839 | -16.1536 | -73.5107 | 106.4893 | 0.41999 | 0.168 | -24.9022 | -24.9022
Line_1 | 2.4666 | 2.4666 | 4.9647 | 0 | 85.4462 | 85.4462 | -1e-07 | 9.4914 | -1e-07 | 10.769 | 106.4893 | -73.5107 | 0 | 0.168 | 0 | -24.9022
Line_2 | 1.2333 | 1.2333 | 0 | 0 | 42.7231 | 42.7231 | -2.3728 | 4.7457 | -2.6923 | 5.3845 | 106.4893 | -73.5107 | 0.083999 | 0.168 | -24.9022 | -24.9022
Line_3 | 1.2333 | 1.2333 | 2.4824 | 0 | 42.7231 | 42.7231 | -1e-07 | 2.3728 | -1e-07 | 2.6923 | 106.4893 | -73.5107 | 0 | 0.083999 | 0 | -24.9022

## LLL_max_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 1.2428 | 1.2428 | 0 | 0 | 43.0531 | 43.0531 | 27.1857 | -24.7761 | 27.7264 | -24.9923 | -54.2264 | 125.7736 | 0.90192 | 0.81741 | -8.6624 | -8.9775
Line_1 | 0.82856 | 0.82856 | 1.6677 | 0 | 28.7021 | 28.7021 | -15.4464 | 16.5174 | -15.4464 | 16.6616 | 125.7736 | -54.2264 | 0.76108 | 0.81741 | -9.2264 | -8.9775
Line_2 | 0.41428 | 0.41428 | 0 | 0 | 14.351 | 14.351 | -7.991 | 8.2587 | -8.027 | 8.3308 | 125.7736 | -54.2264 | 0.78924 | 0.81741 | -9.0975 | -8.9775
Line_3 | 0.41428 | 0.41428 | 0.83384 | 0 | 14.351 | 14.351 | -7.7232 | 7.991 | -7.7232 | 8.027 | 125.7736 | -54.2264 | 0.76108 | 0.78924 | -9.2264 | -9.0975

## LLL_max_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 1.2428 | 1.2428 | 0 | 0 | 43.0531 | 43.0531 | 27.1857 | -24.7761 | 27.7264 | -24.9923 | -54.2264 | 125.7736 | 0.90192 | 0.81741 | -8.6624 | -8.9775
Line_1 | 0.82856 | 0.82856 | 1.6677 | 0 | 28.7021 | 28.7021 | -15.4464 | 16.5174 | -15.4464 | 16.6616 | 125.7736 | -54.2264 | 0.76108 | 0.81741 | -9.2264 | -8.9775
Line_2 | 0.41428 | 0.41428 | 0 | 0 | 14.351 | 14.351 | -7.991 | 8.2587 | -8.027 | 8.3308 | 125.7736 | -54.2264 | 0.78924 | 0.81741 | -9.0975 | -8.9775
Line_3 | 0.41428 | 0.41428 | 0.83384 | 0 | 14.351 | 14.351 | -7.7232 | 7.991 | -7.7232 | 8.027 | 125.7736 | -54.2264 | 0.76108 | 0.78924 | -9.2264 | -9.0975

## LLL_min_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 3.0092 | 3.0092 | 0 | 0 | 104.2421 | 104.2421 | 45.2043 | -18.0817 | 26.7133 | -10.6853 | -62.3733 | 117.6267 | 0.50371 | 0.20148 | -31.7926 | -31.7926
Line_1 | 2.0061 | 2.0061 | 3.4722 | 0 | 69.4947 | 69.4947 | -1e-07 | 12.0545 | -1e-07 | 7.1235 | 117.6267 | -62.3733 | 0 | 0.20148 | 0 | -31.7926
Line_2 | 1.0031 | 1.0031 | 0 | 0 | 34.7474 | 34.7474 | -3.0136 | 6.0272 | -1.7809 | 3.5618 | 117.6267 | -62.3733 | 0.10074 | 0.20148 | -31.7926 | -31.7926
Line_3 | 1.0031 | 1.0031 | 1.7361 | 0 | 34.7474 | 34.7474 | -1e-07 | 3.0136 | -1e-07 | 1.7809 | 117.6267 | -62.3733 | 0 | 0.10074 | 0 | -31.7926

## LLL_min_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 3.0092 | 3.0092 | 0 | 0 | 104.2421 | 104.2421 | 45.2043 | -18.0817 | 26.7133 | -10.6853 | -62.3733 | 117.6267 | 0.50371 | 0.20148 | -31.7926 | -31.7926
Line_1 | 2.0061 | 2.0061 | 3.4722 | 0 | 69.4947 | 69.4947 | -1e-07 | 12.0545 | -1e-07 | 7.1235 | 117.6267 | -62.3733 | 0 | 0.20148 | 0 | -31.7926
Line_2 | 1.0031 | 1.0031 | 0 | 0 | 34.7474 | 34.7474 | -3.0136 | 6.0272 | -1.7809 | 3.5618 | 117.6267 | -62.3733 | 0.10074 | 0.20148 | -31.7926 | -31.7926
Line_3 | 1.0031 | 1.0031 | 1.7361 | 0 | 34.7474 | 34.7474 | -1e-07 | 3.0136 | -1e-07 | 1.7809 | 117.6267 | -62.3733 | 0 | 0.10074 | 0 | -31.7926

## LLL_min_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 1.0697 | 1.0697 | 0 | 0 | 37.0569 | 37.0569 | 22.8777 | -19.4502 | 20.541 | -18.5155 | -51.0933 | 128.9067 | 0.8297 | 0.72467 | -9.1739 | -7.5036
Line_1 | 0.71316 | 0.71316 | 1.2343 | 0 | 24.7046 | 24.7046 | -11.4434 | 12.9668 | -11.4434 | 12.3437 | 128.9067 | -51.0933 | 0.65508 | 0.72467 | -6.0933 | -7.5036
Line_2 | 0.35658 | 0.35658 | 0 | 0 | 12.3523 | 12.3523 | -6.1026 | 6.4834 | -5.9468 | 6.1718 | 128.9067 | -51.0933 | 0.68982 | 0.72467 | -6.834 | -7.5036
Line_3 | 0.35658 | 0.35658 | 0.61717 | 0 | 12.3523 | 12.3523 | -5.7217 | 6.1026 | -5.7217 | 5.9468 | 128.9067 | -51.0933 | 0.65508 | 0.68982 | -6.0933 | -6.834

## LLL_min_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 1.0697 | 1.0697 | 0 | 0 | 37.0569 | 37.0569 | 22.8777 | -19.4502 | 20.541 | -18.5155 | -51.0933 | 128.9067 | 0.8297 | 0.72467 | -9.1739 | -7.5036
Line_1 | 0.71316 | 0.71316 | 1.2343 | 0 | 24.7046 | 24.7046 | -11.4434 | 12.9668 | -11.4434 | 12.3437 | 128.9067 | -51.0933 | 0.65508 | 0.72467 | -6.0933 | -7.5036
Line_2 | 0.35658 | 0.35658 | 0 | 0 | 12.3523 | 12.3523 | -6.1026 | 6.4834 | -5.9468 | 6.1718 | 128.9067 | -51.0933 | 0.68982 | 0.72467 | -6.834 | -7.5036
Line_3 | 0.35658 | 0.35658 | 0.61717 | 0 | 12.3523 | 12.3523 | -5.7217 | 6.1026 | -5.7217 | 5.9468 | 128.9067 | -51.0933 | 0.65508 | 0.68982 | -6.0933 | -6.834

## LL_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 3.2042 | 3.2042 | 0 | 3.2042 | 3.2042 | 0 | 36.9993 | 36.9993 | 0 | 36.9993 | 36.9993 | -1.5632e-14 | 28.4108 | -10.6145 | 1.0421e-14 | -23.0719 | 15.9534 | -3.6475e-14 | 4.32 | 15.8719 | 4.1685e-14 | 1.7376 | -9.8143 | 0 | -163.5107 | 16.4893 | 0 | 16.4893 | -163.5107 | 1.1 | 0.7767 | 0.51607 | 1.1 | 0.62534 | 0.50624 | -2.0157e-13 | -154.8648 | 140.2623 | -2.1137e-13 | -167.8176 | 164.89
Line_1 | 0 | 2.1362 | 2.1362 | 0 | 2.1362 | 2.1362 | 0 | 24.6662 | 24.6662 | 0 | 24.6662 | 24.6662 | -2.6053e-14 | -13.0085 | 13.0085 | 1.5632e-14 | 15.3813 | -10.6356 | 4.1685e-14 | 3.8506 | -3.8506 | -3.1264e-14 | -1.1584 | 6.5429 | 0 | 16.4893 | -163.5107 | 0 | -163.5107 | 16.4893 | 1.1 | 0.55 | 0.55 | 1.1 | 0.62534 | 0.50624 | -2.5843e-13 | 180 | -180 | -2.1137e-13 | -167.8176 | 164.89
Line_2 | 0 | 1.0681 | 1.0681 | 0 | 1.0681 | 1.0681 | 0 | 12.3331 | 12.3331 | 0 | 12.3331 | 12.3331 | -5.2106e-15 | -7.0974 | 5.911 | -5.2106e-15 | 7.6906 | -5.3178 | 2.6053e-14 | 1.2523 | -2.5984 | -2.0843e-14 | -0.57919 | 3.2714 | 0 | 16.4893 | -163.5107 | 0 | -163.5107 | 16.4893 | 1.1 | 0.58437 | 0.52354 | 1.1 | 0.62534 | 0.50624 | -2.5351e-13 | -173.5168 | 172.7598 | -2.1137e-13 | -167.8176 | 164.89
Line_3 | 0 | 1.0681 | 1.0681 | 0 | 1.0681 | 1.0681 | 0 | 12.3331 | 12.3331 | 0 | 12.3331 | 12.3331 | -2.0843e-14 | -6.5042 | 6.5042 | 1.0421e-14 | 7.0974 | -5.911 | 2.0843e-14 | 1.9253 | -1.9253 | -5.2106e-15 | -1.2523 | 2.5984 | 0 | 16.4893 | -163.5107 | 0 | -163.5107 | 16.4893 | 1.1 | 0.55 | 0.55 | 1.1 | 0.58437 | 0.52354 | -2.5843e-13 | 180 | -180 | -2.5351e-13 | -173.5168 | 172.7598

## LL_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 3.2042 | 3.2042 | 0 | 3.2042 | 3.2042 | 0 | 36.9993 | 36.9993 | 0 | 36.9993 | 36.9993 | -1.5632e-14 | 28.4108 | -10.6145 | 1.0421e-14 | -23.0719 | 15.9534 | -3.6475e-14 | 4.32 | 15.8719 | 4.1685e-14 | 1.7376 | -9.8143 | 0 | -163.5107 | 16.4893 | 0 | 16.4893 | -163.5107 | 1.1 | 0.7767 | 0.51607 | 1.1 | 0.62534 | 0.50624 | -2.0157e-13 | -154.8648 | 140.2623 | -2.1137e-13 | -167.8176 | 164.89
Line_1 | 0 | 2.1362 | 2.1362 | 0 | 2.1362 | 2.1362 | 0 | 24.6662 | 24.6662 | 0 | 24.6662 | 24.6662 | -2.6053e-14 | -13.0085 | 13.0085 | 1.5632e-14 | 15.3813 | -10.6356 | 4.1685e-14 | 3.8506 | -3.8506 | -3.1264e-14 | -1.1584 | 6.5429 | 0 | 16.4893 | -163.5107 | 0 | -163.5107 | 16.4893 | 1.1 | 0.55 | 0.55 | 1.1 | 0.62534 | 0.50624 | -2.5843e-13 | 180 | -180 | -2.1137e-13 | -167.8176 | 164.89
Line_2 | 0 | 1.0681 | 1.0681 | 0 | 1.0681 | 1.0681 | 0 | 12.3331 | 12.3331 | 0 | 12.3331 | 12.3331 | -5.2106e-15 | -7.0974 | 5.911 | -5.2106e-15 | 7.6906 | -5.3178 | 2.6053e-14 | 1.2523 | -2.5984 | -2.0843e-14 | -0.57919 | 3.2714 | 0 | 16.4893 | -163.5107 | 0 | -163.5107 | 16.4893 | 1.1 | 0.58437 | 0.52354 | 1.1 | 0.62534 | 0.50624 | -2.5351e-13 | -173.5168 | 172.7598 | -2.1137e-13 | -167.8176 | 164.89
Line_3 | 0 | 1.0681 | 1.0681 | 0 | 1.0681 | 1.0681 | 0 | 12.3331 | 12.3331 | 0 | 12.3331 | 12.3331 | -2.0843e-14 | -6.5042 | 6.5042 | 1.0421e-14 | 7.0974 | -5.911 | 2.0843e-14 | 1.9253 | -1.9253 | -5.2106e-15 | -1.2523 | 2.5984 | 0 | 16.4893 | -163.5107 | 0 | -163.5107 | 16.4893 | 1.1 | 0.55 | 0.55 | 1.1 | 0.58437 | 0.52354 | -2.5843e-13 | 180 | -180 | -2.5351e-13 | -173.5168 | 172.7598

## LL_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 1.6287 | 1.6287 | 0 | 1.6287 | 1.6287 | 0 | 18.8063 | 18.8063 | 0 | 18.8063 | 18.8063 | -1.5632e-14 | 17.8002 | 0.06044 | 1.5632e-14 | -16.4209 | 1.3189 | -1.5632e-14 | 3.9189 | 14.5607 | 2.3448e-14 | -2.3539 | -12.9957 | 0 | -149.0411 | 30.9589 | 0 | 30.9589 | -149.0411 | 1.1 | 0.96917 | 0.77425 | 1.1 | 0.88208 | 0.69458 | -2.1973e-12 | -136.625 | 120.7211 | -2.2033e-12 | -140.8835 | 126.7539
Line_1 | 0 | 1.0858 | 1.0858 | 0 | 1.0858 | 1.0858 | 0 | 12.5375 | 12.5375 | 0 | 12.5375 | 12.5375 | -1.0421e-14 | -10.3342 | 1.4923 | 7.816e-15 | 10.9473 | -0.87927 | 2.6053e-14 | -0.87368 | -7.9682 | -2.0843e-14 | 1.5692 | 8.6638 | 0 | 30.9589 | -149.0411 | 0 | -149.0411 | 30.9589 | 1.1 | 0.8272 | 0.6466 | 1.1 | 0.88208 | 0.69458 | -2.2287e-12 | -144.2087 | 131.5665 | -2.2033e-12 | -140.8835 | 126.7539
Line_2 | 0 | 0.54289 | 0.54289 | 0 | 0.54289 | 0.54289 | 0 | 6.2688 | 6.2688 | 0 | 6.2688 | 6.2688 | 9.1083e-28 | -5.3204 | 0.59289 | 2.6053e-15 | 5.4736 | -0.43963 | 2.3448e-14 | -0.61073 | -4.158 | -1.5632e-14 | 0.78462 | 4.3319 | 0 | 30.9589 | -149.0411 | 0 | -149.0411 | 30.9589 | 1.1 | 0.85428 | 0.67 | 1.1 | 0.88208 | 0.69458 | -2.2256e-12 | -142.4927 | 129.0741 | -2.2033e-12 | -140.8835 | 126.7539
Line_3 | 0 | 0.54289 | 0.54289 | 0 | 0.54289 | 0.54289 | 0 | 6.2688 | 6.2688 | 0 | 6.2688 | 6.2688 | -5.2106e-15 | -5.1671 | 0.74615 | 5.2106e-15 | 5.3204 | -0.59289 | 7.816e-15 | -0.43684 | -3.9841 | -2.0241e-28 | 0.61073 | 4.158 | 0 | 30.9589 | -149.0411 | 0 | -149.0411 | 30.9589 | 1.1 | 0.8272 | 0.6466 | 1.1 | 0.85428 | 0.67 | -2.2287e-12 | -144.2087 | 131.5665 | -2.2256e-12 | -142.4927 | 129.0741

## LL_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 1.6287 | 1.6287 | 0 | 1.6287 | 1.6287 | 0 | 18.8063 | 18.8063 | 0 | 18.8063 | 18.8063 | -1.5632e-14 | 17.8002 | 0.06044 | 1.5632e-14 | -16.4209 | 1.3189 | -1.5632e-14 | 3.9189 | 14.5607 | 2.3448e-14 | -2.3539 | -12.9957 | 0 | -149.0411 | 30.9589 | 0 | 30.9589 | -149.0411 | 1.1 | 0.96917 | 0.77425 | 1.1 | 0.88208 | 0.69458 | -2.1973e-12 | -136.625 | 120.7211 | -2.2033e-12 | -140.8835 | 126.7539
Line_1 | 0 | 1.0858 | 1.0858 | 0 | 1.0858 | 1.0858 | 0 | 12.5375 | 12.5375 | 0 | 12.5375 | 12.5375 | -1.0421e-14 | -10.3342 | 1.4923 | 7.816e-15 | 10.9473 | -0.87927 | 2.6053e-14 | -0.87368 | -7.9682 | -2.0843e-14 | 1.5692 | 8.6638 | 0 | 30.9589 | -149.0411 | 0 | -149.0411 | 30.9589 | 1.1 | 0.8272 | 0.6466 | 1.1 | 0.88208 | 0.69458 | -2.2287e-12 | -144.2087 | 131.5665 | -2.2033e-12 | -140.8835 | 126.7539
Line_2 | 0 | 0.54289 | 0.54289 | 0 | 0.54289 | 0.54289 | 0 | 6.2688 | 6.2688 | 0 | 6.2688 | 6.2688 | 9.1083e-28 | -5.3204 | 0.59289 | 2.6053e-15 | 5.4736 | -0.43963 | 2.3448e-14 | -0.61073 | -4.158 | -1.5632e-14 | 0.78462 | 4.3319 | 0 | 30.9589 | -149.0411 | 0 | -149.0411 | 30.9589 | 1.1 | 0.85428 | 0.67 | 1.1 | 0.88208 | 0.69458 | -2.2256e-12 | -142.4927 | 129.0741 | -2.2033e-12 | -140.8835 | 126.7539
Line_3 | 0 | 0.54289 | 0.54289 | 0 | 0.54289 | 0.54289 | 0 | 6.2688 | 6.2688 | 0 | 6.2688 | 6.2688 | -5.2106e-15 | -5.1671 | 0.74615 | 5.2106e-15 | 5.3204 | -0.59289 | 7.816e-15 | -0.43684 | -3.9841 | -2.0241e-28 | 0.61073 | 4.158 | 0 | 30.9589 | -149.0411 | 0 | -149.0411 | 30.9589 | 1.1 | 0.8272 | 0.6466 | 1.1 | 0.85428 | 0.67 | -2.2287e-12 | -144.2087 | 131.5665 | -2.2256e-12 | -142.4927 | 129.0741

## LL_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 2.6061 | 2.6061 | 0 | 2.6061 | 2.6061 | 0 | 30.0921 | 30.0921 | 0 | 30.0921 | 30.0921 | 1.8948e-14 | 24.6317 | -2.0295 | -2.7237e-14 | -17.851 | 8.8102 | 9.4739e-15 | -0.29866 | 13.6553 | -1.1842e-14 | 4.3057 | -9.6483 | 0 | -152.3733 | 27.6267 | 0 | 27.6267 | -152.3733 | 1 | 0.8186 | 0.45877 | 1 | 0.61023 | 0.43419 | 8.9794e-12 | -153.068 | 126.0805 | 8.9993e-12 | -165.934 | 160.0269
Line_1 | 0 | 1.7374 | 1.7374 | 0 | 1.7374 | 1.7374 | 0 | 20.0614 | 20.0614 | 0 | 20.0614 | 20.0614 | -2.9606e-14 | -8.8871 | 8.8871 | 2.3685e-14 | 11.9007 | -5.8735 | -2.3685e-15 | 4.6513 | -4.6513 | 3.7201e-27 | -2.8704 | 6.4322 | 0 | 27.6267 | -152.3733 | 0 | -152.3733 | 27.6267 | 1 | 0.5 | 0.5 | 1 | 0.61023 | 0.43419 | 8.9996e-12 | -180 | 180 | 8.9993e-12 | -165.934 | 160.0269
Line_2 | 0 | 0.86868 | 0.86868 | 0 | 0.86868 | 0.86868 | 0 | 10.0307 | 10.0307 | 0 | 10.0307 | 10.0307 | -2.7237e-14 | -5.1969 | 3.6901 | 2.1316e-14 | 5.9503 | -2.9367 | -1.1842e-14 | 1.8804 | -2.7709 | 9.4739e-15 | -1.4352 | 3.2161 | 0 | 27.6267 | -152.3733 | 0 | -152.3733 | 27.6267 | 1 | 0.55098 | 0.46005 | 1 | 0.61023 | 0.43419 | 9.0153e-12 | -172.2653 | 170.7242 | 8.9993e-12 | -165.934 | 160.0269
Line_3 | 0 | 0.86868 | 0.86868 | 0 | 0.86868 | 0.86868 | 0 | 10.0307 | 10.0307 | 0 | 10.0307 | 10.0307 | -4.737e-15 | -4.4435 | 4.4435 | 1.4907e-27 | 5.1969 | -3.6901 | 9.4739e-15 | 2.3257 | -2.3257 | -9.4739e-15 | -1.8804 | 2.7709 | 0 | 27.6267 | -152.3733 | 0 | -152.3733 | 27.6267 | 1 | 0.5 | 0.5 | 1 | 0.55098 | 0.46005 | 8.9996e-12 | -180 | 180 | 9.0153e-12 | -172.2653 | 170.7242

## LL_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 2.6061 | 2.6061 | 0 | 2.6061 | 2.6061 | 0 | 30.0921 | 30.0921 | 0 | 30.0921 | 30.0921 | 1.8948e-14 | 24.6317 | -2.0295 | -2.7237e-14 | -17.851 | 8.8102 | 9.4739e-15 | -0.29866 | 13.6553 | -1.1842e-14 | 4.3057 | -9.6483 | 0 | -152.3733 | 27.6267 | 0 | 27.6267 | -152.3733 | 1 | 0.8186 | 0.45877 | 1 | 0.61023 | 0.43419 | 8.9794e-12 | -153.068 | 126.0805 | 8.9993e-12 | -165.934 | 160.0269
Line_1 | 0 | 1.7374 | 1.7374 | 0 | 1.7374 | 1.7374 | 0 | 20.0614 | 20.0614 | 0 | 20.0614 | 20.0614 | -2.9606e-14 | -8.8871 | 8.8871 | 2.3685e-14 | 11.9007 | -5.8735 | -2.3685e-15 | 4.6513 | -4.6513 | 3.7201e-27 | -2.8704 | 6.4322 | 0 | 27.6267 | -152.3733 | 0 | -152.3733 | 27.6267 | 1 | 0.5 | 0.5 | 1 | 0.61023 | 0.43419 | 8.9996e-12 | -180 | 180 | 8.9993e-12 | -165.934 | 160.0269
Line_2 | 0 | 0.86868 | 0.86868 | 0 | 0.86868 | 0.86868 | 0 | 10.0307 | 10.0307 | 0 | 10.0307 | 10.0307 | -2.7237e-14 | -5.1969 | 3.6901 | 2.1316e-14 | 5.9503 | -2.9367 | -1.1842e-14 | 1.8804 | -2.7709 | 9.4739e-15 | -1.4352 | 3.2161 | 0 | 27.6267 | -152.3733 | 0 | -152.3733 | 27.6267 | 1 | 0.55098 | 0.46005 | 1 | 0.61023 | 0.43419 | 9.0153e-12 | -172.2653 | 170.7242 | 8.9993e-12 | -165.934 | 160.0269
Line_3 | 0 | 0.86868 | 0.86868 | 0 | 0.86868 | 0.86868 | 0 | 10.0307 | 10.0307 | 0 | 10.0307 | 10.0307 | -4.737e-15 | -4.4435 | 4.4435 | 1.4907e-27 | 5.1969 | -3.6901 | 9.4739e-15 | 2.3257 | -2.3257 | -9.4739e-15 | -1.8804 | 2.7709 | 0 | 27.6267 | -152.3733 | 0 | -152.3733 | 27.6267 | 1 | 0.5 | 0.5 | 1 | 0.55098 | 0.46005 | 8.9996e-12 | -180 | 180 | 9.0153e-12 | -172.2653 | 170.7242

## LL_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 1.3721 | 1.3721 | 0 | 1.3721 | 1.3721 | 0 | 15.8432 | 15.8432 | 0 | 15.8432 | 15.8432 | 2.3685e-15 | 14.2512 | 1.4266 | -7.1054e-15 | -12.3717 | 0.45296 | 4.737e-15 | 1.9064 | 11.2087 | -7.1054e-15 | -0.79565 | -10.098 | 0 | -144.0449 | 35.9551 | 0 | 35.9551 | -144.0449 | 1 | 0.90753 | 0.71319 | 1 | 0.7825 | 0.63801 | 4.7923e-12 | -136.4258 | 118.7019 | 4.8016e-12 | -140.3651 | 128.5235
Line_1 | 0 | 0.9147 | 0.9147 | 0 | 0.9147 | 0.9147 | 0 | 10.5621 | 10.5621 | 0 | 10.5621 | 10.5621 | -2.0132e-14 | -7.4125 | 1.1373 | 1.5987e-14 | 8.2478 | -0.30197 | 4.737e-15 | -0.036791 | -6.2383 | -4.737e-15 | 0.53044 | 6.732 | 0 | 35.9551 | -144.0449 | 0 | -144.0449 | 35.9551 | 1 | 0.70181 | 0.60037 | 1 | 0.7825 | 0.63801 | 4.7986e-12 | -143.7605 | 136.2873 | 4.8016e-12 | -140.3651 | 128.5235
Line_2 | 0 | 0.45735 | 0.45735 | 0 | 0.45735 | 0.45735 | 0 | 5.2811 | 5.2811 | 0 | 5.2811 | 5.2811 | -1.5395e-14 | -3.9151 | 0.35982 | 1.0658e-14 | 4.1239 | -0.15099 | -1.2917e-27 | -0.14181 | -3.2426 | 8.932e-28 | 0.26522 | 3.366 | 0 | 35.9551 | -144.0449 | 0 | -144.0449 | 35.9551 | 1 | 0.74183 | 0.61777 | 1 | 0.7825 | 0.63801 | 4.8073e-12 | -141.9705 | 132.2872 | 4.8016e-12 | -140.3651 | 128.5235
Line_3 | 0 | 0.45735 | 0.45735 | 0 | 0.45735 | 0.45735 | 0 | 5.2811 | 5.2811 | 0 | 5.2811 | 5.2811 | -5.9212e-15 | -3.7062 | 0.56866 | 1.7764e-15 | 3.9151 | -0.35982 | 4.737e-15 | -0.018396 | -3.1192 | -4.737e-15 | 0.14181 | 3.2426 | 0 | 35.9551 | -144.0449 | 0 | -144.0449 | 35.9551 | 1 | 0.70181 | 0.60037 | 1 | 0.74183 | 0.61777 | 4.7986e-12 | -143.7605 | 136.2873 | 4.8073e-12 | -141.9705 | 132.2872

## LL_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 1.3721 | 1.3721 | 0 | 1.3721 | 1.3721 | 0 | 15.8432 | 15.8432 | 0 | 15.8432 | 15.8432 | 2.3685e-15 | 14.2512 | 1.4266 | -7.1054e-15 | -12.3717 | 0.45296 | 4.737e-15 | 1.9064 | 11.2087 | -7.1054e-15 | -0.79565 | -10.098 | 0 | -144.0449 | 35.9551 | 0 | 35.9551 | -144.0449 | 1 | 0.90753 | 0.71319 | 1 | 0.7825 | 0.63801 | 4.7923e-12 | -136.4258 | 118.7019 | 4.8016e-12 | -140.3651 | 128.5235
Line_1 | 0 | 0.9147 | 0.9147 | 0 | 0.9147 | 0.9147 | 0 | 10.5621 | 10.5621 | 0 | 10.5621 | 10.5621 | -2.0132e-14 | -7.4125 | 1.1373 | 1.5987e-14 | 8.2478 | -0.30197 | 4.737e-15 | -0.036791 | -6.2383 | -4.737e-15 | 0.53044 | 6.732 | 0 | 35.9551 | -144.0449 | 0 | -144.0449 | 35.9551 | 1 | 0.70181 | 0.60037 | 1 | 0.7825 | 0.63801 | 4.7986e-12 | -143.7605 | 136.2873 | 4.8016e-12 | -140.3651 | 128.5235
Line_2 | 0 | 0.45735 | 0.45735 | 0 | 0.45735 | 0.45735 | 0 | 5.2811 | 5.2811 | 0 | 5.2811 | 5.2811 | -1.5395e-14 | -3.9151 | 0.35982 | 1.0658e-14 | 4.1239 | -0.15099 | -1.2917e-27 | -0.14181 | -3.2426 | 8.932e-28 | 0.26522 | 3.366 | 0 | 35.9551 | -144.0449 | 0 | -144.0449 | 35.9551 | 1 | 0.74183 | 0.61777 | 1 | 0.7825 | 0.63801 | 4.8073e-12 | -141.9705 | 132.2872 | 4.8016e-12 | -140.3651 | 128.5235
Line_3 | 0 | 0.45735 | 0.45735 | 0 | 0.45735 | 0.45735 | 0 | 5.2811 | 5.2811 | 0 | 5.2811 | 5.2811 | -5.9212e-15 | -3.7062 | 0.56866 | 1.7764e-15 | 3.9151 | -0.35982 | 4.737e-15 | -0.018396 | -3.1192 | -4.737e-15 | 0.14181 | 3.2426 | 0 | 35.9551 | -144.0449 | 0 | -144.0449 | 35.9551 | 1 | 0.70181 | 0.60037 | 1 | 0.74183 | 0.61777 | 4.7986e-12 | -143.7605 | 136.2873 | 4.8073e-12 | -141.9705 | 132.2872

## LG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.021687 | 0.010844 | 0.010844 | 0.01627 | 0.016261 | 0.016261 | 0.25042 | 0.12521 | 0.12521 | 0.18787 | 0.18776 | 0.18776 | -9.9818e-05 | -0.11845 | 0.12011 | 9.5165e-05 | 0.17826 | -0.17947 | 0.00026363 | 0.20612 | 0.20518 | -5.3833e-05 | -0.30871 | -0.30774 | -89.773 | 90.2269 | 90.2269 | 90.2988 | -89.8449 | -89.8449 |  | 0.0011257 | 1.8987 | 1.8988 | 0.00058199 | 1.8986 | 1.8973 | 20.9651 | -149.8893 | 149.8827 | 60.803 | -149.8403 | 149.9044
Line_1 | 0.0081406 | 0.013547 | 0.013547 | 0.013556 | 0.0081312 | 0.0081312 | 0.094 | 0.15642 | 0.15642 | 0.15653 | 0.093891 | 0.093891 | 4.5323e-15 | 0.14894 | -0.14908 | -7.9307e-05 | -0.089177 | 0.089708 | 3.2612e-14 | -0.25693 | -0.25636 | 4.4825e-05 | 0.15435 | 0.1539 | 90.4204 | -89.8893 | -89.8893 | -89.7219 | 90.1416 | 90.1416 |  | 0 | 1.8986 | 1.8959 | 0.00058199 | 1.8986 | 1.8973 | 0 | -149.7891 | 149.9306 | 60.803 | -149.8403 | 149.9044
Line_2 | 0.0027004 | 0.013544 | 0.013544 | 0.0027139 | 0.0081296 | 0.0081296 | 0.031181 | 0.15639 | 0.15639 | 0.031337 | 0.093873 | 0.093873 | 4.5985e-05 | 0.14894 | -0.14903 | -1.5858e-05 | -0.089088 | 0.089764 | 2.6253e-05 | -0.25691 | -0.25619 | 9.0082e-06 | 0.15436 | 0.15383 | -90.2145 | -89.8611 | -89.8611 | -89.598 | 90.1685 | 90.1685 |  | 0.0016982 | 1.8988 | 1.8951 | 0.00058199 | 1.8986 | 1.8973 | -60.4927 | -149.759 | 149.9523 | 60.803 | -149.8403 | 149.9044
Line_3 | 0.0081349 | 0.0027086 | 0.0027086 | 0.013548 | 0.0027044 | 0.0027044 | 0.093934 | 0.031277 | 0.031277 | 0.15644 | 0.031228 | 0.031228 | 4.4594e-15 | 0.029867 | -0.029723 | 0.00023172 | 0.029653 | -0.029844 | 3.2598e-14 | -0.051323 | -0.051309 | 0.00012992 | -0.05135 | -0.051105 | 90.2979 | -89.9861 | -89.9861 | -89.7712 | -89.7641 | -89.7641 |  | 0 | 1.8986 | 1.8959 | 0.0016982 | 1.8988 | 1.8951 | 0 | -149.7891 | 149.9306 | -60.4927 | -149.759 | 149.9523

## LG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.021687 | 0.010844 | 0.010844 | 0.01627 | 0.016261 | 0.016261 | 0.25042 | 0.12521 | 0.12521 | 0.18787 | 0.18776 | 0.18776 | -9.9818e-05 | -0.11845 | 0.12011 | 9.5165e-05 | 0.17826 | -0.17947 | 0.00026363 | 0.20612 | 0.20518 | -5.3833e-05 | -0.30871 | -0.30774 | -89.773 | 90.2269 | 90.2269 | 90.2988 | -89.8449 | -89.8449 |  | 0.0011257 | 1.8987 | 1.8988 | 0.00058199 | 1.8986 | 1.8973 | 20.9651 | -149.8893 | 149.8827 | 60.803 | -149.8403 | 149.9044
Line_1 | 0.0081406 | 0.013547 | 0.013547 | 0.013556 | 0.0081312 | 0.0081312 | 0.094 | 0.15642 | 0.15642 | 0.15653 | 0.093891 | 0.093891 | 4.5323e-15 | 0.14894 | -0.14908 | -7.9307e-05 | -0.089177 | 0.089708 | 3.2612e-14 | -0.25693 | -0.25636 | 4.4825e-05 | 0.15435 | 0.1539 | 90.4204 | -89.8893 | -89.8893 | -89.7219 | 90.1416 | 90.1416 |  | 0 | 1.8986 | 1.8959 | 0.00058199 | 1.8986 | 1.8973 | 0 | -149.7891 | 149.9306 | 60.803 | -149.8403 | 149.9044
Line_2 | 0.0027004 | 0.013544 | 0.013544 | 0.0027139 | 0.0081296 | 0.0081296 | 0.031181 | 0.15639 | 0.15639 | 0.031337 | 0.093873 | 0.093873 | 4.5985e-05 | 0.14894 | -0.14903 | -1.5858e-05 | -0.089088 | 0.089764 | 2.6253e-05 | -0.25691 | -0.25619 | 9.0082e-06 | 0.15436 | 0.15383 | -90.2145 | -89.8611 | -89.8611 | -89.598 | 90.1685 | 90.1685 |  | 0.0016982 | 1.8988 | 1.8951 | 0.00058199 | 1.8986 | 1.8973 | -60.4927 | -149.759 | 149.9523 | 60.803 | -149.8403 | 149.9044
Line_3 | 0.0081349 | 0.0027086 | 0.0027086 | 0.013548 | 0.0027044 | 0.0027044 | 0.093934 | 0.031277 | 0.031277 | 0.15644 | 0.031228 | 0.031228 | 4.4594e-15 | 0.029867 | -0.029723 | 0.00023172 | 0.029653 | -0.029844 | 3.2598e-14 | -0.051323 | -0.051309 | 0.00012992 | -0.05135 | -0.051105 | 90.2979 | -89.9861 | -89.9861 | -89.7712 | -89.7641 | -89.7641 |  | 0 | 1.8986 | 1.8959 | 0.0016982 | 1.8988 | 1.8951 | 0 | -149.7891 | 149.9306 | -60.4927 | -149.759 | 149.9523

## LG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.02141 | 0.010705 | 0.010705 | 0.016062 | 0.016053 | 0.016053 | 0.24722 | 0.12361 | 0.12361 | 0.18547 | 0.18537 | 0.18537 | 0.0033406 | -0.11607 | 0.11941 | -0.0024896 | 0.17469 | -0.17844 | 0.0036949 | 0.20324 | 0.19934 | -0.0026284 | -0.30439 | -0.29899 | -89.0515 | 90.9484 | 90.9484 | 91.0203 | -89.1234 | -89.1234 |  | 0.020149 | 1.8934 | 1.8798 | 0.01952 | 1.8933 | 1.8784 | -41.1693 | -149.3206 | 150.0262 | -42.4268 | -149.2722 | 150.0473
Line_1 | 0.0080366 | 0.013374 | 0.013374 | 0.013383 | 0.0080273 | 0.0080273 | 0.092799 | 0.15442 | 0.15442 | 0.15453 | 0.092692 | 0.092692 | -0.0012948 | 0.14595 | -0.14824 | 0.0020736 | -0.087388 | 0.089193 | -0.0012861 | -0.25334 | -0.24907 | 0.0021907 | 0.15219 | 0.14953 | 91.1419 | -89.1678 | -89.1678 | -89.0004 | 90.8631 | 90.8631 |  | 0.019666 | 1.8933 | 1.8769 | 0.01952 | 1.8933 | 1.8784 | -44.0516 | -149.2215 | 150.073 | -42.4268 | -149.2722 | 150.0473
Line_2 | 0.0026659 | 0.013371 | 0.013371 | 0.0026792 | 0.0080258 | 0.0080258 | 0.030783 | 0.15439 | 0.15439 | 0.030937 | 0.092674 | 0.092674 | 0.00046958 | 0.14595 | -0.14818 | 0.00041608 | -0.0873 | 0.089246 | 0.00045695 | -0.25332 | -0.2489 | 0.00043768 | 0.1522 | 0.14946 | -89.493 | -89.1396 | -89.1396 | -88.8765 | 90.89 | 90.89 |  | 0.021285 | 1.8936 | 1.8762 | 0.01952 | 1.8933 | 1.8784 | -45.2743 | -149.1917 | 150.0944 | -42.4268 | -149.2722 | 150.0473
Line_3 | 0.008031 | 0.002674 | 0.002674 | 0.013375 | 0.0026699 | 0.0026699 | 0.092734 | 0.030877 | 0.030877 | 0.15444 | 0.030829 | 0.030829 | -0.0012912 | 0.029269 | -0.029556 | 0.0023736 | 0.029057 | -0.029672 | -0.001288 | -0.050607 | -0.049852 | 0.0022742 | -0.050633 | -0.049651 | 91.0194 | -89.2646 | -89.2646 | -89.0498 | -89.0426 | -89.0426 |  | 0.019666 | 1.8933 | 1.8769 | 0.021285 | 1.8936 | 1.8762 | -44.0516 | -149.2215 | 150.073 | -45.2743 | -149.1917 | 150.0944

## LG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.02141 | 0.010705 | 0.010705 | 0.016062 | 0.016053 | 0.016053 | 0.24722 | 0.12361 | 0.12361 | 0.18547 | 0.18537 | 0.18537 | 0.0033406 | -0.11607 | 0.11941 | -0.0024896 | 0.17469 | -0.17844 | 0.0036949 | 0.20324 | 0.19934 | -0.0026284 | -0.30439 | -0.29899 | -89.0515 | 90.9484 | 90.9484 | 91.0203 | -89.1234 | -89.1234 |  | 0.020149 | 1.8934 | 1.8798 | 0.01952 | 1.8933 | 1.8784 | -41.1693 | -149.3206 | 150.0262 | -42.4268 | -149.2722 | 150.0473
Line_1 | 0.0080366 | 0.013374 | 0.013374 | 0.013383 | 0.0080273 | 0.0080273 | 0.092799 | 0.15442 | 0.15442 | 0.15453 | 0.092692 | 0.092692 | -0.0012948 | 0.14595 | -0.14824 | 0.0020736 | -0.087388 | 0.089193 | -0.0012861 | -0.25334 | -0.24907 | 0.0021907 | 0.15219 | 0.14953 | 91.1419 | -89.1678 | -89.1678 | -89.0004 | 90.8631 | 90.8631 |  | 0.019666 | 1.8933 | 1.8769 | 0.01952 | 1.8933 | 1.8784 | -44.0516 | -149.2215 | 150.073 | -42.4268 | -149.2722 | 150.0473
Line_2 | 0.0026659 | 0.013371 | 0.013371 | 0.0026792 | 0.0080258 | 0.0080258 | 0.030783 | 0.15439 | 0.15439 | 0.030937 | 0.092674 | 0.092674 | 0.00046958 | 0.14595 | -0.14818 | 0.00041608 | -0.0873 | 0.089246 | 0.00045695 | -0.25332 | -0.2489 | 0.00043768 | 0.1522 | 0.14946 | -89.493 | -89.1396 | -89.1396 | -88.8765 | 90.89 | 90.89 |  | 0.021285 | 1.8936 | 1.8762 | 0.01952 | 1.8933 | 1.8784 | -45.2743 | -149.1917 | 150.0944 | -42.4268 | -149.2722 | 150.0473
Line_3 | 0.008031 | 0.002674 | 0.002674 | 0.013375 | 0.0026699 | 0.0026699 | 0.092734 | 0.030877 | 0.030877 | 0.15444 | 0.030829 | 0.030829 | -0.0012912 | 0.029269 | -0.029556 | 0.0023736 | 0.029057 | -0.029672 | -0.001288 | -0.050607 | -0.049852 | 0.0022742 | -0.050633 | -0.049651 | 91.0194 | -89.2646 | -89.2646 | -89.0498 | -89.0426 | -89.0426 |  | 0.019666 | 1.8933 | 1.8769 | 0.021285 | 1.8936 | 1.8762 | -44.0516 | -149.2215 | 150.073 | -45.2743 | -149.1917 | 150.0944

## LG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.019712 | 0.0098559 | 0.0098559 | 0.014788 | 0.01478 | 0.01478 | 0.22761 | 0.11381 | 0.11381 | 0.17076 | 0.17066 | 0.17066 | -0.00015829 | -0.097239 | 0.099873 | 0.00015093 | 0.14684 | -0.14875 | 0.00022358 | 0.17062 | 0.16915 | -4.7574e-05 | -0.25537 | -0.25388 | -89.5733 | 90.4266 | 90.4266 | 90.5646 | -89.7113 | -89.7113 |  | 0.0012036 | 1.7256 | 1.7261 | 0.00092673 | 1.7261 | 1.7242 | 35.7246 | -149.8941 | 149.868 | 73.0692 | -149.8126 | 149.9222
Line_1 | 0.0073995 | 0.012313 | 0.012313 | 0.012321 | 0.0073905 | 0.0073905 | 0.085442 | 0.14217 | 0.14217 | 0.14227 | 0.085338 | 0.085338 | 1.0569e-15 | 0.12301 | -0.12324 | -0.00012578 | -0.073483 | 0.074326 | -1.0574e-14 | -0.21246 | -0.21158 | 3.9551e-05 | 0.12766 | 0.12699 | 90.798 | -89.7965 | -89.7965 | -89.4751 | 90.2629 | 90.2629 |  | 0 | 1.7267 | 1.7222 | 0.00092673 | 1.7261 | 1.7242 | 0 | -149.7259 | 149.984 | 73.0692 | -149.8126 | 149.9222
Line_2 | 0.0024544 | 0.01231 | 0.01231 | 0.0024668 | 0.0073891 | 0.0073891 | 0.028341 | 0.14214 | 0.14214 | 0.028485 | 0.085322 | 0.085322 | 7.2932e-05 | 0.12303 | -0.12317 | -2.5149e-05 | -0.073354 | 0.074426 | 2.256e-05 | -0.21249 | -0.21138 | 8.0228e-06 | 0.12771 | 0.12689 | -90.4207 | -89.7423 | -89.7423 | -89.2374 | 90.3145 | 90.3145 |  | 0.0026937 | 1.7274 | 1.7211 | 0.00092673 | 1.7261 | 1.7242 | -73.2323 | -149.6719 | 150.0295 | 73.0692 | -149.8126 | 149.9222
Line_3 | 0.007394 | 0.002462 | 0.002462 | 0.012314 | 0.0024581 | 0.0024581 | 0.085379 | 0.028428 | 0.028428 | 0.14219 | 0.028383 | 0.028383 | 1.0995e-15 | 0.024734 | -0.024505 | 0.00036755 | 0.024429 | -0.024731 | -1.0561e-14 | -0.042401 | -0.042386 | 0.00010774 | -0.04251 | -0.042129 | 90.5629 | -89.9824 | -89.9824 | -89.5699 | -89.556 | -89.556 |  | 0 | 1.7267 | 1.7222 | 0.0026937 | 1.7274 | 1.7211 | 0 | -149.7259 | 149.984 | -73.2323 | -149.6719 | 150.0295

## LG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.019712 | 0.0098559 | 0.0098559 | 0.014788 | 0.01478 | 0.01478 | 0.22761 | 0.11381 | 0.11381 | 0.17076 | 0.17066 | 0.17066 | -0.00015829 | -0.097239 | 0.099873 | 0.00015093 | 0.14684 | -0.14875 | 0.00022358 | 0.17062 | 0.16915 | -4.7574e-05 | -0.25537 | -0.25388 | -89.5733 | 90.4266 | 90.4266 | 90.5646 | -89.7113 | -89.7113 |  | 0.0012036 | 1.7256 | 1.7261 | 0.00092673 | 1.7261 | 1.7242 | 35.7246 | -149.8941 | 149.868 | 73.0692 | -149.8126 | 149.9222
Line_1 | 0.0073995 | 0.012313 | 0.012313 | 0.012321 | 0.0073905 | 0.0073905 | 0.085442 | 0.14217 | 0.14217 | 0.14227 | 0.085338 | 0.085338 | 1.0569e-15 | 0.12301 | -0.12324 | -0.00012578 | -0.073483 | 0.074326 | -1.0574e-14 | -0.21246 | -0.21158 | 3.9551e-05 | 0.12766 | 0.12699 | 90.798 | -89.7965 | -89.7965 | -89.4751 | 90.2629 | 90.2629 |  | 0 | 1.7267 | 1.7222 | 0.00092673 | 1.7261 | 1.7242 | 0 | -149.7259 | 149.984 | 73.0692 | -149.8126 | 149.9222
Line_2 | 0.0024544 | 0.01231 | 0.01231 | 0.0024668 | 0.0073891 | 0.0073891 | 0.028341 | 0.14214 | 0.14214 | 0.028485 | 0.085322 | 0.085322 | 7.2932e-05 | 0.12303 | -0.12317 | -2.5149e-05 | -0.073354 | 0.074426 | 2.256e-05 | -0.21249 | -0.21138 | 8.0228e-06 | 0.12771 | 0.12689 | -90.4207 | -89.7423 | -89.7423 | -89.2374 | 90.3145 | 90.3145 |  | 0.0026937 | 1.7274 | 1.7211 | 0.00092673 | 1.7261 | 1.7242 | -73.2323 | -149.6719 | 150.0295 | 73.0692 | -149.8126 | 149.9222
Line_3 | 0.007394 | 0.002462 | 0.002462 | 0.012314 | 0.0024581 | 0.0024581 | 0.085379 | 0.028428 | 0.028428 | 0.14219 | 0.028383 | 0.028383 | 1.0995e-15 | 0.024734 | -0.024505 | 0.00036755 | 0.024429 | -0.024731 | -1.0561e-14 | -0.042401 | -0.042386 | 0.00010774 | -0.04251 | -0.042129 | 90.5629 | -89.9824 | -89.9824 | -89.5699 | -89.556 | -89.556 |  | 0 | 1.7267 | 1.7222 | 0.0026937 | 1.7274 | 1.7211 | 0 | -149.7259 | 149.984 | -73.2323 | -149.6719 | 150.0295

## LG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.019459 | 0.0097296 | 0.0097296 | 0.014599 | 0.01459 | 0.01459 | 0.2247 | 0.11235 | 0.11235 | 0.16857 | 0.16847 | 0.16847 | 0.0026857 | -0.095284 | 0.09927 | -0.0019886 | 0.14388 | -0.14788 | 0.0030579 | 0.16822 | 0.16433 | -0.0021718 | -0.25178 | -0.24664 | -88.8545 | 91.1454 | 91.1454 | 91.2833 | -88.9925 | -88.9925 |  | 0.018113 | 1.7208 | 1.7088 | 0.017469 | 1.7213 | 1.707 | -40.1473 | -149.3261 | 150.0094 | -41.1954 | -149.2454 | 150.0628
Line_1 | 0.0073047 | 0.012155 | 0.012155 | 0.012163 | 0.0072958 | 0.0072958 | 0.084347 | 0.14035 | 0.14035 | 0.14045 | 0.084245 | 0.084245 | -0.001073 | 0.12054 | -0.12253 | 0.0016557 | -0.072006 | 0.073889 | -0.0010591 | -0.20947 | -0.20555 | 0.0018107 | 0.12587 | 0.12337 | 91.5168 | -89.0777 | -89.0777 | -88.7563 | 90.9817 | 90.9817 |  | 0.017874 | 1.7219 | 1.705 | 0.017469 | 1.7213 | 1.707 | -43.8545 | -149.1596 | 150.1238 | -41.1954 | -149.2454 | 150.0628
Line_2 | 0.002423 | 0.012152 | 0.012152 | 0.0024352 | 0.0072944 | 0.0072944 | 0.027978 | 0.14032 | 0.14032 | 0.02812 | 0.084229 | 0.084229 | 0.00041942 | 0.12055 | -0.12246 | 0.00033298 | -0.071879 | 0.073986 | 0.00038079 | -0.2095 | -0.20536 | 0.00036114 | 0.12591 | 0.12328 | -89.7019 | -89.0235 | -89.0235 | -88.5186 | 91.0333 | 91.0333 |  | 0.020248 | 1.7225 | 1.7039 | 0.017469 | 1.7213 | 1.707 | -47.4657 | -149.106 | 150.1688 | -41.1954 | -149.2454 | 150.0628
Line_3 | 0.0072993 | 0.0024304 | 0.0024304 | 0.012156 | 0.0024266 | 0.0024266 | 0.084285 | 0.028064 | 0.028064 | 0.14037 | 0.02802 | 0.02802 | -0.0010678 | 0.024238 | -0.024366 | 0.0021324 | 0.023936 | -0.024585 | -0.0010628 | -0.041806 | -0.041181 | 0.001879 | -0.041911 | -0.040926 | 91.2817 | -89.2636 | -89.2636 | -88.8511 | -88.8373 | -88.8373 |  | 0.017874 | 1.7219 | 1.705 | 0.020248 | 1.7225 | 1.7039 | -43.8545 | -149.1596 | 150.1238 | -47.4657 | -149.106 | 150.1688

## LG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.019459 | 0.0097296 | 0.0097296 | 0.014599 | 0.01459 | 0.01459 | 0.2247 | 0.11235 | 0.11235 | 0.16857 | 0.16847 | 0.16847 | 0.0026857 | -0.095284 | 0.09927 | -0.0019886 | 0.14388 | -0.14788 | 0.0030579 | 0.16822 | 0.16433 | -0.0021718 | -0.25178 | -0.24664 | -88.8545 | 91.1454 | 91.1454 | 91.2833 | -88.9925 | -88.9925 |  | 0.018113 | 1.7208 | 1.7088 | 0.017469 | 1.7213 | 1.707 | -40.1473 | -149.3261 | 150.0094 | -41.1954 | -149.2454 | 150.0628
Line_1 | 0.0073047 | 0.012155 | 0.012155 | 0.012163 | 0.0072958 | 0.0072958 | 0.084347 | 0.14035 | 0.14035 | 0.14045 | 0.084245 | 0.084245 | -0.001073 | 0.12054 | -0.12253 | 0.0016557 | -0.072006 | 0.073889 | -0.0010591 | -0.20947 | -0.20555 | 0.0018107 | 0.12587 | 0.12337 | 91.5168 | -89.0777 | -89.0777 | -88.7563 | 90.9817 | 90.9817 |  | 0.017874 | 1.7219 | 1.705 | 0.017469 | 1.7213 | 1.707 | -43.8545 | -149.1596 | 150.1238 | -41.1954 | -149.2454 | 150.0628
Line_2 | 0.002423 | 0.012152 | 0.012152 | 0.0024352 | 0.0072944 | 0.0072944 | 0.027978 | 0.14032 | 0.14032 | 0.02812 | 0.084229 | 0.084229 | 0.00041942 | 0.12055 | -0.12246 | 0.00033298 | -0.071879 | 0.073986 | 0.00038079 | -0.2095 | -0.20536 | 0.00036114 | 0.12591 | 0.12328 | -89.7019 | -89.0235 | -89.0235 | -88.5186 | 91.0333 | 91.0333 |  | 0.020248 | 1.7225 | 1.7039 | 0.017469 | 1.7213 | 1.707 | -47.4657 | -149.106 | 150.1688 | -41.1954 | -149.2454 | 150.0628
Line_3 | 0.0072993 | 0.0024304 | 0.0024304 | 0.012156 | 0.0024266 | 0.0024266 | 0.084285 | 0.028064 | 0.028064 | 0.14037 | 0.02802 | 0.02802 | -0.0010678 | 0.024238 | -0.024366 | 0.0021324 | 0.023936 | -0.024585 | -0.0010628 | -0.041806 | -0.041181 | 0.001879 | -0.041911 | -0.040926 | 91.2817 | -89.2636 | -89.2636 | -88.8511 | -88.8373 | -88.8373 |  | 0.017874 | 1.7219 | 1.705 | 0.020248 | 1.7225 | 1.7039 | -43.8545 | -149.1596 | 150.1238 | -47.4657 | -149.106 | 150.1688

## LLG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.0054447 | 3.2035 | 3.205 | 0.0081649 | 3.2042 | 3.2042 | 0.06287 | 36.9905 | 37.0081 | 0.09428 | 36.9994 | 36.9992 | 0.00032892 | 8.8903 | 8.906 | -0.00023422 | -3.5597 | -3.5588 | 0.10364 | 10.1314 | 10.0605 | -0.15538 | -4.0576 | -4.0192 | -89.8439 | -163.5574 | 16.536 | 90.0842 | 16.4892 | -163.5106 |  | 1.6485 | 0.36439 | 0.36306 | 1.6481 | 0.14589 | 0.14509 | -0.025751 | -114.8243 | 65.0196 | -0.0021191 | -114.7712 | 64.966
Line_1 | 0.006802 | 2.1365 | 2.1358 | 0.0040828 | 2.1358 | 2.1365 | 0.078542 | 24.6708 | 24.6616 | 0.047144 | 24.6618 | 24.6705 | -3.6443e-05 | 4.2791e-11 | 4.0377e-11 | 9.8887e-05 | 2.371 | 2.3746 | -0.12941 | -2.692e-11 | 2.4435e-11 | 0.077698 | 2.706 | 2.6785 | 90.0399 | 16.5241 | -163.5455 | -89.9292 | -163.5458 | 16.5244 |  | 1.6477 | 0 | 0 | 1.6481 | 0.14589 | 0.14509 | 0.023745 | 0 | 0 | -0.0021191 | -114.7712 | 64.966
Line_2 | 0.0068006 | 1.0692 | 1.0669 | 0.004082 | 1.0685 | 1.0677 | 0.078527 | 12.3465 | 12.3198 | 0.047135 | 12.3376 | 12.3286 | -6.1049e-05 | -0.59742 | -0.58894 | 0.00013533 | 1.1886 | 1.1842 | -0.12938 | -0.66329 | -0.68281 | 0.077683 | 1.3516 | 1.3407 | 90.0681 | 16.6989 | -163.7207 | -89.9023 | -163.4408 | 16.4193 |  | 1.6475 | 0.072302 | 0.073192 | 1.6481 | 0.14589 | 0.14509 | 0.041071 | -115.3102 | 65.5008 | -0.0021191 | -114.7712 | 64.966
Line_3 | 0.0013601 | 1.0677 | 1.0685 | 0.0013579 | 1.0669 | 1.0692 | 0.015705 | 12.3287 | 12.3375 | 0.01568 | 12.3199 | 12.3464 | 3.644e-05 | 2.1409e-11 | 2.0222e-11 | -5.592e-05 | 0.59127 | 0.59521 | -0.025876 | -1.3413e-11 | 1.2187e-11 | -0.025834 | 0.66622 | 0.67994 | 89.9431 | 16.4191 | -163.4405 | 90.1651 | -163.721 | 16.6991 |  | 1.6477 | 0 | 0 | 1.6475 | 0.072302 | 0.073192 | 0.023745 | 0 | 0 | 0.041071 | -115.3102 | 65.5008

## LLG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.0054447 | 3.2035 | 3.205 | 0.0081649 | 3.2042 | 3.2042 | 0.06287 | 36.9905 | 37.0081 | 0.09428 | 36.9994 | 36.9992 | 0.00032892 | 8.8903 | 8.906 | -0.00023422 | -3.5597 | -3.5588 | 0.10364 | 10.1314 | 10.0605 | -0.15538 | -4.0576 | -4.0192 | -89.8439 | -163.5574 | 16.536 | 90.0842 | 16.4892 | -163.5106 |  | 1.6485 | 0.36439 | 0.36306 | 1.6481 | 0.14589 | 0.14509 | -0.025751 | -114.8243 | 65.0196 | -0.0021191 | -114.7712 | 64.966
Line_1 | 0.006802 | 2.1365 | 2.1358 | 0.0040828 | 2.1358 | 2.1365 | 0.078542 | 24.6708 | 24.6616 | 0.047144 | 24.6618 | 24.6705 | -3.6443e-05 | 4.2791e-11 | 4.0377e-11 | 9.8887e-05 | 2.371 | 2.3746 | -0.12941 | -2.692e-11 | 2.4435e-11 | 0.077698 | 2.706 | 2.6785 | 90.0399 | 16.5241 | -163.5455 | -89.9292 | -163.5458 | 16.5244 |  | 1.6477 | 0 | 0 | 1.6481 | 0.14589 | 0.14509 | 0.023745 | 0 | 0 | -0.0021191 | -114.7712 | 64.966
Line_2 | 0.0068006 | 1.0692 | 1.0669 | 0.004082 | 1.0685 | 1.0677 | 0.078527 | 12.3465 | 12.3198 | 0.047135 | 12.3376 | 12.3286 | -6.1049e-05 | -0.59742 | -0.58894 | 0.00013533 | 1.1886 | 1.1842 | -0.12938 | -0.66329 | -0.68281 | 0.077683 | 1.3516 | 1.3407 | 90.0681 | 16.6989 | -163.7207 | -89.9023 | -163.4408 | 16.4193 |  | 1.6475 | 0.072302 | 0.073192 | 1.6481 | 0.14589 | 0.14509 | 0.041071 | -115.3102 | 65.5008 | -0.0021191 | -114.7712 | 64.966
Line_3 | 0.0013601 | 1.0677 | 1.0685 | 0.0013579 | 1.0669 | 1.0692 | 0.015705 | 12.3287 | 12.3375 | 0.01568 | 12.3199 | 12.3464 | 3.644e-05 | 2.1409e-11 | 2.0222e-11 | -5.592e-05 | 0.59127 | 0.59521 | -0.025876 | -1.3413e-11 | 1.2187e-11 | -0.025834 | 0.66622 | 0.67994 | 89.9431 | 16.4191 | -163.4405 | 90.1651 | -163.721 | 16.6991 |  | 1.6477 | 0 | 0 | 1.6475 | 0.072302 | 0.073192 | 0.023745 | 0 | 0 | 0.041071 | -115.3102 | 65.5008

## LLG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.0054097 | 1.0748 | 1.0779 | 0.0081124 | 1.0763 | 1.0763 | 0.062466 | 12.4104 | 12.4464 | 0.093674 | 12.4285 | 12.4283 | 0.00076368 | 6.787 | 6.806 | -0.00088868 | -6.2067 | -6.1814 | 0.10275 | 6.8841 | 6.9793 | -0.15405 | -6.1933 | -6.3029 | -89.4789 | -144.3442 | 35.891 | 90.4493 | 35.7731 | -144.226 |  | 1.645 | 0.77896 | 0.78323 | 1.6446 | 0.70549 | 0.71032 | 0.095303 | -98.9372 | 81.611 | 0.11877 | -99.2887 | 81.3316
Line_1 | 0.0067582 | 0.71834 | 0.71676 | 0.0040566 | 0.71678 | 0.71833 | 0.078037 | 8.2947 | 8.2765 | 0.046841 | 8.2766 | 8.2946 | -0.00058327 | -3.8787 | -3.8445 | 0.00042631 | 4.1269 | 4.1319 | -0.1283 | -3.8193 | -3.9038 | 0.077032 | 4.1307 | 4.2001 | 90.4049 | 35.8608 | -144.3138 | -89.5642 | -144.3151 | 35.862 |  | 1.6441 | 0.65626 | 0.66199 | 1.6446 | 0.70549 | 0.71032 | 0.14446 | -99.5807 | 81.1248 | 0.11877 | -99.2887 | 81.3316
Line_2 | 0.0067569 | 0.36114 | 0.35644 | 0.0040558 | 0.35956 | 0.35799 | 0.078022 | 4.1701 | 4.1159 | 0.046833 | 4.1519 | 4.1338 | -0.00060772 | -2.032 | -1.9631 | 0.00046237 | 2.0797 | 2.0495 | -0.12827 | -1.9783 | -2.0349 | 0.077017 | 2.0626 | 2.1027 | 90.4332 | 36.2976 | -144.7574 | -89.5373 | -144.051 | 35.5974 |  | 1.644 | 0.68008 | 0.68696 | 1.6446 | 0.70549 | 0.71032 | 0.16169 | -99.4705 | 81.2717 | 0.11877 | -99.2887 | 81.3316
Line_3 | 0.0013513 | 0.358 | 0.35956 | 0.0013492 | 0.35645 | 0.36113 | 0.015604 | 4.1338 | 4.1518 | 0.015579 | 4.116 | 4.17 | -7.3273e-05 | -1.9242 | -1.9375 | -0.00016471 | 1.9693 | 2.0265 | -0.025655 | -1.9124 | -1.9494 | -0.025612 | 1.9892 | 2.0246 | 90.3081 | 35.5962 | -144.0498 | 90.5301 | -144.7586 | 36.2988 |  | 1.6441 | 0.65626 | 0.66199 | 1.644 | 0.68008 | 0.68696 | 0.14446 | -99.5807 | 81.1248 | 0.16169 | -99.4705 | 81.2717

## LLG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.0054097 | 1.0748 | 1.0779 | 0.0081124 | 1.0763 | 1.0763 | 0.062466 | 12.4104 | 12.4464 | 0.093674 | 12.4285 | 12.4283 | 0.00076368 | 6.787 | 6.806 | -0.00088868 | -6.2067 | -6.1814 | 0.10275 | 6.8841 | 6.9793 | -0.15405 | -6.1933 | -6.3029 | -89.4789 | -144.3442 | 35.891 | 90.4493 | 35.7731 | -144.226 |  | 1.645 | 0.77896 | 0.78323 | 1.6446 | 0.70549 | 0.71032 | 0.095303 | -98.9372 | 81.611 | 0.11877 | -99.2887 | 81.3316
Line_1 | 0.0067582 | 0.71834 | 0.71676 | 0.0040566 | 0.71678 | 0.71833 | 0.078037 | 8.2947 | 8.2765 | 0.046841 | 8.2766 | 8.2946 | -0.00058327 | -3.8787 | -3.8445 | 0.00042631 | 4.1269 | 4.1319 | -0.1283 | -3.8193 | -3.9038 | 0.077032 | 4.1307 | 4.2001 | 90.4049 | 35.8608 | -144.3138 | -89.5642 | -144.3151 | 35.862 |  | 1.6441 | 0.65626 | 0.66199 | 1.6446 | 0.70549 | 0.71032 | 0.14446 | -99.5807 | 81.1248 | 0.11877 | -99.2887 | 81.3316
Line_2 | 0.0067569 | 0.36114 | 0.35644 | 0.0040558 | 0.35956 | 0.35799 | 0.078022 | 4.1701 | 4.1159 | 0.046833 | 4.1519 | 4.1338 | -0.00060772 | -2.032 | -1.9631 | 0.00046237 | 2.0797 | 2.0495 | -0.12827 | -1.9783 | -2.0349 | 0.077017 | 2.0626 | 2.1027 | 90.4332 | 36.2976 | -144.7574 | -89.5373 | -144.051 | 35.5974 |  | 1.644 | 0.68008 | 0.68696 | 1.6446 | 0.70549 | 0.71032 | 0.16169 | -99.4705 | 81.2717 | 0.11877 | -99.2887 | 81.3316
Line_3 | 0.0013513 | 0.358 | 0.35956 | 0.0013492 | 0.35645 | 0.36113 | 0.015604 | 4.1338 | 4.1518 | 0.015579 | 4.116 | 4.17 | -7.3273e-05 | -1.9242 | -1.9375 | -0.00016471 | 1.9693 | 2.0265 | -0.025655 | -1.9124 | -1.9494 | -0.025612 | 1.9892 | 2.0246 | 90.3081 | 35.5962 | -144.0498 | 90.5301 | -144.7586 | 36.2988 |  | 1.6441 | 0.65626 | 0.66199 | 1.644 | 0.68008 | 0.68696 | 0.14446 | -99.5807 | 81.1248 | 0.16169 | -99.4705 | 81.2717

## LLG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.0049496 | 2.6049 | 2.6072 | 0.0074222 | 2.6061 | 2.606 | 0.057153 | 30.079 | 30.1052 | 0.085704 | 30.0923 | 30.0919 | 0.00052186 | 11.3064 | 11.2957 | -0.00037161 | -4.5294 | -4.5114 | 0.085647 | 6.7248 | 6.6318 | -0.1284 | -2.6963 | -2.6464 | -89.7026 | -152.4217 | 27.675 | 90.1595 | 27.6264 | -152.3731 |  | 1.4986 | 0.43735 | 0.43509 | 1.4982 | 0.17517 | 0.17381 | -0.051703 | -121.6784 | 58.0927 | -0.0063292 | -121.6094 | 58.0229
Line_1 | 0.0061833 | 1.738 | 1.7368 | 0.0037115 | 1.7368 | 1.7379 | 0.071398 | 20.0682 | 20.0546 | 0.042856 | 20.055 | 20.0679 | -5.7818e-05 | -9.3362e-11 | 1.2723e-11 | 0.00015689 | 3.0175 | 3.0097 | -0.10694 | -7.1801e-11 | -1.1579e-10 | 0.064206 | 1.7988 | 1.7629 | 90.0743 | 27.6624 | -152.4091 | -89.8663 | -152.4098 | 27.6631 |  | 1.4978 | 0 | 0 | 1.4982 | 0.17517 | 0.17381 | 0.043329 | 0 | 0 | -0.0063292 | -121.6094 | 58.0229
Line_2 | 0.006182 | 0.87041 | 0.86697 | 0.0037108 | 0.86926 | 0.86811 | 0.071384 | 10.0506 | 10.0109 | 0.042848 | 10.0373 | 10.0241 | -9.6858e-05 | -0.7538 | -0.75291 | 0.00021471 | 1.5119 | 1.5017 | -0.10691 | -0.43241 | -0.45801 | 0.064194 | 0.89743 | 0.88346 | 90.1285 | 27.8429 | -152.5904 | -89.8147 | -152.3012 | 27.5544 |  | 1.4977 | 0.086465 | 0.088032 | 1.4982 | 0.17517 | 0.17381 | 0.076596 | -122.3169 | 58.7225 | -0.0063292 | -121.6094 | 58.0229
Line_3 | 0.0012364 | 0.86812 | 0.86925 | 0.0012344 | 0.86699 | 0.87039 | 0.014276 | 10.0242 | 10.0372 | 0.014254 | 10.0111 | 10.0504 | 5.7816e-05 | -4.6567e-11 | 6.2582e-12 | -8.8724e-05 | 0.74756 | 0.75934 | -0.021383 | -3.5953e-11 | -5.7966e-11 | -0.021347 | 0.43639 | 0.45408 | 89.8884 | 27.5538 | -152.3005 | 90.3147 | -152.5911 | 27.8436 |  | 1.4978 | 0 | 0 | 1.4977 | 0.086465 | 0.088032 | 0.043329 | 0 | 0 | 0.076596 | -122.3169 | 58.7225

## LLG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.0049496 | 2.6049 | 2.6072 | 0.0074222 | 2.6061 | 2.606 | 0.057153 | 30.079 | 30.1052 | 0.085704 | 30.0923 | 30.0919 | 0.00052186 | 11.3064 | 11.2957 | -0.00037161 | -4.5294 | -4.5114 | 0.085647 | 6.7248 | 6.6318 | -0.1284 | -2.6963 | -2.6464 | -89.7026 | -152.4217 | 27.675 | 90.1595 | 27.6264 | -152.3731 |  | 1.4986 | 0.43735 | 0.43509 | 1.4982 | 0.17517 | 0.17381 | -0.051703 | -121.6784 | 58.0927 | -0.0063292 | -121.6094 | 58.0229
Line_1 | 0.0061833 | 1.738 | 1.7368 | 0.0037115 | 1.7368 | 1.7379 | 0.071398 | 20.0682 | 20.0546 | 0.042856 | 20.055 | 20.0679 | -5.7818e-05 | -9.3362e-11 | 1.2723e-11 | 0.00015689 | 3.0175 | 3.0097 | -0.10694 | -7.1801e-11 | -1.1579e-10 | 0.064206 | 1.7988 | 1.7629 | 90.0743 | 27.6624 | -152.4091 | -89.8663 | -152.4098 | 27.6631 |  | 1.4978 | 0 | 0 | 1.4982 | 0.17517 | 0.17381 | 0.043329 | 0 | 0 | -0.0063292 | -121.6094 | 58.0229
Line_2 | 0.006182 | 0.87041 | 0.86697 | 0.0037108 | 0.86926 | 0.86811 | 0.071384 | 10.0506 | 10.0109 | 0.042848 | 10.0373 | 10.0241 | -9.6858e-05 | -0.7538 | -0.75291 | 0.00021471 | 1.5119 | 1.5017 | -0.10691 | -0.43241 | -0.45801 | 0.064194 | 0.89743 | 0.88346 | 90.1285 | 27.8429 | -152.5904 | -89.8147 | -152.3012 | 27.5544 |  | 1.4977 | 0.086465 | 0.088032 | 1.4982 | 0.17517 | 0.17381 | 0.076596 | -122.3169 | 58.7225 | -0.0063292 | -121.6094 | 58.0229
Line_3 | 0.0012364 | 0.86812 | 0.86925 | 0.0012344 | 0.86699 | 0.87039 | 0.014276 | 10.0242 | 10.0372 | 0.014254 | 10.0111 | 10.0504 | 5.7816e-05 | -4.6567e-11 | 6.2582e-12 | -8.8724e-05 | 0.74756 | 0.75934 | -0.021383 | -3.5953e-11 | -5.7966e-11 | -0.021347 | 0.43639 | 0.45408 | 89.8884 | 27.5538 | -152.3005 | 90.3147 | -152.5911 | 27.8436 |  | 1.4978 | 0 | 0 | 1.4977 | 0.086465 | 0.088032 | 0.043329 | 0 | 0 | 0.076596 | -122.3169 | 58.7225

## LLG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.0049177 | 0.9249 | 0.92795 | 0.0073744 | 0.92643 | 0.92641 | 0.056784 | 10.6798 | 10.715 | 0.085152 | 10.6975 | 10.6973 | 0.00087791 | 5.7132 | 5.7257 | -0.0009095 | -4.873 | -4.8521 | 0.08491 | 5.1036 | 5.1671 | -0.1273 | -4.589 | -4.6687 | -89.3385 | -141.2129 | 39.0259 | 90.5236 | 38.9059 | -141.0925 |  | 1.4954 | 0.71731 | 0.71978 | 1.495 | 0.62572 | 0.62946 | 0.069143 | -99.4388 | 81.09 | 0.11425 | -97.8131 | 82.8041
Line_1 | 0.0061434 | 0.61839 | 0.61684 | 0.0036876 | 0.61686 | 0.61837 | 0.070938 | 7.1406 | 7.1226 | 0.04258 | 7.1229 | 7.1403 | -0.00050848 | -2.8726 | -2.849 | 0.00042611 | 3.2399 | 3.2436 | -0.10602 | -2.828 | -2.8936 | 0.063655 | 3.0607 | 3.1113 | 90.4384 | 38.9945 | -141.1813 | -89.5022 | -141.1836 | 38.9968 |  | 1.4946 | 0.56453 | 0.57012 | 1.495 | 0.62572 | 0.62946 | 0.16364 | -96.4534 | 84.2632 | 0.11425 | -97.8131 | 82.8041
Line_2 | 0.0061422 | 0.31112 | 0.30653 | 0.0036869 | 0.30957 | 0.30804 | 0.070924 | 3.5924 | 3.5395 | 0.042572 | 3.5747 | 3.557 | -0.00054736 | -1.5509 | -1.5 | 0.00048338 | 1.6331 | 1.6085 | -0.10599 | -1.4638 | -1.5093 | 0.063642 | 1.5284 | 1.5574 | 90.4926 | 39.4374 | -141.6319 | -89.4506 | -140.9156 | 38.7282 |  | 1.4945 | 0.59363 | 0.6012 | 1.495 | 0.62572 | 0.62946 | 0.19674 | -97.2176 | 83.5448 | 0.11425 | -97.8131 | 82.8041
Line_3 | 0.0012284 | 0.30805 | 0.30956 | 0.0012265 | 0.30654 | 0.3111 | 0.014184 | 3.5571 | 3.5745 | 0.014162 | 3.5396 | 3.5923 | -3.2892e-05 | -1.4244 | -1.4366 | -0.00017808 | 1.5008 | 1.5508 | -0.0212 | -1.4155 | -1.4455 | -0.021164 | 1.4706 | 1.5031 | 90.2525 | 38.726 | -140.9134 | 90.6788 | -141.6343 | 39.4398 |  | 1.4946 | 0.56453 | 0.57012 | 1.4945 | 0.59363 | 0.6012 | 0.16364 | -96.4534 | 84.2632 | 0.19674 | -97.2176 | 83.5448

## LLG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.0049177 | 0.9249 | 0.92795 | 0.0073744 | 0.92643 | 0.92641 | 0.056784 | 10.6798 | 10.715 | 0.085152 | 10.6975 | 10.6973 | 0.00087791 | 5.7132 | 5.7257 | -0.0009095 | -4.873 | -4.8521 | 0.08491 | 5.1036 | 5.1671 | -0.1273 | -4.589 | -4.6687 | -89.3385 | -141.2129 | 39.0259 | 90.5236 | 38.9059 | -141.0925 |  | 1.4954 | 0.71731 | 0.71978 | 1.495 | 0.62572 | 0.62946 | 0.069143 | -99.4388 | 81.09 | 0.11425 | -97.8131 | 82.8041
Line_1 | 0.0061434 | 0.61839 | 0.61684 | 0.0036876 | 0.61686 | 0.61837 | 0.070938 | 7.1406 | 7.1226 | 0.04258 | 7.1229 | 7.1403 | -0.00050848 | -2.8726 | -2.849 | 0.00042611 | 3.2399 | 3.2436 | -0.10602 | -2.828 | -2.8936 | 0.063655 | 3.0607 | 3.1113 | 90.4384 | 38.9945 | -141.1813 | -89.5022 | -141.1836 | 38.9968 |  | 1.4946 | 0.56453 | 0.57012 | 1.495 | 0.62572 | 0.62946 | 0.16364 | -96.4534 | 84.2632 | 0.11425 | -97.8131 | 82.8041
Line_2 | 0.0061422 | 0.31112 | 0.30653 | 0.0036869 | 0.30957 | 0.30804 | 0.070924 | 3.5924 | 3.5395 | 0.042572 | 3.5747 | 3.557 | -0.00054736 | -1.5509 | -1.5 | 0.00048338 | 1.6331 | 1.6085 | -0.10599 | -1.4638 | -1.5093 | 0.063642 | 1.5284 | 1.5574 | 90.4926 | 39.4374 | -141.6319 | -89.4506 | -140.9156 | 38.7282 |  | 1.4945 | 0.59363 | 0.6012 | 1.495 | 0.62572 | 0.62946 | 0.19674 | -97.2176 | 83.5448 | 0.11425 | -97.8131 | 82.8041
Line_3 | 0.0012284 | 0.30805 | 0.30956 | 0.0012265 | 0.30654 | 0.3111 | 0.014184 | 3.5571 | 3.5745 | 0.014162 | 3.5396 | 3.5923 | -3.2892e-05 | -1.4244 | -1.4366 | -0.00017808 | 1.5008 | 1.5508 | -0.0212 | -1.4155 | -1.4455 | -0.021164 | 1.4706 | 1.5031 | 90.2525 | 38.726 | -140.9134 | 90.6788 | -141.6343 | 39.4398 |  | 1.4946 | 0.56453 | 0.57012 | 1.4945 | 0.59363 | 0.6012 | 0.16364 | -96.4534 | 84.2632 | 0.19674 | -97.2176 | 83.5448