## LLL_max_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 3.6358 | 3.6358 | 0 | 0 | 125.9486 | 125.9486 | 36.0342 | -15.4122 | 41.0034 | -17.6054 | -73.0863 | 106.9137 | 0.43341 | 0.18578 | -24.3956 | -24.2861
Line_1 | 2.7277 | 2.7277 | 5.405 | 0 | 94.4895 | 94.4895 | -1e-07 | 11.6068 | -1e-07 | 13.1692 | 107.1055 | -72.8945 | 0 | 0.18578 | 0 | -24.2861
Line_2 | 0.90821 | 0.90821 | 0 | 0 | 31.4612 | 31.4612 | -2.5187 | 3.8055 | -2.9762 | 4.4362 | 106.3378 | -73.6622 | 0.12393 | 0.18578 | -23.9029 | -24.2861
Line_3 | 1.8196 | 1.8196 | 3.5617 | 0 | 63.0325 | 63.0325 | -1e-07 | 5.165 | -1e-07 | 5.8603 | 107.4886 | -72.5114 | 0 | 0.12393 | 0 | -23.9029

## LLL_max_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 3.6358 | 3.6358 | 0 | 0 | 125.9486 | 125.9486 | 36.0342 | -15.4122 | 41.0034 | -17.6054 | -73.0863 | 106.9137 | 0.43341 | 0.18578 | -24.3956 | -24.2861
Line_1 | 2.7277 | 2.7277 | 5.405 | 0 | 94.4895 | 94.4895 | -1e-07 | 11.6068 | -1e-07 | 13.1692 | 107.1055 | -72.8945 | 0 | 0.18578 | 0 | -24.2861
Line_2 | 0.90821 | 0.90821 | 0 | 0 | 31.4612 | 31.4612 | -2.5187 | 3.8055 | -2.9762 | 4.4362 | 106.3378 | -73.6622 | 0.12393 | 0.18578 | -23.9029 | -24.2861
Line_3 | 1.8196 | 1.8196 | 3.5617 | 0 | 63.0325 | 63.0325 | -1e-07 | 5.165 | -1e-07 | 5.8603 | 107.4886 | -72.5114 | 0 | 0.12393 | 0 | -23.9029

## LLL_max_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.79728 | 0.79728 | 0 | 0 | 27.6185 | 27.6185 | 20.9759 | -19.9843 | 17.3767 | -16.2516 | -45.7967 | 134.2033 | 0.98624 | 0.93264 | -6.158 | -6.6781
Line_1 | 0.63574 | 0.63574 | 1.3036 | 0 | 22.0228 | 22.0228 | -14.7741 | 15.4046 | -12.8701 | 13.5855 | 131.9124 | -48.0876 | 0.8897 | 0.93264 | -7.0275 | -6.6781
Line_2 | 0.16402 | 0.16402 | 0 | 0 | 5.6819 | 5.6819 | -4.5378 | 4.5797 | -2.6184 | 2.6661 | 143.1163 | -36.8837 | 0.92205 | 0.93264 | -6.8973 | -6.6781
Line_3 | 0.47591 | 0.47591 | 0.9321 | 0 | 16.4861 | 16.4861 | -10.3898 | 10.7431 | -10.3535 | 10.7544 | 128.0726 | -51.9274 | 0.8897 | 0.92205 | -7.0275 | -6.8973

## LLL_max_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.79728 | 0.79728 | 0 | 0 | 27.6185 | 27.6185 | 20.9759 | -19.9843 | 17.3767 | -16.2516 | -45.7967 | 134.2033 | 0.98624 | 0.93264 | -6.158 | -6.6781
Line_1 | 0.63574 | 0.63574 | 1.3036 | 0 | 22.0228 | 22.0228 | -14.7741 | 15.4046 | -12.8701 | 13.5855 | 131.9124 | -48.0876 | 0.8897 | 0.93264 | -7.0275 | -6.6781
Line_2 | 0.16402 | 0.16402 | 0 | 0 | 5.6819 | 5.6819 | -4.5378 | 4.5797 | -2.6184 | 2.6661 | 143.1163 | -36.8837 | 0.92205 | 0.93264 | -6.8973 | -6.6781
Line_3 | 0.47591 | 0.47591 | 0.9321 | 0 | 16.4861 | 16.4861 | -10.3898 | 10.7431 | -10.3535 | 10.7544 | 128.0726 | -51.9274 | 0.8897 | 0.92205 | -7.0275 | -6.8973

## LLL_min_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 2.9516 | 2.9516 | 0 | 0 | 102.2474 | 102.2474 | 45.756 | -19.6615 | 26.7104 | -11.29 | -61.5111 | 118.4889 | 0.51817 | 0.22174 | -31.2365 | -31.6459
Line_1 | 2.2078 | 2.2078 | 3.9682 | 0 | 76.4821 | 76.4821 | -1e-07 | 14.6004 | -1e-07 | 8.628 | 117.7734 | -62.2266 | 0 | 0.22174 | 0 | -31.6459
Line_2 | 0.74446 | 0.74446 | 0 | 0 | 25.7889 | 25.7889 | -3.4011 | 5.0611 | -1.681 | 2.6619 | 120.6115 | -59.3885 | 0.14711 | 0.22174 | -33.0879 | -31.6459
Line_3 | 1.4648 | 1.4648 | 2.6326 | 0 | 50.7409 | 50.7409 | -1e-07 | 6.4263 | -1e-07 | 3.7976 | 116.3313 | -63.6687 | 0 | 0.14711 | 0 | -33.0879

## LLL_min_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 2.9516 | 2.9516 | 0 | 0 | 102.2474 | 102.2474 | 45.756 | -19.6615 | 26.7104 | -11.29 | -61.5111 | 118.4889 | 0.51817 | 0.22174 | -31.2365 | -31.6459
Line_1 | 2.2078 | 2.2078 | 3.9682 | 0 | 76.4821 | 76.4821 | -1e-07 | 14.6004 | -1e-07 | 8.628 | 117.7734 | -62.2266 | 0 | 0.22174 | 0 | -31.6459
Line_2 | 0.74446 | 0.74446 | 0 | 0 | 25.7889 | 25.7889 | -3.4011 | 5.0611 | -1.681 | 2.6619 | 120.6115 | -59.3885 | 0.14711 | 0.22174 | -33.0879 | -31.6459
Line_3 | 1.4648 | 1.4648 | 2.6326 | 0 | 50.7409 | 50.7409 | -1e-07 | 6.4263 | -1e-07 | 3.7976 | 116.3313 | -63.6687 | 0 | 0.14711 | 0 | -33.0879

## LLL_min_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.79717 | 0.79717 | 0 | 0 | 27.6148 | 27.6148 | 18.6059 | -16.7025 | 15.5964 | -14.4716 | -47.0211 | 132.9789 | 0.87917 | 0.80029 | -7.0497 | -6.1144
Line_1 | 0.59629 | 0.59629 | 1.0717 | 0 | 20.6561 | 20.6561 | -11.2925 | 12.3575 | -10.3507 | 10.9801 | 132.2633 | -47.7367 | 0.7416 | 0.80029 | -5.2282 | -6.1144
Line_2 | 0.20106 | 0.20106 | 0 | 0 | 6.965 | 6.965 | -4.2239 | 4.345 | -3.4199 | 3.4915 | 135.1015 | -44.8985 | 0.78031 | 0.80029 | -5.9028 | -6.1144
Line_3 | 0.3956 | 0.3956 | 0.71101 | 0 | 13.704 | 13.704 | -7.3166 | 7.7854 | -7.0534 | 7.3304 | 130.8213 | -49.1787 | 0.7416 | 0.78031 | -5.2282 | -5.9028

## LLL_min_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.79717 | 0.79717 | 0 | 0 | 27.6148 | 27.6148 | 18.6059 | -16.7025 | 15.5964 | -14.4716 | -47.0211 | 132.9789 | 0.87917 | 0.80029 | -7.0497 | -6.1144
Line_1 | 0.59629 | 0.59629 | 1.0717 | 0 | 20.6561 | 20.6561 | -11.2925 | 12.3575 | -10.3507 | 10.9801 | 132.2633 | -47.7367 | 0.7416 | 0.80029 | -5.2282 | -6.1144
Line_2 | 0.20106 | 0.20106 | 0 | 0 | 6.965 | 6.965 | -4.2239 | 4.345 | -3.4199 | 3.4915 | 135.1015 | -44.8985 | 0.78031 | 0.80029 | -5.9028 | -6.1144
Line_3 | 0.3956 | 0.3956 | 0.71101 | 0 | 13.704 | 13.704 | -7.3166 | 7.7854 | -7.0534 | 7.3304 | 130.8213 | -49.1787 | 0.7416 | 0.78031 | -5.2282 | -5.9028

## LL_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.36184 | 3.0849 | 3.2334 | 0.36184 | 3.0849 | 3.2334 | 4.1781 | 35.621 | 37.3363 | 4.1781 | 35.621 | 37.3363 | -3.0459 | 29.02 | -12.393 | 3.114 | -24.0714 | 17.8296 | -3.7564 | 3.1835 | 15.3596 | 3.8336 | 2.4312 | -9.1912 | 131.2748 | -159.9336 | 14.078 | -48.7252 | 20.0664 | -165.922 | 1.1575 | 0.81957 | 0.5286 | 1.1821 | 0.6792 | 0.53726 | 2.2371 | -153.6732 | 142.9765 | 2.188 | -165.7008 | 166.8068
Line_1 | 0.18371 | 2.3133 | 2.3918 | 0.18371 | 2.3133 | 2.3918 | 2.1213 | 26.7118 | 27.6179 | 2.1213 | 26.7118 | 27.6179 | 1.6145 | -15.3112 | 16.1185 | -1.597 | 18.0939 | -13.1438 | 1.9532 | 4.4866 | -3.51 | -1.9333 | -1.3293 | 6.8851 | -48.254 | 18.5008 | -165.5462 | 131.746 | -161.4992 | 14.4538 | 1.1946 | 0.5973 | 0.5973 | 1.1821 | 0.6792 | 0.53726 | 2.1688 | -177.8312 | -177.8312 | 2.188 | -165.7008 | 166.8068
Line_2 | 0.17814 | 0.77501 | 0.84184 | 0.17814 | 0.77501 | 0.84184 | 2.057 | 8.949 | 9.7207 | 2.057 | 8.949 | 9.7207 | 1.5335 | -5.6651 | 5.0543 | -1.517 | 5.9775 | -4.6858 | 1.919 | 1.4563 | -1.8879 | -1.9003 | -1.1019 | 2.306 | -49.2111 | 24.7439 | -166.9899 | 130.7889 | -155.2561 | 13.0101 | 1.1942 | 0.65363 | 0.55504 | 1.1821 | 0.6792 | 0.53726 | 2.1597 | -169.6723 | 172.5282 | 2.188 | -165.7008 | 166.8068
Line_3 | 0.006339 | 1.5452 | 1.5504 | 0.006339 | 1.5452 | 1.5504 | 0.073197 | 17.8424 | 17.902 | 0.073197 | 17.8424 | 17.902 | 0.080827 | -10.3755 | 10.4159 | -0.080806 | 11.6171 | -9.166 | 0.03336 | 2.4346 | -2.4179 | -0.033337 | -1.0259 | 3.836 | -20.2589 | 15.3742 | -164.7623 | 159.7411 | -164.6258 | 15.2377 | 1.1946 | 0.5973 | 0.5973 | 1.1942 | 0.65363 | 0.55504 | 2.1688 | -177.8312 | -177.8312 | 2.1597 | -169.6723 | 172.5282

## LL_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.36184 | 3.0849 | 3.2334 | 0.36184 | 3.0849 | 3.2334 | 4.1781 | 35.621 | 37.3363 | 4.1781 | 35.621 | 37.3363 | -3.0459 | 29.02 | -12.393 | 3.114 | -24.0714 | 17.8296 | -3.7564 | 3.1835 | 15.3596 | 3.8336 | 2.4312 | -9.1912 | 131.2748 | -159.9336 | 14.078 | -48.7252 | 20.0664 | -165.922 | 1.1575 | 0.81957 | 0.5286 | 1.1821 | 0.6792 | 0.53726 | 2.2371 | -153.6732 | 142.9765 | 2.188 | -165.7008 | 166.8068
Line_1 | 0.18371 | 2.3133 | 2.3918 | 0.18371 | 2.3133 | 2.3918 | 2.1213 | 26.7118 | 27.6179 | 2.1213 | 26.7118 | 27.6179 | 1.6145 | -15.3112 | 16.1185 | -1.597 | 18.0939 | -13.1438 | 1.9532 | 4.4866 | -3.51 | -1.9333 | -1.3293 | 6.8851 | -48.254 | 18.5008 | -165.5462 | 131.746 | -161.4992 | 14.4538 | 1.1946 | 0.5973 | 0.5973 | 1.1821 | 0.6792 | 0.53726 | 2.1688 | -177.8312 | -177.8312 | 2.188 | -165.7008 | 166.8068
Line_2 | 0.17814 | 0.77501 | 0.84184 | 0.17814 | 0.77501 | 0.84184 | 2.057 | 8.949 | 9.7207 | 2.057 | 8.949 | 9.7207 | 1.5335 | -5.6651 | 5.0543 | -1.517 | 5.9775 | -4.6858 | 1.919 | 1.4563 | -1.8879 | -1.9003 | -1.1019 | 2.306 | -49.2111 | 24.7439 | -166.9899 | 130.7889 | -155.2561 | 13.0101 | 1.1942 | 0.65363 | 0.55504 | 1.1821 | 0.6792 | 0.53726 | 2.1597 | -169.6723 | 172.5282 | 2.188 | -165.7008 | 166.8068
Line_3 | 0.006339 | 1.5452 | 1.5504 | 0.006339 | 1.5452 | 1.5504 | 0.073197 | 17.8424 | 17.902 | 0.073197 | 17.8424 | 17.902 | 0.080827 | -10.3755 | 10.4159 | -0.080806 | 11.6171 | -9.166 | 0.03336 | 2.4346 | -2.4179 | -0.033337 | -1.0259 | 3.836 | -20.2589 | 15.3742 | -164.7623 | 159.7411 | -164.6258 | 15.2377 | 1.1946 | 0.5973 | 0.5973 | 1.1942 | 0.65363 | 0.55504 | 2.1688 | -177.8312 | -177.8312 | 2.1597 | -169.6723 | 172.5282

## LL_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.26649 | 1.2614 | 1.2336 | 0.26649 | 1.2614 | 1.2336 | 3.0772 | 14.5653 | 14.2444 | 3.0772 | 14.5653 | 14.2444 | -1.7911 | 15.2178 | 0.28699 | 1.8281 | -14.3904 | 0.50433 | -3.0409 | 0.78464 | 12.1494 | 3.0828 | 0.15412 | -11.2516 | 121.7957 | -136.1541 | 31.6491 | -58.2043 | 43.8459 | -148.3509 | 1.1469 | 1.0462 | 0.85317 | 1.1647 | 0.98805 | 0.79069 | 1.2969 | -133.2025 | 120.296 | 1.1282 | -136.7676 | 124.2156
Line_1 | 0.13441 | 0.95605 | 0.94778 | 0.13441 | 0.95605 | 0.94778 | 1.552 | 11.0395 | 10.944 | 1.552 | 11.0395 | 10.944 | 0.95258 | -10.4164 | 0.79274 | -0.94319 | 10.8917 | -0.32563 | 1.5527 | -0.049073 | -8.1172 | -1.542 | 0.58835 | 8.6472 | -57.42 | 40.1404 | -147.941 | 122.58 | -139.8596 | 32.059 | 1.1737 | 0.94357 | 0.74523 | 1.1647 | 0.98805 | 0.79069 | 1.051 | -139.5897 | 127.6369 | 1.1282 | -136.7676 | 124.2156
Line_2 | 0.13211 | 0.31349 | 0.28593 | 0.13211 | 0.31349 | 0.28593 | 1.5255 | 3.6199 | 3.3016 | 1.5255 | 3.6199 | 3.3016 | 0.89397 | -3.4476 | 0.22121 | -0.88489 | 3.4987 | -0.1787 | 1.5511 | 0.80045 | -2.5562 | -1.5408 | -0.74246 | 2.6044 | -59.0022 | 55.2134 | -149.7095 | 120.9978 | -124.7866 | 30.2905 | 1.1735 | 0.97774 | 0.77712 | 1.1647 | 0.98805 | 0.79069 | 1.0404 | -137.8576 | 125.2365 | 1.1282 | -136.7676 | 124.2156
Line_3 | 0.0043354 | 0.65841 | 0.66204 | 0.0043354 | 0.65841 | 0.66204 | 0.050061 | 7.6027 | 7.6446 | 0.050061 | 7.6027 | 7.6446 | 0.058746 | -7.1142 | 0.47813 | -0.058736 | 7.3396 | -0.25021 | 0.0012086 | -0.92175 | -5.6769 | -0.0011976 | 1.1775 | 5.9355 | -0.1276 | 33.0278 | -147.1774 | 179.8724 | -146.9722 | 32.8226 | 1.1737 | 0.94357 | 0.74523 | 1.1735 | 0.97774 | 0.77712 | 1.051 | -139.5897 | 127.6369 | 1.0404 | -137.8576 | 125.2365

## LL_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.26649 | 1.2614 | 1.2336 | 0.26649 | 1.2614 | 1.2336 | 3.0772 | 14.5653 | 14.2444 | 3.0772 | 14.5653 | 14.2444 | -1.7911 | 15.2178 | 0.28699 | 1.8281 | -14.3904 | 0.50433 | -3.0409 | 0.78464 | 12.1494 | 3.0828 | 0.15412 | -11.2516 | 121.7957 | -136.1541 | 31.6491 | -58.2043 | 43.8459 | -148.3509 | 1.1469 | 1.0462 | 0.85317 | 1.1647 | 0.98805 | 0.79069 | 1.2969 | -133.2025 | 120.296 | 1.1282 | -136.7676 | 124.2156
Line_1 | 0.13441 | 0.95605 | 0.94778 | 0.13441 | 0.95605 | 0.94778 | 1.552 | 11.0395 | 10.944 | 1.552 | 11.0395 | 10.944 | 0.95258 | -10.4164 | 0.79274 | -0.94319 | 10.8917 | -0.32563 | 1.5527 | -0.049073 | -8.1172 | -1.542 | 0.58835 | 8.6472 | -57.42 | 40.1404 | -147.941 | 122.58 | -139.8596 | 32.059 | 1.1737 | 0.94357 | 0.74523 | 1.1647 | 0.98805 | 0.79069 | 1.051 | -139.5897 | 127.6369 | 1.1282 | -136.7676 | 124.2156
Line_2 | 0.13211 | 0.31349 | 0.28593 | 0.13211 | 0.31349 | 0.28593 | 1.5255 | 3.6199 | 3.3016 | 1.5255 | 3.6199 | 3.3016 | 0.89397 | -3.4476 | 0.22121 | -0.88489 | 3.4987 | -0.1787 | 1.5511 | 0.80045 | -2.5562 | -1.5408 | -0.74246 | 2.6044 | -59.0022 | 55.2134 | -149.7095 | 120.9978 | -124.7866 | 30.2905 | 1.1735 | 0.97774 | 0.77712 | 1.1647 | 0.98805 | 0.79069 | 1.0404 | -137.8576 | 125.2365 | 1.1282 | -136.7676 | 124.2156
Line_3 | 0.0043354 | 0.65841 | 0.66204 | 0.0043354 | 0.65841 | 0.66204 | 0.050061 | 7.6027 | 7.6446 | 0.050061 | 7.6027 | 7.6446 | 0.058746 | -7.1142 | 0.47813 | -0.058736 | 7.3396 | -0.25021 | 0.0012086 | -0.92175 | -5.6769 | -0.0011976 | 1.1775 | 5.9355 | -0.1276 | 33.0278 | -147.1774 | 179.8724 | -146.9722 | 32.8226 | 1.1737 | 0.94357 | 0.74523 | 1.1735 | 0.97774 | 0.77712 | 1.051 | -139.5897 | 127.6369 | 1.0404 | -137.8576 | 125.2365

## LL_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.1573 | 2.5018 | 2.6288 | 0.1573 | 2.5018 | 2.6288 | 1.8163 | 28.8882 | 30.3543 | 1.8163 | 28.8882 | 30.3543 | -1.8033 | 24.2039 | -2.0881 | 1.828 | -17.955 | 8.9874 | -0.29968 | -0.52181 | 13.6286 | 0.31428 | 4.2146 | -9.5515 | 172.4103 | -150.363 | 27.5625 | -7.5897 | 29.637 | -152.4375 | 1.0064 | 0.83804 | 0.45422 | 1.0212 | 0.63843 | 0.43207 | 1.8461 | -151.598 | 126.2732 | 2.1658 | -163.5729 | 160.8196
Line_1 | 0.080807 | 1.868 | 1.9334 | 0.080807 | 1.868 | 1.9334 | 0.93307 | 21.5701 | 22.3245 | 0.93307 | 21.5701 | 22.3245 | 0.9414 | -10.0168 | 10.4875 | -0.93488 | 13.5007 | -6.7556 | 0.18797 | 4.7735 | -4.6795 | -0.18412 | -2.7146 | 6.8848 | -8.9755 | 27.7962 | -153.6375 | 171.0245 | -152.2038 | 26.3625 | 1.0288 | 0.51442 | 0.51442 | 1.0212 | 0.63843 | 0.43207 | 2.3162 | -177.6838 | -177.6838 | 2.1658 | -163.5729 | 160.8196
Line_2 | 0.07654 | 0.63756 | 0.697 | 0.07654 | 0.63756 | 0.697 | 0.88381 | 7.3619 | 8.0483 | 0.88381 | 7.3619 | 8.0483 | 0.89894 | -4.0484 | 2.7169 | -0.89309 | 4.4543 | -2.2318 | 0.13362 | 1.7398 | -2.3801 | -0.13017 | -1.4999 | 2.6667 | -6.1266 | 35.0378 | -149.1073 | 173.8734 | -144.9622 | 30.8927 | 1.0283 | 0.59855 | 0.44878 | 1.0212 | 0.63843 | 0.43207 | 2.3283 | -168.2174 | 169.6733 | 2.1658 | -163.5729 | 160.8196
Line_3 | 0.0057872 | 1.2382 | 1.2398 | 0.0057872 | 1.2382 | 1.2398 | 0.066825 | 14.2971 | 14.3155 | 0.066825 | 14.2971 | 14.3155 | 0.041958 | -6.8307 | 6.8517 | -0.041925 | 8.3613 | -5.3171 | 0.054463 | 2.7263 | -2.6991 | -0.054444 | -1.8218 | 3.6059 | -50.0733 | 24.0746 | -156.1827 | 129.9267 | -155.9254 | 23.8173 | 1.0288 | 0.51442 | 0.51442 | 1.0283 | 0.59855 | 0.44878 | 2.3162 | -177.6838 | -177.6838 | 2.3283 | -168.2174 | 169.6733

## LL_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.1573 | 2.5018 | 2.6288 | 0.1573 | 2.5018 | 2.6288 | 1.8163 | 28.8882 | 30.3543 | 1.8163 | 28.8882 | 30.3543 | -1.8033 | 24.2039 | -2.0881 | 1.828 | -17.955 | 8.9874 | -0.29968 | -0.52181 | 13.6286 | 0.31428 | 4.2146 | -9.5515 | 172.4103 | -150.363 | 27.5625 | -7.5897 | 29.637 | -152.4375 | 1.0064 | 0.83804 | 0.45422 | 1.0212 | 0.63843 | 0.43207 | 1.8461 | -151.598 | 126.2732 | 2.1658 | -163.5729 | 160.8196
Line_1 | 0.080807 | 1.868 | 1.9334 | 0.080807 | 1.868 | 1.9334 | 0.93307 | 21.5701 | 22.3245 | 0.93307 | 21.5701 | 22.3245 | 0.9414 | -10.0168 | 10.4875 | -0.93488 | 13.5007 | -6.7556 | 0.18797 | 4.7735 | -4.6795 | -0.18412 | -2.7146 | 6.8848 | -8.9755 | 27.7962 | -153.6375 | 171.0245 | -152.2038 | 26.3625 | 1.0288 | 0.51442 | 0.51442 | 1.0212 | 0.63843 | 0.43207 | 2.3162 | -177.6838 | -177.6838 | 2.1658 | -163.5729 | 160.8196
Line_2 | 0.07654 | 0.63756 | 0.697 | 0.07654 | 0.63756 | 0.697 | 0.88381 | 7.3619 | 8.0483 | 0.88381 | 7.3619 | 8.0483 | 0.89894 | -4.0484 | 2.7169 | -0.89309 | 4.4543 | -2.2318 | 0.13362 | 1.7398 | -2.3801 | -0.13017 | -1.4999 | 2.6667 | -6.1266 | 35.0378 | -149.1073 | 173.8734 | -144.9622 | 30.8927 | 1.0283 | 0.59855 | 0.44878 | 1.0212 | 0.63843 | 0.43207 | 2.3283 | -168.2174 | 169.6733 | 2.1658 | -163.5729 | 160.8196
Line_3 | 0.0057872 | 1.2382 | 1.2398 | 0.0057872 | 1.2382 | 1.2398 | 0.066825 | 14.2971 | 14.3155 | 0.066825 | 14.2971 | 14.3155 | 0.041958 | -6.8307 | 6.8517 | -0.041925 | 8.3613 | -5.3171 | 0.054463 | 2.7263 | -2.6991 | -0.054444 | -1.8218 | 3.6059 | -50.0733 | 24.0746 | -156.1827 | 129.9267 | -155.9254 | 23.8173 | 1.0288 | 0.51442 | 0.51442 | 1.0283 | 0.59855 | 0.44878 | 2.3162 | -177.6838 | -177.6838 | 2.3283 | -168.2174 | 169.6733

## LL_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.068597 | 1.091 | 1.1464 | 0.068597 | 1.091 | 1.1464 | 0.79209 | 12.5981 | 13.2375 | 0.79209 | 12.5981 | 13.2375 | -0.78949 | 11.8666 | 2.206 | 0.79419 | -10.6782 | -0.89388 | 0.059138 | 0.94684 | 9.8501 | -0.056362 | -0.24454 | -9.0747 | -174.893 | -137.6663 | 40.2592 | 5.107 | 42.3337 | -139.7408 | 0.99951 | 0.94493 | 0.76254 | 1.0052 | 0.84783 | 0.68885 | 0.82315 | -133.1043 | 117.6357 | 1.0476 | -136.3544 | 124.6336
Line_1 | 0.03524 | 0.81464 | 0.84313 | 0.03524 | 0.81464 | 0.84313 | 0.40691 | 9.4067 | 9.7357 | 0.40691 | 9.4067 | 9.7357 | 0.40981 | -7.3006 | 0.19224 | -0.40857 | 7.9632 | 0.5175 | -0.018346 | -0.047078 | -6.267 | 0.019079 | 0.43863 | 6.6864 | 3.7212 | 40.4929 | -140.9408 | -176.2788 | -139.5071 | 39.0592 | 1.0081 | 0.77612 | 0.64402 | 1.0052 | 0.84783 | 0.68885 | 1.1579 | -139.1377 | 130.8161 | 1.0476 | -136.3544 | 124.6336
Line_2 | 0.033379 | 0.27804 | 0.30396 | 0.033379 | 0.27804 | 0.30396 | 0.38543 | 3.2105 | 3.5098 | 0.38543 | 3.2105 | 3.5098 | 0.38673 | -2.6378 | -0.28414 | -0.38562 | 2.715 | 0.37638 | -0.036626 | 0.23969 | -2.3338 | 0.037283 | -0.19408 | 2.3883 | 6.5701 | 47.7344 | -136.4106 | -173.4299 | -132.2656 | 43.5894 | 1.0079 | 0.82502 | 0.66983 | 1.0052 | 0.84783 | 0.68885 | 1.1599 | -137.4576 | 126.6478 | 1.0476 | -136.3544 | 124.6336
Line_3 | 0.0025238 | 0.53996 | 0.54066 | 0.0025238 | 0.53996 | 0.54066 | 0.029142 | 6.2349 | 6.243 | 0.029142 | 6.2349 | 6.243 | 0.022981 | -4.8268 | 0.30161 | -0.022975 | 5.1178 | -0.0097645 | 0.018303 | -0.34522 | -4.0093 | -0.018299 | 0.51724 | 4.1817 | -37.3766 | 36.7713 | -143.486 | 142.6234 | -143.2287 | 36.514 | 1.0081 | 0.77612 | 0.64402 | 1.0079 | 0.82502 | 0.66983 | 1.1579 | -139.1377 | 130.8161 | 1.1599 | -137.4576 | 126.6478

## LL_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.068597 | 1.091 | 1.1464 | 0.068597 | 1.091 | 1.1464 | 0.79209 | 12.5981 | 13.2375 | 0.79209 | 12.5981 | 13.2375 | -0.78949 | 11.8666 | 2.206 | 0.79419 | -10.6782 | -0.89388 | 0.059138 | 0.94684 | 9.8501 | -0.056362 | -0.24454 | -9.0747 | -174.893 | -137.6663 | 40.2592 | 5.107 | 42.3337 | -139.7408 | 0.99951 | 0.94493 | 0.76254 | 1.0052 | 0.84783 | 0.68885 | 0.82315 | -133.1043 | 117.6357 | 1.0476 | -136.3544 | 124.6336
Line_1 | 0.03524 | 0.81464 | 0.84313 | 0.03524 | 0.81464 | 0.84313 | 0.40691 | 9.4067 | 9.7357 | 0.40691 | 9.4067 | 9.7357 | 0.40981 | -7.3006 | 0.19224 | -0.40857 | 7.9632 | 0.5175 | -0.018346 | -0.047078 | -6.267 | 0.019079 | 0.43863 | 6.6864 | 3.7212 | 40.4929 | -140.9408 | -176.2788 | -139.5071 | 39.0592 | 1.0081 | 0.77612 | 0.64402 | 1.0052 | 0.84783 | 0.68885 | 1.1579 | -139.1377 | 130.8161 | 1.0476 | -136.3544 | 124.6336
Line_2 | 0.033379 | 0.27804 | 0.30396 | 0.033379 | 0.27804 | 0.30396 | 0.38543 | 3.2105 | 3.5098 | 0.38543 | 3.2105 | 3.5098 | 0.38673 | -2.6378 | -0.28414 | -0.38562 | 2.715 | 0.37638 | -0.036626 | 0.23969 | -2.3338 | 0.037283 | -0.19408 | 2.3883 | 6.5701 | 47.7344 | -136.4106 | -173.4299 | -132.2656 | 43.5894 | 1.0079 | 0.82502 | 0.66983 | 1.0052 | 0.84783 | 0.68885 | 1.1599 | -137.4576 | 126.6478 | 1.0476 | -136.3544 | 124.6336
Line_3 | 0.0025238 | 0.53996 | 0.54066 | 0.0025238 | 0.53996 | 0.54066 | 0.029142 | 6.2349 | 6.243 | 0.029142 | 6.2349 | 6.243 | 0.022981 | -4.8268 | 0.30161 | -0.022975 | 5.1178 | -0.0097645 | 0.018303 | -0.34522 | -4.0093 | -0.018299 | 0.51724 | 4.1817 | -37.3766 | 36.7713 | -143.486 | 142.6234 | -143.2287 | 36.514 | 1.0081 | 0.77612 | 0.64402 | 1.0079 | 0.82502 | 0.66983 | 1.1579 | -139.1377 | 130.8161 | 1.1599 | -137.4576 | 126.6478

## LG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.9337 | 0.91124 | 0.75379 | 1.9313 | 0.91355 | 0.75612 | 22.3285 | 10.5221 | 8.704 | 22.3003 | 10.5488 | 8.7309 | 5.9664 | -12.1224 | 10.5236 | -3.3314 | 12.3012 | -10.5419 | 4.982 | 7.8409 | 2.2674 | -2.5352 | -7.5803 | -1.9512 | -76.6202 | 86.7428 | 121.8378 | 103.3778 | -93.2095 | -58.2159 |  | 0.34812 | 1.3721 | 1.2368 | 0.18773 | 1.3698 | 1.2279 | -36.758 | -126.1526 | 133.9969 | -39.351 | -124.8519 | 132.2703
Line_1 | 1.6614 | 0.48188 | 0.38307 | 1.664 | 0.47937 | 0.38062 | 19.1844 | 5.5643 | 4.4234 | 19.2143 | 5.5352 | 4.395 | 8.5405e-11 | 6.4571 | -5.5198 | 2.8814 | -6.6475 | 5.2134 | -6.0824e-11 | -3.8252 | -1.372 | 2.1699 | 3.6464 | 1.3949 | 103.675 | -96.0291 | -62.8365 | -76.3336 | 83.8947 | 117.2907 |  | 0 | 1.3488 | 1.2858 | 0.18773 | 1.3698 | 1.2279 | 0 | -126.6717 | 131.1218 | -39.351 | -124.8519 | 132.2703
Line_2 | 0.26501 | 0.43779 | 0.38011 | 0.26741 | 0.43547 | 0.37785 | 3.06 | 5.0552 | 4.3891 | 3.0878 | 5.0284 | 4.363 | -0.54552 | 5.9788 | -5.0711 | 0.45005 | -5.6537 | 5.3285 | -0.37993 | -3.71 | -0.49075 | 0.36532 | 3.9339 | 0.55626 | 101.5424 | -89.9349 | -53.8161 | -78.4182 | 89.9784 | 126.3106 |  | 0.21724 | 1.3919 | 1.1608 | 0.18773 | 1.3698 | 1.2279 | -43.6021 | -121.7558 | 131.7114 | -39.351 | -124.8519 | 132.2703
Line_3 | 1.3955 | 0.066199 | 0.060409 | 1.398 | 0.065013 | 0.059404 | 16.1134 | 0.7644 | 0.69755 | 16.1424 | 0.75071 | 0.68593 | 7.1374e-11 | 1.0032 | 0.086792 | 2.9633 | -0.9806 | -0.11566 | -5.1587e-11 | 0.23802 | -0.89272 | 1.8754 | -0.3609 | 0.78777 | 104.0753 | -140.0198 | -144.4312 | -75.9303 | 38.0383 | 33.3589 |  | 0 | 1.3488 | 1.2858 | 0.21724 | 1.3919 | 1.1608 | 0 | -126.6717 | 131.1218 | -43.6021 | -121.7558 | 131.7114

## LG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.9337 | 0.91124 | 0.75379 | 1.9313 | 0.91355 | 0.75612 | 22.3285 | 10.5221 | 8.704 | 22.3003 | 10.5488 | 8.7309 | 5.9664 | -12.1224 | 10.5236 | -3.3314 | 12.3012 | -10.5419 | 4.982 | 7.8409 | 2.2674 | -2.5352 | -7.5803 | -1.9512 | -76.6202 | 86.7428 | 121.8378 | 103.3778 | -93.2095 | -58.2159 |  | 0.34812 | 1.3721 | 1.2368 | 0.18773 | 1.3698 | 1.2279 | -36.758 | -126.1526 | 133.9969 | -39.351 | -124.8519 | 132.2703
Line_1 | 1.6614 | 0.48188 | 0.38307 | 1.664 | 0.47937 | 0.38062 | 19.1844 | 5.5643 | 4.4234 | 19.2143 | 5.5352 | 4.395 | 8.5405e-11 | 6.4571 | -5.5198 | 2.8814 | -6.6475 | 5.2134 | -6.0824e-11 | -3.8252 | -1.372 | 2.1699 | 3.6464 | 1.3949 | 103.675 | -96.0291 | -62.8365 | -76.3336 | 83.8947 | 117.2907 |  | 0 | 1.3488 | 1.2858 | 0.18773 | 1.3698 | 1.2279 | 0 | -126.6717 | 131.1218 | -39.351 | -124.8519 | 132.2703
Line_2 | 0.26501 | 0.43779 | 0.38011 | 0.26741 | 0.43547 | 0.37785 | 3.06 | 5.0552 | 4.3891 | 3.0878 | 5.0284 | 4.363 | -0.54552 | 5.9788 | -5.0711 | 0.45005 | -5.6537 | 5.3285 | -0.37993 | -3.71 | -0.49075 | 0.36532 | 3.9339 | 0.55626 | 101.5424 | -89.9349 | -53.8161 | -78.4182 | 89.9784 | 126.3106 |  | 0.21724 | 1.3919 | 1.1608 | 0.18773 | 1.3698 | 1.2279 | -43.6021 | -121.7558 | 131.7114 | -39.351 | -124.8519 | 132.2703
Line_3 | 1.3955 | 0.066199 | 0.060409 | 1.398 | 0.065013 | 0.059404 | 16.1134 | 0.7644 | 0.69755 | 16.1424 | 0.75071 | 0.68593 | 7.1374e-11 | 1.0032 | 0.086792 | 2.9633 | -0.9806 | -0.11566 | -5.1587e-11 | 0.23802 | -0.89272 | 1.8754 | -0.3609 | 0.78777 | 104.0753 | -140.0198 | -144.4312 | -75.9303 | 38.0383 | 33.3589 |  | 0 | 1.3488 | 1.2858 | 0.21724 | 1.3919 | 1.1608 | 0 | -126.6717 | 131.1218 | -43.6021 | -121.7558 | 131.7114

## LG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.47494 | 0.20757 | 0.34106 | 0.47418 | 0.20802 | 0.34161 | 5.4841 | 2.3968 | 3.9383 | 5.4753 | 2.402 | 3.9445 | 4.3489 | -2.8616 | 2.9304 | -4.1695 | 2.8805 | -2.9161 | 2.727 | 0.71427 | -3.3532 | -2.5807 | -0.72275 | 3.4418 | -42.1199 | 73.6495 | 174.001 | 137.8956 | -106.1763 | -6.0919 |  | 0.93601 | 1.2305 | 1.1308 | 0.89557 | 1.2364 | 1.1436 | -10.0298 | -120.3654 | 125.1519 | -10.3486 | -120.2618 | 124.1816
Line_1 | 0.45586 | 0.11573 | 0.16671 | 0.45667 | 0.11518 | 0.16618 | 5.2638 | 1.3363 | 1.925 | 5.2732 | 1.33 | 1.9188 | -3.5343 | 1.6057 | -1.5372 | 3.7778 | -1.6022 | 1.4957 | -2.6706 | -0.40529 | 1.6411 | 2.8338 | 0.36996 | -1.6057 | 132.7977 | -106.9523 | -9.0024 | -47.2224 | 72.7399 | 171.2135 |  | 0.84155 | 1.2393 | 1.1681 | 0.89557 | 1.2364 | 1.1436 | -10.1265 | -121.1185 | 124.1237 | -10.3486 | -120.2618 | 124.1816
Line_2 | 0.044873 | 0.093333 | 0.17631 | 0.045089 | 0.092882 | 0.17579 | 0.51815 | 1.0777 | 2.0359 | 0.52064 | 1.0725 | 2.0298 | -0.38913 | 1.2915 | -1.3866 | 0.39164 | -1.2782 | 1.4204 | 0.26591 | -0.34203 | 1.8406 | -0.25304 | 0.35279 | -1.8361 | -156.5448 | -104.4505 | -3.7273 | 22.5181 | 75.1678 | 176.4553 |  | 0.90959 | 1.2397 | 1.1319 | 0.89557 | 1.2364 | 1.1436 | -10.8916 | -119.2838 | 123.2639 | -10.3486 | -120.2618 | 124.1816
Line_3 | 0.44265 | 0.022982 | 0.018538 | 0.44345 | 0.022601 | 0.018291 | 5.1113 | 0.26537 | 0.21405 | 5.1206 | 0.26097 | 0.21121 | -3.1681 | 0.32772 | -0.082931 | 3.4719 | -0.32345 | 0.073315 | -2.9096 | -0.027351 | -0.23588 | 3.1047 | 0.006572 | 0.22755 | 127.3091 | -116.3477 | -126.5056 | -52.6961 | 61.8802 | 51.1224 |  | 0.84155 | 1.2393 | 1.1681 | 0.90959 | 1.2397 | 1.1319 | -10.1265 | -121.1185 | 124.1237 | -10.8916 | -119.2838 | 123.2639

## LG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.47494 | 0.20757 | 0.34106 | 0.47418 | 0.20802 | 0.34161 | 5.4841 | 2.3968 | 3.9383 | 5.4753 | 2.402 | 3.9445 | 4.3489 | -2.8616 | 2.9304 | -4.1695 | 2.8805 | -2.9161 | 2.727 | 0.71427 | -3.3532 | -2.5807 | -0.72275 | 3.4418 | -42.1199 | 73.6495 | 174.001 | 137.8956 | -106.1763 | -6.0919 |  | 0.93601 | 1.2305 | 1.1308 | 0.89557 | 1.2364 | 1.1436 | -10.0298 | -120.3654 | 125.1519 | -10.3486 | -120.2618 | 124.1816
Line_1 | 0.45586 | 0.11573 | 0.16671 | 0.45667 | 0.11518 | 0.16618 | 5.2638 | 1.3363 | 1.925 | 5.2732 | 1.33 | 1.9188 | -3.5343 | 1.6057 | -1.5372 | 3.7778 | -1.6022 | 1.4957 | -2.6706 | -0.40529 | 1.6411 | 2.8338 | 0.36996 | -1.6057 | 132.7977 | -106.9523 | -9.0024 | -47.2224 | 72.7399 | 171.2135 |  | 0.84155 | 1.2393 | 1.1681 | 0.89557 | 1.2364 | 1.1436 | -10.1265 | -121.1185 | 124.1237 | -10.3486 | -120.2618 | 124.1816
Line_2 | 0.044873 | 0.093333 | 0.17631 | 0.045089 | 0.092882 | 0.17579 | 0.51815 | 1.0777 | 2.0359 | 0.52064 | 1.0725 | 2.0298 | -0.38913 | 1.2915 | -1.3866 | 0.39164 | -1.2782 | 1.4204 | 0.26591 | -0.34203 | 1.8406 | -0.25304 | 0.35279 | -1.8361 | -156.5448 | -104.4505 | -3.7273 | 22.5181 | 75.1678 | 176.4553 |  | 0.90959 | 1.2397 | 1.1319 | 0.89557 | 1.2364 | 1.1436 | -10.8916 | -119.2838 | 123.2639 | -10.3486 | -120.2618 | 124.1816
Line_3 | 0.44265 | 0.022982 | 0.018538 | 0.44345 | 0.022601 | 0.018291 | 5.1113 | 0.26537 | 0.21405 | 5.1206 | 0.26097 | 0.21121 | -3.1681 | 0.32772 | -0.082931 | 3.4719 | -0.32345 | 0.073315 | -2.9096 | -0.027351 | -0.23588 | 3.1047 | 0.006572 | 0.22755 | 127.3091 | -116.3477 | -126.5056 | -52.6961 | 61.8802 | 51.1224 |  | 0.84155 | 1.2393 | 1.1681 | 0.90959 | 1.2397 | 1.1319 | -10.1265 | -121.1185 | 124.1237 | -10.8916 | -119.2838 | 123.2639

## LG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.7148 | 0.78992 | 0.66828 | 1.713 | 0.79175 | 0.67012 | 19.8007 | 9.1212 | 7.7167 | 19.7795 | 9.1424 | 7.7379 | 8.5164 | -6.3471 | 7.5618 | -4.6935 | 6.5849 | -7.4835 | 4.0602 | 8.6641 | 1.9198 | -2.1198 | -8.4386 | -1.7237 | -65.3297 | 110.6514 | 117.5497 | 114.6695 | -69.3376 | -62.4562 |  | 0.47648 | 1.1775 | 1.011 | 0.26037 | 1.1708 | 0.99245 | -39.8404 | -123.123 | 131.7954 | -41.0238 | -121.3714 | 130.5144
Line_1 | 1.4254 | 0.42104 | 0.35447 | 1.4274 | 0.419 | 0.35245 | 16.4587 | 4.8617 | 4.0931 | 16.4817 | 4.8382 | 4.0698 | -4.0812e-11 | 3.6445 | -4.1314 | 3.9066 | -3.9617 | 3.7833 | 1.7694e-13 | -4.2288 | -1.5307 | 1.7759 | 4.0486 | 1.4145 | 114.5479 | -75.7581 | -70.029 | -65.4692 | 104.2503 | 110.014 |  | 0 | 1.1483 | 1.0764 | 0.26037 | 1.1708 | 0.99245 | 0 | -125.003 | 130.301 | -41.0238 | -121.3714 | 130.5144
Line_2 | 0.28383 | 0.38007 | 0.32579 | 0.28562 | 0.37828 | 0.32401 | 3.2774 | 4.3887 | 3.7619 | 3.2981 | 4.368 | 3.7414 | -0.93365 | 3.095 | -3.3362 | 0.78683 | -2.6232 | 3.7003 | -0.37153 | -4.2356 | -0.21194 | 0.34398 | 4.39 | 0.30913 | 115.3477 | -62.2319 | -54.3049 | -64.6372 | 117.7682 | 125.7389 |  | 0.3066 | 1.1953 | 0.88862 | 0.26037 | 1.1708 | 0.99245 | -42.9529 | -116.0759 | 129.3302 | -41.0238 | -121.3714 | 130.5144
Line_3 | 1.1407 | 0.10289 | 0.097452 | 1.1426 | 0.10203 | 0.09658 | 13.1718 | 1.1881 | 1.1253 | 13.1939 | 1.1782 | 1.1152 | -3.2662e-11 | 1.3427 | -0.10588 | 3.7314 | -1.3227 | 0.085908 | 2.3852e-14 | 0.24136 | -1.2066 | 1.5622 | -0.48352 | 0.98727 | 114.3413 | -135.1933 | -134.6842 | -65.6696 | 43.8439 | 44.3033 |  | 0 | 1.1483 | 1.0764 | 0.3066 | 1.1953 | 0.88862 | 0 | -125.003 | 130.301 | -42.9529 | -116.0759 | 129.3302

## LG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.7148 | 0.78992 | 0.66828 | 1.713 | 0.79175 | 0.67012 | 19.8007 | 9.1212 | 7.7167 | 19.7795 | 9.1424 | 7.7379 | 8.5164 | -6.3471 | 7.5618 | -4.6935 | 6.5849 | -7.4835 | 4.0602 | 8.6641 | 1.9198 | -2.1198 | -8.4386 | -1.7237 | -65.3297 | 110.6514 | 117.5497 | 114.6695 | -69.3376 | -62.4562 |  | 0.47648 | 1.1775 | 1.011 | 0.26037 | 1.1708 | 0.99245 | -39.8404 | -123.123 | 131.7954 | -41.0238 | -121.3714 | 130.5144
Line_1 | 1.4254 | 0.42104 | 0.35447 | 1.4274 | 0.419 | 0.35245 | 16.4587 | 4.8617 | 4.0931 | 16.4817 | 4.8382 | 4.0698 | -4.0812e-11 | 3.6445 | -4.1314 | 3.9066 | -3.9617 | 3.7833 | 1.7694e-13 | -4.2288 | -1.5307 | 1.7759 | 4.0486 | 1.4145 | 114.5479 | -75.7581 | -70.029 | -65.4692 | 104.2503 | 110.014 |  | 0 | 1.1483 | 1.0764 | 0.26037 | 1.1708 | 0.99245 | 0 | -125.003 | 130.301 | -41.0238 | -121.3714 | 130.5144
Line_2 | 0.28383 | 0.38007 | 0.32579 | 0.28562 | 0.37828 | 0.32401 | 3.2774 | 4.3887 | 3.7619 | 3.2981 | 4.368 | 3.7414 | -0.93365 | 3.095 | -3.3362 | 0.78683 | -2.6232 | 3.7003 | -0.37153 | -4.2356 | -0.21194 | 0.34398 | 4.39 | 0.30913 | 115.3477 | -62.2319 | -54.3049 | -64.6372 | 117.7682 | 125.7389 |  | 0.3066 | 1.1953 | 0.88862 | 0.26037 | 1.1708 | 0.99245 | -42.9529 | -116.0759 | 129.3302 | -41.0238 | -121.3714 | 130.5144
Line_3 | 1.1407 | 0.10289 | 0.097452 | 1.1426 | 0.10203 | 0.09658 | 13.1718 | 1.1881 | 1.1253 | 13.1939 | 1.1782 | 1.1152 | -3.2662e-11 | 1.3427 | -0.10588 | 3.7314 | -1.3227 | 0.085908 | 2.3852e-14 | 0.24136 | -1.2066 | 1.5622 | -0.48352 | 0.98727 | 114.3413 | -135.1933 | -134.6842 | -65.6696 | 43.8439 | 44.3033 |  | 0 | 1.1483 | 1.0764 | 0.3066 | 1.1953 | 0.88862 | 0 | -125.003 | 130.301 | -42.9529 | -116.0759 | 129.3302

## LG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.54767 | 0.25229 | 0.21344 | 0.54709 | 0.25287 | 0.21402 | 6.324 | 2.9132 | 2.4646 | 6.3172 | 2.9199 | 2.4713 | 4.3269 | -1.1093 | 2.3572 | -3.9332 | 1.1343 | -2.3536 | 3.2148 | 2.881 | -0.50613 | -3.0139 | -2.8627 | 0.5279 | -47.1457 | 128.8354 | 135.7337 | 132.8535 | -51.1536 | -44.2722 |  | 0.85237 | 1.0597 | 0.97821 | 0.78438 | 1.0545 | 0.97602 | -10.534 | -120.1053 | 123.6152 | -9.6843 | -119.5389 | 123.0858
Line_1 | 0.45524 | 0.13447 | 0.11321 | 0.45587 | 0.13382 | 0.11257 | 5.2566 | 1.5527 | 1.3073 | 5.264 | 1.5452 | 1.2998 | -2.8695 | 0.73524 | -1.3043 | 3.2713 | -0.76569 | 1.2636 | -2.3341 | -1.4617 | 0.10201 | 2.5193 | 1.4384 | -0.11305 | 132.7319 | -57.5741 | -51.8449 | -47.2852 | 122.4343 | 128.198 |  | 0.70366 | 1.0538 | 1.0008 | 0.78438 | 1.0545 | 0.97602 | -8.143 | -120.8724 | 123.6833 | -9.6843 | -119.5389 | 123.0858
Line_2 | 0.090652 | 0.12139 | 0.10405 | 0.091224 | 0.12082 | 0.10348 | 1.0468 | 1.4017 | 1.2015 | 1.0534 | 1.3951 | 1.1949 | -0.67307 | 0.41717 | -1.0571 | 0.66186 | -0.36857 | 1.09 | -0.49466 | -1.4131 | 0.42667 | 0.49458 | 1.4242 | -0.41486 | 133.5317 | -44.0479 | -36.1209 | -46.4532 | 135.9522 | 143.9229 |  | 0.79798 | 1.0512 | 0.9488 | 0.78438 | 1.0545 | 0.97602 | -10.1551 | -117.6005 | 121.899 | -9.6843 | -119.5389 | 123.0858
Line_3 | 0.36432 | 0.032861 | 0.031124 | 0.36493 | 0.032588 | 0.030846 | 4.2068 | 0.37945 | 0.35939 | 4.2139 | 0.37629 | 0.35618 | -2.2897 | 0.39894 | -0.17884 | 2.6738 | -0.39554 | 0.17197 | -1.8762 | -0.026939 | -0.31207 | 2.0391 | -0.0025647 | 0.29092 | 132.5253 | -117.0093 | -116.5002 | -47.4856 | 62.0279 | 62.4873 |  | 0.70366 | 1.0538 | 1.0008 | 0.79798 | 1.0512 | 0.9488 | -8.143 | -120.8724 | 123.6833 | -10.1551 | -117.6005 | 121.899

## LG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.54767 | 0.25229 | 0.21344 | 0.54709 | 0.25287 | 0.21402 | 6.324 | 2.9132 | 2.4646 | 6.3172 | 2.9199 | 2.4713 | 4.3269 | -1.1093 | 2.3572 | -3.9332 | 1.1343 | -2.3536 | 3.2148 | 2.881 | -0.50613 | -3.0139 | -2.8627 | 0.5279 | -47.1457 | 128.8354 | 135.7337 | 132.8535 | -51.1536 | -44.2722 |  | 0.85237 | 1.0597 | 0.97821 | 0.78438 | 1.0545 | 0.97602 | -10.534 | -120.1053 | 123.6152 | -9.6843 | -119.5389 | 123.0858
Line_1 | 0.45524 | 0.13447 | 0.11321 | 0.45587 | 0.13382 | 0.11257 | 5.2566 | 1.5527 | 1.3073 | 5.264 | 1.5452 | 1.2998 | -2.8695 | 0.73524 | -1.3043 | 3.2713 | -0.76569 | 1.2636 | -2.3341 | -1.4617 | 0.10201 | 2.5193 | 1.4384 | -0.11305 | 132.7319 | -57.5741 | -51.8449 | -47.2852 | 122.4343 | 128.198 |  | 0.70366 | 1.0538 | 1.0008 | 0.78438 | 1.0545 | 0.97602 | -8.143 | -120.8724 | 123.6833 | -9.6843 | -119.5389 | 123.0858
Line_2 | 0.090652 | 0.12139 | 0.10405 | 0.091224 | 0.12082 | 0.10348 | 1.0468 | 1.4017 | 1.2015 | 1.0534 | 1.3951 | 1.1949 | -0.67307 | 0.41717 | -1.0571 | 0.66186 | -0.36857 | 1.09 | -0.49466 | -1.4131 | 0.42667 | 0.49458 | 1.4242 | -0.41486 | 133.5317 | -44.0479 | -36.1209 | -46.4532 | 135.9522 | 143.9229 |  | 0.79798 | 1.0512 | 0.9488 | 0.78438 | 1.0545 | 0.97602 | -10.1551 | -117.6005 | 121.899 | -9.6843 | -119.5389 | 123.0858
Line_3 | 0.36432 | 0.032861 | 0.031124 | 0.36493 | 0.032588 | 0.030846 | 4.2068 | 0.37945 | 0.35939 | 4.2139 | 0.37629 | 0.35618 | -2.2897 | 0.39894 | -0.17884 | 2.6738 | -0.39554 | 0.17197 | -1.8762 | -0.026939 | -0.31207 | 2.0391 | -0.0025647 | 0.29092 | 132.5253 | -117.0093 | -116.5002 | -47.4856 | 62.0279 | 62.4873 |  | 0.70366 | 1.0538 | 1.0008 | 0.79798 | 1.0512 | 0.9488 | -8.143 | -120.8724 | 123.6833 | -10.1551 | -117.6005 | 121.899

## LLG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.48897 | 3.0724 | 3.2773 | 0.49087 | 3.0722 | 3.277 | 5.6462 | 35.4765 | 37.8431 | 5.6681 | 35.4746 | 37.8396 | -1.8185 | 10.3707 | 8.7702 | 1.8191 | -5.0931 | -3.3417 | 7.5965 | 6.3746 | 14.9263 | -7.5883 | -1.7055 | -7.5617 | -97.9552 | -169.8981 | 23.4358 | 82.1379 | 10.1402 | -156.5999 |  | 1.3834 | 0.34314 | 0.45747 | 1.3767 | 0.15141 | 0.21848 | 5.5076 | -138.32 | 82.9986 | 5.6191 | -151.3458 | 89.5583
Line_1 | 0.26603 | 2.3497 | 2.4518 | 0.26397 | 2.3498 | 2.4525 | 3.0718 | 27.1323 | 28.311 | 3.0481 | 27.1337 | 28.3195 | 1.1977 | 6.4024e-11 | 8.6473e-11 | -1.3063 | 3.7622 | 2.9187 | -4.1318 | -5.5593e-11 | -6.6288e-12 | 3.9878 | 1.6504 | 5.4555 | 77.6483 | 5.0216 | -152.3434 | -102.518 | -175.0319 | 27.705 |  | 1.4004 | 0 | 0 | 1.3767 | 0.15141 | 0.21848 | 3.8139 | 0 | 0 | 5.6191 | -151.3458 | 89.5583
Line_2 | 0.23072 | 0.76232 | 0.85169 | 0.22878 | 0.76195 | 0.85152 | 2.6641 | 8.8026 | 9.8345 | 2.6417 | 8.7982 | 9.8325 | 0.62199 | -1.0825 | 0.12389 | -0.51288 | 1.331 | 0.42299 | -3.5349 | 0.64879 | -2.0483 | 3.6005 | 0.055136 | 2.1061 | 87.6711 | 26.4328 | -169.2224 | -92.488 | -153.718 | 10.9143 |  | 1.3473 | 0.14337 | 0.20866 | 1.3767 | 0.15141 | 0.21848 | 7.6504 | 175.4967 | 104.2388 | 5.6191 | -151.3458 | 89.5583
Line_3 | 0.056086 | 1.6631 | 1.6551 | 0.055328 | 1.6636 | 1.656 | 0.64762 | 19.2034 | 19.1113 | 0.63887 | 19.2099 | 19.1218 | 0.79426 | 5.1241e-11 | 5.7057e-11 | -0.79241 | 2.7542 | 1.4974 | -0.43786 | -3.1239e-11 | -1.3112e-11 | 0.33605 | 0.0069821 | 3.6983 | 32.6812 | -4.5778 | -143.7849 | -149.3687 | 175.3514 | 36.2817 |  | 1.4004 | 0 | 0 | 1.3473 | 0.14337 | 0.20866 | 3.8139 | 0 | 0 | 7.6504 | 175.4967 | 104.2388

## LLG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.48897 | 3.0724 | 3.2773 | 0.49087 | 3.0722 | 3.277 | 5.6462 | 35.4765 | 37.8431 | 5.6681 | 35.4746 | 37.8396 | -1.8185 | 10.3707 | 8.7702 | 1.8191 | -5.0931 | -3.3417 | 7.5965 | 6.3746 | 14.9263 | -7.5883 | -1.7055 | -7.5617 | -97.9552 | -169.8981 | 23.4358 | 82.1379 | 10.1402 | -156.5999 |  | 1.3834 | 0.34314 | 0.45747 | 1.3767 | 0.15141 | 0.21848 | 5.5076 | -138.32 | 82.9986 | 5.6191 | -151.3458 | 89.5583
Line_1 | 0.26603 | 2.3497 | 2.4518 | 0.26397 | 2.3498 | 2.4525 | 3.0718 | 27.1323 | 28.311 | 3.0481 | 27.1337 | 28.3195 | 1.1977 | 6.4024e-11 | 8.6473e-11 | -1.3063 | 3.7622 | 2.9187 | -4.1318 | -5.5593e-11 | -6.6288e-12 | 3.9878 | 1.6504 | 5.4555 | 77.6483 | 5.0216 | -152.3434 | -102.518 | -175.0319 | 27.705 |  | 1.4004 | 0 | 0 | 1.3767 | 0.15141 | 0.21848 | 3.8139 | 0 | 0 | 5.6191 | -151.3458 | 89.5583
Line_2 | 0.23072 | 0.76232 | 0.85169 | 0.22878 | 0.76195 | 0.85152 | 2.6641 | 8.8026 | 9.8345 | 2.6417 | 8.7982 | 9.8325 | 0.62199 | -1.0825 | 0.12389 | -0.51288 | 1.331 | 0.42299 | -3.5349 | 0.64879 | -2.0483 | 3.6005 | 0.055136 | 2.1061 | 87.6711 | 26.4328 | -169.2224 | -92.488 | -153.718 | 10.9143 |  | 1.3473 | 0.14337 | 0.20866 | 1.3767 | 0.15141 | 0.21848 | 7.6504 | 175.4967 | 104.2388 | 5.6191 | -151.3458 | 89.5583
Line_3 | 0.056086 | 1.6631 | 1.6551 | 0.055328 | 1.6636 | 1.656 | 0.64762 | 19.2034 | 19.1113 | 0.63887 | 19.2099 | 19.1218 | 0.79426 | 5.1241e-11 | 5.7057e-11 | -0.79241 | 2.7542 | 1.4974 | -0.43786 | -3.1239e-11 | -1.3112e-11 | 0.33605 | 0.0069821 | 3.6983 | 32.6812 | -4.5778 | -143.7849 | -149.3687 | 175.3514 | 36.2817 |  | 1.4004 | 0 | 0 | 1.3473 | 0.14337 | 0.20866 | 3.8139 | 0 | 0 | 7.6504 | 175.4967 | 104.2388

## LLG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.046499 | 0.71789 | 0.69855 | 0.046961 | 0.71794 | 0.69836 | 0.53692 | 8.2895 | 8.0661 | 0.54226 | 8.29 | 8.064 | 0.64664 | 7.364 | 4.2664 | -0.65559 | -7.0781 | -4.0093 | 0.062073 | 1.9339 | 6.9045 | -0.066462 | -1.7016 | -6.5399 | -1.7579 | -139.9024 | 51.2846 | 177.5413 | 40.1562 | -128.7739 |  | 1.2099 | 0.91847 | 1.0062 | 1.2152 | 0.87813 | 0.95127 | 3.7253 | -125.1877 | 109.5718 | 3.33 | -126.3263 | 109.7159
Line_1 | 0.019856 | 0.57227 | 0.57527 | 0.019183 | 0.57229 | 0.57562 | 0.22927 | 6.608 | 6.6427 | 0.22151 | 6.6082 | 6.6467 | -0.23916 | -5.0273 | -3.5971 | 0.22887 | 5.2673 | 3.7784 | -0.15084 | -2.3769 | -4.7151 | 0.14167 | 2.435 | 5.0696 | 150.3923 | 28.9418 | -123.6567 | -28.4276 | -151.1367 | 56.4133 |  | 1.2332 | 0.84153 | 0.89279 | 1.2152 | 0.87813 | 0.95127 | 2.6318 | -125.7537 | 109.0042 | 3.33 | -126.3263 | 109.7159
Line_2 | 0.031189 | 0.19312 | 0.13561 | 0.03088 | 0.19267 | 0.13549 | 0.36014 | 2.23 | 1.5659 | 0.35657 | 2.2248 | 1.5645 | -0.42828 | -1.7828 | -0.20271 | 0.42672 | 1.8108 | 0.23084 | 0.063626 | 0.79338 | -1.4821 | -0.075211 | -0.7334 | 1.4703 | -167.8906 | 75.893 | -151.665 | 13.326 | -104.2774 | 28.6386 |  | 1.2023 | 0.87505 | 0.95527 | 1.2152 | 0.87813 | 0.95127 | 3.6593 | -128.0975 | 110.5466 | 3.33 | -126.3263 | 109.7159
Line_3 | 0.0211 | 0.46232 | 0.45984 | 0.020863 | 0.46261 | 0.46023 | 0.24364 | 5.3385 | 5.3097 | 0.24091 | 5.3417 | 5.3143 | 0.19577 | -3.2838 | -3.367 | -0.19997 | 3.5397 | 3.5134 | -0.22793 | -3.0657 | -3.337 | 0.20954 | 3.0528 | 3.6644 | 51.9717 | 11.2134 | -115.7393 | -130.0023 | -168.8741 | 64.3415 |  | 1.2332 | 0.84153 | 0.89279 | 1.2023 | 0.87505 | 0.95527 | 2.6318 | -125.7537 | 109.0042 | 3.6593 | -128.0975 | 110.5466

## LLG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.046499 | 0.71789 | 0.69855 | 0.046961 | 0.71794 | 0.69836 | 0.53692 | 8.2895 | 8.0661 | 0.54226 | 8.29 | 8.064 | 0.64664 | 7.364 | 4.2664 | -0.65559 | -7.0781 | -4.0093 | 0.062073 | 1.9339 | 6.9045 | -0.066462 | -1.7016 | -6.5399 | -1.7579 | -139.9024 | 51.2846 | 177.5413 | 40.1562 | -128.7739 |  | 1.2099 | 0.91847 | 1.0062 | 1.2152 | 0.87813 | 0.95127 | 3.7253 | -125.1877 | 109.5718 | 3.33 | -126.3263 | 109.7159
Line_1 | 0.019856 | 0.57227 | 0.57527 | 0.019183 | 0.57229 | 0.57562 | 0.22927 | 6.608 | 6.6427 | 0.22151 | 6.6082 | 6.6467 | -0.23916 | -5.0273 | -3.5971 | 0.22887 | 5.2673 | 3.7784 | -0.15084 | -2.3769 | -4.7151 | 0.14167 | 2.435 | 5.0696 | 150.3923 | 28.9418 | -123.6567 | -28.4276 | -151.1367 | 56.4133 |  | 1.2332 | 0.84153 | 0.89279 | 1.2152 | 0.87813 | 0.95127 | 2.6318 | -125.7537 | 109.0042 | 3.33 | -126.3263 | 109.7159
Line_2 | 0.031189 | 0.19312 | 0.13561 | 0.03088 | 0.19267 | 0.13549 | 0.36014 | 2.23 | 1.5659 | 0.35657 | 2.2248 | 1.5645 | -0.42828 | -1.7828 | -0.20271 | 0.42672 | 1.8108 | 0.23084 | 0.063626 | 0.79338 | -1.4821 | -0.075211 | -0.7334 | 1.4703 | -167.8906 | 75.893 | -151.665 | 13.326 | -104.2774 | 28.6386 |  | 1.2023 | 0.87505 | 0.95527 | 1.2152 | 0.87813 | 0.95127 | 3.6593 | -128.0975 | 110.5466 | 3.33 | -126.3263 | 109.7159
Line_3 | 0.0211 | 0.46232 | 0.45984 | 0.020863 | 0.46261 | 0.46023 | 0.24364 | 5.3385 | 5.3097 | 0.24091 | 5.3417 | 5.3143 | 0.19577 | -3.2838 | -3.367 | -0.19997 | 3.5397 | 3.5134 | -0.22793 | -3.0657 | -3.337 | 0.20954 | 3.0528 | 3.6644 | 51.9717 | 11.2134 | -115.7393 | -130.0023 | -168.8741 | 64.3415 |  | 1.2332 | 0.84153 | 0.89279 | 1.2023 | 0.87505 | 0.95527 | 2.6318 | -125.7537 | 109.0042 | 3.6593 | -128.0975 | 110.5466

## LLG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.57165 | 2.4993 | 2.6834 | 0.57319 | 2.4991 | 2.683 | 6.6008 | 28.8589 | 30.985 | 6.6187 | 28.8572 | 30.9811 | 0.37054 | 12.6997 | 12.0986 | -0.28379 | -6.1195 | -4.9118 | 7.5998 | 2.1477 | 12.1119 | -7.5494 | 0.44273 | -6.6298 | -80.5953 | -160.2678 | 36.7778 | 99.4473 | 19.7688 | -143.2556 |  | 1.1527 | 0.44631 | 0.55251 | 1.1414 | 0.21262 | 0.26633 | 6.6134 | -150.6689 | 81.8093 | 7.2945 | -164.3692 | 90.2111
Line_1 | 0.3127 | 1.9169 | 1.9873 | 0.31094 | 1.9168 | 1.9882 | 3.6107 | 22.134 | 22.9479 | 3.5905 | 22.1332 | 22.9575 | 0.13937 | -6.7679e-11 | -3.1979e-11 | -0.33759 | 4.7043 | 3.8963 | -4.2829 | -4.7107e-11 | -8.0419e-11 | 4.0843 | 0.12015 | 4.7119 | 92.6226 | 14.2209 | -140.247 | -87.4306 | -165.8323 | 39.7983 |  | 1.1868 | 0 | 0 | 1.1414 | 0.21262 | 0.26633 | 4.4864 | 0 | 0 | 7.2945 | -164.3692 | 90.2111
Line_2 | 0.26864 | 0.62063 | 0.70566 | 0.2671 | 0.62035 | 0.70568 | 3.102 | 7.1664 | 8.1483 | 3.0842 | 7.1632 | 8.1485 | -0.37412 | -1.076 | -0.3753 | 0.62138 | 1.4152 | 1.0155 | -3.3545 | 1.2585 | -2.1387 | 3.4651 | -0.56289 | 1.9179 | 107.5174 | 37.4631 | -152.0153 | -72.5389 | -142.679 | 28.1116 |  | 1.0881 | 0.23105 | 0.26648 | 1.1414 | 0.21262 | 0.26633 | 11.1536 | 167.993 | 108.0318 | 7.2945 | -164.3692 | 90.2111
Line_3 | 0.087185 | 1.3683 | 1.3043 | 0.086533 | 1.3687 | 1.3051 | 1.0067 | 15.7999 | 15.0611 | 0.99919 | 15.8044 | 15.0704 | 0.96433 | -4.1534e-11 | -2.6655e-11 | -0.95552 | 3.5123 | 1.8908 | -0.70535 | -4.1709e-11 | -5.0157e-11 | 0.51872 | -0.9991 | 3.543 | 40.6694 | 3.9403 | -133.9452 | -140.3506 | -176.128 | 46.1194 |  | 1.1868 | 0 | 0 | 1.0881 | 0.23105 | 0.26648 | 4.4864 | 0 | 0 | 11.1536 | 167.993 | 108.0318

## LLG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.57165 | 2.4993 | 2.6834 | 0.57319 | 2.4991 | 2.683 | 6.6008 | 28.8589 | 30.985 | 6.6187 | 28.8572 | 30.9811 | 0.37054 | 12.6997 | 12.0986 | -0.28379 | -6.1195 | -4.9118 | 7.5998 | 2.1477 | 12.1119 | -7.5494 | 0.44273 | -6.6298 | -80.5953 | -160.2678 | 36.7778 | 99.4473 | 19.7688 | -143.2556 |  | 1.1527 | 0.44631 | 0.55251 | 1.1414 | 0.21262 | 0.26633 | 6.6134 | -150.6689 | 81.8093 | 7.2945 | -164.3692 | 90.2111
Line_1 | 0.3127 | 1.9169 | 1.9873 | 0.31094 | 1.9168 | 1.9882 | 3.6107 | 22.134 | 22.9479 | 3.5905 | 22.1332 | 22.9575 | 0.13937 | -6.7679e-11 | -3.1979e-11 | -0.33759 | 4.7043 | 3.8963 | -4.2829 | -4.7107e-11 | -8.0419e-11 | 4.0843 | 0.12015 | 4.7119 | 92.6226 | 14.2209 | -140.247 | -87.4306 | -165.8323 | 39.7983 |  | 1.1868 | 0 | 0 | 1.1414 | 0.21262 | 0.26633 | 4.4864 | 0 | 0 | 7.2945 | -164.3692 | 90.2111
Line_2 | 0.26864 | 0.62063 | 0.70566 | 0.2671 | 0.62035 | 0.70568 | 3.102 | 7.1664 | 8.1483 | 3.0842 | 7.1632 | 8.1485 | -0.37412 | -1.076 | -0.3753 | 0.62138 | 1.4152 | 1.0155 | -3.3545 | 1.2585 | -2.1387 | 3.4651 | -0.56289 | 1.9179 | 107.5174 | 37.4631 | -152.0153 | -72.5389 | -142.679 | 28.1116 |  | 1.0881 | 0.23105 | 0.26648 | 1.1414 | 0.21262 | 0.26633 | 11.1536 | 167.993 | 108.0318 | 7.2945 | -164.3692 | 90.2111
Line_3 | 0.087185 | 1.3683 | 1.3043 | 0.086533 | 1.3687 | 1.3051 | 1.0067 | 15.7999 | 15.0611 | 0.99919 | 15.8044 | 15.0704 | 0.96433 | -4.1534e-11 | -2.6655e-11 | -0.95552 | 3.5123 | 1.8908 | -0.70535 | -4.1709e-11 | -5.0157e-11 | 0.51872 | -0.9991 | 3.543 | 40.6694 | 3.9403 | -133.9452 | -140.3506 | -176.128 | 46.1194 |  | 1.1868 | 0 | 0 | 1.0881 | 0.23105 | 0.26648 | 4.4864 | 0 | 0 | 11.1536 | 167.993 | 108.0318

## LLG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.20297 | 0.69384 | 0.73888 | 0.20351 | 0.69374 | 0.73876 | 2.3436 | 8.0117 | 8.5318 | 2.35 | 8.0107 | 8.5304 | 1.1083 | 6.2444 | 4.4426 | -1.1012 | -5.723 | -3.8917 | 2.162 | 2.3003 | 6.2775 | -2.1564 | -2.1154 | -5.838 | -59.6945 | -147.2339 | 55.0469 | 120.3386 | 32.8118 | -124.9956 |  | 1.0366 | 0.83061 | 0.90139 | 1.0303 | 0.76166 | 0.8225 | 3.1655 | -127.0111 | 109.76 | 3.2863 | -126.9021 | 111.3167
Line_1 | 0.11035 | 0.53942 | 0.5494 | 0.10973 | 0.53945 | 0.54971 | 1.2743 | 6.2286 | 6.344 | 1.2671 | 6.229 | 6.3475 | -0.47681 | -3.8313 | -2.8961 | 0.44777 | 4.2399 | 3.2057 | -1.2526 | -2.1445 | -3.7126 | 1.2264 | 2.129 | 4.1208 | 113.3789 | 26.5019 | -120.8596 | -66.6559 | -153.5642 | 59.1969 |  | 1.0518 | 0.7049 | 0.74221 | 1.0303 | 0.76166 | 0.8225 | 2.5386 | -124.2607 | 111.1836 | 3.2863 | -126.9021 | 111.3167
Line_2 | 0.096081 | 0.16872 | 0.19472 | 0.095536 | 0.16863 | 0.19471 | 1.1094 | 1.9482 | 2.2485 | 1.1032 | 1.9472 | 2.2483 | -0.6251 | -1.4606 | -0.62772 | 0.65345 | 1.483 | 0.68601 | -0.91987 | 0.079286 | -1.7459 | 0.93002 | -0.013542 | 1.7173 | 128.4151 | 53.805 | -137.0686 | -51.6211 | -126.3789 | 43.0926 |  | 1.0024 | 0.75085 | 0.82513 | 1.0303 | 0.76166 | 0.8225 | 4.2168 | -129.3021 | 113.1554 | 3.2863 | -126.9021 | 111.3167
Line_3 | 0.030526 | 0.39695 | 0.3664 | 0.030289 | 0.39715 | 0.36672 | 0.35248 | 4.5836 | 4.2308 | 0.34975 | 4.5859 | 4.2345 | 0.20461 | -2.4589 | -2.2758 | -0.20703 | 2.8038 | 2.4513 | -0.30916 | -2.096 | -2.1637 | 0.28295 | 1.9987 | 2.4899 | 59.0406 | 15.2948 | -112.3698 | -121.9746 | -164.7852 | 67.7075 |  | 1.0518 | 0.7049 | 0.74221 | 1.0024 | 0.75085 | 0.82513 | 2.5386 | -124.2607 | 111.1836 | 4.2168 | -129.3021 | 113.1554

## LLG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.20297 | 0.69384 | 0.73888 | 0.20351 | 0.69374 | 0.73876 | 2.3436 | 8.0117 | 8.5318 | 2.35 | 8.0107 | 8.5304 | 1.1083 | 6.2444 | 4.4426 | -1.1012 | -5.723 | -3.8917 | 2.162 | 2.3003 | 6.2775 | -2.1564 | -2.1154 | -5.838 | -59.6945 | -147.2339 | 55.0469 | 120.3386 | 32.8118 | -124.9956 |  | 1.0366 | 0.83061 | 0.90139 | 1.0303 | 0.76166 | 0.8225 | 3.1655 | -127.0111 | 109.76 | 3.2863 | -126.9021 | 111.3167
Line_1 | 0.11035 | 0.53942 | 0.5494 | 0.10973 | 0.53945 | 0.54971 | 1.2743 | 6.2286 | 6.344 | 1.2671 | 6.229 | 6.3475 | -0.47681 | -3.8313 | -2.8961 | 0.44777 | 4.2399 | 3.2057 | -1.2526 | -2.1445 | -3.7126 | 1.2264 | 2.129 | 4.1208 | 113.3789 | 26.5019 | -120.8596 | -66.6559 | -153.5642 | 59.1969 |  | 1.0518 | 0.7049 | 0.74221 | 1.0303 | 0.76166 | 0.8225 | 2.5386 | -124.2607 | 111.1836 | 3.2863 | -126.9021 | 111.3167
Line_2 | 0.096081 | 0.16872 | 0.19472 | 0.095536 | 0.16863 | 0.19471 | 1.1094 | 1.9482 | 2.2485 | 1.1032 | 1.9472 | 2.2483 | -0.6251 | -1.4606 | -0.62772 | 0.65345 | 1.483 | 0.68601 | -0.91987 | 0.079286 | -1.7459 | 0.93002 | -0.013542 | 1.7173 | 128.4151 | 53.805 | -137.0686 | -51.6211 | -126.3789 | 43.0926 |  | 1.0024 | 0.75085 | 0.82513 | 1.0303 | 0.76166 | 0.8225 | 4.2168 | -129.3021 | 113.1554 | 3.2863 | -126.9021 | 111.3167
Line_3 | 0.030526 | 0.39695 | 0.3664 | 0.030289 | 0.39715 | 0.36672 | 0.35248 | 4.5836 | 4.2308 | 0.34975 | 4.5859 | 4.2345 | 0.20461 | -2.4589 | -2.2758 | -0.20703 | 2.8038 | 2.4513 | -0.30916 | -2.096 | -2.1637 | 0.28295 | 1.9987 | 2.4899 | 59.0406 | 15.2948 | -112.3698 | -121.9746 | -164.7852 | 67.7075 |  | 1.0518 | 0.7049 | 0.74221 | 1.0024 | 0.75085 | 0.82513 | 2.5386 | -124.2607 | 111.1836 | 4.2168 | -129.3021 | 113.1554