## LLL_max_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 2.1655 | 2.1655 | 0 | 0 | 1.5003 | 1.5003 | 0.62119 | -0.48051 | 1.2215 | -0.94013 | -66.3744 | 113.6256 | 0.91339 | 0.70372 | -3.33 | -3.4464
Line10_11_12 | 0.20111 | 0.20111 | 0 | 0 | 0.13933 | 0.13933 | -0.051928 | 0.053141 | -0.1221 | 0.12452 | 109.5602 | -70.4398 | 0.95226 | 0.9717 | -3.4802 | -3.5508
Line11_12_13 | 0.20111 | 0.20111 | 0 | 0 | 0.13933 | 0.13933 | -0.053141 | 0.054355 | -0.12452 | 0.12695 | 109.5602 | -70.4398 | 0.9717 | 0.99113 | -3.5508 | -3.6186
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.99113 | 0.99113 | -3.6186 | -3.6186
Line13_13_14 | 0.20111 | 0.20111 | 0 | 0 | 0.13933 | 0.13933 | -0.054355 | 0.055568 | -0.12695 | 0.12938 | 109.5602 | -70.4398 | 0.99113 | 1.0106 | -3.6186 | -3.6838
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.99113 | 0.99113 | -3.6186 | -3.6186
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.99113 | 0.99113 | -3.6186 | -3.6186
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.93836 | 0.93836 | -3.4491 | -3.4491
Line17_5_19 | 0.24142 | 0.24142 | 0 | 0 | 0.16726 | 0.16726 | -0.059808 | 0.061557 | -0.14481 | 0.14831 | 109.0058 | -70.9942 | 0.93671 | 0.96002 | -3.4355 | -3.5358
Line1_1_3 | 0.20111 | 0.20111 | 0 | 0 | 0.13933 | 0.13933 | -0.049501 | 0.050715 | -0.11724 | 0.11967 | 109.5602 | -70.4398 | 0.91339 | 0.93283 | -3.33 | -3.4067
Line2_1_4 | 0.25865 | 0.25865 | 0 | 0 | 0.1792 | 0.1792 | -0.061576 | 0.063583 | -0.15165 | 0.15567 | 108.769 | -71.231 | 0.91339 | 0.93836 | -3.33 | -3.4491
Line3_1_5 | 0.24142 | 0.24142 | 0 | 0 | 0.16726 | 0.16726 | -0.05806 | 0.059808 | -0.14131 | 0.14481 | 109.0058 | -70.9942 | 0.91339 | 0.93671 | -3.33 | -3.4355
Line4_2_6 | 2.1655 | 2.1655 | 0 | 0 | 1.5003 | 1.5003 | 0.48051 | -0.33982 | 0.94013 | -0.65876 | -66.3744 | 113.6256 | 0.70372 | 0.49406 | -3.4464 | -3.6615
Line5_6_7 | 2.1655 | 2.1655 | 0 | 0 | 1.5003 | 1.5003 | 0.33982 | -0.19914 | 0.65876 | -0.37739 | -66.3744 | 113.6256 | 0.49406 | 0.28442 | -3.6615 | -4.1938
Line6_7_8 | 2.9374 | 2.9374 | 0 | 5.3526 | 2.0351 | 2.0351 | 0.25885 | -1e-07 | 0.51771 | -1e-07 | -67.6287 | 112.3713 | 0.28442 | 0 | -4.1938 | 0
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 5.9243e-22 | 0 | 2.8476e-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 5.9243e-22 | 0 | 2.8476e-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Line9_3_11 | 0.20111 | 0.20111 | 0 | 0 | 0.13933 | 0.13933 | -0.050715 | 0.051928 | -0.11967 | 0.1221 | 109.5602 | -70.4398 | 0.93283 | 0.95226 | -3.4067 | -3.4802

## LLL_max_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 2.2579 | 2.2579 | 0 | 0 | 1.5643 | 1.5643 | 0.67276 | -0.51982 | 1.3243 | -1.0184 | -66.5264 | 113.4736 | 0.94951 | 0.73089 | -3.4584 | -3.5682
Line10_11_12 | 0.20786 | 0.20786 | 0 | 0 | 0.14401 | 0.14401 | -0.056633 | 0.057929 | -0.13079 | 0.13338 | 109.8207 | -70.1793 | 0.98969 | 1.0098 | -3.592 | -3.6548
Line11_12_13 | 0.20786 | 0.20786 | 0 | 0 | 0.14401 | 0.14401 | -0.057929 | 0.059225 | -0.13338 | 0.13598 | 109.8207 | -70.1793 | 1.0098 | 1.0299 | -3.6548 | -3.7151
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0299 | 1.0299 | -3.7151 | -3.7151
Line13_13_14 | 0.20786 | 0.20786 | 0 | 0 | 0.14401 | 0.14401 | -0.059225 | 0.060521 | -0.13598 | 0.13857 | 109.8207 | -70.1793 | 1.0299 | 1.05 | -3.7151 | -3.7731
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0299 | 1.0299 | -3.7151 | -3.7151
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0299 | 1.0299 | -3.7151 | -3.7151
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97508 | 0.97508 | -3.5655 | -3.5655
Line17_5_19 | 0.24786 | 0.24786 | 0 | 0 | 0.17173 | 0.17173 | -0.064826 | 0.066669 | -0.15409 | 0.15777 | 109.264 | -70.736 | 0.97345 | 0.9974 | -3.5531 | -3.6432
Line1_1_3 | 0.20786 | 0.20786 | 0 | 0 | 0.14401 | 0.14401 | -0.05404 | 0.055336 | -0.12561 | 0.1282 | 109.8207 | -70.1793 | 0.94951 | 0.9696 | -3.4584 | -3.5266
Line2_1_4 | 0.2648 | 0.2648 | 0 | 0 | 0.18346 | 0.18346 | -0.066624 | 0.068728 | -0.16095 | 0.16516 | 109.0286 | -70.9714 | 0.94951 | 0.97508 | -3.4584 | -3.5655
Line3_1_5 | 0.24786 | 0.24786 | 0 | 0 | 0.17173 | 0.17173 | -0.062983 | 0.064826 | -0.1504 | 0.15409 | 109.264 | -70.736 | 0.94951 | 0.97345 | -3.4584 | -3.5531
Line4_2_6 | 2.2579 | 2.2579 | 0 | 0 | 1.5643 | 1.5643 | 0.51982 | -0.36687 | 1.0184 | -0.71247 | -66.5264 | 113.4736 | 0.73089 | 0.51228 | -3.5682 | -3.7716
Line5_6_7 | 2.2579 | 2.2579 | 0 | 0 | 1.5643 | 1.5643 | 0.36687 | -0.21392 | 0.71247 | -0.40657 | -66.5264 | 113.4736 | 0.51228 | 0.29368 | -3.7716 | -4.2779
Line6_7_8 | 3.0331 | 3.0331 | 0 | 5.5337 | 2.1014 | 2.1014 | 0.276 | -1e-07 | 0.552 | -1e-07 | -67.7129 | 112.2871 | 0.29368 | 0 | -4.2779 | 0
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3826e-22 | 0 | -2.7324e-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3826e-22 | 0 | -2.7324e-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Line9_3_11 | 0.20786 | 0.20786 | 0 | 0 | 0.14401 | 0.14401 | -0.055336 | 0.056633 | -0.1282 | 0.13079 | 109.8207 | -70.1793 | 0.9696 | 0.98969 | -3.5266 | -3.592

## LLL_max_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 0.086596 | 0.086596 | 0 | 0 | 0.059995 | 0.059995 | -0.01816 | 0.018385 | -0.063081 | 0.063531 | 106.0786 | -73.9214 | 1.0941 | 1.1024 | 0.018543 | -0.06091
Line10_11_12 | 0.10173 | 0.10173 | 0 | 0 | 0.070478 | 0.070478 | -0.0037087 | 0.0040192 | -0.078293 | 0.078914 | 92.3135 | -87.6865 | 1.1121 | 1.1211 | -0.39862 | -0.60218
Line11_12_13 | 0.10173 | 0.10173 | 0 | 0 | 0.070478 | 0.070478 | -0.0040192 | 0.0043296 | -0.078914 | 0.079535 | 92.3135 | -87.6865 | 1.1211 | 1.1302 | -0.60218 | -0.80249
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1302 | 1.1302 | -0.80249 | -0.80249
Line13_13_14 | 0.10173 | 0.10173 | 0 | 0 | 0.070478 | 0.070478 | -0.0043296 | 0.0046401 | -0.079535 | 0.080155 | 92.3135 | -87.6865 | 1.1302 | 1.1392 | -0.80249 | -0.99961
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1302 | 1.1302 | -0.80249 | -0.80249
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1302 | 1.1302 | -0.80249 | -0.80249
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1057 | 1.1057 | -0.24429 | -0.24429
Line17_5_19 | 0.12147 | 0.12147 | 0 | 0 | 0.084155 | 0.084155 | -0.0046676 | 0.0051102 | -0.092865 | 0.09375 | 92.6485 | -87.3515 | 1.1049 | 1.1157 | -0.22889 | -0.47154
Line1_1_3 | 0.10173 | 0.10173 | 0 | 0 | 0.070478 | 0.070478 | -0.0030878 | 0.0033983 | -0.077051 | 0.077672 | 92.3134 | -87.6866 | 1.0941 | 1.1031 | 0.018543 | -0.19174
Line2_1_4 | 0.12985 | 0.12985 | 0 | 0 | 0.089963 | 0.089963 | -0.0047636 | 0.0052694 | -0.098316 | 0.099328 | 92.7924 | -87.2076 | 1.0941 | 1.1057 | 0.018543 | -0.24429
Line3_1_5 | 0.12147 | 0.12147 | 0 | 0 | 0.084155 | 0.084155 | -0.0042249 | 0.0046676 | -0.09198 | 0.092865 | 92.6485 | -87.3515 | 1.0941 | 1.1049 | 0.018543 | -0.22889
Line4_2_6 | 0.086596 | 0.086596 | 0 | 0 | 0.059995 | 0.059995 | -0.018385 | 0.01861 | -0.063531 | 0.063981 | 106.0786 | -73.9214 | 1.1024 | 1.1106 | -0.06091 | -0.13918
Line5_6_7 | 0.086596 | 0.086596 | 0 | 0 | 0.059995 | 0.059995 | -0.01861 | 0.018835 | -0.063981 | 0.064431 | 106.0786 | -73.9214 | 1.1106 | 1.1189 | -0.13918 | -0.2163
Line6_7_8 | 0.036433 | 0.036433 | 0 | 0.066389 | 0.025242 | 0.025242 | 0.01995 | -0.019911 | 0.01999 | -0.019911 | -45.2734 | 134.7266 | 1.1189 | 1.1155 | -0.2163 | -0.27343
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 8.0426e-10 | 0 | 6.1487e-11 | 0 | 0 | 0 | 1.1155 | 1.1155 | -0.27343 | -0.27343
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 8.0426e-10 | 0 | 6.1487e-11 | 0 | 0 | 0 | 1.1155 | 1.1155 | -0.27343 | -0.27343
Line9_3_11 | 0.10173 | 0.10173 | 0 | 0 | 0.070478 | 0.070478 | -0.0033983 | 0.0037087 | -0.077672 | 0.078293 | 92.3134 | -87.6866 | 1.1031 | 1.1121 | -0.19174 | -0.39862

## LLL_max_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 0.086049 | 0.086049 | 0 | 0 | 0.059616 | 0.059616 | -0.018151 | 0.018373 | -0.06589 | 0.066334 | 105.4174 | -74.5826 | 1.1464 | 1.1546 | 0.015822 | -0.064227
Line10_11_12 | 0.10289 | 0.10289 | 0 | 0 | 0.071285 | 0.071285 | -0.0040702 | 0.0043878 | -0.082919 | 0.083555 | 92.4249 | -87.5751 | 1.1646 | 1.1737 | -0.38532 | -0.58122
Line11_12_13 | 0.10289 | 0.10289 | 0 | 0 | 0.071285 | 0.071285 | -0.0043878 | 0.0047054 | -0.083555 | 0.08419 | 92.4249 | -87.5751 | 1.1737 | 1.1829 | -0.58122 | -0.77409
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1829 | 1.1829 | -0.77409 | -0.77409
Line13_13_14 | 0.10289 | 0.10289 | 0 | 0 | 0.071285 | 0.071285 | -0.0047054 | 0.005023 | -0.08419 | 0.084825 | 92.4249 | -87.5751 | 1.1829 | 1.192 | -0.77409 | -0.96401
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1829 | 1.1829 | -0.77409 | -0.77409
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1829 | 1.1829 | -0.77409 | -0.77409
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.158 | 1.158 | -0.23465 | -0.23465
Line17_5_19 | 0.12206 | 0.12206 | 0 | 0 | 0.084566 | 0.084566 | -0.0050759 | 0.0055229 | -0.09773 | 0.098624 | 92.7526 | -87.2474 | 1.1572 | 1.1681 | -0.22058 | -0.45259
Line1_1_3 | 0.10289 | 0.10289 | 0 | 0 | 0.071285 | 0.071285 | -0.003435 | 0.0037526 | -0.081649 | 0.082284 | 92.4249 | -87.5751 | 1.1464 | 1.1555 | 0.015822 | -0.18633
Line2_1_4 | 0.13013 | 0.13013 | 0 | 0 | 0.090154 | 0.090154 | -0.0051861 | 0.0056941 | -0.10322 | 0.10424 | 92.8921 | -87.1079 | 1.1464 | 1.158 | 0.015822 | -0.23465
Line3_1_5 | 0.12206 | 0.12206 | 0 | 0 | 0.084566 | 0.084566 | -0.004629 | 0.0050759 | -0.096836 | 0.09773 | 92.7526 | -87.2474 | 1.1464 | 1.1572 | 0.015822 | -0.22058
Line4_2_6 | 0.086049 | 0.086049 | 0 | 0 | 0.059616 | 0.059616 | -0.018373 | 0.018595 | -0.066334 | 0.066778 | 105.4174 | -74.5826 | 1.1546 | 1.1628 | -0.064227 | -0.14315
Line5_6_7 | 0.086049 | 0.086049 | 0 | 0 | 0.059616 | 0.059616 | -0.018595 | 0.018817 | -0.066778 | 0.067223 | 105.4174 | -74.5826 | 1.1628 | 1.1709 | -0.14315 | -0.22097
Line6_7_8 | 0.038128 | 0.038128 | 0 | 0.069562 | 0.026416 | 0.026416 | 0.02185 | -0.021806 | 0.021894 | -0.021806 | -45.2781 | 134.7219 | 1.1709 | 1.1674 | -0.22097 | -0.27809
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 8.6611e-10 | 0 | 6.8562e-11 | 0 | 0 | 0 | 1.1674 | 1.1674 | -0.27809 | -0.27809
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 8.6611e-10 | 0 | 6.8562e-11 | 0 | 0 | 0 | 1.1674 | 1.1674 | -0.27809 | -0.27809
Line9_3_11 | 0.10289 | 0.10289 | 0 | 0 | 0.071285 | 0.071285 | -0.0037526 | 0.0040702 | -0.082284 | 0.082919 | 92.4249 | -87.5751 | 1.1555 | 1.1646 | -0.18633 | -0.38532

## LLL_min_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 1.6788 | 1.6788 | 0 | 0 | 1.1631 | 1.1631 | 0.65091 | -0.48857 | 0.67724 | -0.50813 | -52.7965 | 127.2035 | 0.80758 | 0.60604 | -6.661 | -6.6721
Line10_11_12 | 0.0028558 | 0.0028558 | 0 | 0 | 0.0019785 | 0.0019785 | -0.0013252 | 0.0013256 | -0.00089516 | 0.00089565 | 139.3098 | -40.6902 | 0.80825 | 0.80859 | -6.6507 | -6.6456
Line11_12_13 | 0.0028558 | 0.0028558 | 0 | 0 | 0.0019785 | 0.0019785 | -0.0013256 | 0.0013261 | -0.00089565 | 0.00089614 | 139.3097 | -40.6903 | 0.80859 | 0.80892 | -6.6456 | -6.6405
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80892 | 0.80892 | -6.6405 | -6.6405
Line13_13_14 | 0.0028558 | 0.0028558 | 0 | 0 | 0.0019785 | 0.0019785 | -0.0013261 | 0.0013266 | -0.00089614 | 0.00089663 | 139.3095 | -40.6905 | 0.80892 | 0.80926 | -6.6405 | -6.6354
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80892 | 0.80892 | -6.6405 | -6.6405
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80892 | 0.80892 | -6.6405 | -6.6405
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80792 | 0.80792 | -6.6559 | -6.6559
Line17_5_19 | 0.0028708 | 0.0028708 | 0 | 0 | 0.001989 | 0.001989 | -0.0013292 | 0.0013297 | -0.00090294 | 0.00090343 | 139.1565 | -40.8435 | 0.80792 | 0.80826 | -6.6559 | -6.6508
Line1_1_3 | 0.0028558 | 0.0028558 | 0 | 0 | 0.0019785 | 0.0019785 | -0.0013242 | 0.0013247 | -0.00089418 | 0.00089466 | 139.3099 | -40.6901 | 0.80758 | 0.80792 | -6.661 | -6.6558
Line2_1_4 | 0.0028759 | 0.0028759 | 0 | 0 | 0.0019925 | 0.0019925 | -0.0013303 | 0.0013308 | -0.00090522 | 0.00090571 | 139.1052 | -40.8948 | 0.80758 | 0.80792 | -6.661 | -6.6559
Line3_1_5 | 0.0028708 | 0.0028708 | 0 | 0 | 0.001989 | 0.001989 | -0.0013288 | 0.0013293 | -0.00090244 | 0.00090293 | 139.1566 | -40.8434 | 0.80758 | 0.80792 | -6.661 | -6.6559
Line4_2_6 | 1.6788 | 1.6788 | 0 | 0 | 1.1631 | 1.1631 | 0.48857 | -0.32622 | 0.50813 | -0.33902 | -52.7965 | 127.2035 | 0.60604 | 0.40449 | -6.6721 | -6.6945
Line5_6_7 | 1.6788 | 1.6788 | 0 | 0 | 1.1631 | 1.1631 | 0.32622 | -0.16387 | 0.33902 | -0.16991 | -52.7965 | 127.2035 | 0.40449 | 0.20295 | -6.6945 | -6.7611
Line6_7_8 | 1.6905 | 1.6905 | 0 | 2.6836 | 1.1712 | 1.1712 | 0.16461 | -1e-07 | 0.17147 | -1e-07 | -52.9302 | 127.0698 | 0.20295 | 0 | -6.7611 | 0
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7639e-22 | 0 | 8.9208e-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7639e-22 | 0 | 8.9208e-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Line9_3_11 | 0.0028558 | 0.0028558 | 0 | 0 | 0.0019785 | 0.0019785 | -0.0013247 | 0.0013252 | -0.00089467 | 0.00089515 | 139.3098 | -40.6902 | 0.80792 | 0.80825 | -6.6558 | -6.6507

## LLL_min_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 1.5905 | 1.5905 | 0 | 0 | 1.1019 | 1.1019 | 0.5842 | -0.43849 | 0.60783 | -0.45605 | -52.7965 | 127.2035 | 0.76508 | 0.57414 | -6.661 | -6.6721
Line10_11_12 | 0.0027055 | 0.0027055 | 0 | 0 | 0.0018744 | 0.0018744 | -0.0011893 | 0.0011898 | -0.00080341 | 0.00080385 | 139.3098 | -40.6902 | 0.76571 | 0.76603 | -6.6507 | -6.6456
Line11_12_13 | 0.0027055 | 0.0027055 | 0 | 0 | 0.0018744 | 0.0018744 | -0.0011898 | 0.0011902 | -0.00080385 | 0.00080429 | 139.3097 | -40.6903 | 0.76603 | 0.76635 | -6.6456 | -6.6405
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76635 | 0.76635 | -6.6405 | -6.6405
Line13_13_14 | 0.0027055 | 0.0027055 | 0 | 0 | 0.0018744 | 0.0018744 | -0.0011902 | 0.0011906 | -0.00080429 | 0.00080473 | 139.3095 | -40.6905 | 0.76635 | 0.76667 | -6.6405 | -6.6354
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76635 | 0.76635 | -6.6405 | -6.6405
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76635 | 0.76635 | -6.6405 | -6.6405
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7654 | 0.7654 | -6.6559 | -6.6559
Line17_5_19 | 0.0027197 | 0.0027197 | 0 | 0 | 0.0018843 | 0.0018843 | -0.001193 | 0.0011934 | -0.00081039 | 0.00081084 | 139.1565 | -40.8435 | 0.7654 | 0.76572 | -6.6559 | -6.6508
Line1_1_3 | 0.0027055 | 0.0027055 | 0 | 0 | 0.0018744 | 0.0018744 | -0.0011885 | 0.0011889 | -0.00080253 | 0.00080297 | 139.3099 | -40.6901 | 0.76508 | 0.7654 | -6.661 | -6.6558
Line2_1_4 | 0.0027245 | 0.0027245 | 0 | 0 | 0.0018876 | 0.0018876 | -0.001194 | 0.0011944 | -0.00081244 | 0.00081289 | 139.1052 | -40.8948 | 0.76508 | 0.7654 | -6.661 | -6.6559
Line3_1_5 | 0.0027197 | 0.0027197 | 0 | 0 | 0.0018843 | 0.0018843 | -0.0011926 | 0.001193 | -0.00080995 | 0.00081039 | 139.1566 | -40.8434 | 0.76508 | 0.7654 | -6.661 | -6.6559
Line4_2_6 | 1.5905 | 1.5905 | 0 | 0 | 1.1019 | 1.1019 | 0.43849 | -0.29278 | 0.45605 | -0.30427 | -52.7965 | 127.2035 | 0.57414 | 0.3832 | -6.6721 | -6.6945
Line5_6_7 | 1.5905 | 1.5905 | 0 | 0 | 1.1019 | 1.1019 | 0.29278 | -0.14708 | 0.30427 | -0.15249 | -52.7965 | 127.2035 | 0.3832 | 0.19227 | -6.6945 | -6.7611
Line6_7_8 | 1.6016 | 1.6016 | 0 | 2.5424 | 1.1096 | 1.1096 | 0.14774 | -1e-07 | 0.1539 | -1e-07 | -52.9302 | 127.0698 | 0.19227 | 0 | -6.7611 | 0
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0562e-22 | 0 | 8.0069e-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0562e-22 | 0 | 8.0069e-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Line9_3_11 | 0.0027055 | 0.0027055 | 0 | 0 | 0.0018744 | 0.0018744 | -0.0011889 | 0.0011893 | -0.00080297 | 0.00080341 | 139.3098 | -40.6902 | 0.7654 | 0.76571 | -6.6558 | -6.6507

## LLL_min_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 0.030262 | 0.030262 | 0 | 0 | 0.020966 | 0.020966 | 0.014076 | -0.014024 | 0.01402 | -0.013965 | -45.0087 | 134.9913 | 0.94759 | 0.94396 | -0.12299 | -0.12793
Line10_11_12 | 5.1477e-05 | 5.1477e-05 | 0 | 0 | 3.5665e-05 | 3.5665e-05 | -2.8414e-05 | 2.8414e-05 | -1.8297e-05 | 1.8298e-05 | 147.0975 | -32.9025 | 0.9476 | 0.94761 | -0.12282 | -0.12273
Line11_12_13 | 5.1477e-05 | 5.1477e-05 | 0 | 0 | 3.5665e-05 | 3.5665e-05 | -2.8414e-05 | 2.8414e-05 | -1.8298e-05 | 1.8298e-05 | 147.0975 | -32.9025 | 0.94761 | 0.94761 | -0.12273 | -0.12265
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94761 | 0.94761 | -0.12265 | -0.12265
Line13_13_14 | 5.1477e-05 | 5.1477e-05 | 0 | 0 | 3.5665e-05 | 3.5665e-05 | -2.8414e-05 | 2.8415e-05 | -1.8298e-05 | 1.8298e-05 | 147.0973 | -32.9027 | 0.94761 | 0.94762 | -0.12265 | -0.12256
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94761 | 0.94761 | -0.12265 | -0.12265
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94761 | 0.94761 | -0.12265 | -0.12265
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9476 | 0.9476 | -0.12291 | -0.12291
Line17_5_19 | 5.1748e-05 | 5.1748e-05 | 0 | 0 | 3.5852e-05 | 3.5852e-05 | -2.8514e-05 | 2.8514e-05 | -1.847e-05 | 1.847e-05 | 146.9443 | -33.0557 | 0.9476 | 0.9476 | -0.12291 | -0.12282
Line1_1_3 | 5.1477e-05 | 5.1477e-05 | 0 | 0 | 3.5665e-05 | 3.5665e-05 | -2.8414e-05 | 2.8414e-05 | -1.8297e-05 | 1.8297e-05 | 147.0976 | -32.9024 | 0.94759 | 0.9476 | -0.12299 | -0.12291
Line2_1_4 | 5.1839e-05 | 5.1839e-05 | 0 | 0 | 3.5915e-05 | 3.5915e-05 | -2.8548e-05 | 2.8548e-05 | -1.8528e-05 | 1.8528e-05 | 146.893 | -33.107 | 0.94759 | 0.9476 | -0.12299 | -0.12291
Line3_1_5 | 5.1748e-05 | 5.1748e-05 | 0 | 0 | 3.5852e-05 | 3.5852e-05 | -2.8514e-05 | 2.8514e-05 | -1.847e-05 | 1.847e-05 | 146.9443 | -33.0557 | 0.94759 | 0.9476 | -0.12299 | -0.12291
Line4_2_6 | 0.030262 | 0.030262 | 0 | 0 | 0.020966 | 0.020966 | 0.014024 | -0.013971 | 0.013965 | -0.01391 | -45.0087 | 134.9913 | 0.94396 | 0.94033 | -0.12793 | -0.13291
Line5_6_7 | 0.030262 | 0.030262 | 0 | 0 | 0.020966 | 0.020966 | 0.013971 | -0.013918 | 0.01391 | -0.013856 | -45.0087 | 134.9913 | 0.94033 | 0.93669 | -0.13291 | -0.13793
Line6_7_8 | 0.030473 | 0.030473 | 0 | 0.048374 | 0.021112 | 0.021112 | 0.013982 | -0.013929 | 0.013985 | -0.013929 | -45.1425 | 134.8575 | 0.93669 | 0.93304 | -0.13793 | -0.14249
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | -1.7407e-10 | 0 | 2.4248e-11 | 0 | 0 | 0 | 0.93304 | 0.93304 | -0.14249 | -0.14249
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | -1.7407e-10 | 0 | 2.4248e-11 | 0 | 0 | 0 | 0.93304 | 0.93304 | -0.14249 | -0.14249
Line9_3_11 | 5.1477e-05 | 5.1477e-05 | 0 | 0 | 3.5665e-05 | 3.5665e-05 | -2.8414e-05 | 2.8414e-05 | -1.8297e-05 | 1.8297e-05 | 147.0976 | -32.9024 | 0.9476 | 0.9476 | -0.12291 | -0.12282

## LLL_min_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 0.02867 | 0.02867 | 0 | 0 | 0.019863 | 0.019863 | 0.012634 | -0.012586 | 0.012583 | -0.012534 | -45.0087 | 134.9913 | 0.89772 | 0.89428 | -0.12299 | -0.12793
Line10_11_12 | 4.8768e-05 | 4.8768e-05 | 0 | 0 | 3.3788e-05 | 3.3788e-05 | -2.5502e-05 | 2.5502e-05 | -1.6422e-05 | 1.6422e-05 | 147.0975 | -32.9025 | 0.89773 | 0.89773 | -0.12282 | -0.12273
Line11_12_13 | 4.8768e-05 | 4.8768e-05 | 0 | 0 | 3.3788e-05 | 3.3788e-05 | -2.5502e-05 | 2.5502e-05 | -1.6422e-05 | 1.6422e-05 | 147.0975 | -32.9025 | 0.89773 | 0.89774 | -0.12273 | -0.12265
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89774 | 0.89774 | -0.12265 | -0.12265
Line13_13_14 | 4.8768e-05 | 4.8768e-05 | 0 | 0 | 3.3787e-05 | 3.3787e-05 | -2.5502e-05 | 2.5502e-05 | -1.6422e-05 | 1.6423e-05 | 147.0973 | -32.9027 | 0.89774 | 0.89775 | -0.12265 | -0.12256
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89774 | 0.89774 | -0.12265 | -0.12265
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89774 | 0.89774 | -0.12265 | -0.12265
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89772 | 0.89772 | -0.12291 | -0.12291
Line17_5_19 | 4.9025e-05 | 4.9025e-05 | 0 | 0 | 3.3965e-05 | 3.3965e-05 | -2.5592e-05 | 2.5592e-05 | -1.6577e-05 | 1.6577e-05 | 146.9443 | -33.0557 | 0.89772 | 0.89773 | -0.12291 | -0.12282
Line1_1_3 | 4.8768e-05 | 4.8768e-05 | 0 | 0 | 3.3788e-05 | 3.3788e-05 | -2.5502e-05 | 2.5502e-05 | -1.6422e-05 | 1.6422e-05 | 147.0976 | -32.9024 | 0.89772 | 0.89772 | -0.12299 | -0.12291
Line2_1_4 | 4.9111e-05 | 4.9111e-05 | 0 | 0 | 3.4025e-05 | 3.4025e-05 | -2.5622e-05 | 2.5622e-05 | -1.6629e-05 | 1.6629e-05 | 146.893 | -33.107 | 0.89772 | 0.89772 | -0.12299 | -0.12291
Line3_1_5 | 4.9025e-05 | 4.9025e-05 | 0 | 0 | 3.3965e-05 | 3.3965e-05 | -2.5592e-05 | 2.5592e-05 | -1.6577e-05 | 1.6577e-05 | 146.9443 | -33.0557 | 0.89772 | 0.89772 | -0.12299 | -0.12291
Line4_2_6 | 0.02867 | 0.02867 | 0 | 0 | 0.019863 | 0.019863 | 0.012586 | -0.012539 | 0.012534 | -0.012485 | -45.0087 | 134.9913 | 0.89428 | 0.89084 | -0.12793 | -0.13291
Line5_6_7 | 0.02867 | 0.02867 | 0 | 0 | 0.019863 | 0.019863 | 0.012539 | -0.012492 | 0.012485 | -0.012435 | -45.0087 | 134.9913 | 0.89084 | 0.88739 | -0.13291 | -0.13793
Line6_7_8 | 0.028869 | 0.028869 | 0 | 0.045828 | 0.020001 | 0.020001 | 0.012549 | -0.012501 | 0.012551 | -0.012501 | -45.1425 | 134.8575 | 0.88739 | 0.88393 | -0.13793 | -0.14249
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | -1.5623e-10 | 0 | 2.1763e-11 | 0 | 0 | 0 | 0.88393 | 0.88393 | -0.14249 | -0.14249
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | -1.5623e-10 | 0 | 2.1763e-11 | 0 | 0 | 0 | 0.88393 | 0.88393 | -0.14249 | -0.14249
Line9_3_11 | 4.8768e-05 | 4.8768e-05 | 0 | 0 | 3.3788e-05 | 3.3788e-05 | -2.5502e-05 | 2.5502e-05 | -1.6422e-05 | 1.6422e-05 | 147.0976 | -32.9024 | 0.89772 | 0.89773 | -0.12291 | -0.12282

## LL_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.16797 | 1.8575 | 1.9186 | 0.16797 | 1.8575 | 1.9186 | 0.038792 | 0.42897 | 0.44307 | 0.038792 | 0.42897 | 0.44307 | -0.029841 | 0.38129 | -0.078743 | 0.030123 | -0.34679 | 0.11555 | -0.030389 | 0.19259 | 0.40365 | 0.030953 | -0.12358 | -0.33003 | 135.1206 | -153.8016 | 21.4477 | -44.8794 | 26.1984 | -158.5523 | 1.0979 | 0.9958 | 0.9282 | 1.1134 | 0.85822 | 0.78921 | 0.64151 | -127.0031 | 122.4862 | 0.89895 | -134.1869 | 130.7439
Line10_11_12 | 0.099172 | 0.17114 | 0.18961 | 0.099172 | 0.17114 | 0.18961 | 0.022903 | 0.039523 | 0.043789 | 0.022903 | 0.039523 | 0.043789 | -0.0023453 | -0.024374 | -6.6003e-05 | 0.0024436 | 0.024667 | 0.00042554 | -0.025447 | -0.032526 | -0.042078 | 0.025644 | 0.033112 | 0.042797 | 95.5431 | 0.18399 | -148.4344 | -84.4569 | -179.816 | 31.5656 | 1.1158 | 1.0284 | 0.96092 | 1.1248 | 1.0447 | 0.97739 | 0.27747 | -126.6627 | 121.4757 | 0.099794 | -126.5005 | 120.9959
Line11_12_13 | 0.099172 | 0.17114 | 0.18961 | 0.099172 | 0.17114 | 0.18961 | 0.022903 | 0.039523 | 0.043789 | 0.022903 | 0.039523 | 0.043789 | -0.0024436 | -0.024667 | -0.00042554 | 0.002542 | 0.02496 | 0.00078507 | -0.025644 | -0.033112 | -0.042797 | 0.025841 | 0.033697 | 0.043516 | 95.5431 | 0.18399 | -148.4344 | -84.4569 | -179.816 | 31.5656 | 1.1248 | 1.0447 | 0.97739 | 1.1337 | 1.061 | 0.99393 | 0.099794 | -126.5005 | 120.9959 | -0.075077 | -126.3433 | 120.532
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.044e-09 | 2.0361e-10 | -6.1257e-10 | -1.044e-09 | -2.0361e-10 | 6.1257e-10 | 1.7158e-11 | 1.354e-09 | -1.0659e-10 | -1.7158e-11 | -1.354e-09 | 1.0659e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1337 | 1.061 | 0.99393 | 1.1337 | 1.061 | 0.99393 | -0.075077 | -126.3433 | 120.532 | -0.075077 | -126.3433 | 120.532
Line13_13_14 | 0.099172 | 0.17114 | 0.18961 | 0.099172 | 0.17114 | 0.18961 | 0.022903 | 0.039523 | 0.043789 | 0.022903 | 0.039523 | 0.043789 | -0.002542 | -0.02496 | -0.00078507 | 0.0026403 | 0.025252 | 0.0011446 | -0.025841 | -0.033697 | -0.043516 | 0.026037 | 0.034283 | 0.044235 | 95.5431 | 0.18399 | -148.4344 | -84.4569 | -179.816 | 31.5656 | 1.1337 | 1.061 | 0.99393 | 1.1427 | 1.0773 | 1.0105 | -0.075077 | -126.3433 | 120.532 | -0.2472 | -126.1909 | 120.0834
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.9603e-10 | 1.3574e-10 | -4.0838e-10 | -6.9603e-10 | -1.3574e-10 | 4.0838e-10 | 1.1439e-11 | 9.0265e-10 | -7.1063e-11 | -1.1439e-11 | -9.0265e-10 | 7.1063e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1337 | 1.061 | 0.99393 | 1.1337 | 1.061 | 0.99393 | -0.075077 | -126.3433 | 120.532 | -0.075077 | -126.3433 | 120.532
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4801e-10 | 6.7869e-11 | -2.0419e-10 | -3.4801e-10 | -6.7869e-11 | 2.0419e-10 | 5.7192e-12 | 4.5132e-10 | -3.5532e-11 | -5.7193e-12 | -4.5132e-10 | 3.5532e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1337 | 1.061 | 0.99393 | 1.1337 | 1.061 | 0.99393 | -0.075077 | -126.3433 | 120.532 | -0.075077 | -126.3433 | 120.532
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4287e-10 | -9.5036e-11 | -3.5103e-10 | -2.4287e-10 | 9.5037e-11 | 3.5103e-10 | -3.1982e-11 | 4.6464e-10 | -1.1615e-10 | 3.1982e-11 | -4.6464e-10 | 1.1615e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1097 | 1.0171 | 0.94854 | 1.1097 | 1.0171 | 0.94854 | 0.42892 | -126.8146 | 121.8226 | 0.42892 | -126.8146 | 121.8226
Line17_5_19 | 0.11944 | 0.20717 | 0.22389 | 0.11944 | 0.20717 | 0.22389 | 0.027584 | 0.047845 | 0.051705 | 0.027584 | 0.047845 | 0.051705 | -0.0036004 | -0.028432 | 0.00085457 | 0.0037431 | 0.028861 | -0.00035331 | -0.030373 | -0.039404 | -0.048976 | 0.030658 | 0.040263 | 0.049978 | 97.1973 | -1.0057 | -149.1327 | -82.8027 | 178.9943 | 30.8673 | 1.1088 | 1.0156 | 0.94736 | 1.1197 | 1.0354 | 0.96663 | 0.43703 | -126.8176 | 121.867 | 0.23652 | -126.6393 | 121.2724
Line1_1_3 | 0.099172 | 0.17114 | 0.18961 | 0.099172 | 0.17114 | 0.18961 | 0.022903 | 0.039523 | 0.043789 | 0.022903 | 0.039523 | 0.043789 | -0.0021486 | -0.023788 | 0.00065306 | 0.0022469 | 0.024081 | -0.00029353 | -0.025054 | -0.031354 | -0.04064 | 0.02525 | 0.03194 | 0.041359 | 95.5431 | 0.18399 | -148.4344 | -84.4569 | -179.816 | 31.5656 | 1.0979 | 0.9958 | 0.9282 | 1.1069 | 1.0121 | 0.94453 | 0.64151 | -127.0031 | 122.4862 | 0.45802 | -126.8302 | 121.9722
Line2_1_4 | 0.12831 | 0.22261 | 0.23817 | 0.12831 | 0.22261 | 0.23817 | 0.029632 | 0.051409 | 0.055004 | 0.029632 | 0.051409 | 0.055004 | -0.0040837 | -0.029724 | 0.0016783 | 0.0042483 | 0.03022 | -0.001111 | -0.032277 | -0.04168 | -0.051027 | 0.032606 | 0.042671 | 0.052162 | 97.8523 | -1.5086 | -149.3976 | -82.1477 | 178.4914 | 30.6024 | 1.0979 | 0.9958 | 0.9282 | 1.1097 | 1.0171 | 0.94854 | 0.64151 | -127.0031 | 122.4862 | 0.42892 | -126.8146 | 121.8226
Line3_1_5 | 0.11944 | 0.20717 | 0.22389 | 0.11944 | 0.20717 | 0.22389 | 0.027584 | 0.047845 | 0.051705 | 0.027584 | 0.047845 | 0.051705 | -0.0034578 | -0.028002 | 0.0013558 | 0.0036004 | 0.028432 | -0.00085457 | -0.030088 | -0.038546 | -0.047973 | 0.030373 | 0.039404 | 0.048976 | 97.1973 | -1.0057 | -149.1327 | -82.8027 | 178.9943 | 30.8673 | 1.0979 | 0.9958 | 0.9282 | 1.1088 | 1.0156 | 0.94736 | 0.64151 | -127.0031 | 122.4862 | 0.43703 | -126.8176 | 121.867
Line4_2_6 | 0.16797 | 1.8575 | 1.9186 | 0.16797 | 1.8575 | 1.9186 | 0.038792 | 0.42897 | 0.44307 | 0.038792 | 0.42897 | 0.44307 | -0.030123 | 0.34679 | -0.11555 | 0.030405 | -0.31228 | 0.15236 | -0.030953 | 0.12358 | 0.33003 | 0.031517 | -0.054579 | -0.25642 | 135.1206 | -153.8016 | 21.4477 | -44.8794 | 26.1984 | -158.5523 | 1.1134 | 0.85822 | 0.78921 | 1.1289 | 0.73902 | 0.67318 | 0.89895 | -134.1869 | 130.7439 | 1.1493 | -143.8878 | 142.166
Line5_6_7 | 0.16797 | 1.8575 | 1.9186 | 0.16797 | 1.8575 | 1.9186 | 0.038792 | 0.42897 | 0.44307 | 0.038792 | 0.42897 | 0.44307 | -0.030405 | 0.31228 | -0.15236 | 0.030688 | -0.27778 | 0.18917 | -0.031517 | 0.054579 | 0.25642 | 0.032082 | 0.014426 | -0.1828 | 135.1206 | -153.8016 | 21.4477 | -44.8794 | 26.1984 | -158.5523 | 1.1289 | 0.73902 | 0.67318 | 1.1445 | 0.64843 | 0.59372 | 1.1493 | -143.8878 | 142.166 | 1.3929 | -156.7744 | 157.4286
Line6_7_8 | 0 | 2.5094 | 2.5094 | 0 | 2.5094 | 2.5094 | 0 | 0.57952 | 0.57952 | 0 | 0.57952 | 0.57952 | 1.193e-09 | 0.37547 | -0.24954 | -1.193e-09 | -0.3125 | 0.3125 | -3.2131e-10 | 0.014991 | 0.23689 | 3.2131e-10 | 0.11095 | -0.11095 | 0 | -159.0608 | 20.9392 | 0 | 20.9392 | -159.0608 | 1.1445 | 0.64843 | 0.59372 | 1.1445 | 0.57223 | 0.57223 | 1.3929 | -156.7744 | 157.4286 | 1.3929 | -178.6071 | -178.6071
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9768e-10 | 5.3042e-11 | 1.458e-10 | -3.9768e-10 | -5.3041e-11 | -1.458e-10 | -1.0711e-10 | 1.8806e-09 | -1.9341e-09 | 1.0711e-10 | -1.8806e-09 | 1.9341e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1445 | 0.57223 | 0.57223 | 1.1445 | 0.57223 | 0.57223 | 1.3929 | -178.6071 | -178.6071 | 1.3929 | -178.6071 | -178.6071
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9768e-10 | 5.3042e-11 | 1.458e-10 | -3.9768e-10 | -5.3041e-11 | -1.458e-10 | -1.0711e-10 | 1.8806e-09 | -1.9341e-09 | 1.0711e-10 | -1.8806e-09 | 1.9341e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1445 | 0.57223 | 0.57223 | 1.1445 | 0.57223 | 0.57223 | 1.3929 | -178.6071 | -178.6071 | 1.3929 | -178.6071 | -178.6071
Line9_3_11 | 0.099172 | 0.17114 | 0.18961 | 0.099172 | 0.17114 | 0.18961 | 0.022903 | 0.039523 | 0.043789 | 0.022903 | 0.039523 | 0.043789 | -0.0022469 | -0.024081 | 0.00029353 | 0.0023453 | 0.024374 | 6.6004e-05 | -0.02525 | -0.03194 | -0.041359 | 0.025447 | 0.032526 | 0.042078 | 95.5431 | 0.18399 | -148.4344 | -84.4569 | -179.816 | 31.5656 | 1.1069 | 1.0121 | 0.94453 | 1.1158 | 1.0284 | 0.96092 | 0.45802 | -126.8302 | 121.9722 | 0.27747 | -126.6627 | 121.4757

## LL_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.16928 | 1.9371 | 1.9988 | 0.16928 | 1.9371 | 1.9988 | 0.039093 | 0.44736 | 0.4616 | 0.039093 | 0.44736 | 0.4616 | -0.031431 | 0.41506 | -0.087248 | 0.031718 | -0.37753 | 0.1272 | -0.032173 | 0.20941 | 0.43729 | 0.032746 | -0.13437 | -0.35739 | 134.9881 | -154.0648 | 21.3437 | -45.0119 | 25.9352 | -158.6563 | 1.1505 | 1.0392 | 0.966 | 1.1662 | 0.89577 | 0.82181 | 0.65631 | -127.292 | 122.6272 | 0.90203 | -134.4741 | 130.9352
Line10_11_12 | 0.10029 | 0.17683 | 0.19518 | 0.10029 | 0.17683 | 0.19518 | 0.023161 | 0.040838 | 0.045075 | 0.023161 | 0.040838 | 0.045075 | -0.002648 | -0.026745 | 0.00011666 | 0.0027486 | 0.027058 | 0.00026429 | -0.026938 | -0.0347 | -0.045057 | 0.027139 | 0.035325 | 0.045819 | 95.9246 | 0.69354 | -148.5289 | -84.0754 | -179.3065 | 31.4711 | 1.1687 | 1.0728 | 0.99962 | 1.1777 | 1.0896 | 1.0165 | 0.31048 | -126.9299 | 121.6194 | 0.14155 | -126.7572 | 121.1406
Line11_12_13 | 0.10029 | 0.17683 | 0.19518 | 0.10029 | 0.17683 | 0.19518 | 0.023161 | 0.040838 | 0.045075 | 0.023161 | 0.040838 | 0.045075 | -0.0027486 | -0.027058 | -0.00026429 | 0.0028492 | 0.02737 | 0.00064524 | -0.027139 | -0.035325 | -0.045819 | 0.02734 | 0.03595 | 0.046581 | 95.9246 | 0.69354 | -148.5289 | -84.0754 | -179.3065 | 31.4711 | 1.1777 | 1.0896 | 1.0165 | 1.1868 | 1.1064 | 1.0335 | 0.14155 | -126.7572 | 121.1406 | -0.024784 | -126.5897 | 120.6775
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1334e-09 | 1.6651e-10 | -7.5494e-10 | -1.1334e-09 | -1.6651e-10 | 7.5494e-10 | 6.2118e-12 | 1.5364e-09 | -1.4786e-10 | -6.2118e-12 | -1.5364e-09 | 1.4786e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1868 | 1.1064 | 1.0335 | 1.1868 | 1.1064 | 1.0335 | -0.024784 | -126.5897 | 120.6775 | -0.024784 | -126.5897 | 120.6775
Line13_13_14 | 0.10029 | 0.17683 | 0.19518 | 0.10029 | 0.17683 | 0.19518 | 0.023161 | 0.040838 | 0.045075 | 0.023161 | 0.040838 | 0.045075 | -0.0028492 | -0.02737 | -0.00064524 | 0.0029497 | 0.027683 | 0.0010262 | -0.02734 | -0.03595 | -0.046581 | 0.027542 | 0.036576 | 0.047343 | 95.9246 | 0.69354 | -148.5289 | -84.0754 | -179.3065 | 31.4711 | 1.1868 | 1.1064 | 1.0335 | 1.1959 | 1.1232 | 1.0506 | -0.024784 | -126.5897 | 120.6775 | -0.18859 | -126.4273 | 120.2293
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.5561e-10 | 1.1101e-10 | -5.0329e-10 | -7.5561e-10 | -1.1101e-10 | 5.0329e-10 | 4.1411e-12 | 1.0242e-09 | -9.8573e-11 | -4.1411e-12 | -1.0242e-09 | 9.8573e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1868 | 1.1064 | 1.0335 | 1.1868 | 1.1064 | 1.0335 | -0.024784 | -126.5897 | 120.6775 | -0.024784 | -126.5897 | 120.6775
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.778e-10 | 5.5505e-11 | -2.5165e-10 | -3.778e-10 | -5.5505e-11 | 2.5165e-10 | 2.0704e-12 | 5.1212e-10 | -4.9287e-11 | -2.0705e-12 | -5.1212e-10 | 4.9287e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1868 | 1.1064 | 1.0335 | 1.1868 | 1.1064 | 1.0335 | -0.024784 | -126.5897 | 120.6775 | -0.024784 | -126.5897 | 120.6775
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6579e-10 | -1.1923e-10 | -4.0754e-10 | -2.6579e-10 | 1.1923e-10 | 4.0754e-10 | -3.7342e-11 | 5.2823e-10 | -1.3693e-10 | 3.7342e-11 | -5.2823e-10 | 1.3693e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1623 | 1.0609 | 0.9867 | 1.1623 | 1.0609 | 0.9867 | 0.45638 | -127.0909 | 121.9718 | 0.45638 | -127.0909 | 121.9718
Line17_5_19 | 0.12007 | 0.21255 | 0.22897 | 0.12007 | 0.21255 | 0.22897 | 0.02773 | 0.049087 | 0.052878 | 0.02773 | 0.049087 | 0.052878 | -0.0039869 | -0.031003 | 0.0011232 | 0.004131 | 0.031454 | -0.00059893 | -0.031961 | -0.041754 | -0.052103 | 0.032249 | 0.042658 | 0.053151 | 97.574 | -0.50057 | -149.221 | -82.426 | 179.4994 | 30.779 | 1.1615 | 1.0595 | 0.98556 | 1.1725 | 1.0797 | 1.0052 | 0.46348 | -127.0944 | 122.0139 | 0.27425 | -126.9042 | 121.4246
Line1_1_3 | 0.10029 | 0.17683 | 0.19518 | 0.10029 | 0.17683 | 0.19518 | 0.023161 | 0.040838 | 0.045075 | 0.023161 | 0.040838 | 0.045075 | -0.0024468 | -0.02612 | 0.00087855 | 0.0025474 | 0.026432 | -0.0004976 | -0.026536 | -0.033449 | -0.043533 | 0.026737 | 0.034074 | 0.044295 | 95.9246 | 0.69355 | -148.5289 | -84.0754 | -179.3065 | 31.4711 | 1.1505 | 1.0392 | 0.966 | 1.1596 | 1.056 | 0.98277 | 0.65631 | -127.292 | 122.6272 | 0.48204 | -127.1081 | 122.1147
Line2_1_4 | 0.12865 | 0.2277 | 0.24293 | 0.12865 | 0.2277 | 0.24293 | 0.029712 | 0.052586 | 0.056101 | 0.029712 | 0.052586 | 0.056101 | -0.0044998 | -0.032346 | 0.0019949 | 0.0046653 | 0.032864 | -0.0014047 | -0.033887 | -0.044046 | -0.054157 | 0.034218 | 0.045083 | 0.055338 | 98.2202 | -1 | -149.4823 | -81.7798 | 179 | 30.5177 | 1.1505 | 1.0392 | 0.966 | 1.1623 | 1.0609 | 0.9867 | 0.65631 | -127.292 | 122.6272 | 0.45638 | -127.0909 | 121.9718
Line3_1_5 | 0.12007 | 0.21255 | 0.22897 | 0.12007 | 0.21255 | 0.22897 | 0.02773 | 0.049087 | 0.052878 | 0.02773 | 0.049087 | 0.052878 | -0.0038427 | -0.030551 | 0.0016475 | 0.0039869 | 0.031003 | -0.0011232 | -0.031672 | -0.040851 | -0.051054 | 0.031961 | 0.041754 | 0.052103 | 97.574 | -0.50057 | -149.221 | -82.426 | 179.4994 | 30.779 | 1.1505 | 1.0392 | 0.966 | 1.1615 | 1.0595 | 0.98556 | 0.65631 | -127.292 | 122.6272 | 0.46348 | -127.0944 | 122.0139
Line4_2_6 | 0.16928 | 1.9371 | 1.9988 | 0.16928 | 1.9371 | 1.9988 | 0.039093 | 0.44736 | 0.4616 | 0.039093 | 0.44736 | 0.4616 | -0.031718 | 0.37753 | -0.1272 | 0.032005 | -0.34001 | 0.16715 | -0.032746 | 0.13437 | 0.35739 | 0.033319 | -0.059317 | -0.27748 | 134.9881 | -154.0648 | 21.3437 | -45.0119 | 25.9352 | -158.6563 | 1.1662 | 0.89577 | 0.82181 | 1.1818 | 0.77152 | 0.70177 | 0.90203 | -134.4741 | 130.9352 | 1.1413 | -144.1689 | 142.4079
Line5_6_7 | 0.16928 | 1.9371 | 1.9988 | 0.16928 | 1.9371 | 1.9988 | 0.039093 | 0.44736 | 0.4616 | 0.039093 | 0.44736 | 0.4616 | -0.032005 | 0.34001 | -0.16715 | 0.032291 | -0.30249 | 0.2071 | -0.033319 | 0.059317 | 0.27748 | 0.033893 | 0.015732 | -0.19758 | 134.9881 | -154.0648 | 21.3437 | -45.0119 | 25.9352 | -158.6563 | 1.1818 | 0.77152 | 0.70177 | 1.1975 | 0.67707 | 0.62009 | 1.1413 | -144.1689 | 142.4079 | 1.3742 | -157.0421 | 157.6919
Line6_7_8 | 0 | 2.592 | 2.592 | 0 | 2.592 | 2.592 | 0 | 0.5986 | 0.5986 | 0 | 0.5986 | 0.5986 | 1.288e-09 | 0.40503 | -0.27066 | -1.288e-09 | -0.33784 | 0.33784 | -3.4749e-10 | 0.014729 | 0.25402 | 3.4749e-10 | 0.11964 | -0.11964 | 0 | -159.1248 | 20.8752 | 0 | 20.8752 | -159.1248 | 1.1975 | 0.67707 | 0.62009 | 1.1975 | 0.59873 | 0.59873 | 1.3742 | -157.0421 | 157.6919 | 1.3742 | -178.6258 | -178.6258
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2932e-10 | 5.7175e-11 | 1.5749e-10 | -4.2932e-10 | -5.7175e-11 | -1.5749e-10 | -1.1583e-10 | 2.0618e-09 | -2.1197e-09 | 1.1583e-10 | -2.0618e-09 | 2.1197e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1975 | 0.59873 | 0.59873 | 1.1975 | 0.59873 | 0.59873 | 1.3742 | -178.6258 | -178.6258 | 1.3742 | -178.6258 | -178.6258
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2932e-10 | 5.7175e-11 | 1.5749e-10 | -4.2932e-10 | -5.7175e-11 | -1.5749e-10 | -1.1583e-10 | 2.0618e-09 | -2.1197e-09 | 1.1583e-10 | -2.0618e-09 | 2.1197e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1975 | 0.59873 | 0.59873 | 1.1975 | 0.59873 | 0.59873 | 1.3742 | -178.6258 | -178.6258 | 1.3742 | -178.6258 | -178.6258
Line9_3_11 | 0.10029 | 0.17683 | 0.19518 | 0.10029 | 0.17683 | 0.19518 | 0.023161 | 0.040838 | 0.045075 | 0.023161 | 0.040838 | 0.045075 | -0.0025474 | -0.026432 | 0.0004976 | 0.002648 | 0.026745 | -0.00011665 | -0.026737 | -0.034074 | -0.044295 | 0.026938 | 0.0347 | 0.045057 | 95.9246 | 0.69354 | -148.5289 | -84.0754 | -179.3065 | 31.4711 | 1.1596 | 1.056 | 0.98277 | 1.1687 | 1.0728 | 0.99962 | 0.48204 | -127.1081 | 122.1147 | 0.31048 | -126.9299 | 121.6194

## LL_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.11237 | 0.092717 | 0.062508 | 0.11237 | 0.092717 | 0.062508 | 0.025952 | 0.021412 | 0.014436 | 0.025952 | 0.021412 | 0.014436 | -0.01163 | 0.00075754 | -0.0075445 | 0.011757 | -0.00067158 | 0.0075836 | -0.025955 | -0.023429 | -0.013837 | 0.026207 | 0.023601 | 0.013915 | 114.2477 | -31.9579 | -121.3437 | -65.7523 | 148.0421 | 58.6563 | 1.0959 | 1.0948 | 1.0918 | 1.1068 | 1.1027 | 1.0978 | 0.11027 | -120.1059 | 120.0555 | 0.086415 | -120.3279 | 120.0667
Line10_11_12 | 0.10086 | 0.10132 | 0.103 | 0.10086 | 0.10132 | 0.103 | 0.023293 | 0.023399 | 0.023787 | 0.023293 | 0.023399 | 0.023787 | -0.00093367 | -0.0015952 | -0.001165 | 0.0010354 | 0.0016978 | 0.0012711 | -0.025924 | -0.025989 | -0.026377 | 0.026128 | 0.026194 | 0.026589 | 91.7494 | -26.9957 | -147.842 | -88.2506 | 153.0043 | 32.158 | 1.1137 | 1.1128 | 1.1099 | 1.1226 | 1.1218 | 1.1191 | -0.31323 | -120.508 | 119.6291 | -0.51995 | -120.7042 | 119.4212
Line11_12_13 | 0.10086 | 0.10132 | 0.103 | 0.10086 | 0.10132 | 0.103 | 0.023293 | 0.023399 | 0.023787 | 0.023293 | 0.023399 | 0.023787 | -0.0010354 | -0.0016978 | -0.0012711 | 0.0011371 | 0.0018005 | 0.0013771 | -0.026128 | -0.026194 | -0.026589 | 0.026331 | 0.026399 | 0.026802 | 91.7494 | -26.9957 | -147.842 | -88.2506 | 153.0043 | 32.158 | 1.1226 | 1.1218 | 1.1191 | 1.1315 | 1.1309 | 1.1282 | -0.51995 | -120.7042 | 119.4212 | -0.72342 | -120.8973 | 119.2165
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0151e-09 | 1.0075e-09 | 9.7164e-10 | -1.0151e-09 | -1.0075e-09 | -9.7164e-10 | 1.65e-10 | 2.0454e-10 | 1.7818e-10 | -1.65e-10 | -2.0454e-10 | -1.7818e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1315 | 1.1309 | 1.1282 | 1.1315 | 1.1309 | 1.1282 | -0.72342 | -120.8973 | 119.2165 | -0.72342 | -120.8973 | 119.2165
Line13_13_14 | 0.10086 | 0.10132 | 0.103 | 0.10086 | 0.10132 | 0.103 | 0.023293 | 0.023399 | 0.023787 | 0.023293 | 0.023399 | 0.023787 | -0.0011371 | -0.0018005 | -0.0013771 | 0.0012389 | 0.0019031 | 0.0014832 | -0.026331 | -0.026399 | -0.026802 | 0.026534 | 0.026605 | 0.027014 | 91.7494 | -26.9957 | -147.842 | -88.2506 | 153.0043 | 32.158 | 1.1315 | 1.1309 | 1.1282 | 1.1404 | 1.1399 | 1.1373 | -0.72342 | -120.8973 | 119.2165 | -0.92372 | -121.0873 | 119.0152
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7674e-10 | 6.7168e-10 | 6.4776e-10 | -6.7674e-10 | -6.7168e-10 | -6.4776e-10 | 1.1e-10 | 1.3636e-10 | 1.1878e-10 | -1.1e-10 | -1.3636e-10 | -1.1878e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1315 | 1.1309 | 1.1282 | 1.1315 | 1.1309 | 1.1282 | -0.72342 | -120.8973 | 119.2165 | -0.72342 | -120.8973 | 119.2165
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3837e-10 | 3.3584e-10 | 3.2388e-10 | -3.3837e-10 | -3.3584e-10 | -3.2388e-10 | 5.5e-11 | 6.8181e-11 | 5.9392e-11 | -5.5e-11 | -6.8181e-11 | -5.9392e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1315 | 1.1309 | 1.1282 | 1.1315 | 1.1309 | 1.1282 | -0.72342 | -120.8973 | 119.2165 | -0.72342 | -120.8973 | 119.2165
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3262e-10 | 2.2851e-10 | 2.1605e-10 | -2.3262e-10 | -2.2851e-10 | -2.1605e-10 | 1.1596e-11 | 2.6722e-11 | 1.5838e-11 | -1.1596e-11 | -2.6722e-11 | -1.5838e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1073 | 1.1063 | 1.1034 | 1.1073 | 1.1063 | 1.1034 | -0.15585 | -120.3595 | 119.7864 | -0.15585 | -120.3595 | 119.7864
Line17_5_19 | 0.12038 | 0.12109 | 0.12293 | 0.12038 | 0.12109 | 0.12293 | 0.027801 | 0.027964 | 0.028389 | 0.027801 | 0.027964 | 0.028389 | -0.0012192 | -0.0019844 | -0.0014462 | 0.0013641 | 0.0021311 | 0.0015974 | -0.030739 | -0.030852 | -0.03127 | 0.031029 | 0.031145 | 0.031572 | 92.1308 | -26.6643 | -147.5496 | -87.8692 | 153.3357 | 32.4504 | 1.1065 | 1.1056 | 1.1026 | 1.1172 | 1.1164 | 1.1135 | -0.14044 | -120.3445 | 119.8023 | -0.38638 | -120.5786 | 119.554
Line1_1_3 | 0.10086 | 0.10132 | 0.103 | 0.10086 | 0.10132 | 0.103 | 0.023293 | 0.023399 | 0.023787 | 0.023293 | 0.023399 | 0.023787 | -0.00073021 | -0.0013899 | -0.00095276 | 0.00083194 | 0.0014925 | 0.0010589 | -0.025517 | -0.025578 | -0.025953 | 0.025721 | 0.025784 | 0.026165 | 91.7494 | -26.9957 | -147.842 | -88.2506 | 153.0043 | 32.158 | 1.0959 | 1.0948 | 1.0918 | 1.1048 | 1.1038 | 1.1008 | 0.11027 | -120.1059 | 120.0555 | -0.10318 | -120.3086 | 119.8406
Line2_1_4 | 0.12867 | 0.12949 | 0.13138 | 0.12867 | 0.12949 | 0.13138 | 0.029716 | 0.029905 | 0.030342 | 0.029716 | 0.029905 | 0.030342 | -0.0012413 | -0.0020456 | -0.0014578 | 0.0014068 | 0.0022133 | 0.0016304 | -0.032543 | -0.032675 | -0.033094 | 0.032874 | 0.03301 | 0.033439 | 92.2946 | -26.5236 | -147.4222 | -87.7054 | 153.4764 | 32.5778 | 1.0959 | 1.0948 | 1.0918 | 1.1073 | 1.1063 | 1.1034 | 0.11027 | -120.1059 | 120.0555 | -0.15585 | -120.3595 | 119.7864
Line3_1_5 | 0.12038 | 0.12109 | 0.12293 | 0.12038 | 0.12109 | 0.12293 | 0.027801 | 0.027964 | 0.028389 | 0.027801 | 0.027964 | 0.028389 | -0.0010743 | -0.0018378 | -0.0012951 | 0.0012192 | 0.0019844 | 0.0014462 | -0.03045 | -0.030559 | -0.030968 | 0.030739 | 0.030852 | 0.03127 | 92.1308 | -26.6643 | -147.5496 | -87.8692 | 153.3357 | 32.4504 | 1.0959 | 1.0948 | 1.0918 | 1.1065 | 1.1056 | 1.1026 | 0.11027 | -120.1059 | 120.0555 | -0.14044 | -120.3445 | 119.8023
Line4_2_6 | 0.11237 | 0.092717 | 0.062508 | 0.11237 | 0.092717 | 0.062508 | 0.025952 | 0.021412 | 0.014436 | 0.025952 | 0.021412 | 0.014436 | -0.011757 | 0.00067158 | -0.0075836 | 0.011883 | -0.00058561 | 0.0076226 | -0.026207 | -0.023601 | -0.013915 | 0.02646 | 0.023773 | 0.013993 | 114.2477 | -31.9579 | -121.3437 | -65.7523 | 148.0421 | 58.6563 | 1.1068 | 1.1027 | 1.0978 | 1.1177 | 1.1106 | 1.1039 | 0.086415 | -120.3279 | 120.0667 | 0.063021 | -120.5467 | 120.0778
Line5_6_7 | 0.11237 | 0.092717 | 0.062508 | 0.11237 | 0.092717 | 0.062508 | 0.025952 | 0.021412 | 0.014436 | 0.025952 | 0.021412 | 0.014436 | -0.011883 | 0.00058561 | -0.0076226 | 0.012009 | -0.00049965 | 0.0076617 | -0.02646 | -0.023773 | -0.013993 | 0.026712 | 0.023945 | 0.014072 | 114.2477 | -31.9579 | -121.3437 | -65.7523 | 148.0421 | 58.6563 | 1.1177 | 1.1106 | 1.1039 | 1.1285 | 1.1185 | 1.1099 | 0.063021 | -120.5467 | 120.0778 | 0.040078 | -120.7625 | 120.0888
Line6_7_8 | 0 | 0.062383 | 0.062383 | 0 | 0.062383 | 0.062383 | 0 | 0.014407 | 0.014407 | 0 | 0.014407 | 0.014407 | 9.7505e-10 | 0.015578 | 0.0039578 | -9.7505e-10 | -0.015539 | -0.0039189 | -9.1176e-12 | 0.0041213 | 0.015493 | 9.1176e-12 | -0.0040434 | -0.015415 | 0 | -135.5807 | 44.4193 | 0 | 44.4193 | -135.5807 | 1.1285 | 1.1185 | 1.1099 | 1.1285 | 1.1145 | 1.104 | 0.040078 | -120.7625 | 120.0888 | 0.040078 | -120.9954 | 120.1552
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2502e-10 | 2.6438e-10 | 2.1864e-10 | -3.2502e-10 | -2.6438e-10 | -2.1864e-10 | -3.0393e-12 | 7.4546e-11 | -1.1517e-11 | 3.0393e-12 | -7.4546e-11 | 1.1516e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1285 | 1.1145 | 1.104 | 1.1285 | 1.1145 | 1.104 | 0.040078 | -120.9954 | 120.1552 | 0.040078 | -120.9954 | 120.1552
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2502e-10 | 2.6438e-10 | 2.1864e-10 | -3.2502e-10 | -2.6438e-10 | -2.1864e-10 | -3.0392e-12 | 7.4546e-11 | -1.1517e-11 | 3.0392e-12 | -7.4546e-11 | 1.1517e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1285 | 1.1145 | 1.104 | 1.1285 | 1.1145 | 1.104 | 0.040078 | -120.9954 | 120.1552 | 0.040078 | -120.9954 | 120.1552
Line9_3_11 | 0.10086 | 0.10132 | 0.103 | 0.10086 | 0.10132 | 0.103 | 0.023293 | 0.023399 | 0.023787 | 0.023293 | 0.023399 | 0.023787 | -0.00083194 | -0.0014925 | -0.0010589 | 0.00093367 | 0.0015952 | 0.001165 | -0.025721 | -0.025784 | -0.026165 | 0.025924 | 0.025989 | 0.026377 | 91.7494 | -26.9957 | -147.842 | -88.2506 | 153.0043 | 32.158 | 1.1048 | 1.1038 | 1.1008 | 1.1137 | 1.1128 | 1.1099 | -0.10318 | -120.3086 | 119.8406 | -0.31323 | -120.508 | 119.6291

## LL_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.11316 | 0.093008 | 0.060636 | 0.11316 | 0.093008 | 0.060636 | 0.026132 | 0.021479 | 0.014003 | 0.026132 | 0.021479 | 0.014003 | -0.012193 | 0.0014746 | -0.0077217 | 0.012321 | -0.0013881 | 0.0077584 | -0.027421 | -0.024594 | -0.014033 | 0.027678 | 0.024767 | 0.014106 | 114.0837 | -33.5464 | -121.1225 | -65.9163 | 146.4536 | 58.8775 | 1.1484 | 1.1471 | 1.1438 | 1.1593 | 1.1549 | 1.1497 | 0.1121 | -120.1152 | 120.0551 | 0.087596 | -120.3386 | 120.0666
Line10_11_12 | 0.10196 | 0.10247 | 0.10425 | 0.10196 | 0.10247 | 0.10425 | 0.023547 | 0.023664 | 0.024075 | 0.023547 | 0.023664 | 0.024075 | -0.0010212 | -0.0017578 | -0.0012743 | 0.0011252 | 0.0018628 | 0.001383 | -0.027445 | -0.027521 | -0.027951 | 0.027653 | 0.027731 | 0.028168 | 91.8356 | -26.8464 | -147.7451 | -88.1644 | 153.1536 | 32.2549 | 1.1663 | 1.1653 | 1.1622 | 1.1753 | 1.1745 | 1.1714 | -0.2954 | -120.501 | 119.6445 | -0.49447 | -120.6895 | 119.4441
Line11_12_13 | 0.10196 | 0.10247 | 0.10425 | 0.10196 | 0.10247 | 0.10425 | 0.023547 | 0.023664 | 0.024075 | 0.023547 | 0.023664 | 0.024075 | -0.0011252 | -0.0018628 | -0.001383 | 0.0012292 | 0.0019678 | 0.0014917 | -0.027653 | -0.027731 | -0.028168 | 0.027861 | 0.027941 | 0.028385 | 91.8356 | -26.8464 | -147.7451 | -88.1644 | 153.1536 | 32.2549 | 1.1753 | 1.1745 | 1.1714 | 1.1843 | 1.1836 | 1.1807 | -0.49447 | -120.6895 | 119.4441 | -0.69052 | -120.875 | 119.2468
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0998e-09 | 1.0906e-09 | 1.0491e-09 | -1.0998e-09 | -1.0906e-09 | -1.0491e-09 | 1.7271e-10 | 2.1871e-10 | 1.8781e-10 | -1.7271e-10 | -2.1871e-10 | -1.8781e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1843 | 1.1836 | 1.1807 | 1.1843 | 1.1836 | 1.1807 | -0.69052 | -120.875 | 119.2468 | -0.69052 | -120.875 | 119.2468
Line13_13_14 | 0.10196 | 0.10247 | 0.10425 | 0.10196 | 0.10247 | 0.10425 | 0.023547 | 0.023664 | 0.024075 | 0.023547 | 0.023664 | 0.024075 | -0.0012292 | -0.0019678 | -0.0014917 | 0.0013331 | 0.0020728 | 0.0016003 | -0.027861 | -0.027941 | -0.028385 | 0.028069 | 0.028151 | 0.028603 | 91.8356 | -26.8464 | -147.7451 | -88.1644 | 153.1536 | 32.2549 | 1.1843 | 1.1836 | 1.1807 | 1.1934 | 1.1928 | 1.1899 | -0.69052 | -120.875 | 119.2468 | -0.88361 | -121.0576 | 119.0525
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.3318e-10 | 7.2708e-10 | 6.9942e-10 | -7.3318e-10 | -7.2708e-10 | -6.9942e-10 | 1.1514e-10 | 1.458e-10 | 1.2521e-10 | -1.1514e-10 | -1.458e-10 | -1.2521e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1843 | 1.1836 | 1.1807 | 1.1843 | 1.1836 | 1.1807 | -0.69052 | -120.875 | 119.2468 | -0.69052 | -120.875 | 119.2468
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6659e-10 | 3.6354e-10 | 3.4971e-10 | -3.6659e-10 | -3.6354e-10 | -3.4971e-10 | 5.7568e-11 | 7.2902e-11 | 6.2603e-11 | -5.7568e-11 | -7.2902e-11 | -6.2603e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1843 | 1.1836 | 1.1807 | 1.1843 | 1.1836 | 1.1807 | -0.69052 | -120.875 | 119.2468 | -0.69052 | -120.875 | 119.2468
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5418e-10 | 2.4935e-10 | 2.3498e-10 | -2.5418e-10 | -2.4935e-10 | -2.3498e-10 | 1.1565e-11 | 2.9063e-11 | 1.6411e-11 | -1.1565e-11 | -2.9063e-11 | -1.6411e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1598 | 1.1587 | 1.1555 | 1.1598 | 1.1587 | 1.1555 | -0.14166 | -120.3563 | 119.7982 | -0.14166 | -120.3563 | 119.7982
Line17_5_19 | 0.12091 | 0.12167 | 0.12361 | 0.12091 | 0.12167 | 0.12361 | 0.027923 | 0.028099 | 0.028545 | 0.027923 | 0.028099 | 0.028545 | -0.0013206 | -0.0021675 | -0.001568 | 0.0014668 | 0.0023155 | 0.0017208 | -0.032337 | -0.032464 | -0.032925 | 0.032629 | 0.032761 | 0.03323 | 92.211 | -26.523 | -147.4607 | -87.789 | 153.477 | 32.5393 | 1.1591 | 1.1579 | 1.1547 | 1.1697 | 1.1688 | 1.1657 | -0.12758 | -120.3427 | 119.8128 | -0.36288 | -120.566 | 119.575
Line1_1_3 | 0.10196 | 0.10247 | 0.10425 | 0.10196 | 0.10247 | 0.10425 | 0.023547 | 0.023664 | 0.024075 | 0.023547 | 0.023664 | 0.024075 | -0.0008133 | -0.0015478 | -0.001057 | 0.00091726 | 0.0016528 | 0.0011657 | -0.027029 | -0.027101 | -0.027516 | 0.027237 | 0.027311 | 0.027733 | 91.8356 | -26.8464 | -147.7451 | -88.1644 | 153.1536 | 32.2549 | 1.1484 | 1.1471 | 1.1438 | 1.1574 | 1.1562 | 1.153 | 0.1121 | -120.1152 | 120.0551 | -0.09323 | -120.3096 | 119.8482
Line2_1_4 | 0.12888 | 0.12976 | 0.13174 | 0.12888 | 0.12976 | 0.13174 | 0.029763 | 0.029967 | 0.030425 | 0.029763 | 0.029967 | 0.030425 | -0.0013469 | -0.0022351 | -0.0015829 | 0.001513 | 0.0024035 | 0.0017565 | -0.034153 | -0.034302 | -0.034763 | 0.034486 | 0.034638 | 0.035111 | 92.3706 | -26.387 | -147.3378 | -87.6294 | 153.613 | 32.6622 | 1.1484 | 1.1471 | 1.1438 | 1.1598 | 1.1587 | 1.1555 | 0.1121 | -120.1152 | 120.0551 | -0.14166 | -120.3563 | 119.7982
Line3_1_5 | 0.12091 | 0.12167 | 0.12361 | 0.12091 | 0.12167 | 0.12361 | 0.027923 | 0.028099 | 0.028545 | 0.027923 | 0.028099 | 0.028545 | -0.0011744 | -0.0020195 | -0.0014152 | 0.0013206 | 0.0021675 | 0.001568 | -0.032044 | -0.032168 | -0.032619 | 0.032337 | 0.032464 | 0.032925 | 92.211 | -26.523 | -147.4607 | -87.789 | 153.477 | 32.5393 | 1.1484 | 1.1471 | 1.1438 | 1.1591 | 1.1579 | 1.1547 | 0.1121 | -120.1152 | 120.0551 | -0.12758 | -120.3427 | 119.8128
Line4_2_6 | 0.11316 | 0.093008 | 0.060636 | 0.11316 | 0.093008 | 0.060636 | 0.026132 | 0.021479 | 0.014003 | 0.026132 | 0.021479 | 0.014003 | -0.012321 | 0.0013881 | -0.0077584 | 0.012449 | -0.0013016 | 0.0077952 | -0.027678 | -0.024767 | -0.014106 | 0.027934 | 0.02494 | 0.01418 | 114.0837 | -33.5464 | -121.1225 | -65.9163 | 146.4536 | 58.8775 | 1.1593 | 1.1549 | 1.1497 | 1.1703 | 1.1627 | 1.1555 | 0.087596 | -120.3386 | 120.0666 | 0.063553 | -120.5589 | 120.078
Line5_6_7 | 0.11316 | 0.093008 | 0.060636 | 0.11316 | 0.093008 | 0.060636 | 0.026132 | 0.021479 | 0.014003 | 0.026132 | 0.021479 | 0.014003 | -0.012449 | 0.0013016 | -0.0077952 | 0.012577 | -0.0012151 | 0.007832 | -0.027934 | -0.02494 | -0.01418 | 0.02819 | 0.025113 | 0.014253 | 114.0837 | -33.5464 | -121.1225 | -65.9163 | 146.4536 | 58.8775 | 1.1703 | 1.1627 | 1.1555 | 1.1812 | 1.1706 | 1.1614 | 0.063553 | -120.5589 | 120.078 | 0.039956 | -120.7763 | 120.0893
Line6_7_8 | 0 | 0.065276 | 0.065276 | 0 | 0.065276 | 0.065276 | 0 | 0.015075 | 0.015075 | 0 | 0.015075 | 0.015075 | 1.0554e-09 | 0.01706 | 0.0043306 | -1.0554e-09 | -0.017017 | -0.004288 | -9.9674e-12 | 0.0045116 | 0.016964 | 9.9674e-12 | -0.0044264 | -0.016879 | 0 | -135.5898 | 44.4102 | 0 | 44.4102 | -135.5898 | 1.1812 | 1.1706 | 1.1614 | 1.1812 | 1.1664 | 1.1552 | 0.039956 | -120.7763 | 120.0893 | 0.039956 | -121.0093 | 120.1558
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5179e-10 | 2.8466e-10 | 2.3389e-10 | -3.5179e-10 | -2.8466e-10 | -2.3389e-10 | -3.3224e-12 | 8.2867e-11 | -1.2669e-11 | 3.3224e-12 | -8.2867e-11 | 1.2669e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1812 | 1.1664 | 1.1552 | 1.1812 | 1.1664 | 1.1552 | 0.039956 | -121.0093 | 120.1558 | 0.039956 | -121.0093 | 120.1558
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5179e-10 | 2.8466e-10 | 2.3389e-10 | -3.5179e-10 | -2.8466e-10 | -2.3389e-10 | -3.3224e-12 | 8.2867e-11 | -1.2669e-11 | 3.3224e-12 | -8.2867e-11 | 1.2669e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1812 | 1.1664 | 1.1552 | 1.1812 | 1.1664 | 1.1552 | 0.039956 | -121.0093 | 120.1558 | 0.039956 | -121.0093 | 120.1558
Line9_3_11 | 0.10196 | 0.10247 | 0.10425 | 0.10196 | 0.10247 | 0.10425 | 0.023547 | 0.023664 | 0.024075 | 0.023547 | 0.023664 | 0.024075 | -0.00091726 | -0.0016528 | -0.0011657 | 0.0010212 | 0.0017578 | 0.0012743 | -0.027237 | -0.027311 | -0.027733 | 0.027445 | 0.027521 | 0.027951 | 91.8356 | -26.8464 | -147.7451 | -88.1644 | 153.1536 | 32.2549 | 1.1574 | 1.1562 | 1.153 | 1.1663 | 1.1653 | 1.1622 | -0.09323 | -120.3096 | 119.8482 | -0.2954 | -120.501 | 119.6445

## LL_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.001827 | 1.4537 | 1.4548 | 0.001827 | 1.4537 | 1.4548 | 0.00042193 | 0.33571 | 0.33598 | 0.00042193 | 0.33571 | 0.33598 | -0.00038935 | 0.28982 | 0.035582 | 0.00038941 | -0.24924 | 0.0050549 | -9.5328e-05 | 0.072735 | 0.26586 | 9.5394e-05 | -0.030471 | -0.22353 | 166.2612 | -142.7693 | 37.1748 | -13.7388 | 37.2307 | -142.8252 | 0.95003 | 0.89006 | 0.79836 | 0.95022 | 0.74796 | 0.66549 | 0.018766 | -128.6808 | 119.5518 | 0.025854 | -135.7991 | 128.4703
Line10_11_12 | 0.00041918 | 0.0024937 | 0.0021114 | 0.00041918 | 0.0024937 | 0.0021114 | 9.6805e-05 | 0.00057589 | 0.00048761 | 9.6805e-05 | 0.00057589 | 0.00048761 | -8.7758e-05 | -0.00050213 | -9.6592e-05 | 8.7761e-05 | 0.00050225 | 9.6678e-05 | 2.7522e-05 | -0.00010438 | -0.00037734 | -2.7519e-05 | 0.00010451 | 0.00037743 | -162.5636 | 39.5976 | -136.1076 | 17.4364 | -140.4024 | 43.8924 | 0.95008 | 0.89055 | 0.79881 | 0.9501 | 0.8908 | 0.79903 | 0.024202 | -128.659 | 119.5339 | 0.026919 | -128.6481 | 119.525
Line11_12_13 | 0.00041918 | 0.0024937 | 0.0021114 | 0.00041918 | 0.0024937 | 0.0021114 | 9.6805e-05 | 0.00057589 | 0.00048761 | 9.6805e-05 | 0.00057589 | 0.00048761 | -8.7761e-05 | -0.00050225 | -9.6678e-05 | 8.7765e-05 | 0.00050237 | 9.6763e-05 | 2.7519e-05 | -0.00010451 | -0.00037743 | -2.7515e-05 | 0.00010463 | 0.00037752 | -162.5636 | 39.5975 | -136.1077 | 17.4364 | -140.4025 | 43.8923 | 0.9501 | 0.8908 | 0.79903 | 0.95012 | 0.89105 | 0.79925 | 0.026919 | -128.6481 | 119.525 | 0.029637 | -128.6372 | 119.516
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2766e-12 | -4.7222e-10 | -1.3251e-09 | -1.2766e-12 | 4.7222e-10 | 1.3251e-09 | -5.1358e-12 | 1.3984e-09 | 7.0549e-11 | 5.1358e-12 | -1.3984e-09 | -7.0549e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95012 | 0.89105 | 0.79925 | 0.95012 | 0.89105 | 0.79925 | 0.029637 | -128.6372 | 119.516 | 0.029637 | -128.6372 | 119.516
Line13_13_14 | 0.00041918 | 0.0024937 | 0.0021114 | 0.00041918 | 0.0024937 | 0.0021114 | 9.6805e-05 | 0.00057589 | 0.00048761 | 9.6805e-05 | 0.00057589 | 0.00048761 | -8.7765e-05 | -0.00050237 | -9.6761e-05 | 8.7768e-05 | 0.00050249 | 9.6847e-05 | 2.7515e-05 | -0.00010463 | -0.00037752 | -2.7512e-05 | 0.00010476 | 0.00037761 | -162.5636 | 39.5973 | -136.1079 | 17.4364 | -140.4027 | 43.8921 | 0.95012 | 0.89105 | 0.79925 | 0.95014 | 0.89129 | 0.79947 | 0.029637 | -128.6372 | 119.516 | 0.032355 | -128.6264 | 119.5071
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.5108e-13 | -3.1481e-10 | -8.8338e-10 | -8.5109e-13 | 3.1481e-10 | 8.8338e-10 | -3.4239e-12 | 9.3225e-10 | 4.7033e-11 | 3.4238e-12 | -9.3225e-10 | -4.7033e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95012 | 0.89105 | 0.79925 | 0.95012 | 0.89105 | 0.79925 | 0.029637 | -128.6372 | 119.516 | 0.029637 | -128.6372 | 119.516
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2553e-13 | -1.5741e-10 | -4.4169e-10 | -4.2553e-13 | 1.5741e-10 | 4.4169e-10 | -1.7119e-12 | 4.6612e-10 | 2.3516e-11 | 1.7119e-12 | -4.6612e-10 | -2.3516e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95012 | 0.89105 | 0.79925 | 0.95012 | 0.89105 | 0.79925 | 0.029637 | -128.6372 | 119.516 | 0.029637 | -128.6372 | 119.516
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.936e-13 | -1.5942e-10 | -4.4327e-10 | -1.936e-13 | 1.5942e-10 | 4.4327e-10 | -1.2421e-12 | 4.6749e-10 | 2.2199e-11 | 1.2421e-12 | -4.6749e-10 | -2.2199e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95006 | 0.89031 | 0.79859 | 0.95006 | 0.89031 | 0.79859 | 0.021505 | -128.6699 | 119.5428 | 0.021505 | -128.6699 | 119.5428
Line17_5_19 | 0.00042299 | 0.0025055 | 0.0021203 | 0.00042299 | 0.0025055 | 0.0021203 | 9.7685e-05 | 0.00057863 | 0.00048967 | 9.7685e-05 | 0.00057863 | 0.00048967 | -8.8725e-05 | -0.00050403 | -9.5972e-05 | 8.8728e-05 | 0.00050416 | 9.6058e-05 | 2.7219e-05 | -0.00010646 | -0.00037909 | -2.7215e-05 | 0.00010659 | 0.00037918 | -162.9238 | 39.4034 | -136.2503 | 17.0762 | -140.5966 | 43.7497 | 0.95006 | 0.89031 | 0.79859 | 0.95008 | 0.89056 | 0.79881 | 0.0215 | -128.6699 | 119.5428 | 0.024234 | -128.659 | 119.5338
Line1_1_3 | 0.00041918 | 0.0024937 | 0.0021114 | 0.00041918 | 0.0024937 | 0.0021114 | 9.6805e-05 | 0.00057589 | 0.00048761 | 9.6805e-05 | 0.00057589 | 0.00048761 | -8.7751e-05 | -0.00050189 | -9.6422e-05 | 8.7755e-05 | 0.00050201 | 9.6508e-05 | 2.7529e-05 | -0.00010413 | -0.00037716 | -2.7526e-05 | 0.00010426 | 0.00037725 | -162.5636 | 39.5977 | -136.1075 | 17.4364 | -140.4023 | 43.8925 | 0.95003 | 0.89006 | 0.79836 | 0.95005 | 0.89031 | 0.79859 | 0.018766 | -128.6808 | 119.5518 | 0.021484 | -128.6699 | 119.5429
Line2_1_4 | 0.00042427 | 0.0025095 | 0.0021233 | 0.00042427 | 0.0025095 | 0.0021233 | 9.798e-05 | 0.00057954 | 0.00049036 | 9.798e-05 | 0.00057954 | 0.00049036 | -8.9047e-05 | -0.00050459 | -9.5706e-05 | 8.905e-05 | 0.00050471 | 9.5792e-05 | 2.7117e-05 | -0.00010708 | -0.00037961 | -2.7113e-05 | 0.0001072 | 0.0003797 | -163.0445 | 39.3384 | -136.2979 | 16.9555 | -140.6616 | 43.7021 | 0.95003 | 0.89006 | 0.79836 | 0.95006 | 0.89031 | 0.79859 | 0.018766 | -128.6808 | 119.5518 | 0.021505 | -128.6699 | 119.5428
Line3_1_5 | 0.00042299 | 0.0025055 | 0.0021203 | 0.00042299 | 0.0025055 | 0.0021203 | 9.7685e-05 | 0.00057863 | 0.00048967 | 9.7685e-05 | 0.00057863 | 0.00048967 | -8.8721e-05 | -0.00050391 | -9.5886e-05 | 8.8725e-05 | 0.00050403 | 9.5973e-05 | 2.7222e-05 | -0.00010634 | -0.000379 | -2.7219e-05 | 0.00010646 | 0.00037909 | -162.9238 | 39.4034 | -136.2502 | 17.0762 | -140.5966 | 43.7498 | 0.95003 | 0.89006 | 0.79836 | 0.95006 | 0.89031 | 0.79859 | 0.018766 | -128.6808 | 119.5518 | 0.0215 | -128.6699 | 119.5428
Line4_2_6 | 0.001827 | 1.4537 | 1.4548 | 0.001827 | 1.4537 | 1.4548 | 0.00042193 | 0.33571 | 0.33598 | 0.00042193 | 0.33571 | 0.33598 | -0.00038941 | 0.24924 | -0.0050549 | 0.00038948 | -0.20867 | 0.045692 | -9.5394e-05 | 0.030471 | 0.22353 | 9.5461e-05 | 0.011792 | -0.1812 | 166.2612 | -142.7693 | 37.1748 | -13.7388 | 37.2307 | -142.8252 | 0.95022 | 0.74796 | 0.66549 | 0.9504 | 0.62257 | 0.55621 | 0.025854 | -135.7991 | 128.4703 | 0.03294 | -146.0036 | 141.3276
Line5_6_7 | 0.001827 | 1.4537 | 1.4548 | 0.001827 | 1.4537 | 1.4548 | 0.00042193 | 0.33571 | 0.33598 | 0.00042193 | 0.33571 | 0.33598 | -0.00038948 | 0.20867 | -0.045692 | 0.00038954 | -0.1681 | 0.086329 | -9.5461e-05 | -0.011792 | 0.1812 | 9.5528e-05 | 0.054055 | -0.13887 | 166.2612 | -142.7693 | 37.1748 | -13.7388 | 37.2307 | -142.8252 | 0.9504 | 0.62257 | 0.55621 | 0.95059 | 0.52597 | 0.48669 | 0.03294 | -146.0036 | 141.3276 | 0.040023 | -160.5956 | 159.042
Line6_7_8 | 0 | 1.4631 | 1.4631 | 0 | 1.4631 | 1.4631 | 0 | 0.3379 | 0.3379 | 0 | 0.3379 | 0.3379 | 6.1512e-12 | 0.16938 | -0.087176 | -6.1512e-12 | -0.12828 | 0.12828 | -6.939e-12 | -0.053813 | 0.13944 | 6.9389e-12 | 0.096628 | -0.096628 | 0 | -142.9703 | 37.0297 | 0 | 37.0297 | -142.9703 | 0.95059 | 0.52597 | 0.48669 | 0.95059 | 0.47529 | 0.47529 | 0.040023 | -160.5956 | 159.042 | 0.040023 | -179.96 | -179.96
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0504e-12 | -4.89e-13 | 1.5142e-12 | -2.0505e-12 | 4.8896e-13 | -1.514e-12 | -2.313e-12 | 1.4332e-09 | -1.4344e-09 | 2.313e-12 | -1.4332e-09 | 1.4344e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95059 | 0.47529 | 0.47529 | 0.95059 | 0.47529 | 0.47529 | 0.040023 | -179.96 | -179.96 | 0.040023 | -179.96 | -179.96
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0504e-12 | -4.8896e-13 | 1.5143e-12 | -2.0504e-12 | 4.8893e-13 | -1.5142e-12 | -2.313e-12 | 1.4332e-09 | -1.4344e-09 | 2.313e-12 | -1.4332e-09 | 1.4344e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95059 | 0.47529 | 0.47529 | 0.95059 | 0.47529 | 0.47529 | 0.040023 | -179.96 | -179.96 | 0.040023 | -179.96 | -179.96
Line9_3_11 | 0.00041918 | 0.0024937 | 0.0021114 | 0.00041918 | 0.0024937 | 0.0021114 | 9.6805e-05 | 0.00057589 | 0.00048761 | 9.6805e-05 | 0.00057589 | 0.00048761 | -8.7755e-05 | -0.00050201 | -9.6507e-05 | 8.7758e-05 | 0.00050213 | 9.6593e-05 | 2.7526e-05 | -0.00010426 | -0.00037725 | -2.7522e-05 | 0.00010438 | 0.00037734 | -162.5636 | 39.5976 | -136.1075 | 17.4364 | -140.4024 | 43.8925 | 0.95005 | 0.89031 | 0.79859 | 0.95008 | 0.89055 | 0.79881 | 0.021484 | -128.6699 | 119.5429 | 0.024202 | -128.659 | 119.5339

## LL_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.0017309 | 1.3772 | 1.3783 | 0.0017309 | 1.3772 | 1.3783 | 0.00039972 | 0.31804 | 0.31829 | 0.00039972 | 0.31804 | 0.31829 | -0.00034944 | 0.26011 | 0.031935 | 0.0003495 | -0.2237 | 0.0045368 | -8.5557e-05 | 0.06528 | 0.23861 | 8.5617e-05 | -0.027348 | -0.20062 | 166.2612 | -142.7693 | 37.1748 | -13.7388 | 37.2307 | -142.8252 | 0.90003 | 0.84321 | 0.75635 | 0.90021 | 0.70859 | 0.63046 | 0.018766 | -128.6808 | 119.5518 | 0.025854 | -135.7991 | 128.4703
Line10_11_12 | 0.00039712 | 0.0023624 | 0.0020003 | 0.00039712 | 0.0023624 | 0.0020003 | 9.171e-05 | 0.00054558 | 0.00046194 | 9.171e-05 | 0.00054558 | 0.00046194 | -7.8763e-05 | -0.00045066 | -8.6692e-05 | 7.8767e-05 | 0.00045077 | 8.6769e-05 | 2.4701e-05 | -9.3684e-05 | -0.00033866 | -2.4698e-05 | 9.3796e-05 | 0.00033874 | -162.5636 | 39.5976 | -136.1076 | 17.4364 | -140.4024 | 43.8924 | 0.90007 | 0.84368 | 0.75676 | 0.90009 | 0.84392 | 0.75697 | 0.024202 | -128.659 | 119.5339 | 0.026919 | -128.6481 | 119.525
Line11_12_13 | 0.00039712 | 0.0023624 | 0.0020003 | 0.00039712 | 0.0023624 | 0.0020003 | 9.171e-05 | 0.00054558 | 0.00046194 | 9.171e-05 | 0.00054558 | 0.00046194 | -7.8767e-05 | -0.00045077 | -8.6769e-05 | 7.877e-05 | 0.00045088 | 8.6846e-05 | 2.4698e-05 | -9.3796e-05 | -0.00033874 | -2.4695e-05 | 9.3908e-05 | 0.00033882 | -162.5636 | 39.5975 | -136.1077 | 17.4364 | -140.4025 | 43.8923 | 0.90009 | 0.84392 | 0.75697 | 0.90012 | 0.84415 | 0.75718 | 0.026919 | -128.6481 | 119.525 | 0.029637 | -128.6372 | 119.516
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1458e-12 | -4.2382e-10 | -1.1893e-09 | -1.1458e-12 | 4.2382e-10 | 1.1893e-09 | -4.6094e-12 | 1.2551e-09 | 6.3318e-11 | 4.6094e-12 | -1.2551e-09 | -6.3318e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90012 | 0.84415 | 0.75718 | 0.90012 | 0.84415 | 0.75718 | 0.029637 | -128.6372 | 119.516 | 0.029637 | -128.6372 | 119.516
Line13_13_14 | 0.00039712 | 0.0023624 | 0.0020003 | 0.00039712 | 0.0023624 | 0.0020003 | 9.171e-05 | 0.00054558 | 0.00046194 | 9.171e-05 | 0.00054558 | 0.00046194 | -7.877e-05 | -0.00045088 | -8.6844e-05 | 7.8773e-05 | 0.00045099 | 8.6921e-05 | 2.4695e-05 | -9.391e-05 | -0.00033882 | -2.4692e-05 | 9.4021e-05 | 0.0003389 | -162.5636 | 39.5973 | -136.1079 | 17.4364 | -140.4027 | 43.8921 | 0.90012 | 0.84415 | 0.75718 | 0.90014 | 0.84438 | 0.75739 | 0.029637 | -128.6372 | 119.516 | 0.032355 | -128.6264 | 119.5071
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6384e-13 | -2.8255e-10 | -7.9284e-10 | -7.6383e-13 | 2.8255e-10 | 7.9284e-10 | -3.073e-12 | 8.367e-10 | 4.2212e-11 | 3.0729e-12 | -8.367e-10 | -4.2212e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90012 | 0.84415 | 0.75718 | 0.90012 | 0.84415 | 0.75718 | 0.029637 | -128.6372 | 119.516 | 0.029637 | -128.6372 | 119.516
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8191e-13 | -1.4127e-10 | -3.9642e-10 | -3.8191e-13 | 1.4127e-10 | 3.9642e-10 | -1.5364e-12 | 4.1835e-10 | 2.1106e-11 | 1.5365e-12 | -4.1835e-10 | -2.1106e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90012 | 0.84415 | 0.75718 | 0.90012 | 0.84415 | 0.75718 | 0.029637 | -128.6372 | 119.516 | 0.029637 | -128.6372 | 119.516
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7373e-13 | -1.4308e-10 | -3.9784e-10 | -1.7373e-13 | 1.4308e-10 | 3.9784e-10 | -1.1148e-12 | 4.1957e-10 | 1.9924e-11 | 1.1148e-12 | -4.1957e-10 | -1.9924e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90005 | 0.84345 | 0.75656 | 0.90005 | 0.84345 | 0.75656 | 0.021505 | -128.6699 | 119.5428 | 0.021505 | -128.6699 | 119.5428
Line17_5_19 | 0.00040072 | 0.0023737 | 0.0020087 | 0.00040072 | 0.0023737 | 0.0020087 | 9.2543e-05 | 0.00054817 | 0.0004639 | 9.2543e-05 | 0.00054817 | 0.0004639 | -7.9631e-05 | -0.00045237 | -8.6136e-05 | 7.9634e-05 | 0.00045248 | 8.6213e-05 | 2.4429e-05 | -9.5551e-05 | -0.00034023 | -2.4426e-05 | 9.5663e-05 | 0.00034031 | -162.9238 | 39.4034 | -136.2503 | 17.0762 | -140.5966 | 43.7497 | 0.90005 | 0.84345 | 0.75656 | 0.90007 | 0.84369 | 0.75676 | 0.0215 | -128.6699 | 119.5428 | 0.024234 | -128.659 | 119.5338
Line1_1_3 | 0.00039712 | 0.0023624 | 0.0020003 | 0.00039712 | 0.0023624 | 0.0020003 | 9.171e-05 | 0.00054558 | 0.00046194 | 9.171e-05 | 0.00054558 | 0.00046194 | -7.8757e-05 | -0.00045045 | -8.654e-05 | 7.876e-05 | 0.00045056 | 8.6616e-05 | 2.4708e-05 | -9.346e-05 | -0.0003385 | -2.4705e-05 | 9.3572e-05 | 0.00033858 | -162.5636 | 39.5977 | -136.1075 | 17.4364 | -140.4023 | 43.8925 | 0.90003 | 0.84321 | 0.75635 | 0.90005 | 0.84345 | 0.75655 | 0.018766 | -128.6808 | 119.5518 | 0.021484 | -128.6699 | 119.5429
Line2_1_4 | 0.00040194 | 0.0023774 | 0.0020116 | 0.00040194 | 0.0023774 | 0.0020116 | 9.2823e-05 | 0.00054904 | 0.00046456 | 9.2823e-05 | 0.00054904 | 0.00046456 | -7.992e-05 | -0.00045287 | -8.5897e-05 | 7.9923e-05 | 0.00045298 | 8.5974e-05 | 2.4337e-05 | -9.6103e-05 | -0.0003407 | -2.4334e-05 | 9.6216e-05 | 0.00034078 | -163.0445 | 39.3384 | -136.2979 | 16.9555 | -140.6616 | 43.7021 | 0.90003 | 0.84321 | 0.75635 | 0.90005 | 0.84345 | 0.75656 | 0.018766 | -128.6808 | 119.5518 | 0.021505 | -128.6699 | 119.5428
Line3_1_5 | 0.00040072 | 0.0023737 | 0.0020087 | 0.00040072 | 0.0023737 | 0.0020087 | 9.2543e-05 | 0.00054817 | 0.0004639 | 9.2543e-05 | 0.00054817 | 0.0004639 | -7.9628e-05 | -0.00045227 | -8.6059e-05 | 7.9631e-05 | 0.00045237 | 8.6136e-05 | 2.4432e-05 | -9.5438e-05 | -0.00034015 | -2.4429e-05 | 9.555e-05 | 0.00034023 | -162.9238 | 39.4034 | -136.2502 | 17.0762 | -140.5966 | 43.7498 | 0.90003 | 0.84321 | 0.75635 | 0.90005 | 0.84345 | 0.75656 | 0.018766 | -128.6808 | 119.5518 | 0.0215 | -128.6699 | 119.5428
Line4_2_6 | 0.0017309 | 1.3772 | 1.3783 | 0.0017309 | 1.3772 | 1.3783 | 0.00039972 | 0.31804 | 0.31829 | 0.00039972 | 0.31804 | 0.31829 | -0.0003495 | 0.2237 | -0.0045368 | 0.00034956 | -0.18728 | 0.041009 | -8.5617e-05 | 0.027348 | 0.20062 | 8.5677e-05 | 0.010583 | -0.16263 | 166.2612 | -142.7693 | 37.1748 | -13.7388 | 37.2307 | -142.8252 | 0.90021 | 0.70859 | 0.63046 | 0.90038 | 0.5898 | 0.52693 | 0.025854 | -135.7991 | 128.4703 | 0.03294 | -146.0036 | 141.3276
Line5_6_7 | 0.0017309 | 1.3772 | 1.3783 | 0.0017309 | 1.3772 | 1.3783 | 0.00039972 | 0.31804 | 0.31829 | 0.00039972 | 0.31804 | 0.31829 | -0.00034956 | 0.18728 | -0.041009 | 0.00034962 | -0.15087 | 0.077481 | -8.5677e-05 | -0.010583 | 0.16263 | 8.5737e-05 | 0.048515 | -0.12464 | 166.2612 | -142.7693 | 37.1748 | -13.7388 | 37.2307 | -142.8252 | 0.90038 | 0.5898 | 0.52693 | 0.90056 | 0.49829 | 0.46108 | 0.03294 | -146.0036 | 141.3276 | 0.040023 | -160.5956 | 159.042
Line6_7_8 | 0 | 1.3861 | 1.3861 | 0 | 1.3861 | 1.3861 | 0 | 0.32011 | 0.32011 | 0 | 0.32011 | 0.32011 | 5.5208e-12 | 0.15202 | -0.078241 | -5.5208e-12 | -0.11513 | 0.11513 | -6.2277e-12 | -0.048298 | 0.12515 | 6.2278e-12 | 0.086725 | -0.086725 | 0 | -142.9703 | 37.0297 | 0 | 37.0297 | -142.9703 | 0.90056 | 0.49829 | 0.46108 | 0.90056 | 0.45028 | 0.45028 | 0.040023 | -160.5956 | 159.042 | 0.040023 | -179.96 | -179.96
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8401e-12 | -4.3857e-13 | 1.3592e-12 | -1.8401e-12 | 4.3857e-13 | -1.3589e-12 | -2.0758e-12 | 1.2863e-09 | -1.2874e-09 | 2.0759e-12 | -1.2863e-09 | 1.2874e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90056 | 0.45028 | 0.45028 | 0.90056 | 0.45028 | 0.45028 | 0.040023 | -179.96 | -179.96 | 0.040023 | -179.96 | -179.96
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8402e-12 | -4.3883e-13 | 1.3591e-12 | -1.8402e-12 | 4.3884e-13 | -1.3588e-12 | -2.0759e-12 | 1.2863e-09 | -1.2874e-09 | 2.0759e-12 | -1.2863e-09 | 1.2874e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90056 | 0.45028 | 0.45028 | 0.90056 | 0.45028 | 0.45028 | 0.040023 | -179.96 | -179.96 | 0.040023 | -179.96 | -179.96
Line9_3_11 | 0.00039712 | 0.0023624 | 0.0020003 | 0.00039712 | 0.0023624 | 0.0020003 | 9.171e-05 | 0.00054558 | 0.00046194 | 9.171e-05 | 0.00054558 | 0.00046194 | -7.876e-05 | -0.00045056 | -8.6616e-05 | 7.8763e-05 | 0.00045066 | 8.6693e-05 | 2.4705e-05 | -9.3572e-05 | -0.00033858 | -2.4701e-05 | 9.3684e-05 | 0.00033866 | -162.5636 | 39.5976 | -136.1075 | 17.4364 | -140.4024 | 43.8925 | 0.90005 | 0.84345 | 0.75655 | 0.90007 | 0.84368 | 0.75676 | 0.021484 | -128.6699 | 119.5429 | 0.024202 | -128.659 | 119.5339

## LL_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 6.4749e-05 | 0.051518 | 0.051559 | 6.4749e-05 | 0.051518 | 0.051559 | 1.4953e-05 | 0.011898 | 0.011907 | 1.4953e-05 | 0.011898 | 0.011907 | -1.4126e-05 | 0.010908 | 0.0028963 | 1.4127e-05 | -0.010857 | -0.0028452 | -1.4974e-06 | 0.002877 | 0.010869 | 1.4975e-06 | -0.0028239 | -0.010816 | 173.9499 | -135.0805 | 44.8636 | -6.0501 | 44.9195 | -135.1364 | 0.95 | 0.94819 | 0.9447 | 0.95001 | 0.94291 | 0.93929 | 0.00066837 | -120.3052 | 119.9431 | 0.00097045 | -120.501 | 120.1256
Line10_11_12 | 1.4856e-05 | 8.8376e-05 | 7.4828e-05 | 1.4856e-05 | 8.8376e-05 | 7.4828e-05 | 3.4308e-06 | 2.041e-05 | 1.7281e-05 | 3.4308e-06 | 2.041e-05 | 1.7281e-05 | -2.9509e-06 | -1.89e-05 | -6.02e-06 | 2.9509e-06 | 1.8901e-05 | 6.0201e-06 | 1.3838e-06 | -4.1587e-06 | -1.5175e-05 | -1.3838e-06 | 4.1588e-06 | 1.5175e-05 | -154.8748 | 47.2863 | -128.4189 | 25.1252 | -132.7137 | 51.5811 | 0.95 | 0.9482 | 0.94472 | 0.95 | 0.94821 | 0.94473 | 0.00087212 | -120.3045 | 119.9427 | 0.000974 | -120.3041 | 119.9425
Line11_12_13 | 1.4856e-05 | 8.8376e-05 | 7.4828e-05 | 1.4856e-05 | 8.8376e-05 | 7.4828e-05 | 3.4308e-06 | 2.041e-05 | 1.7281e-05 | 3.4308e-06 | 2.041e-05 | 1.7281e-05 | -2.9509e-06 | -1.8901e-05 | -6.0201e-06 | 2.9509e-06 | 1.8901e-05 | 6.0202e-06 | 1.3838e-06 | -4.1589e-06 | -1.5175e-05 | -1.3838e-06 | 4.159e-06 | 1.5175e-05 | -154.8748 | 47.2863 | -128.4189 | 25.1252 | -132.7137 | 51.5811 | 0.95 | 0.94821 | 0.94473 | 0.95 | 0.94822 | 0.94474 | 0.000974 | -120.3041 | 119.9425 | 0.0010759 | -120.3038 | 119.9423
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0389e-14 | -1.8402e-11 | -5.469e-11 | -2.0389e-14 | 1.8402e-11 | 5.469e-11 | -1.8642e-13 | 5.2534e-11 | 9.9489e-12 | 1.8642e-13 | -5.2534e-11 | -9.9489e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94822 | 0.94474 | 0.95 | 0.94822 | 0.94474 | 0.0010759 | -120.3038 | 119.9423 | 0.0010759 | -120.3038 | 119.9423
Line13_13_14 | 1.4856e-05 | 8.8376e-05 | 7.4828e-05 | 1.4856e-05 | 8.8376e-05 | 7.4828e-05 | 3.4308e-06 | 2.041e-05 | 1.7281e-05 | 3.4308e-06 | 2.041e-05 | 1.7281e-05 | -2.9509e-06 | -1.8901e-05 | -6.0201e-06 | 2.9509e-06 | 1.8901e-05 | 6.0203e-06 | 1.3838e-06 | -4.1591e-06 | -1.5175e-05 | -1.3838e-06 | 4.1592e-06 | 1.5175e-05 | -154.8748 | 47.2861 | -128.4192 | 25.1252 | -132.7139 | 51.5808 | 0.95 | 0.94822 | 0.94474 | 0.95 | 0.94823 | 0.94475 | 0.0010759 | -120.3038 | 119.9423 | 0.0011778 | -120.3034 | 119.9421
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3592e-14 | -1.2268e-11 | -3.646e-11 | -1.3592e-14 | 1.2268e-11 | 3.646e-11 | -1.2428e-13 | 3.5023e-11 | 6.6326e-12 | 1.2428e-13 | -3.5023e-11 | -6.6326e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94822 | 0.94474 | 0.95 | 0.94822 | 0.94474 | 0.0010759 | -120.3038 | 119.9423 | 0.0010759 | -120.3038 | 119.9423
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.795e-15 | -6.1338e-12 | -1.823e-11 | -6.7952e-15 | 6.1338e-12 | 1.823e-11 | -6.2138e-14 | 1.7511e-11 | 3.3163e-12 | 6.2137e-14 | -1.7511e-11 | -3.3163e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94822 | 0.94474 | 0.95 | 0.94822 | 0.94474 | 0.0010759 | -120.3038 | 119.9423 | 0.0010759 | -120.3038 | 119.9423
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.9305e-16 | -6.2251e-12 | -1.8316e-11 | -8.9312e-16 | 6.225e-12 | 1.8316e-11 | -4.454e-14 | 1.7573e-11 | 3.2809e-12 | 4.4541e-14 | -1.7573e-11 | -3.2809e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.9482 | 0.94471 | 0.95 | 0.9482 | 0.94471 | 0.00077118 | -120.3048 | 119.9429 | 0.00077118 | -120.3048 | 119.9429
Line17_5_19 | 1.4991e-05 | 8.8796e-05 | 7.5145e-05 | 1.4991e-05 | 8.8796e-05 | 7.5145e-05 | 3.4619e-06 | 2.0506e-05 | 1.7354e-05 | 3.4619e-06 | 2.0506e-05 | 1.7354e-05 | -2.9864e-06 | -1.8976e-05 | -6.0074e-06 | 2.9864e-06 | 1.8976e-05 | 6.0075e-06 | 1.3776e-06 | -4.2426e-06 | -1.5254e-05 | -1.3776e-06 | 4.2428e-06 | 1.5254e-05 | -155.235 | 47.0921 | -128.5615 | 24.765 | -132.9079 | 51.4385 | 0.95 | 0.9482 | 0.94471 | 0.95 | 0.9482 | 0.94472 | 0.00077095 | -120.3048 | 119.9429 | 0.00087353 | -120.3045 | 119.9427
Line1_1_3 | 1.4856e-05 | 8.8376e-05 | 7.4828e-05 | 1.4856e-05 | 8.8376e-05 | 7.4828e-05 | 3.4308e-06 | 2.041e-05 | 1.7281e-05 | 3.4308e-06 | 2.041e-05 | 1.7281e-05 | -2.9509e-06 | -1.89e-05 | -6.0198e-06 | 2.9509e-06 | 1.89e-05 | 6.0199e-06 | 1.3838e-06 | -4.1583e-06 | -1.5175e-05 | -1.3838e-06 | 4.1585e-06 | 1.5175e-05 | -154.8748 | 47.2864 | -128.4187 | 25.1252 | -132.7136 | 51.5813 | 0.95 | 0.94819 | 0.9447 | 0.95 | 0.9482 | 0.94471 | 0.00066837 | -120.3052 | 119.9431 | 0.00077024 | -120.3048 | 119.9429
Line2_1_4 | 1.5036e-05 | 8.8936e-05 | 7.5251e-05 | 1.5036e-05 | 8.8936e-05 | 7.5251e-05 | 3.4724e-06 | 2.0539e-05 | 1.7378e-05 | 3.4724e-06 | 2.0539e-05 | 1.7378e-05 | -2.9983e-06 | -1.9001e-05 | -6.0031e-06 | 2.9983e-06 | 1.9001e-05 | 6.0032e-06 | 1.3755e-06 | -4.2707e-06 | -1.5281e-05 | -1.3755e-06 | 4.2709e-06 | 1.5281e-05 | -155.3558 | 47.0271 | -128.6092 | 24.6442 | -132.9729 | 51.3908 | 0.95 | 0.94819 | 0.9447 | 0.95 | 0.9482 | 0.94471 | 0.00066837 | -120.3052 | 119.9431 | 0.00077118 | -120.3048 | 119.9429
Line3_1_5 | 1.4991e-05 | 8.8796e-05 | 7.5145e-05 | 1.4991e-05 | 8.8796e-05 | 7.5145e-05 | 3.4619e-06 | 2.0506e-05 | 1.7354e-05 | 3.4619e-06 | 2.0506e-05 | 1.7354e-05 | -2.9864e-06 | -1.8975e-05 | -6.0073e-06 | 2.9864e-06 | 1.8976e-05 | 6.0074e-06 | 1.3776e-06 | -4.2424e-06 | -1.5254e-05 | -1.3776e-06 | 4.2426e-06 | 1.5254e-05 | -155.235 | 47.0922 | -128.5615 | 24.765 | -132.9078 | 51.4385 | 0.95 | 0.94819 | 0.9447 | 0.95 | 0.9482 | 0.94471 | 0.00066837 | -120.3052 | 119.9431 | 0.00077095 | -120.3048 | 119.9429
Line4_2_6 | 6.4749e-05 | 0.051518 | 0.051559 | 6.4749e-05 | 0.051518 | 0.051559 | 1.4953e-05 | 0.011898 | 0.011907 | 1.4953e-05 | 0.011898 | 0.011907 | -1.4127e-05 | 0.010857 | 0.0028452 | 1.4127e-05 | -0.010806 | -0.0027942 | -1.4975e-06 | 0.0028239 | 0.010816 | 1.4976e-06 | -0.0027709 | -0.010763 | 173.9499 | -135.0805 | 44.8636 | -6.0501 | 44.9195 | -135.1364 | 0.95001 | 0.94291 | 0.93929 | 0.95001 | 0.93765 | 0.93389 | 0.00097045 | -120.501 | 120.1256 | 0.0012725 | -120.6989 | 120.3103
Line5_6_7 | 6.4749e-05 | 0.051518 | 0.051559 | 6.4749e-05 | 0.051518 | 0.051559 | 1.4953e-05 | 0.011898 | 0.011907 | 1.4953e-05 | 0.011898 | 0.011907 | -1.4127e-05 | 0.010806 | 0.0027942 | 1.4127e-05 | -0.010755 | -0.0027432 | -1.4976e-06 | 0.0027709 | 0.010763 | 1.4976e-06 | -0.0027178 | -0.01071 | 173.9499 | -135.0805 | 44.8636 | -6.0501 | 44.9195 | -135.1364 | 0.95001 | 0.93765 | 0.93389 | 0.95002 | 0.9324 | 0.92849 | 0.0012725 | -120.6989 | 120.3103 | 0.0015746 | -120.8991 | 120.497
Line6_7_8 | 0 | 0.051853 | 0.051853 | 0 | 0.051853 | 0.051853 | 0 | 0.011975 | 0.011975 | 0 | 0.011975 | 0.011975 | 1.8284e-13 | 0.010816 | 0.0027315 | -1.8284e-13 | -0.010764 | -0.0026799 | -2.7283e-13 | 0.0027734 | 0.010778 | 2.7282e-13 | -0.0027197 | -0.010724 | 0 | -135.2816 | 44.7184 | 0 | 44.7184 | -135.2816 | 0.95002 | 0.9324 | 0.92849 | 0.95002 | 0.92711 | 0.92309 | 0.0015746 | -120.8991 | 120.497 | 0.0015746 | -121.1018 | 120.688
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0953e-14 | -7.7203e-11 | -9.0865e-11 | -6.0948e-14 | 7.7203e-11 | 9.0865e-11 | -9.0945e-14 | 6.2097e-11 | -3.8607e-11 | 9.0945e-14 | -6.2097e-11 | 3.8607e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95002 | 0.92711 | 0.92309 | 0.95002 | 0.92711 | 0.92309 | 0.0015746 | -121.1018 | 120.688 | 0.0015746 | -121.1018 | 120.688
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0944e-14 | -7.7203e-11 | -9.0865e-11 | -6.0944e-14 | 7.7203e-11 | 9.0865e-11 | -9.094e-14 | 6.2097e-11 | -3.8607e-11 | 9.094e-14 | -6.2097e-11 | 3.8607e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95002 | 0.92711 | 0.92309 | 0.95002 | 0.92711 | 0.92309 | 0.0015746 | -121.1018 | 120.688 | 0.0015746 | -121.1018 | 120.688
Line9_3_11 | 1.4856e-05 | 8.8376e-05 | 7.4828e-05 | 1.4856e-05 | 8.8376e-05 | 7.4828e-05 | 3.4308e-06 | 2.041e-05 | 1.7281e-05 | 3.4308e-06 | 2.041e-05 | 1.7281e-05 | -2.9509e-06 | -1.89e-05 | -6.0199e-06 | 2.9509e-06 | 1.89e-05 | 6.02e-06 | 1.3838e-06 | -4.1585e-06 | -1.5175e-05 | -1.3838e-06 | 4.1587e-06 | 1.5175e-05 | -154.8748 | 47.2864 | -128.4188 | 25.1252 | -132.7136 | 51.5812 | 0.95 | 0.9482 | 0.94471 | 0.95 | 0.9482 | 0.94472 | 0.00077024 | -120.3048 | 119.9429 | 0.00087212 | -120.3045 | 119.9427

## LL_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 6.1342e-05 | 0.048807 | 0.048845 | 6.1342e-05 | 0.048807 | 0.048845 | 1.4166e-05 | 0.011271 | 0.01128 | 1.4166e-05 | 0.011271 | 0.01128 | -1.2679e-05 | 0.0097901 | 0.0025994 | 1.2679e-05 | -0.0097444 | -0.0025536 | -1.3439e-06 | 0.0025822 | 0.0097553 | 1.344e-06 | -0.0025345 | -0.0097076 | 173.9499 | -135.0805 | 44.8636 | -6.0501 | 44.9195 | -135.1364 | 0.9 | 0.89828 | 0.89498 | 0.90001 | 0.89329 | 0.88985 | 0.00066837 | -120.3052 | 119.9431 | 0.00097045 | -120.501 | 120.1256
Line10_11_12 | 1.4074e-05 | 8.3725e-05 | 7.089e-05 | 1.4074e-05 | 8.3725e-05 | 7.089e-05 | 3.2502e-06 | 1.9335e-05 | 1.6371e-05 | 3.2502e-06 | 1.9335e-05 | 1.6371e-05 | -2.6484e-06 | -1.6963e-05 | -5.403e-06 | 2.6484e-06 | 1.6963e-05 | 5.4031e-06 | 1.242e-06 | -3.7325e-06 | -1.362e-05 | -1.242e-06 | 3.7326e-06 | 1.362e-05 | -154.8748 | 47.2863 | -128.4189 | 25.1252 | -132.7137 | 51.5811 | 0.9 | 0.8983 | 0.895 | 0.9 | 0.89831 | 0.89501 | 0.00087212 | -120.3045 | 119.9427 | 0.000974 | -120.3041 | 119.9425
Line11_12_13 | 1.4074e-05 | 8.3725e-05 | 7.089e-05 | 1.4074e-05 | 8.3725e-05 | 7.089e-05 | 3.2502e-06 | 1.9335e-05 | 1.6371e-05 | 3.2502e-06 | 1.9335e-05 | 1.6371e-05 | -2.6484e-06 | -1.6963e-05 | -5.4031e-06 | 2.6484e-06 | 1.6963e-05 | 5.4032e-06 | 1.242e-06 | -3.7326e-06 | -1.362e-05 | -1.242e-06 | 3.7328e-06 | 1.362e-05 | -154.8748 | 47.2863 | -128.4189 | 25.1252 | -132.7137 | 51.5811 | 0.9 | 0.89831 | 0.89501 | 0.9 | 0.89832 | 0.89501 | 0.000974 | -120.3041 | 119.9425 | 0.0010759 | -120.3038 | 119.9423
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8299e-14 | -1.6515e-11 | -4.9085e-11 | -1.8299e-14 | 1.6515e-11 | 4.9085e-11 | -1.6731e-13 | 4.715e-11 | 8.9292e-12 | 1.6731e-13 | -4.715e-11 | -8.9292e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89832 | 0.89501 | 0.9 | 0.89832 | 0.89501 | 0.0010759 | -120.3038 | 119.9423 | 0.0010759 | -120.3038 | 119.9423
Line13_13_14 | 1.4074e-05 | 8.3725e-05 | 7.089e-05 | 1.4074e-05 | 8.3725e-05 | 7.089e-05 | 3.2502e-06 | 1.9335e-05 | 1.6371e-05 | 3.2502e-06 | 1.9335e-05 | 1.6371e-05 | -2.6484e-06 | -1.6963e-05 | -5.4031e-06 | 2.6484e-06 | 1.6964e-05 | 5.4032e-06 | 1.242e-06 | -3.7328e-06 | -1.362e-05 | -1.242e-06 | 3.733e-06 | 1.362e-05 | -154.8748 | 47.2861 | -128.4192 | 25.1252 | -132.7139 | 51.5808 | 0.9 | 0.89832 | 0.89501 | 0.9 | 0.89832 | 0.89502 | 0.0010759 | -120.3038 | 119.9423 | 0.0011778 | -120.3034 | 119.9421
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2199e-14 | -1.101e-11 | -3.2723e-11 | -1.2199e-14 | 1.101e-11 | 3.2723e-11 | -1.1154e-13 | 3.1433e-11 | 5.9528e-12 | 1.1154e-13 | -3.1433e-11 | -5.9528e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89832 | 0.89501 | 0.9 | 0.89832 | 0.89501 | 0.0010759 | -120.3038 | 119.9423 | 0.0010759 | -120.3038 | 119.9423
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.099e-15 | -5.5052e-12 | -1.6362e-11 | -6.099e-15 | 5.5052e-12 | 1.6362e-11 | -5.577e-14 | 1.5717e-11 | 2.9764e-12 | 5.5769e-14 | -1.5717e-11 | -2.9764e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89832 | 0.89501 | 0.9 | 0.89832 | 0.89501 | 0.0010759 | -120.3038 | 119.9423 | 0.0010759 | -120.3038 | 119.9423
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.0153e-16 | -5.587e-12 | -1.6439e-11 | -8.0166e-16 | 5.587e-12 | 1.6439e-11 | -3.9975e-14 | 1.5772e-11 | 2.9446e-12 | 3.9976e-14 | -1.5772e-11 | -2.9446e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89829 | 0.89499 | 0.9 | 0.89829 | 0.89499 | 0.00077118 | -120.3048 | 119.9429 | 0.00077118 | -120.3048 | 119.9429
Line17_5_19 | 1.4202e-05 | 8.4122e-05 | 7.119e-05 | 1.4202e-05 | 8.4122e-05 | 7.119e-05 | 3.2797e-06 | 1.9427e-05 | 1.6441e-05 | 3.2797e-06 | 1.9427e-05 | 1.6441e-05 | -2.6803e-06 | -1.7031e-05 | -5.3917e-06 | 2.6803e-06 | 1.7031e-05 | 5.3918e-06 | 1.2364e-06 | -3.8078e-06 | -1.3691e-05 | -1.2364e-06 | 3.8079e-06 | 1.3691e-05 | -155.235 | 47.0921 | -128.5615 | 24.765 | -132.9079 | 51.4385 | 0.9 | 0.89829 | 0.89499 | 0.9 | 0.8983 | 0.895 | 0.00077095 | -120.3048 | 119.9429 | 0.00087353 | -120.3045 | 119.9427
Line1_1_3 | 1.4074e-05 | 8.3725e-05 | 7.089e-05 | 1.4074e-05 | 8.3725e-05 | 7.089e-05 | 3.2502e-06 | 1.9335e-05 | 1.6371e-05 | 3.2502e-06 | 1.9335e-05 | 1.6371e-05 | -2.6484e-06 | -1.6963e-05 | -5.4028e-06 | 2.6484e-06 | 1.6963e-05 | 5.4029e-06 | 1.242e-06 | -3.7321e-06 | -1.362e-05 | -1.242e-06 | 3.7323e-06 | 1.362e-05 | -154.8748 | 47.2864 | -128.4187 | 25.1252 | -132.7136 | 51.5813 | 0.9 | 0.89828 | 0.89498 | 0.9 | 0.89829 | 0.89499 | 0.00066837 | -120.3052 | 119.9431 | 0.00077024 | -120.3048 | 119.9429
Line2_1_4 | 1.4245e-05 | 8.4255e-05 | 7.129e-05 | 1.4245e-05 | 8.4255e-05 | 7.129e-05 | 3.2896e-06 | 1.9458e-05 | 1.6464e-05 | 3.2896e-06 | 1.9458e-05 | 1.6464e-05 | -2.691e-06 | -1.7053e-05 | -5.3878e-06 | 2.691e-06 | 1.7053e-05 | 5.3879e-06 | 1.2345e-06 | -3.833e-06 | -1.3714e-05 | -1.2345e-06 | 3.8331e-06 | 1.3715e-05 | -155.3558 | 47.0271 | -128.6092 | 24.6442 | -132.9729 | 51.3908 | 0.9 | 0.89828 | 0.89498 | 0.9 | 0.89829 | 0.89499 | 0.00066837 | -120.3052 | 119.9431 | 0.00077118 | -120.3048 | 119.9429
Line3_1_5 | 1.4202e-05 | 8.4122e-05 | 7.119e-05 | 1.4202e-05 | 8.4122e-05 | 7.119e-05 | 3.2797e-06 | 1.9427e-05 | 1.6441e-05 | 3.2797e-06 | 1.9427e-05 | 1.6441e-05 | -2.6803e-06 | -1.7031e-05 | -5.3916e-06 | 2.6803e-06 | 1.7031e-05 | 5.3917e-06 | 1.2364e-06 | -3.8076e-06 | -1.3691e-05 | -1.2364e-06 | 3.8078e-06 | 1.3691e-05 | -155.235 | 47.0922 | -128.5615 | 24.765 | -132.9078 | 51.4385 | 0.9 | 0.89828 | 0.89498 | 0.9 | 0.89829 | 0.89499 | 0.00066837 | -120.3052 | 119.9431 | 0.00077095 | -120.3048 | 119.9429
Line4_2_6 | 6.1342e-05 | 0.048807 | 0.048845 | 6.1342e-05 | 0.048807 | 0.048845 | 1.4166e-05 | 0.011271 | 0.01128 | 1.4166e-05 | 0.011271 | 0.01128 | -1.2679e-05 | 0.0097444 | 0.0025536 | 1.2679e-05 | -0.0096987 | -0.0025078 | -1.344e-06 | 0.0025345 | 0.0097076 | 1.3441e-06 | -0.0024869 | -0.0096599 | 173.9499 | -135.0805 | 44.8636 | -6.0501 | 44.9195 | -135.1364 | 0.90001 | 0.89329 | 0.88985 | 0.90001 | 0.8883 | 0.88473 | 0.00097045 | -120.501 | 120.1256 | 0.0012725 | -120.6989 | 120.3103
Line5_6_7 | 6.1342e-05 | 0.048807 | 0.048845 | 6.1342e-05 | 0.048807 | 0.048845 | 1.4166e-05 | 0.011271 | 0.01128 | 1.4166e-05 | 0.011271 | 0.01128 | -1.2679e-05 | 0.0096987 | 0.0025078 | 1.2679e-05 | -0.0096529 | -0.002462 | -1.3441e-06 | 0.0024869 | 0.0096599 | 1.3441e-06 | -0.0024392 | -0.0096122 | 173.9499 | -135.0805 | 44.8636 | -6.0501 | 44.9195 | -135.1364 | 0.90001 | 0.8883 | 0.88473 | 0.90002 | 0.88333 | 0.87962 | 0.0012725 | -120.6989 | 120.3103 | 0.0015746 | -120.8991 | 120.497
Line6_7_8 | 0 | 0.049124 | 0.049124 | 0 | 0.049124 | 0.049124 | 0 | 0.011345 | 0.011345 | 0 | 0.011345 | 0.011345 | 1.641e-13 | 0.009707 | 0.0024516 | -1.641e-13 | -0.0096607 | -0.0024052 | -2.4486e-13 | 0.0024892 | 0.0096733 | 2.4486e-13 | -0.0024409 | -0.009625 | 0 | -135.2816 | 44.7184 | 0 | 44.7184 | -135.2816 | 0.90002 | 0.88333 | 0.87962 | 0.90002 | 0.87832 | 0.8745 | 0.0015746 | -120.8991 | 120.497 | 0.0015746 | -121.1018 | 120.688
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4697e-14 | -6.929e-11 | -8.1552e-11 | -5.4699e-14 | 6.929e-11 | 8.1552e-11 | -8.1622e-14 | 5.5733e-11 | -3.465e-11 | 8.162e-14 | -5.5733e-11 | 3.465e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90002 | 0.87832 | 0.8745 | 0.90002 | 0.87832 | 0.8745 | 0.0015746 | -121.1018 | 120.688 | 0.0015746 | -121.1018 | 120.688
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4699e-14 | -6.929e-11 | -8.1552e-11 | -5.4701e-14 | 6.929e-11 | 8.1552e-11 | -8.1622e-14 | 5.5733e-11 | -3.465e-11 | 8.1624e-14 | -5.5733e-11 | 3.465e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90002 | 0.87832 | 0.8745 | 0.90002 | 0.87832 | 0.8745 | 0.0015746 | -121.1018 | 120.688 | 0.0015746 | -121.1018 | 120.688
Line9_3_11 | 1.4074e-05 | 8.3725e-05 | 7.089e-05 | 1.4074e-05 | 8.3725e-05 | 7.089e-05 | 3.2502e-06 | 1.9335e-05 | 1.6371e-05 | 3.2502e-06 | 1.9335e-05 | 1.6371e-05 | -2.6484e-06 | -1.6963e-05 | -5.4029e-06 | 2.6484e-06 | 1.6963e-05 | 5.403e-06 | 1.242e-06 | -3.7323e-06 | -1.362e-05 | -1.242e-06 | 3.7324e-06 | 1.362e-05 | -154.8748 | 47.2864 | -128.4188 | 25.1252 | -132.7136 | 51.5812 | 0.9 | 0.89829 | 0.89499 | 0.9 | 0.8983 | 0.895 | 0.00077024 | -120.3048 | 119.9429 | 0.00087212 | -120.3045 | 119.9427

## LG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 2.1907 | 0.2031 | 0.12192 | 2.1907 | 0.2031 | 0.12192 | 0.50592 | 0.046904 | 0.028156 | 0.50592 | 0.046904 | 0.028156 | 0.18588 | -0.054858 | 0.022212 | -0.14488 | 0.054776 | -0.021163 | 0.35446 | 0.0090703 | -0.022623 | -0.27312 | -0.006825 | 0.022979 | -69.0519 | 66.2206 | 171.6954 | 110.9481 | -113.7794 | -8.3046 |  | 0.79112 | 1.1855 | 1.126 | 0.6111 | 1.1769 | 1.1095 | -6.7248 | -123.1678 | 126.1709 | -6.9959 | -120.8818 | 124.3392
Line10_11_12 | 0.36562 | 0.10208 | 0.17236 | 0.36562 | 0.10208 | 0.17236 | 0.084436 | 0.023574 | 0.039804 | 0.084436 | 0.023574 | 0.039804 | -0.031434 | -0.026545 | 0.041041 | 0.032487 | 0.026694 | -0.041074 | -0.063874 | 0.0096148 | -0.019 | 0.065802 | -0.0096245 | 0.019415 | 109.3195 | 76.9129 | 150.0845 | -70.6805 | -103.0871 | -29.9156 |  | 0.84311 | 1.1976 | 1.1362 | 0.86911 | 1.2037 | 1.1414 | -6.8838 | -122.9978 | 125.2427 | -6.9562 | -122.9141 | 124.7849
Line11_12_13 | 0.36562 | 0.10208 | 0.17236 | 0.36562 | 0.10208 | 0.17236 | 0.084436 | 0.023574 | 0.039804 | 0.084436 | 0.023574 | 0.039804 | -0.032487 | -0.026694 | 0.041074 | 0.033539 | 0.026842 | -0.041108 | -0.065802 | 0.0096245 | -0.019415 | 0.067731 | -0.0096343 | 0.019831 | 109.3195 | 76.9129 | 150.0844 | -70.6805 | -103.087 | -29.9156 |  | 0.86911 | 1.2037 | 1.1414 | 0.89511 | 1.2097 | 1.1467 | -6.9562 | -122.9141 | 124.7849 | -7.0243 | -122.8312 | 124.3312
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5679e-08 | 2.7574e-08 | -4.1301e-08 | -9.97e-09 | -1.9097e-08 | 2.7115e-08 | 3.0448e-08 | -3.7318e-08 | -9.2334e-09 | -2.072e-08 | 2.4649e-08 | 6.489e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.89511 | 1.2097 | 1.1467 | 0.89511 | 1.2097 | 1.1467 | -7.0243 | -122.8312 | 124.3312 | -7.0243 | -122.8312 | 124.3312
Line13_13_14 | 0.36562 | 0.10208 | 0.17236 | 0.36562 | 0.10208 | 0.17236 | 0.084436 | 0.023574 | 0.039804 | 0.084437 | 0.023574 | 0.039804 | -0.033539 | -0.026842 | 0.041108 | 0.034592 | 0.026991 | -0.041142 | -0.067731 | 0.0096343 | -0.019831 | 0.06966 | -0.0096441 | 0.020247 | 109.3195 | 76.913 | 150.0844 | -70.6805 | -103.087 | -29.9156 |  | 0.89511 | 1.2097 | 1.1467 | 0.92111 | 1.2158 | 1.152 | -7.0243 | -122.8312 | 124.3312 | -7.0886 | -122.7492 | 123.8817
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0453e-08 | 1.8383e-08 | -2.7534e-08 | -4.7438e-09 | -9.9057e-09 | 1.3348e-08 | 2.0299e-08 | -2.4879e-08 | -6.1556e-09 | -1.0571e-08 | 1.2209e-08 | 3.4112e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.89511 | 1.2097 | 1.1467 | 0.89511 | 1.2097 | 1.1467 | -7.0243 | -122.8312 | 124.3312 | -7.0243 | -122.8312 | 124.3312
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2263e-09 | 9.1914e-09 | -1.3767e-08 | 4.8249e-10 | -7.1428e-10 | -4.1901e-10 | 1.0149e-08 | -1.2439e-08 | -3.0778e-09 | -4.2143e-10 | -2.3005e-10 | 3.334e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.89511 | 1.2097 | 1.1467 | 0.89511 | 1.2097 | 1.1467 | -7.0243 | -122.8312 | 124.3312 | -7.0243 | -122.8312 | 124.3312
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8176e-09 | 1.1141e-08 | -1.5618e-08 | 6.5993e-10 | -6.3751e-10 | -3.6332e-10 | 1.1137e-08 | -1.3745e-08 | -4.878e-09 | -3.8285e-10 | -2.4375e-10 | 4.2705e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.82386 | 1.1941 | 1.1324 | 0.82386 | 1.1941 | 1.1324 | -6.9326 | -123.0392 | 125.6211 | -6.9326 | -123.0392 | 125.6211
Line17_5_19 | 0.4319 | 0.12813 | 0.19342 | 0.4319 | 0.12813 | 0.19342 | 0.099743 | 0.02959 | 0.044669 | 0.099743 | 0.02959 | 0.044669 | -0.03319 | -0.034246 | 0.046519 | 0.034643 | 0.034488 | -0.046586 | -0.074958 | 0.0086021 | -0.019823 | 0.077671 | -0.00859 | 0.020354 | 106.9911 | 71.0482 | 148.7245 | -73.0089 | -108.9518 | -31.2755 |  | 0.82189 | 1.1933 | 1.132 | 0.85267 | 1.2012 | 1.1381 | -6.8919 | -123.0521 | 125.6442 | -7.0469 | -122.938 | 125.1231
Line1_1_3 | 0.36562 | 0.10208 | 0.17236 | 0.36562 | 0.10208 | 0.17236 | 0.084436 | 0.023574 | 0.039804 | 0.084436 | 0.023574 | 0.039804 | -0.029329 | -0.026248 | 0.040973 | 0.030382 | 0.026396 | -0.041007 | -0.060016 | 0.0095952 | -0.018168 | 0.061945 | -0.009605 | 0.018584 | 109.3195 | 76.9129 | 150.0845 | -70.6805 | -103.0871 | -29.9155 |  | 0.79112 | 1.1855 | 1.126 | 0.81712 | 1.1915 | 1.1311 | -6.7248 | -123.1678 | 126.1709 | -6.8069 | -123.0824 | 125.7047
Line2_1_4 | 0.45926 | 0.13965 | 0.20122 | 0.45926 | 0.13966 | 0.20122 | 0.10606 | 0.032252 | 0.046469 | 0.10606 | 0.032252 | 0.046469 | -0.032475 | -0.037415 | 0.048489 | 0.034111 | 0.037706 | -0.048574 | -0.077369 | 0.0078698 | -0.019665 | 0.080448 | -0.0078426 | 0.020244 | 106.045 | 68.7105 | 148.2462 | -73.955 | -111.2895 | -31.7538 |  | 0.79112 | 1.1855 | 1.126 | 0.82386 | 1.1941 | 1.1324 | -6.7248 | -123.1678 | 126.1709 | -6.9326 | -123.0392 | 125.6211
Line3_1_5 | 0.4319 | 0.12813 | 0.19342 | 0.4319 | 0.12813 | 0.19342 | 0.099743 | 0.02959 | 0.044669 | 0.099743 | 0.02959 | 0.044669 | -0.031737 | -0.034003 | 0.046452 | 0.03319 | 0.034246 | -0.046519 | -0.072245 | 0.0086143 | -0.019292 | 0.074958 | -0.0086021 | 0.019823 | 106.9911 | 71.0482 | 148.7245 | -73.0089 | -108.9518 | -31.2755 |  | 0.79112 | 1.1855 | 1.126 | 0.82189 | 1.1933 | 1.132 | -6.7248 | -123.1678 | 126.1709 | -6.8919 | -123.0521 | 125.6442
Line4_2_6 | 2.1907 | 0.2031 | 0.12192 | 2.1907 | 0.2031 | 0.12192 | 0.50592 | 0.046904 | 0.028156 | 0.50592 | 0.046904 | 0.028156 | 0.14488 | -0.054776 | 0.021163 | -0.10387 | 0.054693 | -0.020113 | 0.27312 | 0.006825 | -0.022979 | -0.19178 | -0.0045798 | 0.023335 | -69.0519 | 66.2206 | 171.6954 | 110.9481 | -113.7794 | -8.3047 |  | 0.6111 | 1.1769 | 1.1095 | 0.4311 | 1.1702 | 1.0942 | -6.9959 | -120.8818 | 124.3392 | -7.4934 | -118.5659 | 122.4541
Line5_6_7 | 2.1907 | 0.2031 | 0.12192 | 2.1907 | 0.2031 | 0.12192 | 0.50592 | 0.046904 | 0.028156 | 0.50592 | 0.046904 | 0.028156 | 0.10387 | -0.054693 | 0.020113 | -0.06287 | 0.054611 | -0.019064 | 0.19178 | 0.0045798 | -0.023335 | -0.11044 | -0.0023345 | 0.023691 | -69.0519 | 66.2206 | 171.6953 | 110.9481 | -113.7794 | -8.3047 |  | 0.4311 | 1.1702 | 1.0942 | 0.25118 | 1.1654 | 1.08 | -7.4934 | -118.5659 | 122.4541 | -8.7039 | -116.2271 | 120.5176
Line6_7_8 | 3.113 | 0 | 0 | 3.113 | 0 | 0 | 0.71893 | 0 | 0 | 0.71893 | 0 | 0 | 0.080759 | 7.7796e-08 | -7.9391e-08 | -4.9742e-15 | -5.4676e-08 | 5.3324e-08 | 0.16152 | -5.3762e-08 | -3.2362e-08 | 6.4665e-14 | 3.4142e-08 | 1.9807e-08 | -72.1388 | 0 | 0 | 107.8612 | 0 | 0 |  | 0.25118 | 1.1654 | 1.08 | 0 | 1.1512 | 1.049 | -8.7039 | -116.2271 | 120.5176 | 0 | -113.8423 | 118.3913
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.3794e-22 | 2.7112e-08 | -2.6661e-08 | -7.9055e-18 | -4.5296e-10 | 2.3648e-12 | -2.2405e-21 | -1.6833e-08 | -9.9604e-09 | 8.1968e-18 | 4.7543e-10 | -1.1338e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 1.1512 | 1.049 | 0 | 1.1512 | 1.049 | 0 | -113.8423 | 118.3913 | 0 | -113.8423 | 118.3913
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.3794e-22 | 2.7112e-08 | -2.6661e-08 | -7.9055e-18 | -4.5296e-10 | 2.3651e-12 | -2.2405e-21 | -1.6833e-08 | -9.9604e-09 | 8.1968e-18 | 4.7543e-10 | -1.1338e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 1.1512 | 1.049 | 0 | 1.1512 | 1.049 | 0 | -113.8423 | 118.3913 | 0 | -113.8423 | 118.3913
Line9_3_11 | 0.36562 | 0.10208 | 0.17236 | 0.36562 | 0.10208 | 0.17236 | 0.084436 | 0.023574 | 0.039804 | 0.084436 | 0.023574 | 0.039804 | -0.030382 | -0.026396 | 0.041007 | 0.031434 | 0.026545 | -0.041041 | -0.061945 | 0.009605 | -0.018584 | 0.063874 | -0.0096148 | 0.019 | 109.3195 | 76.9129 | 150.0845 | -70.6805 | -103.0871 | -29.9155 |  | 0.81712 | 1.1915 | 1.1311 | 0.84311 | 1.1976 | 1.1362 | -6.8069 | -123.0824 | 125.7047 | -6.8838 | -122.9978 | 125.2427

## LG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 2.2728 | 0.20814 | 0.12517 | 2.2728 | 0.20814 | 0.12517 | 0.52487 | 0.048067 | 0.028907 | 0.52487 | 0.048067 | 0.028907 | 0.19923 | -0.058875 | 0.024925 | -0.15509 | 0.05881 | -0.023813 | 0.38073 | 0.010614 | -0.023334 | -0.29315 | -0.0082308 | 0.023743 | -69.3197 | 66.9644 | 169.4333 | 110.6803 | -113.0355 | -10.5667 |  | 0.8187 | 1.2446 | 1.1811 | 0.63187 | 1.2354 | 1.1633 | -6.9424 | -123.2547 | 126.321 | -7.2012 | -121.0026 | 124.5175
Line10_11_12 | 0.37837 | 0.10787 | 0.17693 | 0.37837 | 0.10787 | 0.17693 | 0.08738 | 0.024912 | 0.040861 | 0.08738 | 0.024912 | 0.040861 | -0.033755 | -0.029241 | 0.044589 | 0.034876 | 0.0294 | -0.044627 | -0.068349 | 0.011192 | -0.019513 | 0.070411 | -0.0112 | 0.019944 | 109.1927 | 77.8713 | 149.0533 | -70.8073 | -102.1287 | -30.9467 |  | 0.87239 | 1.2568 | 1.1912 | 0.89923 | 1.2629 | 1.1963 | -7.0903 | -123.0725 | 125.4187 | -7.1577 | -122.9828 | 124.9732
Line11_12_13 | 0.37837 | 0.10787 | 0.17693 | 0.37837 | 0.10787 | 0.17693 | 0.08738 | 0.024912 | 0.040861 | 0.08738 | 0.024912 | 0.040861 | -0.034876 | -0.0294 | 0.044627 | 0.035998 | 0.02956 | -0.044666 | -0.070411 | 0.0112 | -0.019944 | 0.072474 | -0.011208 | 0.020376 | 109.1927 | 77.8713 | 149.0533 | -70.8073 | -102.1286 | -30.9467 |  | 0.89923 | 1.2629 | 1.1963 | 0.92608 | 1.269 | 1.2015 | -7.1577 | -122.9828 | 124.9732 | -7.2211 | -122.8938 | 124.5316
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.751e-08 | 3.159e-08 | -4.7017e-08 | -1.1112e-08 | -2.1853e-08 | 3.0883e-08 | 3.4287e-08 | -4.2446e-08 | -1.0977e-08 | -2.3327e-08 | 2.8039e-08 | 7.701e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.92608 | 1.269 | 1.2015 | 0.92608 | 1.269 | 1.2015 | -7.2211 | -122.8938 | 124.5316 | -7.2211 | -122.8938 | 124.5316
Line13_13_14 | 0.37837 | 0.10787 | 0.17693 | 0.37837 | 0.10787 | 0.17693 | 0.08738 | 0.024912 | 0.040861 | 0.08738 | 0.024912 | 0.040861 | -0.035998 | -0.02956 | 0.044666 | 0.03712 | 0.029719 | -0.044704 | -0.072474 | 0.011208 | -0.020376 | 0.074536 | -0.011217 | 0.020807 | 109.1927 | 77.8714 | 149.0533 | -70.8073 | -102.1286 | -30.9467 |  | 0.92608 | 1.269 | 1.2015 | 0.95293 | 1.2751 | 1.2068 | -7.2211 | -122.8938 | 124.5316 | -7.281 | -122.8058 | 124.0938
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1673e-08 | 2.106e-08 | -3.1345e-08 | -5.2758e-09 | -1.1323e-08 | 1.521e-08 | 2.2858e-08 | -2.8298e-08 | -7.3181e-09 | -1.1898e-08 | 1.389e-08 | 4.0419e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.92608 | 1.269 | 1.2015 | 0.92608 | 1.269 | 1.2015 | -7.2211 | -122.8938 | 124.5316 | -7.2211 | -122.8938 | 124.5316
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.8367e-09 | 1.053e-08 | -1.5672e-08 | 5.6094e-10 | -7.9286e-10 | -4.6225e-10 | 1.1429e-08 | -1.4149e-08 | -3.6591e-09 | -4.6951e-10 | -2.584e-10 | 3.8288e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.92608 | 1.269 | 1.2015 | 0.92608 | 1.269 | 1.2015 | -7.2211 | -122.8938 | 124.5316 | -7.2211 | -122.8938 | 124.5316
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3719e-09 | 1.2674e-08 | -1.7677e-08 | 7.4767e-10 | -7.1155e-10 | -4.0499e-10 | 1.2458e-08 | -1.5566e-08 | -5.6578e-09 | -4.2715e-10 | -2.7517e-10 | 4.8322e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.8522 | 1.2532 | 1.1874 | 0.8522 | 1.2532 | 1.1874 | -7.1387 | -123.1206 | 125.7909 | -7.1387 | -123.1206 | 125.7909
Line17_5_19 | 0.44403 | 0.13388 | 0.19753 | 0.44403 | 0.13388 | 0.19753 | 0.10254 | 0.030918 | 0.045619 | 0.10254 | 0.030918 | 0.045619 | -0.03549 | -0.037347 | 0.050252 | 0.037019 | 0.037602 | -0.050325 | -0.07964 | 0.010227 | -0.020173 | 0.082503 | -0.010212 | 0.020718 | 106.919 | 72.1808 | 147.6845 | -73.081 | -107.8192 | -32.3155 |  | 0.85026 | 1.2524 | 1.187 | 0.88184 | 1.2603 | 1.193 | -7.1002 | -123.1333 | 125.8121 | -7.2467 | -123.0134 | 125.3082
Line1_1_3 | 0.37837 | 0.10787 | 0.17693 | 0.37837 | 0.10787 | 0.17693 | 0.08738 | 0.024912 | 0.040861 | 0.08738 | 0.024912 | 0.040861 | -0.031512 | -0.028922 | 0.044513 | 0.032633 | 0.029081 | -0.044551 | -0.064224 | 0.011175 | -0.01865 | 0.066286 | -0.011183 | 0.019081 | 109.1927 | 77.8713 | 149.0534 | -70.8073 | -102.1287 | -30.9466 |  | 0.8187 | 1.2446 | 1.1811 | 0.84554 | 1.2507 | 1.1861 | -6.9424 | -123.2547 | 126.321 | -7.0187 | -123.1632 | 125.8679
Line2_1_4 | 0.4709 | 0.14524 | 0.2051 | 0.4709 | 0.14524 | 0.2051 | 0.10875 | 0.033541 | 0.047366 | 0.10875 | 0.033541 | 0.047366 | -0.034709 | -0.040645 | 0.052271 | 0.036421 | 0.040949 | -0.052362 | -0.081989 | 0.0095179 | -0.019939 | 0.085219 | -0.009488 | 0.020531 | 106.0023 | 69.9247 | 147.2005 | -73.9977 | -110.0753 | -32.7995 |  | 0.8187 | 1.2446 | 1.1811 | 0.8522 | 1.2532 | 1.1874 | -6.9424 | -123.2547 | 126.321 | -7.1387 | -123.1206 | 125.7909
Line3_1_5 | 0.44403 | 0.13388 | 0.19753 | 0.44403 | 0.13388 | 0.19753 | 0.10254 | 0.030918 | 0.045619 | 0.10254 | 0.030918 | 0.045619 | -0.033961 | -0.037092 | 0.050179 | 0.03549 | 0.037347 | -0.050252 | -0.076777 | 0.010242 | -0.019628 | 0.07964 | -0.010227 | 0.020173 | 106.919 | 72.1808 | 147.6846 | -73.081 | -107.8192 | -32.3155 |  | 0.8187 | 1.2446 | 1.1811 | 0.85026 | 1.2524 | 1.187 | -6.9424 | -123.2547 | 126.321 | -7.1002 | -123.1333 | 125.8121
Line4_2_6 | 2.2728 | 0.20814 | 0.12517 | 2.2728 | 0.20814 | 0.12517 | 0.52487 | 0.048067 | 0.028907 | 0.52487 | 0.048067 | 0.028907 | 0.15509 | -0.05881 | 0.023813 | -0.11095 | 0.058746 | -0.022701 | 0.29315 | 0.0082308 | -0.023743 | -0.20557 | -0.0058479 | 0.024152 | -69.3197 | 66.9645 | 169.4333 | 110.6803 | -113.0355 | -10.5668 |  | 0.63187 | 1.2354 | 1.1633 | 0.44506 | 1.2282 | 1.1466 | -7.2012 | -121.0026 | 124.5175 | -7.6774 | -118.7203 | 122.6598
Line5_6_7 | 2.2728 | 0.20814 | 0.12517 | 2.2728 | 0.20814 | 0.12517 | 0.52487 | 0.048067 | 0.028907 | 0.52487 | 0.048067 | 0.028907 | 0.11095 | -0.058746 | 0.022701 | -0.066814 | 0.058681 | -0.021589 | 0.20557 | 0.0058479 | -0.024152 | -0.11799 | -0.003465 | 0.024561 | -69.3197 | 66.9645 | 169.4332 | 110.6803 | -113.0355 | -10.5668 |  | 0.44506 | 1.2282 | 1.1466 | 0.25833 | 1.2229 | 1.1312 | -7.6774 | -118.7203 | 122.6598 | -8.8421 | -116.4148 | 120.7494
Line6_7_8 | 3.2016 | 0 | 0 | 3.2016 | 0 | 0 | 0.73938 | 0 | 0 | 0.73938 | 0 | 0 | 0.08542 | 8.6238e-08 | -8.7967e-08 | 2.1094e-15 | -6.0559e-08 | 5.9049e-08 | 0.17084 | -6.0043e-08 | -3.6245e-08 | 3.1556e-14 | 3.8164e-08 | 2.2259e-08 | -72.2771 | 0 | 0 | 107.7229 | 0 | 0 |  | 0.25833 | 1.2229 | 1.1312 | 0 | 1.2083 | 1.099 | -8.8421 | -116.4148 | 120.7494 | 0 | -114.0786 | 118.6733
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.991e-22 | 3.0026e-08 | -2.9523e-08 | -8.8005e-18 | -5.0605e-10 | 2.752e-12 | -1.1815e-21 | -1.883e-08 | -1.1181e-08 | 9.0127e-18 | 5.0279e-10 | -1.0263e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 1.2083 | 1.099 | 0 | 1.2083 | 1.099 | 0 | -114.0786 | 118.6733 | 0 | -114.0786 | 118.6733
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.991e-22 | 3.0026e-08 | -2.9523e-08 | -8.8005e-18 | -5.0605e-10 | 2.7522e-12 | -1.1815e-21 | -1.883e-08 | -1.1181e-08 | 9.0127e-18 | 5.0279e-10 | -1.0263e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 1.2083 | 1.099 | 0 | 1.2083 | 1.099 | 0 | -114.0786 | 118.6733 | 0 | -114.0786 | 118.6733
Line9_3_11 | 0.37837 | 0.10787 | 0.17693 | 0.37837 | 0.10787 | 0.17693 | 0.08738 | 0.024912 | 0.040861 | 0.08738 | 0.024912 | 0.040861 | -0.032633 | -0.029081 | 0.044551 | 0.033755 | 0.029241 | -0.044589 | -0.066286 | 0.011183 | -0.019081 | 0.068349 | -0.011192 | 0.019513 | 109.1927 | 77.8713 | 149.0534 | -70.8073 | -102.1287 | -30.9467 |  | 0.84554 | 1.2507 | 1.1861 | 0.87239 | 1.2568 | 1.1912 | -7.0187 | -123.1632 | 125.8679 | -7.0903 | -123.0725 | 125.4187

## LG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.088164 | 0.11042 | 0.11199 | 0.088164 | 0.11042 | 0.11199 | 0.020361 | 0.025499 | 0.025862 | 0.020361 | 0.025499 | 0.025862 | -0.0061445 | -0.011436 | -0.010803 | 0.0062214 | 0.01155 | 0.010937 | -0.021394 | -0.025536 | -0.026195 | 0.021557 | 0.025775 | 0.026441 | 105.9835 | -5.7906 | -127.4199 | -74.0165 | 174.2094 | 52.5801 |  | 1.0932 | 1.0973 | 1.0956 | 1.102 | 1.1076 | 1.1064 | -0.040679 | -119.9158 | 120.1685 | -0.11446 | -119.9275 | 120.1086
Line10_11_12 | 0.103 | 0.099118 | 0.10159 | 0.103 | 0.099118 | 0.10159 | 0.023788 | 0.02289 | 0.023462 | 0.023788 | 0.02289 | 0.023462 | -0.0016148 | -0.00098603 | -0.00045032 | 0.0017219 | 0.0010858 | 0.00055095 | -0.026388 | -0.025501 | -0.026117 | 0.026598 | 0.0257 | 0.026324 | 93.0466 | -28.1213 | -149.2763 | -86.9534 | 151.8787 | 30.7237 |  | 1.1114 | 1.1149 | 1.1133 | 1.1205 | 1.1237 | 1.1222 | -0.45524 | -120.3356 | 119.7359 | -0.65749 | -120.5406 | 119.5247
Line11_12_13 | 0.103 | 0.099118 | 0.10159 | 0.103 | 0.099118 | 0.10159 | 0.023788 | 0.02289 | 0.023462 | 0.023788 | 0.02289 | 0.023462 | -0.0017219 | -0.0010858 | -0.00055095 | 0.001829 | 0.0011855 | 0.00065157 | -0.026598 | -0.0257 | -0.026324 | 0.026807 | 0.025899 | 0.02653 | 93.0466 | -28.1213 | -149.2763 | -86.9534 | 151.8787 | 30.7237 |  | 1.1205 | 1.1237 | 1.1222 | 1.1296 | 1.1326 | 1.1311 | -0.65749 | -120.5406 | 119.5247 | -0.85648 | -120.7423 | 119.3169
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.379e-09 | 1.109e-09 | 5.4243e-10 | -1.2493e-09 | -1.0827e-09 | -6.9843e-10 | 5.0935e-10 | -3.2589e-10 | 3.3446e-10 | -4.0457e-10 | 1.6077e-10 | -2.7489e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1296 | 1.1326 | 1.1311 | 1.1296 | 1.1326 | 1.1311 | -0.85648 | -120.7423 | 119.3169 | -0.85648 | -120.7423 | 119.3169
Line13_13_14 | 0.103 | 0.099118 | 0.10159 | 0.103 | 0.099118 | 0.10159 | 0.023788 | 0.02289 | 0.023462 | 0.023788 | 0.02289 | 0.023462 | -0.001829 | -0.0011855 | -0.00065157 | 0.0019361 | 0.0012853 | 0.0007522 | -0.026807 | -0.025899 | -0.02653 | 0.027017 | 0.026097 | 0.026737 | 93.0466 | -28.1213 | -149.2763 | -86.9534 | 151.8787 | 30.7237 |  | 1.1296 | 1.1326 | 1.1311 | 1.1387 | 1.1415 | 1.1401 | -0.85648 | -120.7423 | 119.3169 | -1.0523 | -120.9409 | 119.1122
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.1936e-10 | 7.3935e-10 | 3.6162e-10 | -7.8964e-10 | -7.1307e-10 | -5.1762e-10 | 3.3956e-10 | -2.1726e-10 | 2.2297e-10 | -2.3479e-10 | 5.2139e-11 | -1.6341e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1296 | 1.1326 | 1.1311 | 1.1296 | 1.1326 | 1.1311 | -0.85648 | -120.7423 | 119.3169 | -0.85648 | -120.7423 | 119.3169
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5968e-10 | 3.6967e-10 | 1.8081e-10 | -3.2996e-10 | -3.434e-10 | -3.3681e-10 | 1.6978e-10 | -1.0863e-10 | 1.1149e-10 | -6.5005e-11 | -5.6491e-11 | -5.1922e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1296 | 1.1326 | 1.1311 | 1.1296 | 1.1326 | 1.1311 | -0.85648 | -120.7423 | 119.3169 | -0.85648 | -120.7423 | 119.3169
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6136e-10 | 2.8063e-10 | 4.9482e-11 | -2.2225e-10 | -2.3806e-10 | -2.3117e-10 | 1.5132e-10 | -1.7205e-10 | 6.3231e-11 | -2.2465e-11 | -1.3384e-11 | -7.7042e-12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1048 | 1.1086 | 1.107 | 1.1048 | 1.1086 | 1.107 | -0.3026 | -120.1797 | 119.8964 | -0.3026 | -120.1797 | 119.8964
Line17_5_19 | 0.12307 | 0.11839 | 0.1211 | 0.12307 | 0.11839 | 0.1211 | 0.028421 | 0.027341 | 0.027968 | 0.028421 | 0.027341 | 0.027968 | -0.0019605 | -0.0013032 | -0.0006319 | 0.0021131 | 0.0014456 | 0.000775 | -0.031318 | -0.03026 | -0.030932 | 0.031618 | 0.030543 | 0.031226 | 93.2949 | -27.6984 | -148.9174 | -86.7051 | 152.3016 | 31.0826 |  | 1.1041 | 1.1078 | 1.1062 | 1.1149 | 1.1184 | 1.1168 | -0.28706 | -120.1644 | 119.9122 | -0.52865 | -120.4082 | 119.6608
Line1_1_3 | 0.103 | 0.099118 | 0.10159 | 0.103 | 0.099118 | 0.10159 | 0.023788 | 0.02289 | 0.023462 | 0.023788 | 0.02289 | 0.023462 | -0.0014006 | -0.00078652 | -0.00024907 | 0.0015077 | 0.00088627 | 0.0003497 | -0.025968 | -0.025104 | -0.025704 | 0.026178 | 0.025303 | 0.02591 | 93.0466 | -28.1213 | -149.2763 | -86.9534 | 151.8787 | 30.7237 |  | 1.0932 | 1.0973 | 1.0956 | 1.1023 | 1.1061 | 1.1045 | -0.040679 | -119.9158 | 120.1685 | -0.24966 | -120.1274 | 119.9505
Line2_1_4 | 0.13159 | 0.12658 | 0.12938 | 0.13159 | 0.12658 | 0.12938 | 0.030389 | 0.029232 | 0.029878 | 0.030389 | 0.029232 | 0.029878 | -0.001995 | -0.0013413 | -0.00061172 | 0.0021694 | 0.0015042 | 0.0007751 | -0.033162 | -0.032048 | -0.032729 | 0.033505 | 0.032371 | 0.033065 | 93.4021 | -27.5192 | -148.7607 | -86.5979 | 152.4808 | 31.2393 |  | 1.0932 | 1.0973 | 1.0956 | 1.1048 | 1.1086 | 1.107 | -0.040679 | -119.9158 | 120.1685 | -0.3026 | -120.1797 | 119.8964
Line3_1_5 | 0.12307 | 0.11839 | 0.1211 | 0.12307 | 0.11839 | 0.1211 | 0.028421 | 0.027341 | 0.027968 | 0.028421 | 0.027341 | 0.027968 | -0.0018079 | -0.0011607 | -0.00048879 | 0.0019605 | 0.0013032 | 0.0006319 | -0.031019 | -0.029977 | -0.030638 | 0.031318 | 0.03026 | 0.030932 | 93.2949 | -27.6984 | -148.9174 | -86.7051 | 152.3016 | 31.0826 |  | 1.0932 | 1.0973 | 1.0956 | 1.1041 | 1.1078 | 1.1062 | -0.040679 | -119.9158 | 120.1685 | -0.28706 | -120.1644 | 119.9122
Line4_2_6 | 0.088164 | 0.11042 | 0.11199 | 0.088164 | 0.11042 | 0.11199 | 0.020361 | 0.025499 | 0.025862 | 0.020361 | 0.025499 | 0.025862 | -0.0062214 | -0.01155 | -0.010937 | 0.0062983 | 0.011663 | 0.01107 | -0.021557 | -0.025775 | -0.026441 | 0.02172 | 0.026014 | 0.026687 | 105.9835 | -5.7906 | -127.4199 | -74.0165 | 174.2094 | 52.5801 |  | 1.102 | 1.1076 | 1.1064 | 1.1107 | 1.118 | 1.1171 | -0.11446 | -119.9275 | 120.1086 | -0.18708 | -119.9389 | 120.0498
Line5_6_7 | 0.088164 | 0.11042 | 0.11199 | 0.088164 | 0.11042 | 0.11199 | 0.020361 | 0.025499 | 0.025862 | 0.020361 | 0.025499 | 0.025862 | -0.0062983 | -0.011663 | -0.01107 | 0.0063752 | 0.011776 | 0.011204 | -0.02172 | -0.026014 | -0.026687 | 0.021884 | 0.026254 | 0.026932 | 105.9835 | -5.7906 | -127.4199 | -74.0165 | 174.2094 | 52.5801 |  | 1.1107 | 1.118 | 1.1171 | 1.1195 | 1.1284 | 1.1279 | -0.18708 | -119.9389 | 120.0498 | -0.25856 | -119.9501 | 119.9922
Line6_7_8 | 0.036471 | 0 | 0 | 0.036471 | 0 | 0 | 0.0084225 | 0 | 0 | 0.0084225 | 0 | 0 | 0.0066616 | 1.4137e-09 | -8.1363e-11 | -0.0066505 | -1.2772e-09 | -2.493e-10 | 0.0066727 | -9.6784e-10 | 9.9732e-11 | -0.0066505 | 6.6374e-10 | -6.5519e-11 | -45.3062 | 0 | 0 | 134.6938 | 0 | 0 |  | 1.1195 | 1.1284 | 1.1279 | 1.1167 | 1.128 | 1.1278 | -0.25856 | -119.9501 | 119.9922 | -0.30619 | -119.9301 | 119.9629
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7608e-10 | 4.7734e-10 | -3.6172e-11 | -2.7309e-10 | -3.2252e-10 | -3.2165e-10 | 3.1473e-10 | -3.2922e-10 | 3.1354e-11 | -2.2975e-11 | 5.2988e-12 | -2.812e-12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1167 | 1.128 | 1.1278 | 1.1167 | 1.128 | 1.1278 | -0.30619 | -119.9301 | 119.9629 | -0.30619 | -119.9301 | 119.9629
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7608e-10 | 4.7734e-10 | -3.6172e-11 | -2.7309e-10 | -3.2252e-10 | -3.2165e-10 | 3.1473e-10 | -3.2922e-10 | 3.1354e-11 | -2.2975e-11 | 5.2989e-12 | -2.812e-12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1167 | 1.128 | 1.1278 | 1.1167 | 1.128 | 1.1278 | -0.30619 | -119.9301 | 119.9629 | -0.30619 | -119.9301 | 119.9629
Line9_3_11 | 0.103 | 0.099118 | 0.10159 | 0.103 | 0.099118 | 0.10159 | 0.023788 | 0.02289 | 0.023462 | 0.023788 | 0.02289 | 0.023462 | -0.0015077 | -0.00088627 | -0.0003497 | 0.0016148 | 0.00098603 | 0.00045032 | -0.026178 | -0.025303 | -0.02591 | 0.026388 | 0.025501 | 0.026117 | 93.0466 | -28.1213 | -149.2763 | -86.9534 | 151.8787 | 30.7237 |  | 1.1023 | 1.1061 | 1.1045 | 1.1114 | 1.1149 | 1.1133 | -0.24966 | -120.1274 | 119.9505 | -0.45524 | -120.3356 | 119.7359

## LG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.087708 | 0.1111 | 0.11276 | 0.087708 | 0.1111 | 0.11276 | 0.020255 | 0.025658 | 0.02604 | 0.020255 | 0.025658 | 0.02604 | -0.0061605 | -0.01199 | -0.011288 | 0.0062365 | 0.012104 | 0.011424 | -0.022368 | -0.026956 | -0.027682 | 0.02253 | 0.027199 | 0.027931 | 105.3525 | -5.9367 | -127.6424 | -74.6475 | 174.0633 | 52.3576 |  | 1.1454 | 1.1498 | 1.148 | 1.1541 | 1.1603 | 1.1589 | -0.045998 | -119.9151 | 120.173 | -0.12023 | -119.927 | 120.1124
Line10_11_12 | 0.10425 | 0.10012 | 0.10273 | 0.10425 | 0.10012 | 0.10273 | 0.024076 | 0.023122 | 0.023724 | 0.024076 | 0.023122 | 0.023724 | -0.0017733 | -0.0010803 | -0.00048344 | 0.001883 | 0.0011821 | 0.0005862 | -0.027963 | -0.026977 | -0.027657 | 0.028178 | 0.02718 | 0.027868 | 93.184 | -28.0257 | -149.2423 | -86.816 | 151.9743 | 30.7577 |  | 1.1638 | 1.1677 | 1.166 | 1.173 | 1.1766 | 1.175 | -0.44459 | -120.3188 | 119.7562 | -0.6392 | -120.5161 | 119.5526
Line11_12_13 | 0.10425 | 0.10012 | 0.10273 | 0.10425 | 0.10012 | 0.10273 | 0.024076 | 0.023122 | 0.023724 | 0.024076 | 0.023122 | 0.023724 | -0.001883 | -0.0011821 | -0.0005862 | 0.0019928 | 0.001284 | 0.00068896 | -0.028178 | -0.02718 | -0.027868 | 0.028393 | 0.027383 | 0.028079 | 93.184 | -28.0257 | -149.2423 | -86.816 | 151.9743 | 30.7577 |  | 1.173 | 1.1766 | 1.175 | 1.1822 | 1.1856 | 1.184 | -0.6392 | -120.5161 | 119.5526 | -0.83078 | -120.7104 | 119.3521
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5196e-09 | 1.2108e-09 | 5.5153e-10 | -1.3698e-09 | -1.1796e-09 | -7.3249e-10 | 5.7319e-10 | -3.9554e-10 | 3.6675e-10 | -4.5126e-10 | 2.044e-10 | -2.985e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1822 | 1.1856 | 1.184 | 1.1822 | 1.1856 | 1.184 | -0.83078 | -120.7104 | 119.3521 | -0.83078 | -120.7104 | 119.3521
Line13_13_14 | 0.10425 | 0.10012 | 0.10273 | 0.10425 | 0.10012 | 0.10273 | 0.024076 | 0.023122 | 0.023724 | 0.024076 | 0.023122 | 0.023724 | -0.0019928 | -0.001284 | -0.00068897 | 0.0021025 | 0.0013859 | 0.00079173 | -0.028393 | -0.027383 | -0.028079 | 0.028608 | 0.027585 | 0.028291 | 93.184 | -28.0257 | -149.2423 | -86.816 | 151.9743 | 30.7577 |  | 1.1822 | 1.1856 | 1.184 | 1.1914 | 1.1945 | 1.193 | -0.83078 | -120.7104 | 119.3521 | -1.0194 | -120.9018 | 119.1546
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.013e-09 | 8.0717e-10 | 3.6769e-10 | -8.6329e-10 | -7.7597e-10 | -5.4865e-10 | 3.8213e-10 | -2.6369e-10 | 2.445e-10 | -2.602e-10 | 7.2554e-11 | -1.7625e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1822 | 1.1856 | 1.184 | 1.1822 | 1.1856 | 1.184 | -0.83078 | -120.7104 | 119.3521 | -0.83078 | -120.7104 | 119.3521
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.0652e-10 | 4.0359e-10 | 1.8384e-10 | -3.5677e-10 | -3.7238e-10 | -3.648e-10 | 1.9106e-10 | -1.3185e-10 | 1.2225e-10 | -6.9135e-11 | -5.9291e-11 | -5.3996e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1822 | 1.1856 | 1.184 | 1.1822 | 1.1856 | 1.184 | -0.83078 | -120.7104 | 119.3521 | -0.83078 | -120.7104 | 119.3521
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0216e-10 | 3.0993e-10 | 4.3026e-11 | -2.4217e-10 | -2.6043e-10 | -2.5252e-10 | 1.7285e-10 | -1.9998e-10 | 7.0621e-11 | -2.4076e-11 | -1.3615e-11 | -7.0837e-12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1571 | 1.1612 | 1.1594 | 1.1571 | 1.1612 | 1.1594 | -0.29559 | -120.1666 | 119.9132 | -0.29559 | -120.1666 | 119.9132
Line17_5_19 | 0.12375 | 0.11881 | 0.12166 | 0.12375 | 0.11881 | 0.12166 | 0.028579 | 0.027438 | 0.028096 | 0.028579 | 0.027438 | 0.028096 | -0.0021352 | -0.0014133 | -0.0006719 | 0.0022896 | 0.0015569 | 0.00081615 | -0.032978 | -0.03181 | -0.032548 | 0.033281 | 0.032095 | 0.032844 | 93.4231 | -27.6085 | -148.8897 | -86.5769 | 152.3915 | 31.1103 |  | 1.1563 | 1.1604 | 1.1587 | 1.1673 | 1.1711 | 1.1694 | -0.28138 | -120.1526 | 119.9277 | -0.51235 | -120.3858 | 119.6869
Line1_1_3 | 0.10425 | 0.10012 | 0.10273 | 0.10425 | 0.10012 | 0.10273 | 0.024076 | 0.023122 | 0.023724 | 0.024076 | 0.023122 | 0.023724 | -0.0015538 | -0.00087653 | -0.00027792 | 0.0016636 | 0.0009784 | 0.00038068 | -0.027534 | -0.026572 | -0.027234 | 0.027749 | 0.026775 | 0.027445 | 93.184 | -28.0257 | -149.2423 | -86.816 | 151.9743 | 30.7577 |  | 1.1454 | 1.1498 | 1.148 | 1.1546 | 1.1588 | 1.157 | -0.045998 | -119.9151 | 120.173 | -0.24688 | -120.1185 | 119.963
Line2_1_4 | 0.13196 | 0.12669 | 0.12961 | 0.13196 | 0.12669 | 0.12961 | 0.030474 | 0.029257 | 0.029932 | 0.030474 | 0.029257 | 0.029932 | -0.0021744 | -0.0014566 | -0.00065363 | 0.0023497 | 0.0016199 | 0.00081742 | -0.034838 | -0.033609 | -0.034357 | 0.035182 | 0.033933 | 0.034694 | 93.5254 | -27.4335 | -148.7371 | -86.4746 | 152.5665 | 31.2629 |  | 1.1454 | 1.1498 | 1.148 | 1.1571 | 1.1612 | 1.1594 | -0.045998 | -119.9151 | 120.173 | -0.29559 | -120.1666 | 119.9132
Line3_1_5 | 0.12375 | 0.11881 | 0.12166 | 0.12375 | 0.11881 | 0.12166 | 0.028579 | 0.027438 | 0.028096 | 0.028579 | 0.027438 | 0.028096 | -0.0019809 | -0.0012697 | -0.00052765 | 0.0021352 | 0.0014133 | 0.0006719 | -0.032676 | -0.031524 | -0.032251 | 0.032978 | 0.03181 | 0.032548 | 93.4231 | -27.6085 | -148.8897 | -86.5769 | 152.3915 | 31.1103 |  | 1.1454 | 1.1498 | 1.148 | 1.1563 | 1.1604 | 1.1587 | -0.045998 | -119.9151 | 120.173 | -0.28138 | -120.1526 | 119.9277
Line4_2_6 | 0.087708 | 0.1111 | 0.11276 | 0.087708 | 0.1111 | 0.11276 | 0.020255 | 0.025658 | 0.02604 | 0.020255 | 0.025658 | 0.02604 | -0.0062365 | -0.012104 | -0.011424 | 0.0063125 | 0.012219 | 0.01156 | -0.02253 | -0.027199 | -0.027931 | 0.022692 | 0.027441 | 0.02818 | 105.3525 | -5.9367 | -127.6424 | -74.6475 | 174.0633 | 52.3576 |  | 1.1541 | 1.1603 | 1.1589 | 1.1628 | 1.1707 | 1.1697 | -0.12023 | -119.927 | 120.1124 | -0.19336 | -119.9387 | 120.0529
Line5_6_7 | 0.087708 | 0.1111 | 0.11276 | 0.087708 | 0.1111 | 0.11276 | 0.020255 | 0.025658 | 0.02604 | 0.020255 | 0.025658 | 0.02604 | -0.0063125 | -0.012219 | -0.01156 | 0.0063885 | 0.012333 | 0.011696 | -0.022692 | -0.027441 | -0.02818 | 0.022853 | 0.027683 | 0.028429 | 105.3525 | -5.9367 | -127.6424 | -74.6475 | 174.0633 | 52.3576 |  | 1.1628 | 1.1707 | 1.1697 | 1.1715 | 1.1811 | 1.1805 | -0.19336 | -119.9387 | 120.0529 | -0.2654 | -119.9503 | 119.9945
Line6_7_8 | 0.038167 | 0 | 0 | 0.038167 | 0 | 0 | 0.0088142 | 0 | 0 | 0.0088142 | 0 | 0 | 0.0072956 | 1.5477e-09 | -1.3601e-10 | -0.0072835 | -1.3945e-09 | -2.375e-10 | 0.0073077 | -1.093e-09 | 1.1546e-10 | -0.0072835 | 7.4891e-10 | -7.5734e-11 | -45.313 | 0 | 0 | 134.687 | 0 | 0 |  | 1.1715 | 1.1811 | 1.1805 | 1.1686 | 1.1807 | 1.1804 | -0.2654 | -119.9503 | 119.9945 | -0.31303 | -119.9303 | 119.9653
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2401e-10 | 5.2261e-10 | -5.5248e-11 | -2.9405e-10 | -3.4932e-10 | -3.48e-10 | 3.5377e-10 | -3.7156e-10 | 3.6423e-11 | -2.5751e-11 | 5.7948e-12 | -2.8872e-12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1686 | 1.1807 | 1.1804 | 1.1686 | 1.1807 | 1.1804 | -0.31303 | -119.9303 | 119.9653 | -0.31303 | -119.9303 | 119.9653
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2401e-10 | 5.2261e-10 | -5.5248e-11 | -2.9405e-10 | -3.4932e-10 | -3.48e-10 | 3.5377e-10 | -3.7156e-10 | 3.6423e-11 | -2.5751e-11 | 5.7947e-12 | -2.8872e-12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1686 | 1.1807 | 1.1804 | 1.1686 | 1.1807 | 1.1804 | -0.31303 | -119.9303 | 119.9653 | -0.31303 | -119.9303 | 119.9653
Line9_3_11 | 0.10425 | 0.10012 | 0.10273 | 0.10425 | 0.10012 | 0.10273 | 0.024076 | 0.023122 | 0.023724 | 0.024076 | 0.023122 | 0.023724 | -0.0016636 | -0.0009784 | -0.00038068 | 0.0017733 | 0.0010803 | 0.00048344 | -0.027749 | -0.026775 | -0.027445 | 0.027963 | 0.026977 | 0.027657 | 93.184 | -28.0257 | -149.2423 | -86.816 | 151.9743 | 30.7577 |  | 1.1546 | 1.1588 | 1.157 | 1.1638 | 1.1677 | 1.166 | -0.24688 | -120.1185 | 119.963 | -0.44459 | -120.3188 | 119.7562

## LG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.26704 | 0.024198 | 0.023967 | 0.26704 | 0.024198 | 0.023967 | 0.061671 | 0.0055882 | 0.0055349 | 0.061671 | 0.0055883 | 0.005535 | 0.0048022 | -0.0043997 | 0.0048023 | -0.00362 | 0.0044278 | -0.0047745 | 0.0049937 | 0.0076762 | 0.0068284 | -0.0037623 | -0.0076468 | -0.0067996 | -85.0499 | 94.5264 | 95.2013 | 94.9501 | -85.4736 | -84.7987 |  | 0.11234 | 1.5833 | 1.5082 | 0.08466 | 1.5812 | 1.5011 | -38.9301 | -145.6541 | 150.0832 | -38.9452 | -145.4012 | 150.1259
Line10_11_12 | 0.024555 | 0.024135 | 0.024056 | 0.024555 | 0.024135 | 0.024056 | 0.0056707 | 0.0055737 | 0.0055555 | 0.0056707 | 0.0055737 | 0.0055555 | -0.00045512 | -0.0043268 | 0.0048013 | 0.00046098 | 0.0043324 | -0.0047959 | -0.00046961 | 0.0076858 | 0.0068477 | 0.00047572 | -0.0076801 | -0.0068421 | 95.181 | 95.0683 | 95.1363 | -84.819 | -84.9317 | -84.8637 |  | 0.11532 | 1.5824 | 1.5054 | 0.11682 | 1.582 | 1.504 | -38.9215 | -145.5542 | 150.0999 | -38.9174 | -145.5042 | 150.1082
Line11_12_13 | 0.024555 | 0.024135 | 0.024056 | 0.024555 | 0.024135 | 0.024056 | 0.0056707 | 0.0055737 | 0.0055555 | 0.0056708 | 0.0055738 | 0.0055556 | -0.00046098 | -0.0043324 | 0.0047959 | 0.00046684 | 0.004338 | -0.0047904 | -0.00047572 | 0.0076801 | 0.0068421 | 0.00048184 | -0.0076744 | -0.0068364 | 95.181 | 95.0682 | 95.1362 | -84.819 | -84.9318 | -84.8638 |  | 0.11682 | 1.582 | 1.504 | 0.11831 | 1.5816 | 1.5026 | -38.9174 | -145.5042 | 150.1082 | -38.9134 | -145.4541 | 150.1166
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6557e-08 | 1.7716e-07 | -1.7068e-07 | -1.0768e-08 | -1.223e-07 | 1.1003e-07 | 1.8775e-08 | -2.8393e-07 | -2.6825e-07 | -1.2775e-08 | 1.8692e-07 | 1.8146e-07 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.11831 | 1.5816 | 1.5026 | 0.11831 | 1.5816 | 1.5026 | -38.9134 | -145.4541 | 150.1166 | -38.9134 | -145.4541 | 150.1166
Line13_13_14 | 0.024556 | 0.024136 | 0.024057 | 0.024556 | 0.024137 | 0.024058 | 0.005671 | 0.005574 | 0.0055558 | 0.0056711 | 0.0055741 | 0.0055559 | -0.00046686 | -0.0043382 | 0.0047906 | 0.00047272 | 0.0043438 | -0.0047851 | -0.00048186 | 0.0076747 | 0.0068367 | 0.00048797 | -0.007669 | -0.006831 | 95.1808 | 95.0681 | 95.1361 | -84.8192 | -84.9319 | -84.8639 |  | 0.11831 | 1.5816 | 1.5026 | 0.1198 | 1.5812 | 1.5012 | -38.9134 | -145.4541 | 150.1166 | -38.9095 | -145.4041 | 150.1249
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1038e-08 | 1.1811e-07 | -1.1378e-07 | -5.2495e-09 | -6.3251e-08 | 5.3141e-08 | 1.2517e-08 | -1.8929e-07 | -1.7883e-07 | -6.5172e-09 | 9.2276e-08 | 9.2043e-08 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.11831 | 1.5816 | 1.5026 | 0.11831 | 1.5816 | 1.5026 | -38.9134 | -145.4541 | 150.1166 | -38.9134 | -145.4541 | 150.1166
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5189e-09 | 5.9053e-08 | -5.6892e-08 | 2.6934e-10 | -4.1977e-09 | -3.751e-09 | 6.2583e-09 | -9.4644e-08 | -8.9416e-08 | -2.5886e-10 | -2.3678e-09 | 2.6262e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.11831 | 1.5816 | 1.5026 | 0.11831 | 1.5816 | 1.5026 | -38.9134 | -145.4541 | 150.1166 | -38.9134 | -145.4541 | 150.1166
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3104e-09 | 5.9412e-08 | -5.6985e-08 | 2.6096e-10 | -4.2144e-09 | -3.7839e-09 | 6.062e-09 | -9.5018e-08 | -9.0185e-08 | -2.4917e-10 | -2.3827e-09 | 2.6317e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.11384 | 1.5829 | 1.5068 | 0.11384 | 1.5829 | 1.5068 | -38.9293 | -145.6038 | 150.0918 | -38.9293 | -145.6038 | 150.0918
Line17_5_19 | 0.024649 | 0.024227 | 0.024147 | 0.024649 | 0.024227 | 0.024148 | 0.0056924 | 0.005595 | 0.0055766 | 0.0056924 | 0.005595 | 0.0055767 | -0.00044937 | -0.0043654 | 0.0048005 | 0.00045527 | 0.0043711 | -0.004795 | -0.00046688 | 0.0077054 | 0.0068967 | 0.00047304 | -0.0076997 | -0.006891 | 94.9769 | 94.863 | 94.9319 | -85.0232 | -85.137 | -85.0681 |  | 0.11384 | 1.5829 | 1.5068 | 0.11534 | 1.5824 | 1.5054 | -38.9284 | -145.6039 | 150.0918 | -38.9268 | -145.5537 | 150.1003
Line1_1_3 | 0.024554 | 0.024134 | 0.024055 | 0.024554 | 0.024134 | 0.024056 | 0.0056705 | 0.0055735 | 0.0055553 | 0.0056706 | 0.0055736 | 0.0055554 | -0.0004434 | -0.0043155 | 0.0048122 | 0.00044926 | 0.0043211 | -0.0048068 | -0.00045738 | 0.0076972 | 0.006859 | 0.00046349 | -0.0076915 | -0.0068534 | 95.1811 | 95.0683 | 95.1363 | -84.8189 | -84.9317 | -84.8637 |  | 0.11234 | 1.5833 | 1.5082 | 0.11383 | 1.5829 | 1.5068 | -38.9301 | -145.6541 | 150.0832 | -38.9258 | -145.6041 | 150.0915
Line2_1_4 | 0.024679 | 0.024257 | 0.024177 | 0.02468 | 0.024257 | 0.024178 | 0.0056994 | 0.0056019 | 0.0055835 | 0.0056995 | 0.005602 | 0.0055836 | -0.00044347 | -0.0043744 | 0.0048037 | 0.00044939 | 0.0043801 | -0.0047982 | -0.00046182 | 0.0077155 | 0.0069168 | 0.000468 | -0.0077098 | -0.0069111 | 94.9085 | 94.7943 | 94.8635 | -85.0915 | -85.2057 | -85.1365 |  | 0.11234 | 1.5833 | 1.5082 | 0.11384 | 1.5829 | 1.5068 | -38.9301 | -145.6541 | 150.0832 | -38.9293 | -145.6038 | 150.0918
Line3_1_5 | 0.024648 | 0.024227 | 0.024147 | 0.024649 | 0.024227 | 0.024147 | 0.0056923 | 0.0055949 | 0.0055765 | 0.0056924 | 0.005595 | 0.0055766 | -0.00044346 | -0.0043597 | 0.004806 | 0.00044937 | 0.0043654 | -0.0048005 | -0.00046071 | 0.0077111 | 0.0069024 | 0.00046688 | -0.0077054 | -0.0068967 | 94.9769 | 94.863 | 94.9319 | -85.0231 | -85.137 | -85.0681 |  | 0.11234 | 1.5833 | 1.5082 | 0.11384 | 1.5829 | 1.5068 | -38.9301 | -145.6541 | 150.0832 | -38.9284 | -145.6039 | 150.0918
Line4_2_6 | 0.26704 | 0.024198 | 0.023967 | 0.26704 | 0.024198 | 0.023967 | 0.061671 | 0.0055883 | 0.005535 | 0.061671 | 0.0055884 | 0.005535 | 0.00362 | -0.0044278 | 0.0047745 | -0.0024378 | 0.0044559 | -0.0047466 | 0.0037623 | 0.0076468 | 0.0067996 | -0.002531 | -0.0076174 | -0.0067708 | -85.0499 | 94.5264 | 95.2013 | 94.9501 | -85.4736 | -84.7987 |  | 0.08466 | 1.5812 | 1.5011 | 0.056981 | 1.5792 | 1.4939 | -38.9452 | -145.4012 | 150.1259 | -38.975 | -145.1476 | 150.1689
Line5_6_7 | 0.26704 | 0.024198 | 0.023967 | 0.26704 | 0.024199 | 0.023968 | 0.061671 | 0.0055884 | 0.005535 | 0.06167 | 0.0055884 | 0.0055351 | 0.0024378 | -0.0044559 | 0.0047466 | -0.0012556 | 0.004484 | -0.0047188 | 0.002531 | 0.0076174 | 0.0067708 | -0.0012997 | -0.007588 | -0.0067419 | -85.0499 | 94.5263 | 95.2012 | 94.9501 | -85.4737 | -84.7988 |  | 0.056981 | 1.5792 | 1.4939 | 0.029302 | 1.5772 | 1.4867 | -38.975 | -145.1476 | 150.1689 | -39.0611 | -144.8933 | 150.2124
Line6_7_8 | 0.2929 | 0 | 0 | 0.2929 | 0 | 0 | 0.067643 | 0 | 0 | 0.067643 | 0 | 0 | 0.0013727 | 1.884e-07 | -1.6738e-07 | 4.0685e-15 | -1.3052e-07 | 1.0741e-07 | 0.0014299 | -2.8437e-07 | -2.7456e-07 | -8.7571e-15 | 1.8671e-07 | 1.8523e-07 | -85.2303 | 0 | 0 | 94.7697 | 0 | 0 |  | 0.029302 | 1.5772 | 1.4867 | 0 | 1.5756 | 1.481 | -39.0611 | -144.8933 | 150.2124 | 0 | -144.6883 | 150.2489
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.9002e-21 | 6.32e-08 | -5.5499e-08 | -2.2451e-17 | -4.1157e-09 | -3.5856e-09 | 9.006e-21 | -9.4503e-08 | -9.1318e-08 | 2.3271e-17 | -2.2923e-09 | 2.5987e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 1.5756 | 1.481 | 0 | 1.5756 | 1.481 | 0 | -144.6883 | 150.2489 | 0 | -144.6883 | 150.2489
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.9002e-21 | 6.32e-08 | -5.5499e-08 | -2.2451e-17 | -4.1157e-09 | -3.5856e-09 | 9.006e-21 | -9.4503e-08 | -9.1318e-08 | 2.3271e-17 | -2.2923e-09 | 2.5987e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 1.5756 | 1.481 | 0 | 1.5756 | 1.481 | 0 | -144.6883 | 150.2489 | 0 | -144.6883 | 150.2489
Line9_3_11 | 0.024554 | 0.024134 | 0.024056 | 0.024555 | 0.024135 | 0.024056 | 0.0056706 | 0.0055736 | 0.0055554 | 0.0056707 | 0.0055737 | 0.0055555 | -0.00044926 | -0.0043211 | 0.0048068 | 0.00045512 | 0.0043268 | -0.0048013 | -0.00046349 | 0.0076915 | 0.0068534 | 0.00046961 | -0.0076858 | -0.0068477 | 95.181 | 95.0683 | 95.1363 | -84.819 | -84.9317 | -84.8637 |  | 0.11383 | 1.5829 | 1.5068 | 0.11532 | 1.5824 | 1.5054 | -38.9258 | -145.6041 | 150.0915 | -38.9215 | -145.5542 | 150.0999

## LG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.25299 | 0.022924 | 0.022705 | 0.25299 | 0.022924 | 0.022706 | 0.058425 | 0.0052941 | 0.0052436 | 0.058425 | 0.0052942 | 0.0052437 | 0.00431 | -0.0039487 | 0.0043101 | -0.003249 | 0.003974 | -0.0042851 | 0.0044818 | 0.0068894 | 0.0061285 | -0.0033767 | -0.0068631 | -0.0061027 | -85.0499 | 94.5264 | 95.2013 | 94.9501 | -85.4736 | -84.7987 |  | 0.10643 | 1.4999 | 1.4289 | 0.080204 | 1.498 | 1.4221 | -38.9301 | -145.6541 | 150.0832 | -38.9452 | -145.4012 | 150.1259
Line10_11_12 | 0.023262 | 0.022864 | 0.02279 | 0.023263 | 0.022865 | 0.02279 | 0.0053722 | 0.0052803 | 0.0052631 | 0.0053723 | 0.0052804 | 0.0052631 | -0.00040847 | -0.0038833 | 0.0043092 | 0.00041373 | 0.0038884 | -0.0043043 | -0.00042147 | 0.0068981 | 0.0061459 | 0.00042696 | -0.006893 | -0.0061408 | 95.181 | 95.0683 | 95.1363 | -84.819 | -84.9317 | -84.8637 |  | 0.10925 | 1.4992 | 1.4262 | 0.11067 | 1.4988 | 1.4248 | -38.9215 | -145.5542 | 150.0999 | -38.9174 | -145.5042 | 150.1082
Line11_12_13 | 0.023263 | 0.022865 | 0.02279 | 0.023263 | 0.022865 | 0.02279 | 0.0053723 | 0.0052804 | 0.0052631 | 0.0053723 | 0.0052805 | 0.0052632 | -0.00041373 | -0.0038884 | 0.0043043 | 0.00041899 | 0.0038934 | -0.0042994 | -0.00042696 | 0.0068929 | 0.0061408 | 0.00043245 | -0.0068878 | -0.0061357 | 95.181 | 95.0682 | 95.1362 | -84.819 | -84.9318 | -84.8638 |  | 0.11067 | 1.4988 | 1.4248 | 0.11208 | 1.4984 | 1.4235 | -38.9174 | -145.5042 | 150.1082 | -38.9134 | -145.4541 | 150.1166
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.486e-08 | 1.59e-07 | -1.5318e-07 | -9.6647e-09 | -1.0977e-07 | 9.8756e-08 | 1.6851e-08 | -2.5483e-07 | -2.4076e-07 | -1.1466e-08 | 1.6776e-07 | 1.6286e-07 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.11208 | 1.4984 | 1.4235 | 0.11208 | 1.4984 | 1.4235 | -38.9134 | -145.4541 | 150.1166 | -38.9134 | -145.4541 | 150.1166
Line13_13_14 | 0.023264 | 0.022866 | 0.022791 | 0.023264 | 0.022866 | 0.022791 | 0.0053725 | 0.0052807 | 0.0052634 | 0.0053726 | 0.0052807 | 0.0052635 | -0.00041901 | -0.0038936 | 0.0042996 | 0.00042427 | 0.0038986 | -0.0042947 | -0.00043247 | 0.0068881 | 0.006136 | 0.00043796 | -0.006883 | -0.0061309 | 95.1808 | 95.0681 | 95.1361 | -84.8192 | -84.9319 | -84.8639 |  | 0.11208 | 1.4984 | 1.4235 | 0.1135 | 1.498 | 1.4222 | -38.9134 | -145.4541 | 150.1166 | -38.9095 | -145.4041 | 150.1249
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.9065e-09 | 1.06e-07 | -1.0212e-07 | -4.7115e-09 | -5.6768e-08 | 4.7695e-08 | 1.1234e-08 | -1.6989e-07 | -1.605e-07 | -5.8492e-09 | 8.2819e-08 | 8.2609e-08 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.11208 | 1.4984 | 1.4235 | 0.11208 | 1.4984 | 1.4235 | -38.9134 | -145.4541 | 150.1166 | -38.9134 | -145.4541 | 150.1166
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.9532e-09 | 5.3e-08 | -5.1061e-08 | 2.4173e-10 | -3.7674e-09 | -3.3665e-09 | 5.6169e-09 | -8.4944e-08 | -8.0252e-08 | -2.3233e-10 | -2.1251e-09 | 2.357e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.11208 | 1.4984 | 1.4235 | 0.11208 | 1.4984 | 1.4235 | -38.9134 | -145.4541 | 150.1166 | -38.9134 | -145.4541 | 150.1166
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7662e-09 | 5.3323e-08 | -5.1144e-08 | 2.3421e-10 | -3.7825e-09 | -3.3961e-09 | 5.4407e-09 | -8.5279e-08 | -8.0941e-08 | -2.2363e-10 | -2.1385e-09 | 2.3619e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.10785 | 1.4996 | 1.4275 | 0.10785 | 1.4996 | 1.4275 | -38.9293 | -145.6038 | 150.0918 | -38.9293 | -145.6038 | 150.0918
Line17_5_19 | 0.023351 | 0.022952 | 0.022876 | 0.023352 | 0.022952 | 0.022877 | 0.0053928 | 0.0053005 | 0.0052831 | 0.0053928 | 0.0053006 | 0.0052832 | -0.00040331 | -0.003918 | 0.0043085 | 0.00040861 | 0.0039231 | -0.0043036 | -0.00041903 | 0.0069156 | 0.0061899 | 0.00042456 | -0.0069105 | -0.0061848 | 94.9769 | 94.863 | 94.9319 | -85.0232 | -85.137 | -85.0681 |  | 0.10785 | 1.4996 | 1.4275 | 0.10926 | 1.4992 | 1.4262 | -38.9284 | -145.6039 | 150.0918 | -38.9268 | -145.5537 | 150.1003
Line1_1_3 | 0.023262 | 0.022864 | 0.022789 | 0.023262 | 0.022864 | 0.022789 | 0.0053721 | 0.0052802 | 0.0052629 | 0.0053721 | 0.0052803 | 0.005263 | -0.00039795 | -0.0038732 | 0.004319 | 0.00040321 | 0.0038782 | -0.0043141 | -0.0004105 | 0.0069083 | 0.006156 | 0.00041599 | -0.0069032 | -0.006151 | 95.1811 | 95.0683 | 95.1363 | -84.8189 | -84.9317 | -84.8637 |  | 0.10643 | 1.4999 | 1.4289 | 0.10784 | 1.4995 | 1.4275 | -38.9301 | -145.6541 | 150.0832 | -38.9258 | -145.6041 | 150.0915
Line2_1_4 | 0.02338 | 0.02298 | 0.022905 | 0.023381 | 0.022981 | 0.022905 | 0.0053995 | 0.0053071 | 0.0052896 | 0.0053995 | 0.0053071 | 0.0052897 | -0.00039802 | -0.0039261 | 0.0043114 | 0.00040333 | 0.0039312 | -0.0043065 | -0.00041449 | 0.0069248 | 0.0062079 | 0.00042003 | -0.0069196 | -0.0062027 | 94.9085 | 94.7943 | 94.8635 | -85.0915 | -85.2057 | -85.1365 |  | 0.10643 | 1.4999 | 1.4289 | 0.10785 | 1.4996 | 1.4275 | -38.9301 | -145.6541 | 150.0832 | -38.9293 | -145.6038 | 150.0918
Line3_1_5 | 0.023351 | 0.022952 | 0.022876 | 0.023351 | 0.022952 | 0.022876 | 0.0053927 | 0.0053004 | 0.005283 | 0.0053928 | 0.0053005 | 0.0052831 | -0.00039801 | -0.0039129 | 0.0043134 | 0.00040331 | 0.003918 | -0.0043085 | -0.00041349 | 0.0069208 | 0.006195 | 0.00041902 | -0.0069156 | -0.0061899 | 94.9769 | 94.863 | 94.9319 | -85.0231 | -85.137 | -85.0681 |  | 0.10643 | 1.4999 | 1.4289 | 0.10785 | 1.4996 | 1.4275 | -38.9301 | -145.6541 | 150.0832 | -38.9284 | -145.6039 | 150.0918
Line4_2_6 | 0.25299 | 0.022924 | 0.022706 | 0.25299 | 0.022925 | 0.022706 | 0.058425 | 0.0052942 | 0.0052437 | 0.058425 | 0.0052942 | 0.0052437 | 0.003249 | -0.003974 | 0.0042851 | -0.0021879 | 0.0039992 | -0.0042601 | 0.0033767 | 0.0068631 | 0.0061027 | -0.0022716 | -0.0068367 | -0.0060768 | -85.0499 | 94.5264 | 95.2013 | 94.9501 | -85.4736 | -84.7987 |  | 0.080204 | 1.498 | 1.4221 | 0.053982 | 1.4961 | 1.4153 | -38.9452 | -145.4012 | 150.1259 | -38.975 | -145.1476 | 150.1689
Line5_6_7 | 0.25299 | 0.022925 | 0.022706 | 0.25299 | 0.022925 | 0.022706 | 0.058425 | 0.0052942 | 0.0052437 | 0.058425 | 0.0052943 | 0.0052438 | 0.0021879 | -0.0039992 | 0.0042601 | -0.0011269 | 0.0040244 | -0.0042352 | 0.0022716 | 0.0068367 | 0.0060768 | -0.0011665 | -0.0068103 | -0.0060509 | -85.0499 | 94.5263 | 95.2012 | 94.9501 | -85.4737 | -84.7988 |  | 0.053982 | 1.4961 | 1.4153 | 0.02776 | 1.4942 | 1.4085 | -38.975 | -145.1476 | 150.1689 | -39.0611 | -144.8933 | 150.2124
Line6_7_8 | 0.27749 | 0 | 0 | 0.27749 | 0 | 0 | 0.064083 | 0 | 0 | 0.064083 | 0 | 0 | 0.001232 | 1.6909e-07 | -1.5023e-07 | 3.6525e-15 | -1.1714e-07 | 9.6404e-08 | 0.0012833 | -2.5522e-07 | -2.4642e-07 | -7.851e-15 | 1.6758e-07 | 1.6625e-07 | -85.2303 | 0 | 0 | 94.7697 | 0 | 0 |  | 0.02776 | 1.4942 | 1.4085 | 0 | 1.4926 | 1.403 | -39.0611 | -144.8933 | 150.2124 | 0 | -144.6883 | 150.2489
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.3984e-21 | 5.6723e-08 | -4.9811e-08 | -2.015e-17 | -3.6938e-09 | -3.2181e-09 | 8.0738e-21 | -8.4817e-08 | -8.1959e-08 | 2.0886e-17 | -2.0574e-09 | 2.3324e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 1.4926 | 1.403 | 0 | 1.4926 | 1.403 | 0 | -144.6883 | 150.2489 | 0 | -144.6883 | 150.2489
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.3984e-21 | 5.6723e-08 | -4.9811e-08 | -2.015e-17 | -3.6938e-09 | -3.2181e-09 | 8.0738e-21 | -8.4817e-08 | -8.1959e-08 | 2.0886e-17 | -2.0574e-09 | 2.3324e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 1.4926 | 1.403 | 0 | 1.4926 | 1.403 | 0 | -144.6883 | 150.2489 | 0 | -144.6883 | 150.2489
Line9_3_11 | 0.023262 | 0.022864 | 0.022789 | 0.023262 | 0.022864 | 0.02279 | 0.0053721 | 0.0052803 | 0.005263 | 0.0053722 | 0.0052803 | 0.0052631 | -0.00040321 | -0.0038782 | 0.0043141 | 0.00040847 | 0.0038833 | -0.0043092 | -0.00041599 | 0.0069032 | 0.006151 | 0.00042147 | -0.0068981 | -0.0061459 | 95.181 | 95.0683 | 95.1363 | -84.819 | -84.9317 | -84.8637 |  | 0.10784 | 1.4995 | 1.4275 | 0.10925 | 1.4992 | 1.4262 | -38.9258 | -145.6041 | 150.0915 | -38.9215 | -145.5542 | 150.0999

## LG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.026119 | 0.0023667 | 0.0023441 | 0.026119 | 0.0023668 | 0.0023442 | 0.0060319 | 0.00054657 | 0.00054136 | 0.0060319 | 0.00054658 | 0.00054136 | 0.003799 | -0.00016814 | 0.00050368 | -0.0037876 | 0.00016841 | -0.00050342 | 0.0037772 | 0.000536 | -6.1031e-05 | -0.0037655 | -0.00053572 | 6.1309e-05 | -48.4415 | 131.1349 | 131.8098 | 131.5585 | -48.8651 | -48.1902 |  | 0.88815 | 1.0278 | 0.93721 | 0.88544 | 1.0274 | 0.93678 | -3.6057 | -121.4487 | 124.9009 | -3.6098 | -121.4139 | 124.8663
Line10_11_12 | 0.0024016 | 0.0023606 | 0.0023528 | 0.0024017 | 0.0023606 | 0.0023529 | 0.00055463 | 0.00054515 | 0.00054337 | 0.00055464 | 0.00054516 | 0.00054337 | -0.00035083 | -0.00016275 | 0.00050551 | 0.00035089 | 0.0001628 | -0.00050547 | -0.00034603 | 0.00053606 | -6.0794e-05 | 0.00034609 | -0.00053601 | 6.0849e-05 | 131.7895 | 131.6767 | 131.7447 | -48.2105 | -48.3233 | -48.2553 |  | 0.88844 | 1.0276 | 0.93704 | 0.88859 | 1.0276 | 0.93696 | -3.6052 | -121.435 | 124.8872 | -3.6049 | -121.4281 | 124.8804
Line11_12_13 | 0.0024017 | 0.0023606 | 0.0023529 | 0.0024017 | 0.0023606 | 0.0023529 | 0.00055464 | 0.00054516 | 0.00054337 | 0.00055465 | 0.00054516 | 0.00054338 | -0.00035089 | -0.0001628 | 0.00050547 | 0.00035095 | 0.00016286 | -0.00050542 | -0.00034609 | 0.00053601 | -6.0849e-05 | 0.00034615 | -0.00053596 | 6.0905e-05 | 131.7895 | 131.6767 | 131.7447 | -48.2105 | -48.3233 | -48.2553 |  | 0.88859 | 1.0276 | 0.93696 | 0.88873 | 1.0275 | 0.93687 | -3.6049 | -121.4281 | 124.8804 | -3.6047 | -121.4212 | 124.8735
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2474e-08 | 7.0587e-09 | -1.9334e-08 | -8.1228e-09 | -4.9989e-09 | 1.2923e-08 | 1.3515e-08 | -2.006e-08 | 1.4601e-09 | -9.2047e-09 | 1.3284e-08 | -6.9614e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.88873 | 1.0275 | 0.93687 | 0.88873 | 1.0275 | 0.93687 | -3.6047 | -121.4212 | 124.8735 | -3.6047 | -121.4212 | 124.8735
Line13_13_14 | 0.0024018 | 0.0023607 | 0.002353 | 0.0024018 | 0.0023607 | 0.002353 | 0.00055467 | 0.00054518 | 0.0005434 | 0.00055468 | 0.00054519 | 0.00054341 | -0.00035096 | -0.00016286 | 0.00050544 | 0.00035102 | 0.00016292 | -0.00050539 | -0.00034617 | 0.00053598 | -6.0906e-05 | 0.00034623 | -0.00053593 | 6.0962e-05 | 131.7893 | 131.6766 | 131.7446 | -48.2107 | -48.3234 | -48.2554 |  | 0.88873 | 1.0275 | 0.93687 | 0.88888 | 1.0274 | 0.93679 | -3.6047 | -121.4212 | 124.8735 | -3.6044 | -121.4144 | 124.8667
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3163e-09 | 4.7058e-09 | -1.289e-08 | -3.9646e-09 | -2.646e-09 | 6.4781e-09 | 9.0101e-09 | -1.3373e-08 | 9.7339e-10 | -4.6997e-09 | 6.5977e-09 | -2.0944e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.88873 | 1.0275 | 0.93687 | 0.88873 | 1.0275 | 0.93687 | -3.6047 | -121.4212 | 124.8735 | -3.6047 | -121.4212 | 124.8735
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1582e-09 | 2.3529e-09 | -6.4448e-09 | 1.9353e-10 | -2.9308e-10 | 3.33e-11 | 4.505e-09 | -6.6865e-09 | 4.8669e-10 | -1.9464e-10 | -8.8772e-11 | 2.7725e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.88873 | 1.0275 | 0.93687 | 0.88873 | 1.0275 | 0.93687 | -3.6047 | -121.4212 | 124.8735 | -3.6047 | -121.4212 | 124.8735
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1556e-09 | 2.3837e-09 | -6.4726e-09 | 1.9485e-10 | -2.9395e-10 | 3.2344e-11 | 4.5345e-09 | -6.7053e-09 | 4.6327e-10 | -1.9458e-10 | -9.0072e-11 | 2.7849e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.8883 | 1.0277 | 0.93712 | 0.8883 | 1.0277 | 0.93712 | -3.6055 | -121.4418 | 124.8941 | -3.6055 | -121.4418 | 124.8941
Line17_5_19 | 0.0024108 | 0.0023696 | 0.0023618 | 0.0024109 | 0.0023696 | 0.0023618 | 0.00055676 | 0.00054723 | 0.00054544 | 0.00055676 | 0.00054724 | 0.00054544 | -0.00035087 | -0.00016524 | 0.00050771 | 0.00035093 | 0.0001653 | -0.00050766 | -0.00034854 | 0.00053757 | -5.9159e-05 | 0.00034861 | -0.00053752 | 5.9215e-05 | 131.5853 | 131.4715 | 131.5403 | -48.4147 | -48.5285 | -48.4597 |  | 0.8883 | 1.0277 | 0.93712 | 0.88844 | 1.0276 | 0.93704 | -3.6055 | -121.4418 | 124.8941 | -3.6053 | -121.4349 | 124.8872
Line1_1_3 | 0.0024016 | 0.0023605 | 0.0023528 | 0.0024016 | 0.0023605 | 0.0023528 | 0.00055462 | 0.00054514 | 0.00054335 | 0.00055463 | 0.00054514 | 0.00054336 | -0.00035071 | -0.00016264 | 0.00050561 | 0.00035077 | 0.00016269 | -0.00050556 | -0.0003459 | 0.00053615 | -6.0683e-05 | 0.00034596 | -0.0005361 | 6.0739e-05 | 131.7896 | 131.6768 | 131.7448 | -48.2104 | -48.3232 | -48.2552 |  | 0.88815 | 1.0278 | 0.93721 | 0.8883 | 1.0277 | 0.93712 | -3.6057 | -121.4487 | 124.9009 | -3.6055 | -121.4418 | 124.8941
Line2_1_4 | 0.0024138 | 0.0023725 | 0.0023647 | 0.0024139 | 0.0023726 | 0.0023648 | 0.00055745 | 0.00054791 | 0.00054611 | 0.00055745 | 0.00054792 | 0.00054612 | -0.00035084 | -0.00016604 | 0.00050846 | 0.0003509 | 0.00016609 | -0.00050841 | -0.00034934 | 0.00053809 | -5.857e-05 | 0.0003494 | -0.00053804 | 5.8626e-05 | 131.517 | 131.4028 | 131.4719 | -48.483 | -48.5972 | -48.5281 |  | 0.88815 | 1.0278 | 0.93721 | 0.8883 | 1.0277 | 0.93712 | -3.6057 | -121.4487 | 124.9009 | -3.6055 | -121.4418 | 124.8941
Line3_1_5 | 0.0024108 | 0.0023696 | 0.0023618 | 0.0024108 | 0.0023696 | 0.0023618 | 0.00055675 | 0.00054723 | 0.00054543 | 0.00055676 | 0.00054723 | 0.00054544 | -0.00035081 | -0.00016519 | 0.00050775 | 0.00035087 | 0.00016524 | -0.00050771 | -0.00034848 | 0.00053762 | -5.9103e-05 | 0.00034854 | -0.00053757 | 5.9159e-05 | 131.5854 | 131.4715 | 131.5404 | -48.4146 | -48.5285 | -48.4596 |  | 0.88815 | 1.0278 | 0.93721 | 0.8883 | 1.0277 | 0.93712 | -3.6057 | -121.4487 | 124.9009 | -3.6055 | -121.4418 | 124.8941
Line4_2_6 | 0.026119 | 0.0023668 | 0.0023442 | 0.026119 | 0.0023668 | 0.0023442 | 0.0060319 | 0.00054658 | 0.00054136 | 0.0060319 | 0.00054658 | 0.00054137 | 0.0037876 | -0.00016841 | 0.00050342 | -0.0037763 | 0.00016868 | -0.00050316 | 0.0037655 | 0.00053572 | -6.1308e-05 | -0.0037537 | -0.00053545 | 6.1585e-05 | -48.4415 | 131.1348 | 131.8098 | 131.5585 | -48.8652 | -48.1902 |  | 0.88544 | 1.0274 | 0.93678 | 0.88274 | 1.0271 | 0.93635 | -3.6098 | -121.4139 | 124.8663 | -3.6139 | -121.3792 | 124.8316
Line5_6_7 | 0.026119 | 0.0023668 | 0.0023442 | 0.026119 | 0.0023668 | 0.0023442 | 0.0060319 | 0.00054658 | 0.00054137 | 0.0060319 | 0.00054659 | 0.00054138 | 0.0037763 | -0.00016868 | 0.00050316 | -0.003765 | 0.00016895 | -0.0005029 | 0.0037537 | 0.00053545 | -6.1585e-05 | -0.0037419 | -0.00053517 | 6.1862e-05 | -48.4415 | 131.1348 | 131.8097 | 131.5585 | -48.8652 | -48.1903 |  | 0.88274 | 1.0271 | 0.93635 | 0.88003 | 1.0267 | 0.93593 | -3.6139 | -121.3792 | 124.8316 | -3.618 | -121.3444 | 124.7969
Line6_7_8 | 0.028648 | 0 | 0 | 0.028648 | 0 | 0 | 0.006616 | 0 | 0 | 0.006616 | 0 | 0 | 0.0041167 | 7.5946e-09 | -1.9764e-08 | -0.0041036 | -5.3714e-09 | 1.3221e-08 | 0.0041173 | -2.0349e-08 | 1.1715e-09 | -0.0041036 | 1.3486e-08 | -5.0714e-10 | -48.6218 | 0 | 0 | 131.3782 | 0 | 0 |  | 0.88003 | 1.0267 | 0.93593 | 0.87716 | 1.0265 | 0.93558 | -3.618 | -121.3444 | 124.7969 | -3.6218 | -121.3164 | 124.769
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0724e-09 | 2.5414e-09 | -6.5914e-09 | 2.2816e-10 | -2.8873e-10 | 3.8185e-11 | 4.6244e-09 | -6.7839e-09 | 3.8904e-10 | -1.9301e-10 | -8.214e-11 | 2.7094e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.87716 | 1.0265 | 0.93558 | 0.87716 | 1.0265 | 0.93558 | -3.6218 | -121.3164 | 124.769 | -3.6218 | -121.3164 | 124.769
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0724e-09 | 2.5414e-09 | -6.5914e-09 | 2.2816e-10 | -2.8873e-10 | 3.8185e-11 | 4.6244e-09 | -6.7839e-09 | 3.8904e-10 | -1.9301e-10 | -8.214e-11 | 2.7094e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.87716 | 1.0265 | 0.93558 | 0.87716 | 1.0265 | 0.93558 | -3.6218 | -121.3164 | 124.769 | -3.6218 | -121.3164 | 124.769
Line9_3_11 | 0.0024016 | 0.0023605 | 0.0023528 | 0.0024016 | 0.0023606 | 0.0023528 | 0.00055463 | 0.00054514 | 0.00054336 | 0.00055463 | 0.00054515 | 0.00054337 | -0.00035077 | -0.00016269 | 0.00050556 | 0.00035083 | 0.00016275 | -0.00050551 | -0.00034596 | 0.0005361 | -6.0738e-05 | 0.00034603 | -0.00053606 | 6.0794e-05 | 131.7895 | 131.6768 | 131.7448 | -48.2105 | -48.3232 | -48.2552 |  | 0.8883 | 1.0277 | 0.93712 | 0.88844 | 1.0276 | 0.93704 | -3.6055 | -121.4418 | 124.8941 | -3.6052 | -121.435 | 124.8872

## LG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.024744 | 0.0022422 | 0.0022208 | 0.024744 | 0.0022422 | 0.0022208 | 0.0057144 | 0.0005178 | 0.00051286 | 0.0057144 | 0.00051781 | 0.00051287 | 0.0034096 | -0.00015091 | 0.00045206 | -0.0033994 | 0.00015115 | -0.00045182 | 0.0033901 | 0.00048106 | -5.4776e-05 | -0.0033795 | -0.00048082 | 5.5025e-05 | -48.4415 | 131.1349 | 131.8098 | 131.5585 | -48.8651 | -48.1902 |  | 0.8414 | 0.97368 | 0.88788 | 0.83884 | 0.97336 | 0.88748 | -3.6057 | -121.4487 | 124.9009 | -3.6098 | -121.4139 | 124.8663
Line10_11_12 | 0.0022752 | 0.0022363 | 0.002229 | 0.0022753 | 0.0022364 | 0.002229 | 0.00052544 | 0.00051646 | 0.00051477 | 0.00052545 | 0.00051646 | 0.00051478 | -0.00031487 | -0.00014607 | 0.0004537 | 0.00031492 | 0.00014612 | -0.00045366 | -0.00031056 | 0.00048111 | -5.4563e-05 | 0.00031062 | -0.00048107 | 5.4613e-05 | 131.7895 | 131.6767 | 131.7447 | -48.2105 | -48.3233 | -48.2553 |  | 0.84168 | 0.97355 | 0.88772 | 0.84182 | 0.97349 | 0.88764 | -3.6052 | -121.435 | 124.8872 | -3.6049 | -121.4281 | 124.8804
Line11_12_13 | 0.0022753 | 0.0022364 | 0.002229 | 0.0022753 | 0.0022364 | 0.0022291 | 0.00052545 | 0.00051646 | 0.00051478 | 0.00052546 | 0.00051647 | 0.00051478 | -0.00031492 | -0.00014612 | 0.00045366 | 0.00031498 | 0.00014617 | -0.00045362 | -0.00031062 | 0.00048107 | -5.4612e-05 | 0.00031067 | -0.00048103 | 5.4662e-05 | 131.7895 | 131.6767 | 131.7447 | -48.2105 | -48.3233 | -48.2553 |  | 0.84182 | 0.97349 | 0.88764 | 0.84196 | 0.97342 | 0.88756 | -3.6049 | -121.4281 | 124.8804 | -3.6047 | -121.4212 | 124.8735
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1196e-08 | 6.3353e-09 | -1.7353e-08 | -7.2903e-09 | -4.4865e-09 | 1.1598e-08 | 1.213e-08 | -1.8004e-08 | 1.3104e-09 | -8.2613e-09 | 1.1923e-08 | -6.2479e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.84196 | 0.97342 | 0.88756 | 0.84196 | 0.97342 | 0.88756 | -3.6047 | -121.4212 | 124.8735 | -3.6047 | -121.4212 | 124.8735
Line13_13_14 | 0.0022754 | 0.0022365 | 0.0022292 | 0.0022754 | 0.0022365 | 0.0022292 | 0.00052548 | 0.00051649 | 0.0005148 | 0.00052548 | 0.0005165 | 0.00051481 | -0.00031499 | -0.00014617 | 0.00045364 | 0.00031504 | 0.00014622 | -0.0004536 | -0.00031069 | 0.00048104 | -5.4663e-05 | 0.00031074 | -0.000481 | 5.4713e-05 | 131.7893 | 131.6766 | 131.7446 | -48.2107 | -48.3234 | -48.2554 |  | 0.84196 | 0.97342 | 0.88756 | 0.8421 | 0.97336 | 0.88748 | -3.6047 | -121.4212 | 124.8735 | -3.6044 | -121.4144 | 124.8667
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.464e-09 | 4.2235e-09 | -1.1569e-08 | -3.5583e-09 | -2.3748e-09 | 5.8141e-09 | 8.0866e-09 | -1.2002e-08 | 8.7362e-10 | -4.218e-09 | 5.9215e-09 | -1.8798e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.84196 | 0.97342 | 0.88756 | 0.84196 | 0.97342 | 0.88756 | -3.6047 | -121.4212 | 124.8735 | -3.6047 | -121.4212 | 124.8735
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.732e-09 | 2.1118e-09 | -5.7843e-09 | 1.7369e-10 | -2.6304e-10 | 2.9887e-11 | 4.0433e-09 | -6.0012e-09 | 4.3681e-10 | -1.7469e-10 | -7.9673e-11 | 2.4883e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.84196 | 0.97342 | 0.88756 | 0.84196 | 0.97342 | 0.88756 | -3.6047 | -121.4212 | 124.8735 | -3.6047 | -121.4212 | 124.8735
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7297e-09 | 2.1394e-09 | -5.8092e-09 | 1.7488e-10 | -2.6383e-10 | 2.9029e-11 | 4.0698e-09 | -6.0181e-09 | 4.1579e-10 | -1.7464e-10 | -8.084e-11 | 2.4995e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.84154 | 0.97362 | 0.8878 | 0.84154 | 0.97362 | 0.8878 | -3.6055 | -121.4418 | 124.8941 | -3.6055 | -121.4418 | 124.8941
Line17_5_19 | 0.0022839 | 0.0022449 | 0.0022375 | 0.002284 | 0.0022449 | 0.0022375 | 0.00052745 | 0.00051843 | 0.00051673 | 0.00052746 | 0.00051844 | 0.00051674 | -0.00031491 | -0.00014831 | 0.00045567 | 0.00031497 | 0.00014836 | -0.00045563 | -0.00031282 | 0.00048247 | -5.3096e-05 | 0.00031288 | -0.00048243 | 5.3146e-05 | 131.5853 | 131.4715 | 131.5403 | -48.4147 | -48.5285 | -48.4597 |  | 0.84154 | 0.97362 | 0.8878 | 0.84168 | 0.97355 | 0.88772 | -3.6055 | -121.4418 | 124.8941 | -3.6053 | -121.4349 | 124.8872
Line1_1_3 | 0.0022752 | 0.0022363 | 0.002229 | 0.0022752 | 0.0022363 | 0.002229 | 0.00052543 | 0.00051644 | 0.00051476 | 0.00052544 | 0.00051645 | 0.00051476 | -0.00031476 | -0.00014597 | 0.00045379 | 0.00031481 | 0.00014602 | -0.00045374 | -0.00031045 | 0.0004812 | -5.4463e-05 | 0.0003105 | -0.00048116 | 5.4513e-05 | 131.7896 | 131.6768 | 131.7448 | -48.2104 | -48.3232 | -48.2552 |  | 0.8414 | 0.97368 | 0.88788 | 0.84154 | 0.97362 | 0.8878 | -3.6057 | -121.4487 | 124.9009 | -3.6055 | -121.4418 | 124.8941
Line2_1_4 | 0.0022868 | 0.0022477 | 0.0022403 | 0.0022868 | 0.0022477 | 0.0022403 | 0.00052811 | 0.00051907 | 0.00051737 | 0.00052812 | 0.00051908 | 0.00051737 | -0.00031488 | -0.00014902 | 0.00045634 | 0.00031493 | 0.00014907 | -0.0004563 | -0.00031353 | 0.00048294 | -5.2567e-05 | 0.00031359 | -0.0004829 | 5.2617e-05 | 131.517 | 131.4028 | 131.4719 | -48.483 | -48.5972 | -48.5281 |  | 0.8414 | 0.97368 | 0.88788 | 0.84154 | 0.97362 | 0.8878 | -3.6057 | -121.4487 | 124.9009 | -3.6055 | -121.4418 | 124.8941
Line3_1_5 | 0.0022839 | 0.0022448 | 0.0022375 | 0.0022839 | 0.0022449 | 0.0022375 | 0.00052745 | 0.00051842 | 0.00051672 | 0.00052745 | 0.00051843 | 0.00051673 | -0.00031486 | -0.00014826 | 0.00045571 | 0.00031491 | 0.00014831 | -0.00045567 | -0.00031276 | 0.00048252 | -5.3046e-05 | 0.00031282 | -0.00048247 | 5.3096e-05 | 131.5854 | 131.4715 | 131.5404 | -48.4146 | -48.5285 | -48.4596 |  | 0.8414 | 0.97368 | 0.88788 | 0.84154 | 0.97362 | 0.8878 | -3.6057 | -121.4487 | 124.9009 | -3.6055 | -121.4418 | 124.8941
Line4_2_6 | 0.024744 | 0.0022422 | 0.0022208 | 0.024744 | 0.0022422 | 0.0022208 | 0.0057144 | 0.00051781 | 0.00051287 | 0.0057144 | 0.00051782 | 0.00051288 | 0.0033994 | -0.00015115 | 0.00045182 | -0.0033893 | 0.00015139 | -0.00045159 | 0.0033795 | 0.00048082 | -5.5025e-05 | -0.0033689 | -0.00048057 | 5.5273e-05 | -48.4415 | 131.1348 | 131.8098 | 131.5585 | -48.8652 | -48.1902 |  | 0.83884 | 0.97336 | 0.88748 | 0.83628 | 0.97303 | 0.88707 | -3.6098 | -121.4139 | 124.8663 | -3.6139 | -121.3792 | 124.8316
Line5_6_7 | 0.024744 | 0.0022422 | 0.0022208 | 0.024744 | 0.0022422 | 0.0022209 | 0.0057144 | 0.00051782 | 0.00051288 | 0.0057144 | 0.00051782 | 0.00051288 | 0.0033893 | -0.00015139 | 0.00045159 | -0.0033791 | 0.00015164 | -0.00045136 | 0.0033689 | 0.00048057 | -5.5273e-05 | -0.0033584 | -0.00048032 | 5.5522e-05 | -48.4415 | 131.1348 | 131.8097 | 131.5585 | -48.8652 | -48.1903 |  | 0.83628 | 0.97303 | 0.88707 | 0.83371 | 0.9727 | 0.88667 | -3.6139 | -121.3792 | 124.8316 | -3.618 | -121.3444 | 124.7969
Line6_7_8 | 0.02714 | 0 | 0 | 0.02714 | 0 | 0 | 0.0062678 | 0 | 0 | 0.0062678 | 0 | 0 | 0.0036948 | 6.8162e-09 | -1.7738e-08 | -0.003683 | -4.8209e-09 | 1.1866e-08 | 0.0036953 | -1.8263e-08 | 1.0514e-09 | -0.003683 | 1.2103e-08 | -4.5516e-10 | -48.6218 | 0 | 0 | 131.3782 | 0 | 0 |  | 0.83371 | 0.9727 | 0.88667 | 0.831 | 0.97244 | 0.88634 | -3.618 | -121.3444 | 124.7969 | -3.6218 | -121.3164 | 124.769
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.655e-09 | 2.2809e-09 | -5.9158e-09 | 2.0477e-10 | -2.5914e-10 | 3.4271e-11 | 4.1504e-09 | -6.0886e-09 | 3.4917e-10 | -1.7323e-10 | -7.3721e-11 | 2.4317e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.831 | 0.97244 | 0.88634 | 0.831 | 0.97244 | 0.88634 | -3.6218 | -121.3164 | 124.769 | -3.6218 | -121.3164 | 124.769
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.655e-09 | 2.2809e-09 | -5.9158e-09 | 2.0477e-10 | -2.5914e-10 | 3.4271e-11 | 4.1504e-09 | -6.0886e-09 | 3.4917e-10 | -1.7323e-10 | -7.3721e-11 | 2.4317e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.831 | 0.97244 | 0.88634 | 0.831 | 0.97244 | 0.88634 | -3.6218 | -121.3164 | 124.769 | -3.6218 | -121.3164 | 124.769
Line9_3_11 | 0.0022752 | 0.0022363 | 0.002229 | 0.0022752 | 0.0022363 | 0.002229 | 0.00052544 | 0.00051645 | 0.00051476 | 0.00052544 | 0.00051646 | 0.00051477 | -0.00031481 | -0.00014602 | 0.00045374 | 0.00031487 | 0.00014607 | -0.0004537 | -0.0003105 | 0.00048116 | -5.4513e-05 | 0.00031056 | -0.00048111 | 5.4563e-05 | 131.7895 | 131.6768 | 131.7448 | -48.2105 | -48.3232 | -48.2552 |  | 0.84154 | 0.97362 | 0.8878 | 0.84168 | 0.97355 | 0.88772 | -3.6055 | -121.4418 | 124.8941 | -3.6052 | -121.435 | 124.8872

## LLG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.095303 | 2.0708 | 2.2796 | 0.095303 | 2.0708 | 2.2796 | 0.022009 | 0.47823 | 0.52645 | 0.022009 | 0.47823 | 0.52645 | -0.02329 | 0.12494 | 0.26671 | 0.022782 | -0.098792 | -0.20525 | 0.013318 | 0.37034 | 0.3853 | -0.012653 | -0.28494 | -0.29716 | -147.7755 | 172.0079 | 52.278 | 32.2245 | -7.9921 | -127.722 |  | 1.219 | 0.81727 | 0.89011 | 1.184 | 0.63062 | 0.68601 | 2.4618 | -116.6347 | 107.5863 | 3.1778 | -117.1138 | 107.6449
Line10_11_12 | 0.081529 | 0.33669 | 0.32499 | 0.081529 | 0.33669 | 0.32499 | 0.018828 | 0.077755 | 0.075053 | 0.018828 | 0.077755 | 0.075053 | 0.014892 | 0.012453 | -0.060248 | -0.014966 | -0.011976 | 0.06142 | 0.017592 | -0.065729 | -0.036013 | -0.017593 | 0.067535 | 0.03736 | -47.5636 | -38.8161 | -102.3301 | 132.4364 | 141.1839 | 77.6699 |  | 1.2242 | 0.86037 | 0.93522 | 1.2268 | 0.88211 | 0.95786 | 2.1864 | -118.0877 | 108.5387 | 2.0496 | -118.7607 | 108.9813
Line11_12_13 | 0.081529 | 0.33669 | 0.32499 | 0.081529 | 0.33669 | 0.32499 | 0.018828 | 0.077755 | 0.075053 | 0.018828 | 0.077755 | 0.075053 | 0.014966 | 0.011976 | -0.06142 | -0.01504 | -0.011498 | 0.062592 | 0.017593 | -0.067535 | -0.03736 | -0.017595 | 0.069342 | 0.038708 | -47.5636 | -38.8161 | -102.3301 | 132.4364 | 141.1839 | 77.6699 |  | 1.2268 | 0.88211 | 0.95786 | 1.2293 | 0.90397 | 0.98055 | 2.0496 | -118.7607 | 108.9813 | 1.9134 | -119.4013 | 109.4033
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.4348e-08 | -2.5112e-08 | 3.9885e-08 | 8.754e-09 | 1.7225e-08 | -2.6405e-08 | -4.8346e-08 | 2.8728e-08 | 7.9237e-10 | 3.2389e-08 | -1.9116e-08 | -1.2225e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.2293 | 0.90397 | 0.98055 | 1.2293 | 0.90397 | 0.98055 | 1.9134 | -119.4013 | 109.4033 | 1.9134 | -119.4013 | 109.4033
Line13_13_14 | 0.081529 | 0.33669 | 0.32499 | 0.08153 | 0.33669 | 0.32499 | 0.018828 | 0.077756 | 0.075053 | 0.018828 | 0.077756 | 0.075053 | 0.01504 | 0.011498 | -0.062592 | -0.015113 | -0.01102 | 0.063763 | 0.017595 | -0.069342 | -0.038708 | -0.017596 | 0.071148 | 0.040055 | -47.5637 | -38.8162 | -102.33 | 132.4363 | 141.1838 | 77.67 |  | 1.2293 | 0.90397 | 0.98055 | 1.2319 | 0.92594 | 1.0033 | 1.9134 | -119.4013 | 109.4033 | 1.7777 | -120.0115 | 109.8063
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -9.5651e-09 | -1.6741e-08 | 2.659e-08 | 3.9715e-09 | 8.8544e-09 | -1.311e-08 | -3.2231e-08 | 1.9152e-08 | 5.2825e-10 | 1.6273e-08 | -9.5397e-09 | -9.5835e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.2293 | 0.90397 | 0.98055 | 1.2293 | 0.90397 | 0.98055 | 1.9134 | -119.4013 | 109.4033 | 1.9134 | -119.4013 | 109.4033
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.7825e-09 | -8.3706e-09 | 1.3295e-08 | -8.1105e-10 | 4.8383e-10 | 1.853e-10 | -1.6115e-08 | 9.5761e-09 | 2.6412e-10 | 1.5803e-10 | 3.6367e-11 | -6.9423e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.2293 | 0.90397 | 0.98055 | 1.2293 | 0.90397 | 0.98055 | 1.9134 | -119.4013 | 109.4033 | 1.9134 | -119.4013 | 109.4033
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.4686e-09 | -1.0089e-08 | 1.4339e-08 | -7.8041e-10 | 6.351e-10 | 3.6429e-10 | -1.9034e-08 | 9.4922e-09 | 7.8537e-10 | 1.9223e-10 | 1.353e-10 | -7.2818e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.2231 | 0.84382 | 0.91949 | 1.2231 | 0.84382 | 0.91949 | 2.3395 | -117.613 | 108.1296 | 2.3395 | -117.613 | 108.1296
Line17_5_19 | 0.08539 | 0.39312 | 0.38941 | 0.08539 | 0.39312 | 0.38941 | 0.01972 | 0.090788 | 0.089931 | 0.01972 | 0.090788 | 0.089931 | 0.012661 | 0.017164 | -0.069194 | -0.012745 | -0.01653 | 0.070854 | 0.020518 | -0.074524 | -0.04494 | -0.02055 | 0.077017 | 0.046902 | -55.9882 | -40.513 | -104.8862 | 124.0117 | 139.487 | 75.1138 |  | 1.2226 | 0.84235 | 0.91744 | 1.2262 | 0.86763 | 0.94484 | 2.3334 | -117.5435 | 108.1167 | 2.2058 | -118.3995 | 108.6163
Line1_1_3 | 0.081529 | 0.33669 | 0.32499 | 0.081529 | 0.33669 | 0.32499 | 0.018828 | 0.077755 | 0.075053 | 0.018828 | 0.077755 | 0.075053 | 0.014745 | 0.013409 | -0.057904 | -0.014819 | -0.012931 | 0.059076 | 0.017589 | -0.062116 | -0.033318 | -0.01759 | 0.063923 | 0.034666 | -47.5635 | -38.8161 | -102.3301 | 132.4364 | 141.1839 | 77.6699 |  | 1.219 | 0.81727 | 0.89011 | 1.2216 | 0.83875 | 0.91263 | 2.4618 | -116.6347 | 107.5863 | 2.3238 | -117.3798 | 108.0743
Line2_1_4 | 0.086161 | 0.41609 | 0.41654 | 0.086161 | 0.41609 | 0.41654 | 0.019898 | 0.096091 | 0.096196 | 0.019898 | 0.096091 | 0.096197 | 0.011265 | 0.019727 | -0.071382 | -0.011349 | -0.019025 | 0.073272 | 0.021482 | -0.076014 | -0.04729 | -0.02153 | 0.07882 | 0.049548 | -59.8663 | -41.1832 | -105.9375 | 120.1337 | 138.8168 | 74.0625 |  | 1.219 | 0.81727 | 0.89011 | 1.2231 | 0.84382 | 0.91949 | 2.4618 | -116.6347 | 107.5863 | 2.3395 | -117.613 | 108.1296
Line3_1_5 | 0.085389 | 0.39312 | 0.38941 | 0.08539 | 0.39312 | 0.38941 | 0.01972 | 0.090788 | 0.089931 | 0.01972 | 0.090788 | 0.089931 | 0.012578 | 0.017797 | -0.067533 | -0.012661 | -0.017164 | 0.069194 | 0.020485 | -0.072032 | -0.042978 | -0.020518 | 0.074524 | 0.04494 | -55.9882 | -40.513 | -104.8862 | 124.0118 | 139.487 | 75.1138 |  | 1.219 | 0.81727 | 0.89011 | 1.2226 | 0.84235 | 0.91744 | 2.4618 | -116.6347 | 107.5863 | 2.3334 | -117.5435 | 108.1167
Line4_2_6 | 0.095303 | 2.0708 | 2.2796 | 0.095303 | 2.0708 | 2.2796 | 0.022009 | 0.47823 | 0.52645 | 0.022009 | 0.47823 | 0.52645 | -0.022782 | 0.098792 | 0.20525 | 0.022274 | -0.072646 | -0.14379 | 0.012653 | 0.28494 | 0.29716 | -0.011987 | -0.19955 | -0.20902 | -147.7755 | 172.0079 | 52.278 | 32.2246 | -7.9921 | -127.722 |  | 1.184 | 0.63062 | 0.68601 | 1.1492 | 0.44406 | 0.48191 | 3.1778 | -117.1138 | 107.6449 | 3.9372 | -117.9957 | 107.7531
Line5_6_7 | 0.095303 | 2.0708 | 2.2796 | 0.095303 | 2.0708 | 2.2796 | 0.022009 | 0.47823 | 0.52645 | 0.022009 | 0.47823 | 0.52645 | -0.022274 | 0.072646 | 0.14379 | 0.021765 | -0.046499 | -0.082331 | 0.011987 | 0.19955 | 0.20902 | -0.011321 | -0.11416 | -0.12088 | -147.7754 | 172.0079 | 52.278 | 32.2246 | -7.9921 | -127.722 |  | 1.1492 | 0.44406 | 0.48191 | 1.1147 | 0.25776 | 0.27782 | 3.9372 | -117.9957 | 107.7531 | 4.7439 | -120.1536 | 108.0202
Line6_7_8 | 0 | 2.899 | 3.1817 | 0 | 2.899 | 3.1817 | 0 | 0.6695 | 0.73477 | 0 | 0.6695 | 0.73477 | -1.8759e-09 | 0.047392 | 0.11863 | -1.9707e-10 | 3.5662e-14 | 5.5678e-15 | -9.794e-08 | 0.16593 | 0.16612 | 6.4171e-08 | 4.5092e-15 | 5.6261e-16 | 0 | 165.7863 | 53.5527 | 0 | -14.2137 | -126.4473 |  | 1.1147 | 0.25776 | 0.27782 | 1.062 | 0 | 0 | 4.7439 | -120.1536 | 108.0202 | 5.5395 | 0 | 0
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.5691e-11 | -2.6516e-22 | -1.6786e-22 | -6.5691e-11 | -1.2242e-19 | -5.8656e-18 | -3.1888e-08 | -1.7445e-21 | 1.0788e-22 | 3.9468e-10 | 1.7216e-17 | -2.783e-18 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.062 | 0 | 0 | 1.062 | 0 | 0 | 5.5395 | 0 | 0 | 5.5395 | 0 | 0
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.5691e-11 | -2.6516e-22 | -1.6786e-22 | -6.569e-11 | -1.2242e-19 | -5.8656e-18 | -3.1888e-08 | -1.7445e-21 | 1.0788e-22 | 3.9468e-10 | 1.7216e-17 | -2.783e-18 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.062 | 0 | 0 | 1.062 | 0 | 0 | 5.5395 | 0 | 0 | 5.5395 | 0 | 0
Line9_3_11 | 0.081529 | 0.33669 | 0.32499 | 0.081529 | 0.33669 | 0.32499 | 0.018828 | 0.077755 | 0.075053 | 0.018828 | 0.077755 | 0.075053 | 0.014819 | 0.012931 | -0.059076 | -0.014893 | -0.012453 | 0.060248 | 0.01759 | -0.063923 | -0.034666 | -0.017592 | 0.065729 | 0.036013 | -47.5636 | -38.8161 | -102.3301 | 132.4364 | 141.1839 | 77.6699 |  | 1.2216 | 0.83875 | 0.91263 | 1.2242 | 0.86037 | 0.93522 | 2.3238 | -117.3798 | 108.0743 | 2.1864 | -118.0877 | 108.5387

## LLG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.09754 | 2.1512 | 2.3723 | 0.09754 | 2.1512 | 2.3723 | 0.022526 | 0.49679 | 0.54786 | 0.022526 | 0.49679 | 0.54786 | -0.024454 | 0.13478 | 0.28747 | 0.023942 | -0.10641 | -0.22099 | 0.015282 | 0.39911 | 0.41695 | -0.014553 | -0.30682 | -0.3213 | -145.5076 | 172.0894 | 51.8316 | 34.4924 | -7.9106 | -128.1684 |  | 1.2801 | 0.84795 | 0.9244 | 1.2438 | 0.65369 | 0.7118 | 2.4906 | -116.5707 | 107.247 | 3.1999 | -117.0385 | 107.3116
Line10_11_12 | 0.085176 | 0.3464 | 0.33673 | 0.085176 | 0.3464 | 0.33673 | 0.019671 | 0.079998 | 0.077764 | 0.019671 | 0.079998 | 0.077764 | 0.015572 | 0.01352 | -0.06492 | -0.015647 | -0.013021 | 0.066173 | 0.019914 | -0.07009 | -0.038561 | -0.019919 | 0.072004 | 0.040008 | -49.7389 | -38.9278 | -102.5002 | 130.2611 | 141.0722 | 77.4998 |  | 1.2852 | 0.8923 | 0.971 | 1.2877 | 0.91467 | 0.99439 | 2.237 | -118.01 | 108.2092 | 2.1109 | -118.6771 | 108.6564
Line11_12_13 | 0.085176 | 0.3464 | 0.33673 | 0.085176 | 0.3464 | 0.33673 | 0.019671 | 0.079998 | 0.077764 | 0.019671 | 0.079998 | 0.077764 | 0.015647 | 0.013021 | -0.066173 | -0.015721 | -0.012523 | 0.067427 | 0.019919 | -0.072004 | -0.040008 | -0.019924 | 0.073917 | 0.041454 | -49.7389 | -38.9278 | -102.5002 | 130.2611 | 141.0722 | 77.4998 |  | 1.2877 | 0.91467 | 0.99439 | 1.2902 | 0.93715 | 1.0178 | 2.1109 | -118.6771 | 108.6564 | 1.9853 | -119.3122 | 109.0831
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.5891e-08 | -2.848e-08 | 4.4705e-08 | 9.6907e-09 | 1.9546e-08 | -2.9571e-08 | -5.5033e-08 | 3.1969e-08 | 9.4653e-10 | 3.6869e-08 | -2.1267e-08 | -1.4085e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.2902 | 0.93715 | 1.0178 | 1.2902 | 0.93715 | 1.0178 | 1.9853 | -119.3122 | 109.0831 | 1.9853 | -119.3122 | 109.0831
Line13_13_14 | 0.085176 | 0.3464 | 0.33673 | 0.085176 | 0.3464 | 0.33673 | 0.019671 | 0.079998 | 0.077764 | 0.019671 | 0.079998 | 0.077764 | 0.015721 | 0.012523 | -0.067427 | -0.015796 | -0.012024 | 0.068681 | 0.019924 | -0.073917 | -0.041454 | -0.019929 | 0.075831 | 0.042901 | -49.7389 | -38.9278 | -102.5002 | 130.261 | 141.0722 | 77.4998 |  | 1.2902 | 0.93715 | 1.0178 | 1.2928 | 0.95975 | 1.0413 | 1.9853 | -119.3122 | 109.0831 | 1.8602 | -119.9176 | 109.4905
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.0594e-08 | -1.8987e-08 | 2.9803e-08 | 4.3938e-09 | 1.0053e-08 | -1.4669e-08 | -3.6688e-08 | 2.1313e-08 | 6.3102e-10 | 1.8525e-08 | -1.0611e-08 | -1.093e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.2902 | 0.93715 | 1.0178 | 1.2902 | 0.93715 | 1.0178 | 1.9853 | -119.3122 | 109.0831 | 1.9853 | -119.3122 | 109.0831
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.2968e-09 | -9.4934e-09 | 1.4902e-08 | -9.0302e-10 | 5.5931e-10 | 2.3234e-10 | -1.8344e-08 | 1.0656e-08 | 3.1551e-10 | 1.8028e-10 | 4.5372e-11 | -7.7748e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.2902 | 0.93715 | 1.0178 | 1.2902 | 0.93715 | 1.0178 | 1.9853 | -119.3122 | 109.0831 | 1.9853 | -119.3122 | 109.0831
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.9246e-09 | -1.1334e-08 | 1.5989e-08 | -8.7164e-10 | 7.1849e-10 | 4.2235e-10 | -2.1522e-08 | 1.0511e-08 | 8.6972e-10 | 2.1513e-10 | 1.5208e-10 | -8.1394e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.2842 | 0.87504 | 0.95445 | 1.2842 | 0.87504 | 0.95445 | 2.3805 | -117.5304 | 107.7936 | 2.3805 | -117.5304 | 107.7936
Line17_5_19 | 0.08944 | 0.40203 | 0.40063 | 0.08944 | 0.40203 | 0.40063 | 0.020655 | 0.092844 | 0.092521 | 0.020655 | 0.092844 | 0.092521 | 0.013106 | 0.018404 | -0.074097 | -0.013189 | -0.01775 | 0.07585 | 0.023049 | -0.078993 | -0.047693 | -0.023086 | 0.081601 | 0.049769 | -58.002 | -40.5797 | -104.9866 | 121.9979 | 139.4203 | 75.0134 |  | 1.2837 | 0.8736 | 0.95243 | 1.2872 | 0.89945 | 0.98054 | 2.3742 | -117.4647 | 107.781 | 2.2585 | -118.3074 | 108.2844
Line1_1_3 | 0.085176 | 0.3464 | 0.33673 | 0.085176 | 0.3464 | 0.33673 | 0.01967 | 0.079998 | 0.077764 | 0.019671 | 0.079998 | 0.077764 | 0.015423 | 0.014517 | -0.062412 | -0.015498 | -0.014018 | 0.063666 | 0.019905 | -0.066263 | -0.035668 | -0.01991 | 0.068176 | 0.037114 | -49.7388 | -38.9277 | -102.5003 | 130.2612 | 141.0722 | 77.4997 |  | 1.2801 | 0.84795 | 0.9244 | 1.2827 | 0.87005 | 0.94767 | 2.4906 | -116.5707 | 107.247 | 2.3635 | -117.3087 | 107.7399
Line2_1_4 | 0.090442 | 0.42448 | 0.42728 | 0.090442 | 0.42448 | 0.42728 | 0.020887 | 0.098029 | 0.098676 | 0.020887 | 0.098029 | 0.098676 | 0.011623 | 0.021033 | -0.076285 | -0.011706 | -0.020312 | 0.078268 | 0.02408 | -0.080419 | -0.05001 | -0.024133 | 0.08334 | 0.052385 | -61.7437 | -41.2276 | -106.0007 | 118.2563 | 138.7724 | 73.9993 |  | 1.2801 | 0.84795 | 0.9244 | 1.2842 | 0.87504 | 0.95445 | 2.4906 | -116.5707 | 107.247 | 2.3805 | -117.5304 | 107.7936
Line3_1_5 | 0.08944 | 0.40203 | 0.40063 | 0.08944 | 0.40203 | 0.40063 | 0.020655 | 0.092844 | 0.092521 | 0.020655 | 0.092844 | 0.092521 | 0.013023 | 0.019058 | -0.072345 | -0.013106 | -0.018404 | 0.074097 | 0.023012 | -0.076386 | -0.045617 | -0.023049 | 0.078993 | 0.047693 | -58.002 | -40.5797 | -104.9866 | 121.998 | 139.4203 | 75.0134 |  | 1.2801 | 0.84795 | 0.9244 | 1.2837 | 0.8736 | 0.95243 | 2.4906 | -116.5707 | 107.247 | 2.3742 | -117.4647 | 107.781
Line4_2_6 | 0.09754 | 2.1512 | 2.3723 | 0.09754 | 2.1512 | 2.3723 | 0.022526 | 0.49679 | 0.54786 | 0.022526 | 0.49679 | 0.54786 | -0.023942 | 0.10641 | 0.22099 | 0.023429 | -0.078044 | -0.15452 | 0.014553 | 0.30682 | 0.3213 | -0.013823 | -0.21453 | -0.22566 | -145.5076 | 172.0894 | 51.8316 | 34.4925 | -7.9106 | -128.1684 |  | 1.2438 | 0.65369 | 0.7118 | 1.2077 | 0.45952 | 0.49921 | 3.1999 | -117.0385 | 107.3116 | 3.9517 | -117.9018 | 107.4311
Line5_6_7 | 0.09754 | 2.1512 | 2.3723 | 0.09754 | 2.1512 | 2.3723 | 0.022526 | 0.49679 | 0.54786 | 0.022526 | 0.49679 | 0.54786 | -0.023429 | 0.078044 | 0.15452 | 0.022917 | -0.049676 | -0.088043 | 0.013823 | 0.21453 | 0.22566 | -0.013094 | -0.12224 | -0.13002 | -145.5075 | 172.0894 | 51.8316 | 34.4925 | -7.9106 | -128.1684 |  | 1.2077 | 0.45952 | 0.49921 | 1.1717 | 0.2656 | 0.28662 | 3.9517 | -117.9018 | 107.4311 | 4.7497 | -120.027 | 107.7279
Line6_7_8 | 0 | 2.9821 | 3.2787 | 0 | 2.9821 | 3.2787 | 0 | 0.68868 | 0.75718 | 0 | 0.68868 | 0.75718 | -1.9729e-09 | 0.050353 | 0.12594 | -2.8274e-10 | 6.6555e-14 | 3.2333e-14 | -1.0844e-07 | 0.17584 | 0.17674 | 7.1097e-08 | -5.1788e-15 | -1.2347e-14 | 0 | 165.9521 | 53.2002 | 0 | -14.0479 | -126.7998 |  | 1.1717 | 0.2656 | 0.28662 | 1.1179 | 0 | 0 | 4.7497 | -120.027 | 107.7279 | 5.5332 | 0 | 0
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.4247e-11 | -1.1543e-21 | -6.3522e-22 | -9.4247e-11 | -1.4819e-19 | -6.484e-18 | -3.5331e-08 | -3.1468e-21 | 1.0898e-21 | 4.3474e-10 | 1.8956e-17 | -3.0971e-18 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1179 | 0 | 0 | 1.1179 | 0 | 0 | 5.5332 | 0 | 0 | 5.5332 | 0 | 0
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.4247e-11 | -1.1543e-21 | -6.3522e-22 | -9.4247e-11 | -1.4819e-19 | -6.484e-18 | -3.5331e-08 | -3.1468e-21 | 1.0898e-21 | 4.3474e-10 | 1.8956e-17 | -3.0971e-18 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1179 | 0 | 0 | 1.1179 | 0 | 0 | 5.5332 | 0 | 0 | 5.5332 | 0 | 0
Line9_3_11 | 0.085176 | 0.3464 | 0.33673 | 0.085176 | 0.3464 | 0.33673 | 0.019671 | 0.079998 | 0.077764 | 0.019671 | 0.079998 | 0.077764 | 0.015498 | 0.014018 | -0.063666 | -0.015572 | -0.01352 | 0.06492 | 0.01991 | -0.068176 | -0.037114 | -0.019914 | 0.07009 | 0.038561 | -49.7388 | -38.9278 | -102.5003 | 130.2611 | 141.0722 | 77.4998 |  | 1.2827 | 0.87005 | 0.94767 | 1.2852 | 0.8923 | 0.971 | 2.3635 | -117.3087 | 107.7399 | 2.237 | -118.01 | 108.2092

## LLG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.1104 | 0.088363 | 0.086423 | 0.1104 | 0.088363 | 0.086423 | 0.025496 | 0.020407 | 0.019959 | 0.025496 | 0.020407 | 0.019959 | -0.011072 | -0.0057959 | -0.0064023 | 0.011194 | 0.0058801 | 0.0064702 | -0.025681 | -0.021535 | -0.020886 | 0.025915 | 0.021696 | 0.021038 | 113.4785 | -14.9054 | -133.011 | -66.5215 | 165.0946 | 46.989 |  | 1.0969 | 1.0929 | 1.0945 | 1.1072 | 1.1015 | 1.1028 | 0.15584 | -119.9687 | 119.9466 | 0.11723 | -120.0694 | 119.8941
Line10_11_12 | 0.099729 | 0.10358 | 0.10116 | 0.099729 | 0.10358 | 0.10116 | 0.023031 | 0.023922 | 0.023361 | 0.023031 | 0.023922 | 0.023361 | -0.00052854 | -0.0011579 | -0.0016936 | 0.00062694 | 0.0012636 | 0.0017985 | -0.025663 | -0.026551 | -0.025934 | 0.025864 | 0.026763 | 0.026139 | 90.9082 | -27.894 | -146.7265 | -89.0918 | 152.106 | 33.2735 |  | 1.1145 | 1.111 | 1.1125 | 1.1233 | 1.12 | 1.1216 | -0.27164 | -120.3911 | 119.5372 | -0.48035 | -120.5971 | 119.3374
Line11_12_13 | 0.099729 | 0.10358 | 0.10116 | 0.099729 | 0.10358 | 0.10116 | 0.023031 | 0.023922 | 0.023361 | 0.023031 | 0.023922 | 0.023361 | -0.00062694 | -0.0012636 | -0.0017985 | 0.00072535 | 0.0013693 | 0.0019034 | -0.025864 | -0.026763 | -0.026139 | 0.026065 | 0.026976 | 0.026343 | 90.9082 | -27.894 | -146.7265 | -89.0918 | 152.106 | 33.2735 |  | 1.1233 | 1.12 | 1.1216 | 1.1322 | 1.1291 | 1.1306 | -0.48035 | -120.5971 | 119.3374 | -0.6858 | -120.7998 | 119.1409
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.3477e-10 | 9.0588e-10 | 1.4715e-09 | -7.6463e-10 | -9.3192e-10 | -1.3156e-09 | -1.6e-10 | 6.7652e-10 | 1.5495e-11 | 5.4498e-11 | -5.117e-10 | -7.5596e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1322 | 1.1291 | 1.1306 | 1.1322 | 1.1291 | 1.1306 | -0.6858 | -120.7998 | 119.1409 | -0.6858 | -120.7998 | 119.1409
Line13_13_14 | 0.099729 | 0.10358 | 0.10116 | 0.099729 | 0.10358 | 0.10116 | 0.023031 | 0.023922 | 0.023361 | 0.023031 | 0.023922 | 0.023361 | -0.00072535 | -0.0013693 | -0.0019034 | 0.00082376 | 0.001475 | 0.0020083 | -0.026065 | -0.026976 | -0.026343 | 0.026267 | 0.027188 | 0.026547 | 90.9082 | -27.894 | -146.7265 | -89.0918 | 152.106 | 33.2735 |  | 1.1322 | 1.1291 | 1.1306 | 1.141 | 1.1382 | 1.1396 | -0.6858 | -120.7998 | 119.1409 | -0.88806 | -120.9993 | 118.9474
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2318e-10 | 6.0392e-10 | 9.8101e-10 | -5.5304e-10 | -6.2996e-10 | -8.2511e-10 | -1.0667e-10 | 4.5102e-10 | 1.033e-11 | 1.163e-12 | -2.8619e-10 | -7.0431e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1322 | 1.1291 | 1.1306 | 1.1322 | 1.1291 | 1.1306 | -0.6858 | -120.7998 | 119.1409 | -0.6858 | -120.7998 | 119.1409
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1159e-10 | 3.0196e-10 | 4.9051e-10 | -3.4145e-10 | -3.28e-10 | -3.346e-10 | -5.3335e-11 | 2.2551e-10 | 5.165e-12 | -5.2172e-11 | -6.0682e-11 | -6.5266e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1322 | 1.1291 | 1.1306 | 1.1322 | 1.1291 | 1.1306 | -0.6858 | -120.7998 | 119.1409 | -0.6858 | -120.7998 | 119.1409
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.7056e-11 | 1.7824e-10 | 4.0893e-10 | -2.3633e-10 | -2.205e-10 | -2.2741e-10 | -1.2144e-10 | 2.0245e-10 | -3.3069e-11 | -8.3831e-12 | -1.746e-11 | -2.3158e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1082 | 1.1044 | 1.1061 | 1.1082 | 1.1044 | 1.1061 | -0.11258 | -120.2353 | 119.6884 | -0.11258 | -120.2353 | 119.6884
Line17_5_19 | 0.11896 | 0.12361 | 0.12094 | 0.11896 | 0.12361 | 0.12094 | 0.027472 | 0.028545 | 0.02793 | 0.027472 | 0.028545 | 0.02793 | -0.0007649 | -0.0014227 | -0.0020941 | 0.00090517 | 0.0015731 | 0.0022439 | -0.030413 | -0.031473 | -0.0308 | 0.030699 | 0.031776 | 0.031092 | 91.3436 | -27.6313 | -146.4069 | -88.6564 | 152.3687 | 33.5931 |  | 1.1074 | 1.1037 | 1.1053 | 1.118 | 1.1145 | 1.1161 | -0.097091 | -120.2195 | 119.7036 | -0.34525 | -120.4655 | 119.4653
Line1_1_3 | 0.099729 | 0.10358 | 0.10116 | 0.099729 | 0.10358 | 0.10116 | 0.023031 | 0.023922 | 0.023361 | 0.023031 | 0.023922 | 0.023361 | -0.00033172 | -0.00094644 | -0.0014838 | 0.00043013 | 0.0010522 | 0.0015887 | -0.025261 | -0.026126 | -0.025526 | 0.025462 | 0.026338 | 0.02573 | 90.9082 | -27.894 | -146.7265 | -89.0918 | 152.106 | 33.2735 |  | 1.0969 | 1.0929 | 1.0945 | 1.1057 | 1.1019 | 1.1035 | 0.15584 | -119.9687 | 119.9466 | -0.059601 | -120.1816 | 119.7402
Line2_1_4 | 0.12712 | 0.1321 | 0.12936 | 0.12712 | 0.1321 | 0.12936 | 0.029357 | 0.030506 | 0.029873 | 0.029357 | 0.030506 | 0.029873 | -0.00077258 | -0.0014269 | -0.0021565 | 0.00093288 | 0.0015986 | 0.0023278 | -0.032192 | -0.033308 | -0.032626 | 0.032519 | 0.033654 | 0.03296 | 91.5306 | -27.5157 | -146.2717 | -88.4694 | 152.4843 | 33.7283 |  | 1.0969 | 1.0929 | 1.0945 | 1.1082 | 1.1044 | 1.1061 | 0.15584 | -119.9687 | 119.9466 | -0.11258 | -120.2353 | 119.6884
Line3_1_5 | 0.11896 | 0.12361 | 0.12094 | 0.11896 | 0.12361 | 0.12094 | 0.027472 | 0.028545 | 0.02793 | 0.027472 | 0.028545 | 0.02793 | -0.00062463 | -0.0012723 | -0.0019443 | 0.0007649 | 0.0014227 | 0.0020941 | -0.030127 | -0.03117 | -0.030508 | 0.030413 | 0.031473 | 0.0308 | 91.3436 | -27.6313 | -146.4069 | -88.6564 | 152.3687 | 33.5931 |  | 1.0969 | 1.0929 | 1.0945 | 1.1074 | 1.1037 | 1.1053 | 0.15584 | -119.9687 | 119.9466 | -0.097091 | -120.2195 | 119.7036
Line4_2_6 | 0.1104 | 0.088363 | 0.086423 | 0.1104 | 0.088363 | 0.086423 | 0.025496 | 0.020407 | 0.019959 | 0.025496 | 0.020407 | 0.019959 | -0.011194 | -0.0058801 | -0.0064702 | 0.011316 | 0.0059643 | 0.006538 | -0.025915 | -0.021696 | -0.021038 | 0.02615 | 0.021857 | 0.021191 | 113.4785 | -14.9054 | -133.011 | -66.5215 | 165.0946 | 46.989 |  | 1.1072 | 1.1015 | 1.1028 | 1.1175 | 1.1102 | 1.1111 | 0.11723 | -120.0694 | 119.8941 | 0.079324 | -120.1686 | 119.8423
Line5_6_7 | 0.1104 | 0.088363 | 0.086423 | 0.1104 | 0.088363 | 0.086423 | 0.025496 | 0.020407 | 0.019959 | 0.025496 | 0.020407 | 0.019959 | -0.011316 | -0.0059643 | -0.006538 | 0.011437 | 0.0060485 | 0.0066059 | -0.02615 | -0.021857 | -0.021191 | 0.026384 | 0.022018 | 0.021343 | 113.4785 | -14.9054 | -133.011 | -66.5215 | 165.0946 | 46.989 |  | 1.1175 | 1.1102 | 1.1111 | 1.1279 | 1.1189 | 1.1194 | 0.079324 | -120.1686 | 119.8423 | 0.042115 | -120.2662 | 119.7913
Line6_7_8 | 0 | 0.036449 | 0.036455 | 0 | 0.036449 | 0.036455 | 0 | 0.0084175 | 0.0084189 | 0 | 0.0084175 | 0.0084189 | 3.5714e-10 | 0.0066509 | 0.0066609 | -5.5162e-10 | -0.0066426 | -0.0066449 | -8.6948e-10 | 0.0066688 | 0.0066673 | 5.9952e-10 | -0.0066426 | -0.0066449 | 0 | -165.3433 | 74.7637 | 0 | 14.6567 | -105.2363 |  | 1.1279 | 1.1189 | 1.1194 | 1.1273 | 1.116 | 1.1162 | 0.042115 | -120.2662 | 119.7913 | 0.032814 | -120.3433 | 119.7637
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1606e-10 | 1.192e-10 | 6.2542e-10 | -3.195e-10 | -2.7019e-10 | -2.7099e-10 | -2.9852e-10 | 3.477e-10 | -1.1837e-11 | 2.4856e-12 | -2.5746e-11 | -1.7724e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1273 | 1.116 | 1.1162 | 1.1273 | 1.116 | 1.1162 | 0.032814 | -120.3433 | 119.7637 | 0.032814 | -120.3433 | 119.7637
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1606e-10 | 1.192e-10 | 6.2543e-10 | -3.195e-10 | -2.7019e-10 | -2.7099e-10 | -2.9852e-10 | 3.477e-10 | -1.1837e-11 | 2.4855e-12 | -2.5746e-11 | -1.7724e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1273 | 1.116 | 1.1162 | 1.1273 | 1.116 | 1.1162 | 0.032814 | -120.3433 | 119.7637 | 0.032814 | -120.3433 | 119.7637
Line9_3_11 | 0.099729 | 0.10358 | 0.10116 | 0.099729 | 0.10358 | 0.10116 | 0.023031 | 0.023922 | 0.023361 | 0.023031 | 0.023922 | 0.023361 | -0.00043013 | -0.0010522 | -0.0015887 | 0.00052854 | 0.0011579 | 0.0016936 | -0.025462 | -0.026338 | -0.02573 | 0.025663 | 0.026551 | 0.025934 | 90.9082 | -27.894 | -146.7265 | -89.0918 | 152.106 | 33.2735 |  | 1.1057 | 1.1019 | 1.1035 | 1.1145 | 1.111 | 1.1125 | -0.059601 | -120.1816 | 119.7402 | -0.27164 | -120.3911 | 119.5372

## LLG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.11108 | 0.087928 | 0.085857 | 0.11108 | 0.087928 | 0.085857 | 0.025653 | 0.020306 | 0.019828 | 0.025653 | 0.020306 | 0.019828 | -0.011582 | -0.0057703 | -0.006441 | 0.011705 | 0.005854 | 0.0065076 | -0.027117 | -0.022523 | -0.021808 | 0.027354 | 0.022683 | 0.021958 | 113.288 | -15.6011 | -133.6044 | -66.712 | 164.3989 | 46.3956 |  | 1.1494 | 1.145 | 1.1468 | 1.1598 | 1.1536 | 1.1551 | 0.15973 | -119.9709 | 119.9408 | 0.12056 | -120.0723 | 119.8879
Line10_11_12 | 0.10076 | 0.10485 | 0.1023 | 0.10076 | 0.10485 | 0.1023 | 0.023269 | 0.024215 | 0.023625 | 0.023269 | 0.024215 | 0.023625 | -0.00057321 | -0.0012668 | -0.0018637 | 0.00067361 | 0.001375 | 0.001971 | -0.027154 | -0.028142 | -0.027461 | 0.02736 | 0.028359 | 0.02767 | 90.9575 | -27.7998 | -146.5702 | -89.0425 | 152.2002 | 33.4298 |  | 1.1672 | 1.1633 | 1.1651 | 1.1762 | 1.1725 | 1.1742 | -0.25178 | -120.3773 | 119.5474 | -0.45286 | -120.5757 | 119.3553
Line11_12_13 | 0.10076 | 0.10485 | 0.1023 | 0.10076 | 0.10485 | 0.1023 | 0.023269 | 0.024215 | 0.023625 | 0.023269 | 0.024215 | 0.023625 | -0.00067361 | -0.001375 | -0.0019711 | 0.00077402 | 0.0014833 | 0.0020784 | -0.02736 | -0.028359 | -0.02767 | 0.027565 | 0.028577 | 0.027879 | 90.9575 | -27.7998 | -146.5702 | -89.0425 | 152.2002 | 33.4298 |  | 1.1762 | 1.1725 | 1.1742 | 1.1851 | 1.1817 | 1.1833 | -0.45286 | -120.5757 | 119.3553 | -0.6509 | -120.7711 | 119.1662
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.6074e-10 | 9.7083e-10 | 1.6289e-09 | -8.1066e-10 | -1.0017e-09 | -1.448e-09 | -2.0555e-10 | 7.6469e-10 | 1.6713e-12 | 8.2731e-11 | -5.7393e-10 | -7.0568e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1851 | 1.1817 | 1.1833 | 1.1851 | 1.1817 | 1.1833 | -0.6509 | -120.7711 | 119.1662 | -0.6509 | -120.7711 | 119.1662
Line13_13_14 | 0.10076 | 0.10485 | 0.1023 | 0.10076 | 0.10485 | 0.1023 | 0.023269 | 0.024215 | 0.023625 | 0.023269 | 0.024215 | 0.023625 | -0.00077402 | -0.0014833 | -0.0020784 | 0.00087443 | 0.0015915 | 0.0021858 | -0.027565 | -0.028577 | -0.027879 | 0.027771 | 0.028794 | 0.028088 | 90.9575 | -27.7998 | -146.5702 | -89.0425 | 152.2002 | 33.4298 |  | 1.1851 | 1.1817 | 1.1833 | 1.1941 | 1.1909 | 1.1925 | -0.6509 | -120.7711 | 119.1662 | -0.84598 | -120.9634 | 118.98
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.405e-10 | 6.4722e-10 | 1.0859e-09 | -5.9041e-10 | -6.7813e-10 | -9.0508e-10 | -1.3703e-10 | 5.0979e-10 | 1.1143e-12 | 1.4215e-11 | -3.1904e-10 | -7.0011e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1851 | 1.1817 | 1.1833 | 1.1851 | 1.1817 | 1.1833 | -0.6509 | -120.7711 | 119.1662 | -0.6509 | -120.7711 | 119.1662
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2025e-10 | 3.2361e-10 | 5.4295e-10 | -3.7016e-10 | -3.5452e-10 | -3.6212e-10 | -6.8516e-11 | 2.549e-10 | 5.5716e-13 | -5.4301e-11 | -6.4141e-11 | -6.9454e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1851 | 1.1817 | 1.1833 | 1.1851 | 1.1817 | 1.1833 | -0.6509 | -120.7711 | 119.1662 | -0.6509 | -120.7711 | 119.1662
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.8285e-11 | 1.9104e-10 | 4.5738e-10 | -2.5845e-10 | -2.4017e-10 | -2.481e-10 | -1.4208e-10 | 2.3137e-10 | -3.9488e-11 | -7.8715e-12 | -1.8327e-11 | -2.4881e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1607 | 1.1566 | 1.1584 | 1.1607 | 1.1566 | 1.1584 | -0.096336 | -120.2251 | 119.6949 | -0.096336 | -120.2251 | 119.6949
Line17_5_19 | 0.1194 | 0.12431 | 0.12152 | 0.1194 | 0.12431 | 0.12152 | 0.027575 | 0.028707 | 0.028063 | 0.027575 | 0.028707 | 0.028063 | -0.00082067 | -0.0015431 | -0.0022846 | 0.00096194 | 0.0016951 | 0.002436 | -0.031976 | -0.033147 | -0.032408 | 0.032265 | 0.033453 | 0.032702 | 91.388 | -27.5453 | -146.2588 | -88.612 | 152.4547 | 33.7412 |  | 1.16 | 1.1559 | 1.1577 | 1.1706 | 1.1668 | 1.1685 | -0.082176 | -120.2107 | 119.7088 | -0.31971 | -120.446 | 119.4811
Line1_1_3 | 0.10076 | 0.10485 | 0.1023 | 0.10076 | 0.10485 | 0.1023 | 0.023269 | 0.024215 | 0.023625 | 0.023269 | 0.024215 | 0.023625 | -0.0003724 | -0.0010504 | -0.0016489 | 0.0004728 | 0.0011586 | 0.0017563 | -0.026743 | -0.027706 | -0.027044 | 0.026949 | 0.027924 | 0.027252 | 90.9575 | -27.7998 | -146.5702 | -89.0425 | 152.2002 | 33.4298 |  | 1.1494 | 1.145 | 1.1468 | 1.1583 | 1.1542 | 1.1559 | 0.15973 | -119.9709 | 119.9408 | -0.047605 | -120.1757 | 119.7425
Line2_1_4 | 0.12724 | 0.13248 | 0.12962 | 0.12724 | 0.13248 | 0.12962 | 0.029386 | 0.030595 | 0.029934 | 0.029386 | 0.030595 | 0.029934 | -0.00083193 | -0.0015503 | -0.0023532 | 0.00099249 | 0.0017229 | 0.0025254 | -0.033767 | -0.034997 | -0.034248 | 0.034094 | 0.035345 | 0.034583 | 91.5711 | -27.4344 | -146.1285 | -88.4289 | 152.5656 | 33.8715 |  | 1.1494 | 1.145 | 1.1468 | 1.1607 | 1.1566 | 1.1584 | 0.15973 | -119.9709 | 119.9408 | -0.096336 | -120.2251 | 119.6949
Line3_1_5 | 0.1194 | 0.12431 | 0.12152 | 0.1194 | 0.12431 | 0.12152 | 0.027575 | 0.028707 | 0.028063 | 0.027575 | 0.028707 | 0.028063 | -0.0006794 | -0.0013911 | -0.0021332 | 0.00082067 | 0.0015431 | 0.0022846 | -0.031688 | -0.032841 | -0.032113 | 0.031976 | 0.033147 | 0.032408 | 91.388 | -27.5453 | -146.2588 | -88.612 | 152.4547 | 33.7412 |  | 1.1494 | 1.145 | 1.1468 | 1.16 | 1.1559 | 1.1577 | 0.15973 | -119.9709 | 119.9408 | -0.082176 | -120.2107 | 119.7088
Line4_2_6 | 0.11108 | 0.087928 | 0.085857 | 0.11108 | 0.087928 | 0.085857 | 0.025653 | 0.020306 | 0.019828 | 0.025653 | 0.020306 | 0.019828 | -0.011705 | -0.005854 | -0.0065076 | 0.011829 | 0.0059377 | 0.0065741 | -0.027354 | -0.022683 | -0.021958 | 0.02759 | 0.022842 | 0.022109 | 113.288 | -15.6011 | -133.6044 | -66.712 | 164.3989 | 46.3956 |  | 1.1598 | 1.1536 | 1.1551 | 1.1702 | 1.1623 | 1.1633 | 0.12056 | -120.0723 | 119.8879 | 0.082087 | -120.1722 | 119.8357
Line5_6_7 | 0.11108 | 0.087928 | 0.085857 | 0.11108 | 0.087928 | 0.085857 | 0.025653 | 0.020306 | 0.019828 | 0.025653 | 0.020306 | 0.019828 | -0.011829 | -0.0059377 | -0.0065741 | 0.011952 | 0.0060214 | 0.0066407 | -0.02759 | -0.022842 | -0.022109 | 0.027827 | 0.023002 | 0.02226 | 113.288 | -15.6011 | -133.6044 | -66.712 | 164.3989 | 46.3956 |  | 1.1702 | 1.1623 | 1.1633 | 1.1805 | 1.1709 | 1.1715 | 0.082087 | -120.1722 | 119.8357 | 0.044286 | -120.2707 | 119.7843
Line6_7_8 | 0 | 0.038143 | 0.038152 | 0 | 0.038143 | 0.038152 | 0 | 0.0088087 | 0.0088108 | 0 | 0.0088087 | 0.0088108 | 3.5614e-10 | 0.0072835 | 0.0072954 | -5.7679e-10 | -0.0072744 | -0.0072779 | -9.7901e-10 | 0.0073031 | 0.0073025 | 6.746e-10 | -0.0072744 | -0.0072779 | 0 | -165.3478 | 74.7567 | 0 | 14.6522 | -105.2433 |  | 1.1805 | 1.1709 | 1.1715 | 1.1799 | 1.1679 | 1.1682 | 0.044286 | -120.2707 | 119.7843 | 0.034993 | -120.3478 | 119.7567
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1545e-10 | 1.2185e-10 | 6.9137e-10 | -3.459e-10 | -2.9077e-10 | -2.92e-10 | -3.3585e-10 | 3.9204e-10 | -1.4706e-11 | 2.9066e-12 | -2.8594e-11 | -2.001e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1799 | 1.1679 | 1.1682 | 1.1799 | 1.1679 | 1.1682 | 0.034993 | -120.3478 | 119.7567 | 0.034993 | -120.3478 | 119.7567
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1545e-10 | 1.2185e-10 | 6.9137e-10 | -3.459e-10 | -2.9077e-10 | -2.92e-10 | -3.3585e-10 | 3.9204e-10 | -1.4706e-11 | 2.9067e-12 | -2.8594e-11 | -2.001e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1799 | 1.1679 | 1.1682 | 1.1799 | 1.1679 | 1.1682 | 0.034993 | -120.3478 | 119.7567 | 0.034993 | -120.3478 | 119.7567
Line9_3_11 | 0.10076 | 0.10485 | 0.1023 | 0.10076 | 0.10485 | 0.1023 | 0.023269 | 0.024215 | 0.023625 | 0.023269 | 0.024215 | 0.023625 | -0.0004728 | -0.0011586 | -0.0017563 | 0.00057321 | 0.0012668 | 0.0018637 | -0.026949 | -0.027924 | -0.027252 | 0.027154 | 0.028142 | 0.027461 | 90.9575 | -27.7998 | -146.5702 | -89.0425 | 152.2002 | 33.4298 |  | 1.1583 | 1.1542 | 1.1559 | 1.1672 | 1.1633 | 1.1651 | -0.047605 | -120.1757 | 119.7425 | -0.25178 | -120.3773 | 119.5474

## LLG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.012611 | 1.417 | 1.4934 | 0.012612 | 1.417 | 1.4934 | 0.0029125 | 0.32725 | 0.34488 | 0.0029125 | 0.32725 | 0.34488 | -0.00047112 | 0.15396 | 0.17211 | 0.00047819 | -0.11558 | -0.12916 | 0.0040508 | 0.16353 | 0.17561 | -0.0040421 | -0.12262 | -0.13181 | -95.9699 | -144.9367 | 39.2333 | 84.0302 | 35.0633 | -140.7667 |  | 1.4002 | 0.68632 | 0.71296 | 1.3975 | 0.51491 | 0.53509 | 0.66394 | -98.2097 | 84.8097 | 0.77703 | -98.2446 | 84.8144
Line10_11_12 | 0.013108 | 0.011765 | 0.014614 | 0.013108 | 0.011765 | 0.014614 | 0.0030272 | 0.0027169 | 0.003375 | 0.0030273 | 0.002717 | 0.003375 | -1.443e-05 | 0.0017474 | -0.0024106 | 1.6137e-05 | -0.0017465 | 0.0024131 | 0.0042354 | -0.00064881 | 4.9961e-05 | -0.0042338 | 0.00065032 | -4.7791e-05 | -89.4849 | -77.9464 | -93.8971 | 90.5151 | 102.0534 | 86.103 |  | 1.3991 | 0.68606 | 0.71441 | 1.3986 | 0.68592 | 0.71513 | 0.71028 | -98.3164 | 84.9156 | 0.73347 | -98.3698 | 84.9684
Line11_12_13 | 0.013108 | 0.011765 | 0.014614 | 0.013109 | 0.011765 | 0.014614 | 0.0030273 | 0.002717 | 0.003375 | 0.0030273 | 0.002717 | 0.003375 | -1.6139e-05 | 0.0017465 | -0.0024131 | 1.7846e-05 | -0.0017456 | 0.0024156 | 0.0042338 | -0.00065032 | 4.779e-05 | -0.0042322 | 0.00065182 | -4.5619e-05 | -89.4849 | -77.9466 | -93.897 | 90.5151 | 102.0533 | 86.103 |  | 1.3986 | 0.68592 | 0.71513 | 1.398 | 0.68579 | 0.71585 | 0.73347 | -98.3698 | 84.9684 | 0.75668 | -98.4232 | 85.0211
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7613e-09 | -7.8311e-08 | 8.0457e-08 | -4.1378e-09 | 5.2704e-08 | -5.3474e-08 | -1.5949e-07 | 1.1831e-08 | -5.9673e-09 | 1.0639e-07 | -7.0088e-09 | 2.5487e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.398 | 0.68579 | 0.71585 | 1.398 | 0.68579 | 0.71585 | 0.75668 | -98.4232 | 85.0211 | 0.75668 | -98.4232 | 85.0211
Line13_13_14 | 0.013109 | 0.011765 | 0.014615 | 0.013109 | 0.011766 | 0.014615 | 0.0030274 | 0.0027171 | 0.0033752 | 0.0030275 | 0.0027172 | 0.0033752 | -1.7851e-05 | 0.0017456 | -0.0024157 | 1.9558e-05 | -0.0017447 | 0.0024182 | 0.0042323 | -0.00065183 | 4.5624e-05 | -0.0042307 | 0.00065334 | -4.3454e-05 | -89.485 | -77.9473 | -93.8969 | 90.515 | 102.0526 | 86.1032 |  | 1.398 | 0.68579 | 0.71585 | 1.3975 | 0.68566 | 0.71658 | 0.75668 | -98.4232 | 85.0211 | 0.77992 | -98.4766 | 85.0737
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8408e-09 | -5.2207e-08 | 5.3638e-08 | -3.2174e-09 | 2.6601e-08 | -2.6655e-08 | -1.0633e-07 | 7.8873e-09 | -3.9782e-09 | 5.3228e-08 | -3.0652e-09 | 5.5962e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.398 | 0.68579 | 0.71585 | 1.398 | 0.68579 | 0.71585 | 0.75668 | -98.4232 | 85.0211 | 0.75668 | -98.4232 | 85.0211
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.2042e-10 | -2.6104e-08 | 2.6819e-08 | -2.2969e-09 | 4.9697e-10 | 1.6416e-10 | -5.3164e-08 | 3.9437e-09 | -1.9891e-09 | 6.4311e-11 | 8.7849e-10 | -1.4295e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.398 | 0.68579 | 0.71585 | 1.398 | 0.68579 | 0.71585 | 0.75668 | -98.4232 | 85.0211 | 0.75668 | -98.4232 | 85.0211
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0504e-09 | -2.6242e-08 | 2.684e-08 | -2.3081e-09 | 4.9381e-10 | 1.6538e-10 | -5.3424e-08 | 3.7943e-09 | -1.9687e-09 | 5.8487e-11 | 8.852e-10 | -1.4308e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3997 | 0.68618 | 0.71369 | 1.3997 | 0.68618 | 0.71369 | 0.68734 | -98.2633 | 84.8627 | 0.68734 | -98.2633 | 84.8627
Line17_5_19 | 0.013158 | 0.011808 | 0.014672 | 0.013158 | 0.011808 | 0.014672 | 0.0030387 | 0.002727 | 0.0033884 | 0.0030387 | 0.002727 | 0.0033884 | -2.8778e-05 | 0.001757 | -0.0024178 | 3.0499e-05 | -0.0017561 | 0.0024204 | 0.004253 | -0.00064371 | 4.3887e-05 | -0.0042514 | 0.00064523 | -4.1699e-05 | -89.7004 | -78.1418 | -94.0974 | 90.2996 | 101.8581 | 85.9027 |  | 1.3997 | 0.68619 | 0.71369 | 1.3991 | 0.68605 | 0.71442 | 0.68728 | -98.2632 | 84.8627 | 0.71063 | -98.3167 | 84.9156
Line1_1_3 | 0.013108 | 0.011764 | 0.014614 | 0.013108 | 0.011764 | 0.014614 | 0.0030272 | 0.0027168 | 0.0033749 | 0.0030272 | 0.0027169 | 0.0033749 | -1.1011e-05 | 0.0017492 | -0.0024056 | 1.2718e-05 | -0.0017483 | 0.0024081 | 0.0042386 | -0.0006458 | 5.4304e-05 | -0.004237 | 0.0006473 | -5.2134e-05 | -89.4849 | -77.9461 | -93.8971 | 90.5151 | 102.0538 | 86.1029 |  | 1.4002 | 0.68632 | 0.71296 | 1.3997 | 0.68619 | 0.71368 | 0.66394 | -98.2097 | 84.8097 | 0.6871 | -98.2631 | 84.8627
Line2_1_4 | 0.013174 | 0.011822 | 0.014691 | 0.013174 | 0.011822 | 0.014691 | 0.0030424 | 0.0027302 | 0.0033928 | 0.0030424 | 0.0027302 | 0.0033928 | -3.2456e-05 | 0.0017608 | -0.0024185 | 3.4181e-05 | -0.0017598 | 0.0024211 | 0.0042599 | -0.00064097 | 4.3301e-05 | -0.0042582 | 0.00064249 | -4.1107e-05 | -89.7726 | -78.2067 | -94.1646 | 90.2274 | 101.7931 | 85.8354 |  | 1.4002 | 0.68632 | 0.71296 | 1.3997 | 0.68618 | 0.71369 | 0.66394 | -98.2097 | 84.8097 | 0.68734 | -98.2633 | 84.8627
Line3_1_5 | 0.013158 | 0.011808 | 0.014672 | 0.013158 | 0.011808 | 0.014672 | 0.0030386 | 0.0027269 | 0.0033883 | 0.0030387 | 0.002727 | 0.0033884 | -2.7056e-05 | 0.0017579 | -0.0024153 | 2.8776e-05 | -0.001757 | 0.0024178 | 0.0042546 | -0.0006422 | 4.6077e-05 | -0.004253 | 0.00064372 | -4.3889e-05 | -89.7004 | -78.1416 | -94.0974 | 90.2996 | 101.8583 | 85.9026 |  | 1.4002 | 0.68632 | 0.71296 | 1.3997 | 0.68619 | 0.71369 | 0.66394 | -98.2097 | 84.8097 | 0.68728 | -98.2632 | 84.8627
Line4_2_6 | 0.012612 | 1.417 | 1.4934 | 0.012612 | 1.417 | 1.4934 | 0.0029125 | 0.32725 | 0.34488 | 0.0029126 | 0.32725 | 0.34488 | -0.00047819 | 0.11558 | 0.12916 | 0.00048525 | -0.077205 | -0.086214 | 0.0040421 | 0.12262 | 0.13181 | -0.0040334 | -0.081706 | -0.08801 | -95.9698 | -144.9367 | 39.2333 | 84.0303 | 35.0633 | -140.7667 |  | 1.3975 | 0.51491 | 0.53509 | 1.3948 | 0.34351 | 0.35723 | 0.77703 | -98.2446 | 84.8144 | 0.89055 | -98.3144 | 84.8237
Line5_6_7 | 0.012612 | 1.417 | 1.4934 | 0.012612 | 1.417 | 1.4934 | 0.0029126 | 0.32725 | 0.34488 | 0.0029126 | 0.32725 | 0.34488 | -0.00048526 | 0.077205 | 0.086214 | 0.00049233 | -0.038829 | -0.043266 | 0.0040334 | 0.081706 | 0.08801 | -0.0040247 | -0.040794 | -0.04421 | -95.9698 | -144.9367 | 39.2333 | 84.0303 | 35.0633 | -140.7667 |  | 1.3948 | 0.34351 | 0.35723 | 1.3921 | 0.1721 | 0.17936 | 0.89055 | -98.3144 | 84.8237 | 1.0045 | -98.523 | 84.8517
Line6_7_8 | 0 | 1.4193 | 1.5099 | 0 | 1.4193 | 1.5099 | 0 | 0.32776 | 0.34871 | 0 | 0.32776 | 0.34871 | 6.3607e-09 | 0.038429 | 0.04394 | -6.7261e-09 | -1.5528e-14 | 2.0004e-14 | -1.6224e-07 | 0.041292 | 0.044509 | 1.0815e-07 | -1.6577e-14 | 7.4464e-15 | 0 | -145.5798 | 39.4831 | 0 | 34.4203 | -140.5169 |  | 1.3921 | 0.1721 | 0.17936 | 1.3898 | 0 | 0 | 1.0045 | -98.523 | 84.8517 | 1.0932 | 0 | 0
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.242e-09 | -2.8752e-21 | -1.9259e-21 | -2.242e-09 | 6.742e-18 | -1.1953e-17 | -5.4031e-08 | 3.7017e-22 | 1.0455e-21 | 9.236e-11 | 2.2026e-17 | -2.1319e-18 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3898 | 0 | 0 | 1.3898 | 0 | 0 | 1.0932 | 0 | 0 | 1.0932 | 0 | 0
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.242e-09 | -2.8752e-21 | -1.9259e-21 | -2.242e-09 | 6.742e-18 | -1.1953e-17 | -5.4031e-08 | 3.7017e-22 | 1.0455e-21 | 9.236e-11 | 2.2026e-17 | -2.1319e-18 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3898 | 0 | 0 | 1.3898 | 0 | 0 | 1.0932 | 0 | 0 | 1.0932 | 0 | 0
Line9_3_11 | 0.013108 | 0.011764 | 0.014614 | 0.013108 | 0.011765 | 0.014614 | 0.0030272 | 0.0027169 | 0.0033749 | 0.0030272 | 0.0027169 | 0.003375 | -1.2721e-05 | 0.0017483 | -0.0024081 | 1.4427e-05 | -0.0017474 | 0.0024106 | 0.004237 | -0.0006473 | 5.2132e-05 | -0.0042354 | 0.00064881 | -4.9962e-05 | -89.4849 | -77.9463 | -93.8971 | 90.5151 | 102.0536 | 86.103 |  | 1.3997 | 0.68619 | 0.71368 | 1.3991 | 0.68606 | 0.71441 | 0.6871 | -98.2631 | 84.8627 | 0.71028 | -98.3164 | 84.9156

## LLG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.011948 | 1.3424 | 1.4148 | 0.011948 | 1.3424 | 1.4148 | 0.0027592 | 0.31002 | 0.32673 | 0.0027592 | 0.31002 | 0.32673 | -0.00042283 | 0.13818 | 0.15447 | 0.00042917 | -0.10373 | -0.11592 | 0.0036356 | 0.14677 | 0.15761 | -0.0036278 | -0.11005 | -0.1183 | -95.9699 | -144.9367 | 39.2333 | 84.0302 | 35.0633 | -140.7667 |  | 1.3265 | 0.6502 | 0.67544 | 1.324 | 0.48781 | 0.50693 | 0.66394 | -98.2097 | 84.8097 | 0.77703 | -98.2446 | 84.8144
Line10_11_12 | 0.012418 | 0.011145 | 0.013845 | 0.012419 | 0.011146 | 0.013845 | 0.0028679 | 0.0025739 | 0.0031973 | 0.0028679 | 0.002574 | 0.0031974 | -1.2951e-05 | 0.0015683 | -0.0021635 | 1.4483e-05 | -0.0015675 | 0.0021658 | 0.0038013 | -0.00058231 | 4.484e-05 | -0.0037999 | 0.00058366 | -4.2893e-05 | -89.4849 | -77.9464 | -93.8971 | 90.5151 | 102.0534 | 86.103 |  | 1.3255 | 0.64995 | 0.67681 | 1.325 | 0.64982 | 0.67749 | 0.71028 | -98.3164 | 84.9156 | 0.73347 | -98.3698 | 84.9684
Line11_12_13 | 0.012419 | 0.011146 | 0.013845 | 0.012419 | 0.011146 | 0.013845 | 0.0028679 | 0.002574 | 0.0031974 | 0.002868 | 0.002574 | 0.0031974 | -1.4485e-05 | 0.0015675 | -0.0021658 | 1.6017e-05 | -0.0015667 | 0.002168 | 0.0037999 | -0.00058366 | 4.2891e-05 | -0.0037984 | 0.00058501 | -4.0944e-05 | -89.4849 | -77.9466 | -93.897 | 90.5151 | 102.0533 | 86.103 |  | 1.325 | 0.64982 | 0.67749 | 1.3244 | 0.6497 | 0.67818 | 0.73347 | -98.3698 | 84.9684 | 0.75668 | -98.4232 | 85.0211
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4783e-09 | -7.0285e-08 | 7.2211e-08 | -3.7137e-09 | 4.7302e-08 | -4.7993e-08 | -1.4315e-07 | 1.0618e-08 | -5.3557e-09 | 9.5488e-08 | -6.2905e-09 | 2.2875e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3244 | 0.6497 | 0.67818 | 1.3244 | 0.6497 | 0.67818 | 0.75668 | -98.4232 | 85.0211 | 0.75668 | -98.4232 | 85.0211
Line13_13_14 | 0.012419 | 0.011146 | 0.013846 | 0.012419 | 0.011146 | 0.013846 | 0.0028681 | 0.0025741 | 0.0031975 | 0.0028681 | 0.0025741 | 0.0031975 | -1.6021e-05 | 0.0015667 | -0.0021681 | 1.7554e-05 | -0.0015659 | 0.0021703 | 0.0037985 | -0.00058502 | 4.0948e-05 | -0.0037971 | 0.00058638 | -3.9e-05 | -89.485 | -77.9473 | -93.8969 | 90.515 | 102.0526 | 86.1032 |  | 1.3244 | 0.6497 | 0.67818 | 1.3239 | 0.64957 | 0.67886 | 0.75668 | -98.4232 | 85.0211 | 0.77992 | -98.4766 | 85.0737
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6522e-09 | -4.6856e-08 | 4.8141e-08 | -2.8876e-09 | 2.3874e-08 | -2.3923e-08 | -9.543e-08 | 7.0789e-09 | -3.5705e-09 | 4.7773e-08 | -2.751e-09 | 5.0226e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3244 | 0.6497 | 0.67818 | 1.3244 | 0.6497 | 0.67818 | 0.75668 | -98.4232 | 85.0211 | 0.75668 | -98.4232 | 85.0211
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.2609e-10 | -2.3428e-08 | 2.407e-08 | -2.0615e-09 | 4.4604e-10 | 1.4734e-10 | -4.7715e-08 | 3.5395e-09 | -1.7852e-09 | 5.772e-11 | 7.8845e-10 | -1.283e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3244 | 0.6497 | 0.67818 | 1.3244 | 0.6497 | 0.67818 | 0.75668 | -98.4232 | 85.0211 | 0.75668 | -98.4232 | 85.0211
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.4274e-10 | -2.3552e-08 | 2.4089e-08 | -2.0715e-09 | 4.432e-10 | 1.4843e-10 | -4.7948e-08 | 3.4054e-09 | -1.7669e-09 | 5.2492e-11 | 7.9447e-10 | -1.2842e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.326 | 0.65007 | 0.67613 | 1.326 | 0.65007 | 0.67613 | 0.68734 | -98.2633 | 84.8627 | 0.68734 | -98.2633 | 84.8627
Line17_5_19 | 0.012465 | 0.011187 | 0.0139 | 0.012465 | 0.011187 | 0.0139 | 0.0028787 | 0.0025834 | 0.00321 | 0.0028788 | 0.0025835 | 0.0032101 | -2.5829e-05 | 0.0015769 | -0.00217 | 2.7373e-05 | -0.0015761 | 0.0021723 | 0.0038171 | -0.00057774 | 3.9389e-05 | -0.0038157 | 0.0005791 | -3.7426e-05 | -89.7004 | -78.1418 | -94.0974 | 90.2996 | 101.8581 | 85.9027 |  | 1.326 | 0.65007 | 0.67613 | 1.3255 | 0.64994 | 0.67682 | 0.68728 | -98.2632 | 84.8627 | 0.71063 | -98.3167 | 84.9156
Line1_1_3 | 0.012418 | 0.011145 | 0.013845 | 0.012418 | 0.011145 | 0.013845 | 0.0028678 | 0.0025739 | 0.0031973 | 0.0028679 | 0.0025739 | 0.0031973 | -9.8827e-06 | 0.0015699 | -0.002159 | 1.1415e-05 | -0.0015691 | 0.0021613 | 0.0038042 | -0.00057961 | 4.8738e-05 | -0.0038028 | 0.00058096 | -4.6791e-05 | -89.4849 | -77.9461 | -93.8971 | 90.5151 | 102.0538 | 86.1029 |  | 1.3265 | 0.6502 | 0.67544 | 1.326 | 0.65007 | 0.67612 | 0.66394 | -98.2097 | 84.8097 | 0.6871 | -98.2631 | 84.8627
Line2_1_4 | 0.012481 | 0.0112 | 0.013918 | 0.012481 | 0.0112 | 0.013918 | 0.0028823 | 0.0025865 | 0.0032142 | 0.0028823 | 0.0025866 | 0.0032142 | -2.913e-05 | 0.0015803 | -0.0021706 | 3.0678e-05 | -0.0015795 | 0.0021729 | 0.0038233 | -0.00057528 | 3.8863e-05 | -0.0038218 | 0.00057664 | -3.6894e-05 | -89.7726 | -78.2067 | -94.1646 | 90.2274 | 101.7931 | 85.8354 |  | 1.3265 | 0.6502 | 0.67544 | 1.326 | 0.65007 | 0.67613 | 0.66394 | -98.2097 | 84.8097 | 0.68734 | -98.2633 | 84.8627
Line3_1_5 | 0.012465 | 0.011186 | 0.0139 | 0.012465 | 0.011187 | 0.0139 | 0.0028787 | 0.0025834 | 0.00321 | 0.0028787 | 0.0025834 | 0.00321 | -2.4283e-05 | 0.0015777 | -0.0021678 | 2.5827e-05 | -0.0015769 | 0.00217 | 0.0038186 | -0.00057638 | 4.1354e-05 | -0.0038171 | 0.00057774 | -3.939e-05 | -89.7004 | -78.1416 | -94.0974 | 90.2996 | 101.8583 | 85.9026 |  | 1.3265 | 0.6502 | 0.67544 | 1.326 | 0.65007 | 0.67613 | 0.66394 | -98.2097 | 84.8097 | 0.68728 | -98.2632 | 84.8627
Line4_2_6 | 0.011948 | 1.3424 | 1.4148 | 0.011948 | 1.3424 | 1.4148 | 0.0027592 | 0.31002 | 0.32673 | 0.0027593 | 0.31002 | 0.32673 | -0.00042918 | 0.10373 | 0.11592 | 0.00043552 | -0.069292 | -0.077378 | 0.0036278 | 0.11005 | 0.1183 | -0.00362 | -0.073331 | -0.078989 | -95.9698 | -144.9367 | 39.2333 | 84.0303 | 35.0633 | -140.7667 |  | 1.324 | 0.48781 | 0.50693 | 1.3214 | 0.32543 | 0.33843 | 0.77703 | -98.2446 | 84.8144 | 0.89055 | -98.3144 | 84.8237
Line5_6_7 | 0.011948 | 1.3424 | 1.4148 | 0.011948 | 1.3424 | 1.4148 | 0.0027593 | 0.31002 | 0.32673 | 0.0027593 | 0.31002 | 0.32673 | -0.00043552 | 0.069292 | 0.077378 | 0.00044187 | -0.034849 | -0.038831 | 0.00362 | 0.073331 | 0.078989 | -0.0036122 | -0.036613 | -0.039679 | -95.9698 | -144.9367 | 39.2333 | 84.0303 | 35.0633 | -140.7667 |  | 1.3214 | 0.32543 | 0.33843 | 1.3188 | 0.16304 | 0.16992 | 0.89055 | -98.3144 | 84.8237 | 1.0045 | -98.523 | 84.8517
Line6_7_8 | 0 | 1.3446 | 1.4305 | 0 | 1.3446 | 1.4305 | 0 | 0.31051 | 0.33035 | 0 | 0.31051 | 0.33035 | 5.7088e-09 | 0.034491 | 0.039436 | -6.0368e-09 | -1.3737e-14 | 1.7787e-14 | -1.4561e-07 | 0.03706 | 0.039947 | 9.7069e-08 | -1.5077e-14 | 6.9681e-15 | 0 | -145.5798 | 39.4831 | 0 | 34.4203 | -140.5169 |  | 1.3188 | 0.16304 | 0.16992 | 1.3166 | 0 | 0 | 1.0045 | -98.523 | 84.8517 | 1.0932 | 0 | 0
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0123e-09 | -2.5862e-21 | -1.7393e-21 | -2.0123e-09 | 6.051e-18 | -1.0728e-17 | -4.8493e-08 | 2.9677e-22 | 9.0626e-22 | 8.2894e-11 | 1.9768e-17 | -1.9134e-18 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3166 | 0 | 0 | 1.3166 | 0 | 0 | 1.0932 | 0 | 0 | 1.0932 | 0 | 0
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0123e-09 | -2.5862e-21 | -1.7393e-21 | -2.0123e-09 | 6.051e-18 | -1.0728e-17 | -4.8493e-08 | 2.9677e-22 | 9.0626e-22 | 8.2894e-11 | 1.9768e-17 | -1.9134e-18 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3166 | 0 | 0 | 1.3166 | 0 | 0 | 1.0932 | 0 | 0 | 1.0932 | 0 | 0
Line9_3_11 | 0.012418 | 0.011145 | 0.013845 | 0.012418 | 0.011145 | 0.013845 | 0.0028679 | 0.0025739 | 0.0031973 | 0.0028679 | 0.0025739 | 0.0031973 | -1.1417e-05 | 0.0015691 | -0.0021613 | 1.2949e-05 | -0.0015683 | 0.0021635 | 0.0038028 | -0.00058096 | 4.6789e-05 | -0.0038013 | 0.00058231 | -4.4842e-05 | -89.4849 | -77.9463 | -93.8971 | 90.5151 | 102.0536 | 86.103 |  | 1.326 | 0.65007 | 0.67612 | 1.3255 | 0.64995 | 0.67681 | 0.6871 | -98.2631 | 84.8627 | 0.71028 | -98.3164 | 84.9156

## LLG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.0021926 | 0.027297 | 0.029656 | 0.0021927 | 0.027297 | 0.029656 | 0.00050637 | 0.0063039 | 0.0068487 | 0.00050638 | 0.0063039 | 0.0068487 | 0.0002943 | 0.0041918 | 0.0043755 | -0.00029407 | -0.0041798 | -0.0043578 | 0.00041912 | 0.0036025 | 0.0049234 | -0.00041888 | -0.0035865 | -0.0049085 | -52.2203 | -158.9532 | 66.982 | 127.7797 | 21.0468 | -113.0181 |  | 1.0114 | 0.87679 | 0.96175 | 1.0107 | 0.87368 | 0.9584 | 2.7039 | -118.2769 | 115.3542 | 2.7094 | -118.3218 | 115.3831
Line10_11_12 | 0.002215 | 0.0022297 | 0.0022486 | 0.0022151 | 0.0022297 | 0.0022487 | 0.00051154 | 0.00051493 | 0.0005193 | 0.00051155 | 0.00051493 | 0.0005193 | 0.00030211 | 0.00016822 | -0.00048796 | -0.00030207 | -0.00016817 | 0.00048802 | 0.00041982 | -0.00041904 | 0.0001068 | -0.00041977 | 0.00041909 | -0.00010675 | -51.5544 | -50.165 | -52.2865 | 128.4456 | 129.835 | 127.7135 |  | 1.0111 | 0.8769 | 0.9619 | 1.011 | 0.87696 | 0.96197 | 2.7061 | -118.2927 | 115.3678 | 2.7072 | -118.3006 | 115.3747
Line11_12_13 | 0.0022151 | 0.0022297 | 0.0022487 | 0.0022151 | 0.0022298 | 0.0022487 | 0.00051155 | 0.00051493 | 0.0005193 | 0.00051155 | 0.00051494 | 0.00051931 | 0.00030207 | 0.00016817 | -0.00048802 | -0.00030202 | -0.00016813 | 0.00048807 | 0.00041977 | -0.00041909 | 0.00010675 | -0.00041973 | 0.00041915 | -0.0001067 | -51.5544 | -50.1651 | -52.2865 | 128.4456 | 129.8349 | 127.7135 |  | 1.011 | 0.87696 | 0.96197 | 1.0108 | 0.87702 | 0.96204 | 2.7072 | -118.3006 | 115.3747 | 2.7083 | -118.3085 | 115.3815
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.0835e-08 | -7.3913e-09 | 1.8375e-08 | 6.994e-09 | 5.1609e-09 | -1.2303e-08 | -1.6427e-08 | 1.5419e-08 | -3.4668e-09 | 1.1117e-08 | -1.0189e-08 | 2.0413e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0108 | 0.87702 | 0.96204 | 1.0108 | 0.87702 | 0.96204 | 2.7083 | -118.3085 | 115.3815 | 2.7083 | -118.3085 | 115.3815
Line13_13_14 | 0.0022152 | 0.0022298 | 0.0022488 | 0.0022152 | 0.0022299 | 0.0022488 | 0.00051157 | 0.00051496 | 0.00051933 | 0.00051158 | 0.00051497 | 0.00051934 | 0.00030203 | 0.00016814 | -0.00048809 | -0.00030199 | -0.00016809 | 0.00048815 | 0.00041975 | -0.00041916 | 0.00010671 | -0.0004197 | 0.00041922 | -0.00010666 | -51.5545 | -50.1652 | -52.2866 | 128.4455 | 129.8347 | 127.7134 |  | 1.0108 | 0.87702 | 0.96204 | 1.0107 | 0.87707 | 0.96211 | 2.7083 | -118.3085 | 115.3815 | 2.7093 | -118.3164 | 115.3884
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.2234e-09 | -4.9276e-09 | 1.225e-08 | 3.3823e-09 | 2.6971e-09 | -6.1783e-09 | -1.0951e-08 | 1.0279e-08 | -2.3112e-09 | 5.6419e-09 | -5.0493e-09 | 8.8576e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0108 | 0.87702 | 0.96204 | 1.0108 | 0.87702 | 0.96204 | 2.7083 | -118.3085 | 115.3815 | 2.7083 | -118.3085 | 115.3815
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.6117e-09 | -2.4638e-09 | 6.1249e-09 | -2.2944e-10 | 2.3336e-10 | -5.3359e-11 | -5.4756e-09 | 5.1395e-09 | -1.1556e-09 | 1.6637e-10 | 9.0176e-11 | -2.6983e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0108 | 0.87702 | 0.96204 | 1.0108 | 0.87702 | 0.96204 | 2.7083 | -118.3085 | 115.3815 | 2.7083 | -118.3085 | 115.3815
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.6074e-09 | -2.493e-09 | 6.1502e-09 | -2.3097e-10 | 2.3383e-10 | -5.2675e-11 | -5.5109e-09 | 5.1479e-09 | -1.1399e-09 | 1.6624e-10 | 9.1417e-11 | -2.7097e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0112 | 0.87684 | 0.96182 | 1.0112 | 0.87684 | 0.96182 | 2.7051 | -118.2849 | 115.361 | 2.7051 | -118.2849 | 115.361
Line17_5_19 | 0.0022235 | 0.0022382 | 0.0022573 | 0.0022235 | 0.0022382 | 0.0022573 | 0.00051348 | 0.00051689 | 0.00052129 | 0.00051349 | 0.0005169 | 0.0005213 | 0.00030179 | 0.0001704 | -0.00049017 | -0.00030175 | -0.00017035 | 0.00049022 | 0.00042255 | -0.00041998 | 0.00010551 | -0.0004225 | 0.00042004 | -0.00010546 | -51.7601 | -50.3683 | -52.4914 | 128.2399 | 129.6317 | 127.5087 |  | 1.0112 | 0.87684 | 0.96182 | 1.0111 | 0.8769 | 0.9619 | 2.7051 | -118.2849 | 115.361 | 2.7062 | -118.2928 | 115.3679
Line1_1_3 | 0.002215 | 0.0022296 | 0.0022486 | 0.002215 | 0.0022297 | 0.0022486 | 0.00051153 | 0.00051491 | 0.00051929 | 0.00051153 | 0.00051492 | 0.00051929 | 0.0003022 | 0.00016831 | -0.00048785 | -0.00030215 | -0.00016826 | 0.0004879 | 0.0004199 | -0.00041893 | 0.0001069 | -0.00041986 | 0.00041898 | -0.00010685 | -51.5543 | -50.1649 | -52.2865 | 128.4457 | 129.8351 | 127.7135 |  | 1.0114 | 0.87679 | 0.96175 | 1.0112 | 0.87684 | 0.96182 | 2.7039 | -118.2769 | 115.3542 | 2.705 | -118.2848 | 115.361
Line2_1_4 | 0.0022262 | 0.002241 | 0.0022601 | 0.0022262 | 0.002241 | 0.0022601 | 0.00051412 | 0.00051753 | 0.00052194 | 0.00051412 | 0.00051753 | 0.00052195 | 0.0003017 | 0.00017115 | -0.00049085 | -0.00030166 | -0.00017111 | 0.00049091 | 0.00042348 | -0.00042025 | 0.0001051 | -0.00042344 | 0.0004203 | -0.00010505 | -51.829 | -50.4362 | -52.5599 | 128.171 | 129.5638 | 127.4401 |  | 1.0114 | 0.87679 | 0.96175 | 1.0112 | 0.87684 | 0.96182 | 2.7039 | -118.2769 | 115.3542 | 2.7051 | -118.2849 | 115.361
Line3_1_5 | 0.0022234 | 0.0022382 | 0.0022572 | 0.0022235 | 0.0022382 | 0.0022573 | 0.00051348 | 0.00051688 | 0.00052129 | 0.00051348 | 0.00051689 | 0.00052129 | 0.00030183 | 0.00017044 | -0.00049011 | -0.00030179 | -0.00017039 | 0.00049017 | 0.00042259 | -0.00041993 | 0.00010556 | -0.00042255 | 0.00041998 | -0.00010551 | -51.7601 | -50.3682 | -52.4913 | 128.2399 | 129.6318 | 127.5087 |  | 1.0114 | 0.87679 | 0.96175 | 1.0112 | 0.87684 | 0.96182 | 2.7039 | -118.2769 | 115.3542 | 2.7051 | -118.2849 | 115.361
Line4_2_6 | 0.0021927 | 0.027297 | 0.029656 | 0.0021927 | 0.027297 | 0.029656 | 0.00050638 | 0.0063039 | 0.0068487 | 0.00050638 | 0.0063039 | 0.0068487 | 0.00029407 | 0.0041798 | 0.0043578 | -0.00029384 | -0.0041678 | -0.00434 | 0.00041888 | 0.0035865 | 0.0049085 | -0.00041864 | -0.0035705 | -0.0048935 | -52.2203 | -158.9532 | 66.9819 | 127.7797 | 21.0469 | -113.0181 |  | 1.0107 | 0.87368 | 0.9584 | 1.01 | 0.87058 | 0.95505 | 2.7094 | -118.3218 | 115.3831 | 2.7149 | -118.367 | 115.4122
Line5_6_7 | 0.0021927 | 0.027297 | 0.029656 | 0.0021927 | 0.027297 | 0.029656 | 0.00050638 | 0.0063039 | 0.0068487 | 0.00050639 | 0.0063039 | 0.0068487 | 0.00029384 | 0.0041678 | 0.00434 | -0.00029361 | -0.0041557 | -0.0043223 | 0.00041864 | 0.0035705 | 0.0048935 | -0.0004184 | -0.0035544 | -0.0048786 | -52.2204 | -158.9531 | 66.9819 | 127.7796 | 21.047 | -113.0182 |  | 1.01 | 0.87058 | 0.95505 | 1.0094 | 0.86747 | 0.9517 | 2.7149 | -118.367 | 115.4122 | 2.7203 | -118.4126 | 115.4415
Line6_7_8 | 0 | 0.028228 | 0.03097 | 0 | 0.028228 | 0.03097 | 0 | 0.0065189 | 0.0071522 | 0 | 0.0065189 | 0.0071522 | -1.076e-08 | 0.0039961 | 0.004815 | 6.9449e-09 | -0.003984 | -0.0047957 | -1.696e-08 | 0.0040013 | 0.0048111 | 1.1483e-08 | -0.0039841 | -0.0047957 | 0 | -163.4501 | 70.4648 | 0 | 16.5499 | -109.5352 |  | 1.0094 | 0.86747 | 0.9517 | 1.0089 | 0.8643 | 0.94826 | 2.7203 | -118.4126 | 115.4415 | 2.7247 | -118.45 | 115.4647
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.5833e-09 | -2.6079e-09 | 6.1467e-09 | -2.2168e-10 | 2.705e-10 | -4.278e-12 | -5.658e-09 | 5.1427e-09 | -1.0422e-09 | 1.6706e-10 | 8.1438e-11 | -2.6119e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0089 | 0.8643 | 0.94826 | 1.0089 | 0.8643 | 0.94826 | 2.7247 | -118.45 | 115.4647 | 2.7247 | -118.45 | 115.4647
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.5833e-09 | -2.6079e-09 | 6.1467e-09 | -2.2168e-10 | 2.705e-10 | -4.278e-12 | -5.658e-09 | 5.1427e-09 | -1.0422e-09 | 1.6706e-10 | 8.1438e-11 | -2.6119e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0089 | 0.8643 | 0.94826 | 1.0089 | 0.8643 | 0.94826 | 2.7247 | -118.45 | 115.4647 | 2.7247 | -118.45 | 115.4647
Line9_3_11 | 0.002215 | 0.0022297 | 0.0022486 | 0.002215 | 0.0022297 | 0.0022486 | 0.00051153 | 0.00051492 | 0.00051929 | 0.00051154 | 0.00051493 | 0.0005193 | 0.00030215 | 0.00016826 | -0.0004879 | -0.00030211 | -0.00016822 | 0.00048796 | 0.00041986 | -0.00041898 | 0.00010685 | -0.00041982 | 0.00041904 | -0.0001068 | -51.5544 | -50.165 | -52.2865 | 128.4456 | 129.835 | 127.7135 |  | 1.0112 | 0.87684 | 0.96182 | 1.0111 | 0.8769 | 0.9619 | 2.705 | -118.2848 | 115.361 | 2.7061 | -118.2927 | 115.3678

## LLG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.0020772 | 0.02586 | 0.028095 | 0.0020773 | 0.02586 | 0.028095 | 0.00047972 | 0.0059721 | 0.0064882 | 0.00047972 | 0.0059721 | 0.0064882 | 0.00026413 | 0.0037622 | 0.003927 | -0.00026393 | -0.0037514 | -0.0039111 | 0.00037616 | 0.0032333 | 0.0044188 | -0.00037595 | -0.0032189 | -0.0044054 | -52.2203 | -158.9532 | 66.982 | 127.7797 | 21.0468 | -113.0181 |  | 0.95814 | 0.83064 | 0.91113 | 0.95751 | 0.8277 | 0.90796 | 2.7039 | -118.2769 | 115.3542 | 2.7094 | -118.3218 | 115.3831
Line10_11_12 | 0.0020985 | 0.0021123 | 0.0021303 | 0.0020985 | 0.0021124 | 0.0021303 | 0.00048462 | 0.00048783 | 0.00049197 | 0.00048462 | 0.00048783 | 0.00049197 | 0.00027114 | 0.00015098 | -0.00043795 | -0.00027111 | -0.00015094 | 0.000438 | 0.00037679 | -0.00037609 | 9.5853e-05 | -0.00037675 | 0.00037614 | -9.581e-05 | -51.5544 | -50.165 | -52.2865 | 128.4456 | 129.835 | 127.7135 |  | 0.95789 | 0.83075 | 0.91127 | 0.95776 | 0.8308 | 0.91134 | 2.7061 | -118.2927 | 115.3678 | 2.7072 | -118.3006 | 115.3747
Line11_12_13 | 0.0020985 | 0.0021124 | 0.0021303 | 0.0020985 | 0.0021124 | 0.0021303 | 0.00048462 | 0.00048783 | 0.00049197 | 0.00048463 | 0.00048784 | 0.00049198 | 0.00027111 | 0.00015094 | -0.000438 | -0.00027107 | -0.0001509 | 0.00043805 | 0.00037675 | -0.00037614 | 9.5809e-05 | -0.00037671 | 0.00037619 | -9.5766e-05 | -51.5544 | -50.1651 | -52.2865 | 128.4456 | 129.8349 | 127.7135 |  | 0.95776 | 0.8308 | 0.91134 | 0.95764 | 0.83086 | 0.91141 | 2.7072 | -118.3006 | 115.3747 | 2.7083 | -118.3085 | 115.3815
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -9.7246e-09 | -6.6338e-09 | 1.6491e-08 | 6.2771e-09 | 4.632e-09 | -1.1042e-08 | -1.4743e-08 | 1.3838e-08 | -3.1114e-09 | 9.978e-09 | -9.1445e-09 | 1.8321e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.95764 | 0.83086 | 0.91141 | 0.95764 | 0.83086 | 0.91141 | 2.7083 | -118.3085 | 115.3815 | 2.7083 | -118.3085 | 115.3815
Line13_13_14 | 0.0020986 | 0.0021125 | 0.0021304 | 0.0020986 | 0.0021125 | 0.0021304 | 0.00048465 | 0.00048786 | 0.000492 | 0.00048465 | 0.00048786 | 0.000492 | 0.00027108 | 0.0001509 | -0.00043806 | -0.00027104 | -0.00015086 | 0.00043811 | 0.00037673 | -0.0003762 | 9.5769e-05 | -0.00037669 | 0.00037625 | -9.5725e-05 | -51.5545 | -50.1652 | -52.2866 | 128.4455 | 129.8347 | 127.7134 |  | 0.95764 | 0.83086 | 0.91141 | 0.95752 | 0.83091 | 0.91148 | 2.7083 | -118.3085 | 115.3815 | 2.7093 | -118.3164 | 115.3884
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.483e-09 | -4.4225e-09 | 1.0994e-08 | 3.0356e-09 | 2.4207e-09 | -5.545e-09 | -9.8287e-09 | 9.2255e-09 | -2.0743e-09 | 5.0637e-09 | -4.5318e-09 | 7.9497e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.95764 | 0.83086 | 0.91141 | 0.95764 | 0.83086 | 0.91141 | 2.7083 | -118.3085 | 115.3815 | 2.7083 | -118.3085 | 115.3815
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.2415e-09 | -2.2113e-09 | 5.4972e-09 | -2.0593e-10 | 2.0944e-10 | -4.789e-11 | -4.9144e-09 | 4.6127e-09 | -1.0371e-09 | 1.4932e-10 | 8.0933e-11 | -2.4218e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.95764 | 0.83086 | 0.91141 | 0.95764 | 0.83086 | 0.91141 | 2.7083 | -118.3085 | 115.3815 | 2.7083 | -118.3085 | 115.3815
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.2376e-09 | -2.2375e-09 | 5.5199e-09 | -2.073e-10 | 2.0987e-10 | -4.7276e-11 | -4.9461e-09 | 4.6203e-09 | -1.0231e-09 | 1.492e-10 | 8.2047e-11 | -2.4319e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.95801 | 0.83069 | 0.9112 | 0.95801 | 0.83069 | 0.9112 | 2.7051 | -118.2849 | 115.361 | 2.7051 | -118.2849 | 115.361
Line17_5_19 | 0.0021064 | 0.0021204 | 0.0021385 | 0.0021065 | 0.0021204 | 0.0021385 | 0.00048646 | 0.00048969 | 0.00049386 | 0.00048646 | 0.00048969 | 0.00049386 | 0.00027086 | 0.00015293 | -0.00043993 | -0.00027082 | -0.00015289 | 0.00043998 | 0.00037924 | -0.00037694 | 9.4695e-05 | -0.0003792 | 0.00037699 | -9.4651e-05 | -51.7601 | -50.3683 | -52.4914 | 128.2399 | 129.6317 | 127.5087 |  | 0.95801 | 0.83069 | 0.9112 | 0.95789 | 0.83075 | 0.91127 | 2.7051 | -118.2849 | 115.361 | 2.7062 | -118.2928 | 115.3679
Line1_1_3 | 0.0020984 | 0.0021123 | 0.0021302 | 0.0020984 | 0.0021123 | 0.0021303 | 0.0004846 | 0.00048781 | 0.00049195 | 0.00048461 | 0.00048782 | 0.00049196 | 0.00027122 | 0.00015105 | -0.00043785 | -0.00027118 | -0.00015102 | 0.0004379 | 0.00037687 | -0.00037599 | 9.5941e-05 | -0.00037683 | 0.00037604 | -9.5898e-05 | -51.5543 | -50.1649 | -52.2865 | 128.4457 | 129.8351 | 127.7135 |  | 0.95814 | 0.83064 | 0.91113 | 0.95801 | 0.83069 | 0.9112 | 2.7039 | -118.2769 | 115.3542 | 2.705 | -118.2848 | 115.361
Line2_1_4 | 0.002109 | 0.002123 | 0.0021411 | 0.002109 | 0.002123 | 0.0021412 | 0.00048706 | 0.00049029 | 0.00049447 | 0.00048706 | 0.0004903 | 0.00049448 | 0.00027078 | 0.00015361 | -0.00044054 | -0.00027074 | -0.00015357 | 0.00044059 | 0.00038008 | -0.00037717 | 9.4331e-05 | -0.00038004 | 0.00037722 | -9.4287e-05 | -51.829 | -50.4362 | -52.5599 | 128.171 | 129.5638 | 127.4401 |  | 0.95814 | 0.83064 | 0.91113 | 0.95801 | 0.83069 | 0.9112 | 2.7039 | -118.2769 | 115.3542 | 2.7051 | -118.2849 | 115.361
Line3_1_5 | 0.0021064 | 0.0021204 | 0.0021384 | 0.0021064 | 0.0021204 | 0.0021385 | 0.00048645 | 0.00048968 | 0.00049385 | 0.00048646 | 0.00048969 | 0.00049386 | 0.0002709 | 0.00015297 | -0.00043988 | -0.00027086 | -0.00015293 | 0.00043993 | 0.00037928 | -0.00037689 | 9.4739e-05 | -0.00037924 | 0.00037694 | -9.4695e-05 | -51.7601 | -50.3682 | -52.4913 | 128.2399 | 129.6318 | 127.5087 |  | 0.95814 | 0.83064 | 0.91113 | 0.95801 | 0.83069 | 0.9112 | 2.7039 | -118.2769 | 115.3542 | 2.7051 | -118.2849 | 115.361
Line4_2_6 | 0.0020773 | 0.02586 | 0.028095 | 0.0020773 | 0.02586 | 0.028095 | 0.00047972 | 0.0059721 | 0.0064882 | 0.00047973 | 0.0059721 | 0.0064882 | 0.00026393 | 0.0037514 | 0.0039111 | -0.00026372 | -0.0037406 | -0.0038952 | 0.00037595 | 0.0032189 | 0.0044054 | -0.00037573 | -0.0032045 | -0.004392 | -52.2203 | -158.9532 | 66.9819 | 127.7797 | 21.0469 | -113.0181 |  | 0.95751 | 0.8277 | 0.90796 | 0.95689 | 0.82476 | 0.90478 | 2.7094 | -118.3218 | 115.3831 | 2.7149 | -118.367 | 115.4122
Line5_6_7 | 0.0020773 | 0.02586 | 0.028095 | 0.0020773 | 0.02586 | 0.028095 | 0.00047973 | 0.0059721 | 0.0064882 | 0.00047974 | 0.0059721 | 0.0064882 | 0.00026372 | 0.0037406 | 0.0038952 | -0.00026352 | -0.0037298 | -0.0038793 | 0.00037573 | 0.0032045 | 0.004392 | -0.00037552 | -0.0031901 | -0.0043785 | -52.2204 | -158.9531 | 66.9819 | 127.7796 | 21.047 | -113.0182 |  | 0.95689 | 0.82476 | 0.90478 | 0.95626 | 0.82182 | 0.90161 | 2.7149 | -118.367 | 115.4122 | 2.7203 | -118.4126 | 115.4415
Line6_7_8 | 0 | 0.026742 | 0.02934 | 0 | 0.026742 | 0.02934 | 0 | 0.0061758 | 0.0067758 | 0 | 0.0061758 | 0.0067758 | -9.6573e-09 | 0.0035865 | 0.0043215 | 6.2331e-09 | -0.0035757 | -0.0043042 | -1.5221e-08 | 0.0035912 | 0.004318 | 1.0306e-08 | -0.0035757 | -0.0043041 | 0 | -163.4501 | 70.4648 | 0 | 16.5499 | -109.5352 |  | 0.95626 | 0.82182 | 0.90161 | 0.95576 | 0.81881 | 0.89835 | 2.7203 | -118.4126 | 115.4415 | 2.7247 | -118.45 | 115.4647
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.216e-09 | -2.3406e-09 | 5.5167e-09 | -1.9896e-10 | 2.4278e-10 | -3.8395e-12 | -5.0781e-09 | 4.6156e-09 | -9.3541e-10 | 1.4993e-10 | 7.3091e-11 | -2.3442e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.95576 | 0.81881 | 0.89835 | 0.95576 | 0.81881 | 0.89835 | 2.7247 | -118.45 | 115.4647 | 2.7247 | -118.45 | 115.4647
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.216e-09 | -2.3406e-09 | 5.5167e-09 | -1.9896e-10 | 2.4278e-10 | -3.8396e-12 | -5.0781e-09 | 4.6156e-09 | -9.3541e-10 | 1.4993e-10 | 7.3091e-11 | -2.3442e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.95576 | 0.81881 | 0.89835 | 0.95576 | 0.81881 | 0.89835 | 2.7247 | -118.45 | 115.4647 | 2.7247 | -118.45 | 115.4647
Line9_3_11 | 0.0020984 | 0.0021123 | 0.0021303 | 0.0020985 | 0.0021123 | 0.0021303 | 0.00048461 | 0.00048782 | 0.00049196 | 0.00048462 | 0.00048783 | 0.00049197 | 0.00027118 | 0.00015102 | -0.0004379 | -0.00027114 | -0.00015098 | 0.00043795 | 0.00037683 | -0.00037604 | 9.5897e-05 | -0.00037679 | 0.00037609 | -9.5854e-05 | -51.5544 | -50.165 | -52.2865 | 128.4456 | 129.835 | 127.7135 |  | 0.95801 | 0.83069 | 0.9112 | 0.95789 | 0.83075 | 0.91127 | 2.705 | -118.2848 | 115.361 | 2.7061 | -118.2927 | 115.3678