## LLL_max_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 2.1767 | 2.1767 | 0 | 0 | 1.508 | 1.508 | 0.56854 | -0.42641 | 1.1371 | -0.85282 | -67.8829 | 112.1171 | 0.84302 | 0.63226 | -4.4479 | -4.4479
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84302 | 0.84302 | -4.4479 | -4.4479
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84302 | 0.84302 | -4.4479 | -4.4479
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84302 | 0.84302 | -4.4479 | -4.4479
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84302 | 0.84302 | -4.4479 | -4.4479
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84302 | 0.84302 | -4.4479 | -4.4479
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84302 | 0.84302 | -4.4479 | -4.4479
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84302 | 0.84302 | -4.4479 | -4.4479
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84302 | 0.84302 | -4.4479 | -4.4479
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84302 | 0.84302 | -4.4479 | -4.4479
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84302 | 0.84302 | -4.4479 | -4.4479
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84302 | 0.84302 | -4.4479 | -4.4479
Line4_2_6 | 2.1767 | 2.1767 | 0 | 0 | 1.508 | 1.508 | 0.42641 | -0.28427 | 0.85282 | -0.56854 | -67.8829 | 112.1171 | 0.63226 | 0.42151 | -4.4479 | -4.4479
Line5_6_7 | 2.1767 | 2.1767 | 0 | 0 | 1.508 | 1.508 | 0.28427 | -0.14214 | 0.56854 | -0.28427 | -67.8829 | 112.1171 | 0.42151 | 0.21075 | -4.4479 | -4.4479
Line6_7_8 | 2.1767 | 2.1767 | 0 | 4.0311 | 1.508 | 1.508 | 0.14214 | -1e-07 | 0.28427 | -1e-07 | -67.8829 | 112.1171 | 0.21075 | 0 | -4.4479 | 0
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 7.9247e-22 | 0 | 4.6423e-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 7.9247e-22 | 0 | 4.6423e-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84302 | 0.84302 | -4.4479 | -4.4479

## LLL_max_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 2.259 | 2.259 | 0 | 0 | 1.5651 | 1.5651 | 0.61237 | -0.45928 | 1.2247 | -0.91856 | -68.05 | 111.95 | 0.87491 | 0.65618 | -4.615 | -4.615
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87491 | 0.87491 | -4.615 | -4.615
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87491 | 0.87491 | -4.615 | -4.615
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87491 | 0.87491 | -4.615 | -4.615
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87491 | 0.87491 | -4.615 | -4.615
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87491 | 0.87491 | -4.615 | -4.615
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87491 | 0.87491 | -4.615 | -4.615
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87491 | 0.87491 | -4.615 | -4.615
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87491 | 0.87491 | -4.615 | -4.615
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87491 | 0.87491 | -4.615 | -4.615
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87491 | 0.87491 | -4.615 | -4.615
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87491 | 0.87491 | -4.615 | -4.615
Line4_2_6 | 2.259 | 2.259 | 0 | 0 | 1.5651 | 1.5651 | 0.45928 | -0.30619 | 0.91856 | -0.61237 | -68.05 | 111.95 | 0.65618 | 0.43745 | -4.615 | -4.615
Line5_6_7 | 2.259 | 2.259 | 0 | 0 | 1.5651 | 1.5651 | 0.30619 | -0.15309 | 0.61237 | -0.30619 | -68.05 | 111.95 | 0.43745 | 0.21873 | -4.615 | -4.615
Line6_7_8 | 2.259 | 2.259 | 0 | 4.1931 | 1.5651 | 1.5651 | 0.15309 | -1e-07 | 0.30619 | -1e-07 | -68.05 | 111.95 | 0.21873 | 0 | -4.615 | 0
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1123e-21 | 0 | -5.2195e-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1123e-21 | 0 | -5.2195e-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87491 | 0.87491 | -4.615 | -4.615

## LLL_max_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 0.033802 | 0.033802 | 0 | 0 | 0.023418 | 0.023418 | 0.017275 | -0.017241 | 0.017412 | -0.017344 | -45.346 | 134.654 | 1.0474 | 1.0443 | -0.11952 | -0.17563
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.11952 | -0.11952
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.11952 | -0.11952
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.11952 | -0.11952
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.11952 | -0.11952
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.11952 | -0.11952
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.11952 | -0.11952
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.11952 | -0.11952
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.11952 | -0.11952
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.11952 | -0.11952
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.11952 | -0.11952
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.11952 | -0.11952
Line4_2_6 | 0.033802 | 0.033802 | 0 | 0 | 0.023418 | 0.023418 | 0.017241 | -0.017207 | 0.017344 | -0.017275 | -45.346 | 134.654 | 1.0443 | 1.0412 | -0.17563 | -0.23207
Line5_6_7 | 0.033802 | 0.033802 | 0 | 0 | 0.023418 | 0.023418 | 0.017207 | -0.017173 | 0.017275 | -0.017207 | -45.346 | 134.654 | 1.0412 | 1.0381 | -0.23207 | -0.28886
Line6_7_8 | 0.033802 | 0.033802 | 0 | 0.0626 | 0.023418 | 0.023418 | 0.017173 | -0.017138 | 0.017207 | -0.017138 | -45.346 | 134.654 | 1.0381 | 1.035 | -0.28886 | -0.34598
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | -1.7102e-10 | 0 | 7.2182e-11 | 0 | 0 | 0 | 1.035 | 1.035 | -0.34598 | -0.34598
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | -1.7102e-10 | 0 | 7.2182e-11 | 0 | 0 | 0 | 1.035 | 1.035 | -0.34598 | -0.34598
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.11952 | -0.11952

## LLL_max_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 0.035407 | 0.035407 | 0 | 0 | 0.024531 | 0.024531 | 0.018955 | -0.018918 | 0.019106 | -0.019031 | -45.3516 | 134.6484 | 1.0971 | 1.0939 | -0.12515 | -0.18126
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12515 | -0.12515
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12515 | -0.12515
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12515 | -0.12515
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12515 | -0.12515
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12515 | -0.12515
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12515 | -0.12515
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12515 | -0.12515
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12515 | -0.12515
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12515 | -0.12515
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12515 | -0.12515
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12515 | -0.12515
Line4_2_6 | 0.035407 | 0.035407 | 0 | 0 | 0.024531 | 0.024531 | 0.018918 | -0.01888 | 0.019031 | -0.018955 | -45.3516 | 134.6484 | 1.0939 | 1.0906 | -0.18126 | -0.23771
Line5_6_7 | 0.035407 | 0.035407 | 0 | 0 | 0.024531 | 0.024531 | 0.01888 | -0.018842 | 0.018955 | -0.01888 | -45.3516 | 134.6484 | 1.0906 | 1.0874 | -0.23771 | -0.29449
Line6_7_8 | 0.035407 | 0.035407 | 0 | 0.065722 | 0.024531 | 0.024531 | 0.018842 | -0.018805 | 0.01888 | -0.018805 | -45.3516 | 134.6484 | 1.0874 | 1.0841 | -0.29449 | -0.35161
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | -1.8919e-10 | 0 | 8.0501e-11 | 0 | 0 | 0 | 1.0841 | 1.0841 | -0.35161 | -0.35161
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | -1.8919e-10 | 0 | 8.0501e-11 | 0 | 0 | 0 | 1.0841 | 1.0841 | -0.35161 | -0.35161
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12515 | -0.12515

## LLL_min_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 1.6801 | 1.6801 | 0 | 0 | 1.164 | 1.164 | 0.65034 | -0.48775 | 0.67743 | -0.50807 | -52.8727 | 127.1273 | 0.80677 | 0.60508 | -6.7036 | -6.7036
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80677 | 0.80677 | -6.7036 | -6.7036
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80677 | 0.80677 | -6.7036 | -6.7036
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80677 | 0.80677 | -6.7036 | -6.7036
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80677 | 0.80677 | -6.7036 | -6.7036
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80677 | 0.80677 | -6.7036 | -6.7036
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80677 | 0.80677 | -6.7036 | -6.7036
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80677 | 0.80677 | -6.7036 | -6.7036
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80677 | 0.80677 | -6.7036 | -6.7036
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80677 | 0.80677 | -6.7036 | -6.7036
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80677 | 0.80677 | -6.7036 | -6.7036
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80677 | 0.80677 | -6.7036 | -6.7036
Line4_2_6 | 1.6801 | 1.6801 | 0 | 0 | 1.164 | 1.164 | 0.48775 | -0.32517 | 0.50807 | -0.33872 | -52.8727 | 127.1273 | 0.60508 | 0.40338 | -6.7036 | -6.7036
Line5_6_7 | 1.6801 | 1.6801 | 0 | 0 | 1.164 | 1.164 | 0.32517 | -0.16258 | 0.33872 | -0.16936 | -52.8727 | 127.1273 | 0.40338 | 0.20169 | -6.7036 | -6.7036
Line6_7_8 | 1.6801 | 1.6801 | 0 | 2.6638 | 1.164 | 1.164 | 0.16258 | -1e-07 | 0.16936 | -1e-07 | -52.8727 | 127.1273 | 0.20169 | 0 | -6.7036 | 0
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7987e-22 | 0 | 9.0104e-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7987e-22 | 0 | 9.0104e-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80677 | 0.80677 | -6.7036 | -6.7036

## LLL_min_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 1.5916 | 1.5916 | 0 | 0 | 1.1027 | 1.1027 | 0.58368 | -0.43776 | 0.608 | -0.456 | -52.8727 | 127.1273 | 0.76431 | 0.57323 | -6.7036 | -6.7036
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76431 | 0.76431 | -6.7036 | -6.7036
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76431 | 0.76431 | -6.7036 | -6.7036
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76431 | 0.76431 | -6.7036 | -6.7036
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76431 | 0.76431 | -6.7036 | -6.7036
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76431 | 0.76431 | -6.7036 | -6.7036
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76431 | 0.76431 | -6.7036 | -6.7036
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76431 | 0.76431 | -6.7036 | -6.7036
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76431 | 0.76431 | -6.7036 | -6.7036
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76431 | 0.76431 | -6.7036 | -6.7036
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76431 | 0.76431 | -6.7036 | -6.7036
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76431 | 0.76431 | -6.7036 | -6.7036
Line4_2_6 | 1.5916 | 1.5916 | 0 | 0 | 1.1027 | 1.1027 | 0.43776 | -0.29184 | 0.456 | -0.304 | -52.8727 | 127.1273 | 0.57323 | 0.38215 | -6.7036 | -6.7036
Line5_6_7 | 1.5916 | 1.5916 | 0 | 0 | 1.1027 | 1.1027 | 0.29184 | -0.14592 | 0.304 | -0.152 | -52.8727 | 127.1273 | 0.38215 | 0.19108 | -6.7036 | -6.7036
Line6_7_8 | 1.5916 | 1.5916 | 0 | 2.5236 | 1.1027 | 1.1027 | 0.14592 | -1e-07 | 0.152 | -1e-07 | -52.8727 | 127.1273 | 0.19108 | 0 | -6.7036 | 0
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 6.1001e-22 | 0 | 8.0913e-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 6.1001e-22 | 0 | 8.0913e-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76431 | 0.76431 | -6.7036 | -6.7036

## LLL_min_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 0.030469 | 0.030469 | 0 | 0 | 0.02111 | 0.02111 | 0.01414 | -0.014086 | 0.014149 | -0.014093 | -45.1423 | 134.8577 | 0.94756 | 0.9439 | -0.12428 | -0.12874
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94756 | 0.94756 | -0.12428 | -0.12428
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94756 | 0.94756 | -0.12428 | -0.12428
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94756 | 0.94756 | -0.12428 | -0.12428
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94756 | 0.94756 | -0.12428 | -0.12428
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94756 | 0.94756 | -0.12428 | -0.12428
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94756 | 0.94756 | -0.12428 | -0.12428
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94756 | 0.94756 | -0.12428 | -0.12428
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94756 | 0.94756 | -0.12428 | -0.12428
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94756 | 0.94756 | -0.12428 | -0.12428
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94756 | 0.94756 | -0.12428 | -0.12428
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94756 | 0.94756 | -0.12428 | -0.12428
Line4_2_6 | 0.030469 | 0.030469 | 0 | 0 | 0.02111 | 0.02111 | 0.014086 | -0.014033 | 0.014093 | -0.014037 | -45.1423 | 134.8577 | 0.9439 | 0.94024 | -0.12874 | -0.13323
Line5_6_7 | 0.030469 | 0.030469 | 0 | 0 | 0.02111 | 0.02111 | 0.014033 | -0.013979 | 0.014037 | -0.013981 | -45.1423 | 134.8577 | 0.94024 | 0.93659 | -0.13323 | -0.13776
Line6_7_8 | 0.030469 | 0.030469 | 0 | 0.04831 | 0.02111 | 0.02111 | 0.013979 | -0.013926 | 0.013981 | -0.013926 | -45.1423 | 134.8577 | 0.93659 | 0.93293 | -0.13776 | -0.14233
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | -1.7514e-10 | 0 | 2.4218e-11 | 0 | 0 | 0 | 0.93293 | 0.93293 | -0.14233 | -0.14233
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | -1.7514e-10 | 0 | 2.4218e-11 | 0 | 0 | 0 | 0.93293 | 0.93293 | -0.14233 | -0.14233
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94756 | 0.94756 | -0.12428 | -0.12428

## LLL_min_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 0.028866 | 0.028866 | 0 | 0 | 0.019999 | 0.019999 | 0.01269 | -0.012642 | 0.012698 | -0.012648 | -45.1423 | 134.8577 | 0.89769 | 0.89422 | -0.12428 | -0.12874
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89769 | 0.89769 | -0.12428 | -0.12428
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89769 | 0.89769 | -0.12428 | -0.12428
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89769 | 0.89769 | -0.12428 | -0.12428
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89769 | 0.89769 | -0.12428 | -0.12428
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89769 | 0.89769 | -0.12428 | -0.12428
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89769 | 0.89769 | -0.12428 | -0.12428
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89769 | 0.89769 | -0.12428 | -0.12428
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89769 | 0.89769 | -0.12428 | -0.12428
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89769 | 0.89769 | -0.12428 | -0.12428
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89769 | 0.89769 | -0.12428 | -0.12428
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89769 | 0.89769 | -0.12428 | -0.12428
Line4_2_6 | 0.028866 | 0.028866 | 0 | 0 | 0.019999 | 0.019999 | 0.012642 | -0.012594 | 0.012648 | -0.012598 | -45.1423 | 134.8577 | 0.89422 | 0.89076 | -0.12874 | -0.13323
Line5_6_7 | 0.028866 | 0.028866 | 0 | 0 | 0.019999 | 0.019999 | 0.012594 | -0.012546 | 0.012598 | -0.012548 | -45.1423 | 134.8577 | 0.89076 | 0.88729 | -0.13323 | -0.13776
Line6_7_8 | 0.028866 | 0.028866 | 0 | 0.045767 | 0.019999 | 0.019999 | 0.012546 | -0.012498 | 0.012548 | -0.012498 | -45.1423 | 134.8577 | 0.88729 | 0.88383 | -0.13776 | -0.14233
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | -1.5719e-10 | 0 | 2.1736e-11 | 0 | 0 | 0 | 0.88383 | 0.88383 | -0.14233 | -0.14233
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | -1.5719e-10 | 0 | 2.1736e-11 | 0 | 0 | 0 | 0.88383 | 0.88383 | -0.14233 | -0.14233
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89769 | 0.89769 | -0.12428 | -0.12428

## LL_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 1.885 | 1.885 | 0 | 1.885 | 1.885 | 0 | 0.43533 | 0.43533 | 0 | 0.43533 | 0.43533 | 5.8287e-16 | 0.35387 | -0.069596 | -6.2172e-16 | -0.31833 | 0.10513 | 1.5543e-16 | 0.19822 | 0.37032 | -1.5543e-16 | -0.12715 | -0.29925 | 0 | -157.8829 | 22.1171 | 0 | 22.1171 | -157.8829 | 1.05 | 0.93171 | 0.86555 | 1.05 | 0.78742 | 0.7286 | 6.8953e-13 | -128.6271 | 122.7608 | 6.7745e-13 | -136.1092 | 131.4739
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.6629e-16 | -2.1811e-09 | -3.489e-09 | -4.4686e-16 | 2.1811e-09 | 3.489e-09 | 2.3315e-16 | 3.2284e-09 | -9.6307e-10 | -2.3315e-16 | -3.2284e-09 | 9.6307e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.93171 | 0.86555 | 1.05 | 0.93171 | 0.86555 | 6.7576e-13 | -128.6271 | 122.7608 | 6.7049e-13 | -128.6271 | 122.7608
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0801e-16 | -1.8176e-09 | -2.9075e-09 | -4.2744e-16 | 1.8176e-09 | 2.9075e-09 | 2.3315e-16 | 2.6904e-09 | -8.0256e-10 | -2.1372e-16 | -2.6904e-09 | 8.0256e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.93171 | 0.86555 | 1.05 | 0.93171 | 0.86555 | 6.7049e-13 | -128.6271 | 122.7608 | 6.653e-13 | -128.6271 | 122.7608
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1372e-16 | -1.0906e-09 | -1.7445e-09 | -1.7486e-16 | 1.0906e-09 | 1.7445e-09 | 2.4816e-30 | 1.6142e-09 | -4.8153e-10 | -1.9429e-17 | -1.6142e-09 | 4.8153e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.93171 | 0.86555 | 1.05 | 0.93171 | 0.86555 | 6.653e-13 | -128.6271 | 122.7608 | 6.6317e-13 | -128.6271 | 122.7608
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7486e-16 | -3.6352e-10 | -5.8151e-10 | -1.36e-16 | 3.6352e-10 | 5.8151e-10 | 2.1372e-16 | 5.3807e-10 | -1.6051e-10 | -2.3315e-16 | -5.3807e-10 | 1.6051e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.93171 | 0.86555 | 1.05 | 0.93171 | 0.86555 | 6.653e-13 | -128.6271 | 122.7608 | 6.6465e-13 | -128.6271 | 122.7608
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1657e-16 | -7.2704e-10 | -1.163e-09 | -1.36e-16 | 7.2704e-10 | 1.163e-09 | 1.3493e-30 | 1.0761e-09 | -3.2102e-10 | -1.5716e-30 | -1.0761e-09 | 3.2102e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.93171 | 0.86555 | 1.05 | 0.93171 | 0.86555 | 6.6317e-13 | -128.6271 | 122.7608 | 6.6211e-13 | -128.6271 | 122.7608
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.8858e-17 | -3.6352e-10 | -5.8151e-10 | 3.8858e-17 | 3.6352e-10 | 5.8151e-10 | 1.9429e-17 | 5.3807e-10 | -1.6051e-10 | 4.488e-31 | -5.3807e-10 | 1.6051e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.93171 | 0.86555 | 1.05 | 0.93171 | 0.86555 | 6.6211e-13 | -128.6271 | 122.7608 | 6.6176e-13 | -128.6271 | 122.7608
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.331e-31 | -3.6352e-10 | -5.8151e-10 | 0 | 3.6352e-10 | 5.8151e-10 | -1.9429e-17 | 5.3807e-10 | -1.6051e-10 | 0 | -5.3807e-10 | 1.6051e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.93171 | 0.86555 | 1.05 | 0.93171 | 0.86555 | 6.8741e-13 | -128.6271 | 122.7608 | 6.8706e-13 | -128.6271 | 122.7608
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.8287e-17 | -3.6352e-10 | -5.8151e-10 | -5.8287e-17 | 3.6352e-10 | 5.8151e-10 | 2.9143e-16 | 5.3807e-10 | -1.6051e-10 | -2.72e-16 | -5.3807e-10 | 1.6051e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.93171 | 0.86555 | 1.05 | 0.93171 | 0.86555 | 6.8665e-13 | -128.6271 | 122.7608 | 6.8749e-13 | -128.6271 | 122.7608
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.2172e-16 | -2.9082e-09 | -4.6521e-09 | -6.023e-16 | 2.9082e-09 | 4.6521e-09 | 2.3315e-16 | 4.3046e-09 | -1.2841e-09 | -2.3315e-16 | -4.3046e-09 | 1.2841e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.93171 | 0.86555 | 1.05 | 0.93171 | 0.86555 | 6.8953e-13 | -128.6271 | 122.7608 | 6.8179e-13 | -128.6271 | 122.7608
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3315e-16 | -7.2704e-10 | -1.163e-09 | -1.7486e-16 | 7.2704e-10 | 1.163e-09 | 2.1372e-16 | 1.0761e-09 | -3.2102e-10 | -2.1372e-16 | -1.0761e-09 | 3.2102e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.93171 | 0.86555 | 1.05 | 0.93171 | 0.86555 | 6.8953e-13 | -128.6271 | 122.7608 | 6.8741e-13 | -128.6271 | 122.7608
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3315e-16 | -7.2704e-10 | -1.163e-09 | -1.9429e-16 | 7.2704e-10 | 1.163e-09 | 2.1372e-16 | 1.0761e-09 | -3.2102e-10 | -2.1372e-16 | -1.0761e-09 | 3.2102e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.93171 | 0.86555 | 1.05 | 0.93171 | 0.86555 | 6.8953e-13 | -128.6271 | 122.7608 | 6.8665e-13 | -128.6271 | 122.7608
Line4_2_6 | 0 | 1.885 | 1.885 | 0 | 1.885 | 1.885 | 0 | 0.43533 | 0.43533 | 0 | 0.43533 | 0.43533 | 4.6629e-16 | 0.31833 | -0.10513 | -4.6629e-16 | -0.2828 | 0.14066 | 2.3315e-16 | 0.12715 | 0.29925 | -2.3315e-16 | -0.056087 | -0.22819 | 0 | -157.8829 | 22.1171 | 0 | 22.1171 | -157.8829 | 1.05 | 0.78742 | 0.7286 | 1.05 | 0.66227 | 0.61575 | 6.7745e-13 | -136.1092 | 131.4739 | 6.6553e-13 | -146.6652 | 143.7688
Line5_6_7 | 0 | 1.885 | 1.885 | 0 | 1.885 | 1.885 | 0 | 0.43533 | 0.43533 | 0 | 0.43533 | 0.43533 | 5.4401e-16 | 0.2828 | -0.14066 | -5.4401e-16 | -0.24727 | 0.1762 | 7.7716e-17 | 0.056087 | 0.22819 | -1.1657e-16 | 0.014981 | -0.15712 | 0 | -157.8829 | 22.1171 | 0 | 22.1171 | -157.8829 | 1.05 | 0.66227 | 0.61575 | 1.05 | 0.56903 | 0.54229 | 6.6553e-13 | -146.6652 | 143.7688 | 6.5539e-13 | -161.35 | 160.3935
Line6_7_8 | 0 | 1.885 | 1.885 | 0 | 1.885 | 1.885 | 0 | 0.43533 | 0.43533 | 0 | 0.43533 | 0.43533 | 3.8858e-16 | 0.24727 | -0.1762 | -3.1086e-16 | -0.21173 | 0.21173 | -7.7716e-17 | -0.014981 | 0.15712 | 7.7716e-17 | 0.086049 | -0.086049 | 0 | -157.8829 | 22.1171 | 0 | 22.1171 | -157.8829 | 1.05 | 0.56903 | 0.54229 | 1.05 | 0.525 | 0.525 | 6.5539e-13 | -161.35 | 160.3935 | 6.5123e-13 | 180 | -180
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.7716e-17 | 4.6629e-16 | 4.442e-24 | 1.5543e-16 | -1.5335e-16 | -4.6421e-16 | -3.8858e-17 | 1.7505e-09 | -1.7505e-09 | 3.8858e-17 | -1.7505e-09 | 1.7505e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.525 | 0.525 | 1.05 | 0.525 | 0.525 | 6.5123e-13 | 180 | -180 | 6.4803e-13 | -180 | 180
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.3315e-16 | 4.6629e-16 | 4.442e-24 | 3.1086e-16 | -1.5335e-16 | -4.6421e-16 | 3.8858e-17 | 1.7505e-09 | -1.7505e-09 | 3.5257e-30 | -1.7505e-09 | 1.7505e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.525 | 0.525 | 1.05 | 0.525 | 0.525 | 6.5123e-13 | 180 | -180 | 6.4984e-13 | -180 | 180
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2458e-16 | -2.5447e-09 | -4.0705e-09 | -5.2458e-16 | 2.5447e-09 | 4.0705e-09 | 2.72e-16 | 3.7665e-09 | -1.1236e-09 | -2.72e-16 | -3.7665e-09 | 1.1236e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.93171 | 0.86555 | 1.05 | 0.93171 | 0.86555 | 6.8179e-13 | -128.6271 | 122.7608 | 6.7576e-13 | -128.6271 | 122.7608

## LL_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 1.9564 | 1.9564 | 0 | 1.9564 | 1.9564 | 0 | 0.4518 | 0.4518 | 0 | 0.4518 | 0.4518 | 6.5133e-16 | 0.38357 | -0.077384 | -6.5133e-16 | -0.3453 | 0.11566 | -8.1416e-17 | 0.2133 | 0.39907 | 8.1416e-17 | -0.13675 | -0.32252 | 0 | -158.05 | 21.95 | 0 | 21.95 | -158.05 | 1.1 | 0.97142 | 0.89974 | 1.1 | 0.82203 | 0.75838 | -5.6469e-14 | -128.9719 | 122.9242 | -6.4188e-14 | -136.444 | 131.678
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6637e-16 | -2.4603e-09 | -3.9356e-09 | -3.2567e-16 | 2.4603e-09 | 3.9356e-09 | 3.2567e-16 | 3.6661e-09 | -1.1108e-09 | -3.0531e-16 | -3.6661e-09 | 1.1108e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.97142 | 0.89974 | 1.1 | 0.97142 | 0.89974 | -6.6956e-14 | -128.9719 | 122.9242 | -7.0761e-14 | -128.9719 | 122.9242
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6637e-16 | -2.0502e-09 | -3.2797e-09 | -3.6637e-16 | 2.0502e-09 | 3.2797e-09 | 2.646e-16 | 3.0551e-09 | -9.2564e-10 | -2.2389e-16 | -3.0551e-09 | 9.2564e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.97142 | 0.89974 | 1.1 | 0.97142 | 0.89974 | -7.0761e-14 | -128.9719 | 122.9242 | -7.4487e-14 | -128.9719 | 122.9242
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8319e-16 | -1.2301e-09 | -1.9678e-09 | -1.6283e-16 | 1.2301e-09 | 1.9678e-09 | 4.0708e-17 | 1.8331e-09 | -5.5539e-10 | 2.1794e-31 | -1.8331e-09 | 5.5539e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.97142 | 0.89974 | 1.1 | 0.97142 | 0.89974 | -7.4487e-14 | -128.9719 | 122.9242 | -7.6688e-14 | -128.9719 | 122.9242
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0354e-17 | -4.1005e-10 | -6.5593e-10 | -3.673e-31 | 4.1005e-10 | 6.5593e-10 | 3.0531e-16 | 6.1102e-10 | -1.8513e-10 | -2.8496e-16 | -6.1102e-10 | 1.8513e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.97142 | 0.89974 | 1.1 | 0.97142 | 0.89974 | -7.4487e-14 | -128.9719 | 122.9242 | -7.3852e-14 | -128.9719 | 122.9242
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.1062e-17 | -8.2009e-10 | -1.3119e-09 | -8.1416e-17 | 8.2009e-10 | 1.3119e-09 | 2.0354e-17 | 1.222e-09 | -3.7026e-10 | -2.0354e-17 | -1.222e-09 | 3.7026e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.97142 | 0.89974 | 1.1 | 0.97142 | 0.89974 | -7.6688e-14 | -128.9719 | 122.9242 | -7.7793e-14 | -128.9719 | 122.9242
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.7636e-32 | -4.1005e-10 | -6.5593e-10 | 2.0354e-17 | 4.1005e-10 | 6.5593e-10 | -2.0354e-17 | 6.1102e-10 | -1.8513e-10 | 2.0354e-17 | -6.1102e-10 | 1.8513e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.97142 | 0.89974 | 1.1 | 0.97142 | 0.89974 | -7.7793e-14 | -128.9719 | 122.9242 | -7.8155e-14 | -128.9719 | 122.9242
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.0708e-17 | -4.1005e-10 | -6.5593e-10 | 2.0354e-17 | 4.1005e-10 | 6.5593e-10 | -2.0354e-17 | 6.1102e-10 | -1.8513e-10 | 2.0354e-17 | -6.1102e-10 | 1.8513e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.97142 | 0.89974 | 1.1 | 0.97142 | 0.89974 | -5.6933e-14 | -128.9719 | 122.9242 | -5.7295e-14 | -128.9719 | 122.9242
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.1062e-17 | -4.1005e-10 | -6.5593e-10 | 4.0708e-17 | 4.1005e-10 | 6.5593e-10 | 3.0531e-16 | 6.1102e-10 | -1.8513e-10 | -2.8496e-16 | -6.1102e-10 | 1.8513e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.97142 | 0.89974 | 1.1 | 0.97142 | 0.89974 | -5.7347e-14 | -128.9719 | 122.9242 | -5.6419e-14 | -128.9719 | 122.9242
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2921e-16 | -3.2804e-09 | -5.2475e-09 | -5.2921e-16 | 3.2804e-09 | 5.2475e-09 | 2.646e-16 | 4.8882e-09 | -1.481e-09 | -2.646e-16 | -4.8882e-09 | 1.481e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.97142 | 0.89974 | 1.1 | 0.97142 | 0.89974 | -5.6469e-14 | -128.9719 | 122.9242 | -6.2361e-14 | -128.9719 | 122.9242
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0708e-17 | -8.2009e-10 | -1.3119e-09 | -2.0354e-17 | 8.2009e-10 | 1.3119e-09 | 2.646e-16 | 1.222e-09 | -3.7026e-10 | -2.646e-16 | -1.222e-09 | 3.7026e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.97142 | 0.89974 | 1.1 | 0.97142 | 0.89974 | -5.6469e-14 | -128.9719 | 122.9242 | -5.6933e-14 | -128.9719 | 122.9242
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.1062e-17 | -8.2009e-10 | -1.3119e-09 | -4.0708e-17 | 8.2009e-10 | 1.3119e-09 | 2.646e-16 | 1.222e-09 | -3.7026e-10 | -2.646e-16 | -1.222e-09 | 3.7026e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.97142 | 0.89974 | 1.1 | 0.97142 | 0.89974 | -5.6469e-14 | -128.9719 | 122.9242 | -5.7347e-14 | -128.9719 | 122.9242
Line4_2_6 | 0 | 1.9564 | 1.9564 | 0 | 1.9564 | 1.9564 | 0 | 0.4518 | 0.4518 | 0 | 0.4518 | 0.4518 | 4.885e-16 | 0.3453 | -0.11566 | -5.6991e-16 | -0.30702 | 0.15393 | -8.1416e-17 | 0.13675 | 0.32252 | 4.0708e-17 | -0.060208 | -0.24598 | 0 | -158.05 | 21.95 | 0 | 21.95 | -158.05 | 1.1 | 0.82203 | 0.75838 | 1.1 | 0.6925 | 0.64226 | -6.4188e-14 | -136.444 | 131.678 | -7.2829e-14 | -146.955 | 143.988
Line5_6_7 | 0 | 1.9564 | 1.9564 | 0 | 1.9564 | 1.9564 | 0 | 0.4518 | 0.4518 | 0 | 0.4518 | 0.4518 | 3.2567e-16 | 0.30702 | -0.15393 | -3.2567e-16 | -0.26875 | 0.1922 | -4.0708e-17 | 0.060208 | 0.24598 | 4.0708e-17 | 0.016339 | -0.16943 | 0 | -158.05 | 21.95 | 0 | 21.95 | -158.05 | 1.1 | 0.6925 | 0.64226 | 1.1 | 0.59594 | 0.56711 | -7.2829e-14 | -146.955 | 143.988 | -7.665e-14 | -161.529 | 160.5532
Line6_7_8 | 0 | 1.9564 | 1.9564 | 0 | 1.9564 | 1.9564 | 0 | 0.4518 | 0.4518 | 0 | 0.4518 | 0.4518 | 8.1416e-16 | 0.26875 | -0.1922 | -6.5133e-16 | -0.23048 | 0.23048 | -4.0708e-16 | -0.016339 | 0.16943 | 4.0708e-16 | 0.092885 | -0.092885 | 0 | -158.05 | 21.95 | 0 | 21.95 | -158.05 | 1.1 | 0.59594 | 0.56711 | 1.1 | 0.55 | 0.55 | -7.665e-14 | -161.529 | 160.5532 | -8.3164e-14 | 180 | -180
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.6283e-16 | 2.4425e-16 | -3.2567e-16 | 1.6283e-16 | -3.2338e-16 | 2.2876e-18 | -8.1416e-17 | 1.9211e-09 | -1.9211e-09 | -2.4543e-31 | -1.9211e-09 | 1.9211e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.55 | 0.55 | 1.1 | 0.55 | 0.55 | -8.3164e-14 | 180 | -180 | -8.6361e-14 | -180 | 180
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.2567e-16 | 8.1416e-17 | 3.2567e-16 | 3.2567e-16 | -1.6055e-16 | -3.2338e-16 | 8.1416e-17 | 1.9211e-09 | -1.9211e-09 | -8.1416e-17 | -1.9211e-09 | 1.9211e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.55 | 0.55 | 1.1 | 0.55 | 0.55 | -8.3164e-14 | 180 | -180 | -8.6528e-14 | -180 | 180
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0708e-16 | -2.8703e-09 | -4.5915e-09 | -3.8673e-16 | 2.8703e-09 | 4.5915e-09 | 2.8496e-16 | 4.2771e-09 | -1.2959e-09 | -2.8496e-16 | -4.2771e-09 | 1.2959e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.97142 | 0.89974 | 1.1 | 0.97142 | 0.89974 | -6.2361e-14 | -128.9719 | 122.9242 | -6.6956e-14 | -128.9719 | 122.9242

## LL_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0.057717 | 0.057717 | 0 | 0.057717 | 0.057717 | 0 | 0.013329 | 0.013329 | 0 | 0.013329 | 0.013329 | 2.4286e-17 | 0.013468 | 0.0034547 | -2.4286e-17 | -0.013435 | -0.0034214 | 1.0929e-17 | 0.0037057 | 0.013484 | -1.0929e-17 | -0.0036391 | -0.013417 | 0 | -135.6822 | 44.3178 | 0 | 44.3178 | -135.6822 | 1.05 | 1.048 | 1.0443 | 1.05 | 1.0443 | 1.0388 | 2.6564e-14 | -120.2981 | 119.9471 | 2.619e-14 | -120.5262 | 120.0122
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3054e-17 | -4.627e-11 | -1.3184e-10 | -1.3661e-17 | 4.627e-11 | 1.3184e-10 | 4.2501e-18 | 1.2595e-10 | 2.226e-11 | -4.8572e-18 | -1.2595e-10 | -2.226e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0443 | 1.05 | 1.048 | 1.0443 | 2.6156e-14 | -120.2981 | 119.9471 | 2.5994e-14 | -120.2981 | 119.9471
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3054e-17 | -3.8558e-11 | -1.0987e-10 | -1.3054e-17 | 3.8558e-11 | 1.0987e-10 | 3.6429e-18 | 1.0496e-10 | 1.855e-11 | -3.6429e-18 | -1.0496e-10 | -1.855e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0443 | 1.05 | 1.048 | 1.0443 | 2.5994e-14 | -120.2981 | 119.9471 | 2.5824e-14 | -120.2981 | 119.9471
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0358e-18 | -2.3135e-11 | -6.592e-11 | -2.4286e-18 | 2.3135e-11 | 6.592e-11 | 1.8215e-18 | 6.2976e-11 | 1.113e-11 | -1.8215e-18 | -6.2976e-11 | -1.113e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0443 | 1.05 | 1.048 | 1.0443 | 2.5824e-14 | -120.2981 | 119.9471 | 2.5765e-14 | -120.2981 | 119.9471
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4644e-18 | -7.7116e-12 | -2.1973e-11 | -4.8572e-18 | 7.7116e-12 | 2.1973e-11 | 3.0358e-18 | 2.0992e-11 | 3.71e-12 | -3.6429e-18 | -2.0992e-11 | -3.71e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0443 | 1.05 | 1.048 | 1.0443 | 2.5824e-14 | -120.2981 | 119.9471 | 2.5768e-14 | -120.2981 | 119.9471
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9465e-18 | -1.5423e-11 | -4.3946e-11 | -3.3393e-18 | 1.5423e-11 | 4.3946e-11 | 6.0715e-19 | 4.1984e-11 | 7.42e-12 | -1.8215e-18 | -4.1984e-11 | -7.42e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0443 | 1.05 | 1.048 | 1.0443 | 2.5765e-14 | -120.2981 | 119.9471 | 2.5736e-14 | -120.2981 | 119.9471
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.0715e-19 | -7.7116e-12 | -2.1973e-11 | 6.0715e-19 | 7.7116e-12 | 2.1973e-11 | -2.7272e-34 | 2.0992e-11 | 3.71e-12 | 2.7252e-34 | -2.0992e-11 | -3.71e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0443 | 1.05 | 1.048 | 1.0443 | 2.5736e-14 | -120.2981 | 119.9471 | 2.5717e-14 | -120.2981 | 119.9471
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.8056e-34 | -7.7116e-12 | -2.1973e-11 | 2.8036e-34 | 7.7116e-12 | 2.1973e-11 | 6.0715e-19 | 2.0992e-11 | 3.71e-12 | -6.0715e-19 | -2.0992e-11 | -3.71e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0443 | 1.05 | 1.048 | 1.0443 | 2.6476e-14 | -120.2981 | 119.9471 | 2.6457e-14 | -120.2981 | 119.9471
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5536e-18 | -7.7116e-12 | -2.1973e-11 | -4.5536e-18 | 7.7116e-12 | 2.1973e-11 | 4.2501e-18 | 2.0992e-11 | 3.71e-12 | -4.2501e-18 | -2.0992e-11 | -3.71e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0443 | 1.05 | 1.048 | 1.0443 | 2.6455e-14 | -120.2981 | 119.9471 | 2.6418e-14 | -120.2981 | 119.9471
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8518e-17 | -6.1693e-11 | -1.7579e-10 | -1.8518e-17 | 6.1693e-11 | 1.7579e-10 | 7.893e-18 | 1.6794e-10 | 2.968e-11 | -7.2858e-18 | -1.6794e-10 | -2.968e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0443 | 1.05 | 1.048 | 1.0443 | 2.6564e-14 | -120.2981 | 119.9471 | 2.6339e-14 | -120.2981 | 119.9471
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.5894e-18 | -1.5423e-11 | -4.3946e-11 | -7.5894e-18 | 1.5423e-11 | 4.3946e-11 | 4.8572e-18 | 4.1984e-11 | 7.42e-12 | -4.8572e-18 | -4.1984e-11 | -7.42e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0443 | 1.05 | 1.048 | 1.0443 | 2.6564e-14 | -120.2981 | 119.9471 | 2.6476e-14 | -120.2981 | 119.9471
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.893e-18 | -1.5423e-11 | -4.3946e-11 | -7.893e-18 | 1.5423e-11 | 4.3946e-11 | 5.4644e-18 | 4.1984e-11 | 7.42e-12 | -5.4644e-18 | -4.1984e-11 | -7.42e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0443 | 1.05 | 1.048 | 1.0443 | 2.6564e-14 | -120.2981 | 119.9471 | 2.6455e-14 | -120.2981 | 119.9471
Line4_2_6 | 0 | 0.057717 | 0.057717 | 0 | 0.057717 | 0.057717 | 0 | 0.013329 | 0.013329 | 0 | 0.013329 | 0.013329 | 1.7e-17 | 0.013435 | 0.0034214 | -1.8215e-17 | -0.013402 | -0.003388 | 9.7145e-18 | 0.0036391 | 0.013417 | -9.7145e-18 | -0.0035725 | -0.01335 | 0 | -135.6822 | 44.3178 | 0 | 44.3178 | -135.6822 | 1.05 | 1.0443 | 1.0388 | 1.05 | 1.0405 | 1.0333 | 2.619e-14 | -120.5262 | 120.0122 | 2.5862e-14 | -120.7558 | 120.078
Line5_6_7 | 0 | 0.057717 | 0.057717 | 0 | 0.057717 | 0.057717 | 0 | 0.013329 | 0.013329 | 0 | 0.013329 | 0.013329 | 1.2143e-17 | 0.013402 | 0.003388 | -1.2143e-17 | -0.013368 | -0.0033547 | 9.7145e-18 | 0.0035725 | 0.01335 | -7.2858e-18 | -0.0035059 | -0.013284 | 0 | -135.6822 | 44.3178 | 0 | 44.3178 | -135.6822 | 1.05 | 1.0405 | 1.0333 | 1.05 | 1.0368 | 1.0279 | 2.5862e-14 | -120.7558 | 120.078 | 2.5561e-14 | -120.9872 | 120.1445
Line6_7_8 | 0 | 0.057717 | 0.057717 | 0 | 0.057717 | 0.057717 | 0 | 0.013329 | 0.013329 | 0 | 0.013329 | 0.013329 | 9.7145e-18 | 0.013368 | 0.0033547 | -4.8572e-18 | -0.013335 | -0.0033214 | 4.3339e-33 | 0.0035059 | 0.013284 | -2.1568e-33 | -0.0034392 | -0.013217 | 0 | -135.6822 | 44.3178 | 0 | 44.3178 | -135.6822 | 1.05 | 1.0368 | 1.0279 | 1.05 | 1.0332 | 1.0224 | 2.5561e-14 | -120.9872 | 120.1445 | 2.5441e-14 | -121.2201 | 120.2117
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.8572e-18 | -6.2856e-11 | -1.0336e-10 | 7.2858e-18 | 6.2856e-11 | 1.0336e-10 | 2.4286e-18 | 8.4699e-11 | -1.4546e-11 | -4.8572e-18 | -8.4699e-11 | 1.4546e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.0332 | 1.0224 | 1.05 | 1.0332 | 1.0224 | 2.5441e-14 | -121.2201 | 120.2117 | 2.5355e-14 | -121.2201 | 120.2117
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.4286e-18 | -6.2856e-11 | -1.0336e-10 | 4.8572e-18 | 6.2856e-11 | 1.0336e-10 | 2.4286e-18 | 8.4699e-11 | -1.4546e-11 | -4.8572e-18 | -8.4699e-11 | 1.4546e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.0332 | 1.0224 | 1.05 | 1.0332 | 1.0224 | 2.5441e-14 | -121.2201 | 120.2117 | 2.5408e-14 | -121.2201 | 120.2117
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4572e-17 | -5.3981e-11 | -1.5381e-10 | -1.5179e-17 | 5.3981e-11 | 1.5381e-10 | 6.0715e-18 | 1.4694e-10 | 2.597e-11 | -5.4644e-18 | -1.4694e-10 | -2.597e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0443 | 1.05 | 1.048 | 1.0443 | 2.6339e-14 | -120.2981 | 119.9471 | 2.6156e-14 | -120.2981 | 119.9471

## LL_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0.060452 | 0.060452 | 0 | 0.060452 | 0.060452 | 0 | 0.013961 | 0.013961 | 0 | 0.013961 | 0.013961 | 2.417e-17 | 0.014777 | 0.0037874 | -2.417e-17 | -0.01474 | -0.0037509 | 5.0885e-18 | 0.004065 | 0.014792 | -5.0885e-18 | -0.0039919 | -0.014719 | 0 | -135.6932 | 44.3068 | 0 | 44.3068 | -135.6932 | 1.1 | 1.0978 | 1.0937 | 1.1 | 1.0939 | 1.088 | 1.0759e-14 | -120.3121 | 119.9447 | 1.0454e-14 | -120.5402 | 120.0098
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.859e-18 | -5.3155e-11 | -1.5146e-10 | -9.859e-18 | 5.3155e-11 | 1.5146e-10 | 6.3607e-18 | 1.4472e-10 | 2.555e-11 | -6.9967e-18 | -1.4472e-10 | -2.555e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0937 | 1.1 | 1.0978 | 1.0937 | 1.0424e-14 | -120.3121 | 119.9447 | 1.0293e-14 | -120.3121 | 119.9447
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0813e-17 | -4.4296e-11 | -1.2622e-10 | -1.0177e-17 | 4.4296e-11 | 1.2622e-10 | 6.9967e-18 | 1.206e-10 | 2.1292e-11 | -6.9967e-18 | -1.206e-10 | -2.1292e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0937 | 1.1 | 1.0978 | 1.0937 | 1.0293e-14 | -120.3121 | 119.9447 | 1.0154e-14 | -120.3121 | 119.9447
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.7246e-18 | -2.6578e-11 | -7.5731e-11 | -4.4525e-18 | 2.6578e-11 | 7.5731e-11 | 1.2721e-18 | 7.2361e-11 | 1.2775e-11 | -2.5443e-18 | -7.2361e-11 | -1.2775e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0937 | 1.1 | 1.0978 | 1.0937 | 1.0154e-14 | -120.3121 | 119.9447 | 1.0091e-14 | -120.3121 | 119.9447
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4525e-18 | -8.8592e-12 | -2.5244e-11 | -3.8164e-18 | 8.8592e-12 | 2.5244e-11 | 4.4525e-18 | 2.412e-11 | 4.2584e-12 | -5.7246e-18 | -2.412e-11 | -4.2584e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0937 | 1.1 | 1.0978 | 1.0937 | 1.0154e-14 | -120.3121 | 119.9447 | 1.0118e-14 | -120.3121 | 119.9447
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2262e-18 | -1.7718e-11 | -5.0487e-11 | -2.2262e-18 | 1.7718e-11 | 5.0487e-11 | 1.2721e-18 | 4.824e-11 | 8.5168e-12 | -1.2721e-18 | -4.824e-11 | -8.5168e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0937 | 1.1 | 1.0978 | 1.0937 | 1.0091e-14 | -120.3121 | 119.9447 | 1.0061e-14 | -120.3121 | 119.9447
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.541e-19 | -8.8592e-12 | -2.5244e-11 | -9.541e-19 | 8.8592e-12 | 2.5244e-11 | -1.2721e-18 | 2.412e-11 | 4.2584e-12 | 1.9082e-18 | -2.412e-11 | -4.2584e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0937 | 1.1 | 1.0978 | 1.0937 | 1.0061e-14 | -120.3121 | 119.9447 | 1.0042e-14 | -120.3121 | 119.9447
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.3607e-19 | -8.8592e-12 | -2.5244e-11 | 0 | 8.8592e-12 | 2.5244e-11 | -1.1895e-34 | 2.412e-11 | 4.2584e-12 | 0 | -2.412e-11 | -4.2584e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0937 | 1.1 | 1.0978 | 1.0937 | 1.0715e-14 | -120.3121 | 119.9447 | 1.0695e-14 | -120.3121 | 119.9447
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.3607e-19 | -8.8592e-12 | -2.5244e-11 | -1.2721e-18 | 8.8592e-12 | 2.5244e-11 | 5.7246e-18 | 2.412e-11 | 4.2584e-12 | -5.7246e-18 | -2.412e-11 | -4.2584e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0937 | 1.1 | 1.0978 | 1.0937 | 1.07e-14 | -120.3121 | 119.9447 | 1.071e-14 | -120.3121 | 119.9447
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5584e-17 | -7.0874e-11 | -2.0195e-10 | -1.4948e-17 | 7.0874e-11 | 2.0195e-10 | 8.2688e-18 | 1.9296e-10 | 3.4067e-11 | -7.6328e-18 | -1.9296e-10 | -3.4067e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0937 | 1.1 | 1.0978 | 1.0937 | 1.0759e-14 | -120.3121 | 119.9447 | 1.0576e-14 | -120.3121 | 119.9447
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9082e-18 | -1.7718e-11 | -5.0487e-11 | -1.9082e-18 | 1.7718e-11 | 5.0487e-11 | 5.0885e-18 | 4.8241e-11 | 8.5168e-12 | -4.4525e-18 | -4.8241e-11 | -8.5168e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0937 | 1.1 | 1.0978 | 1.0937 | 1.0759e-14 | -120.3121 | 119.9447 | 1.0715e-14 | -120.3121 | 119.9447
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4984e-18 | -1.7718e-11 | -5.0487e-11 | -3.4984e-18 | 1.7718e-11 | 5.0487e-11 | 7.6328e-18 | 4.824e-11 | 8.5168e-12 | -5.7246e-18 | -4.824e-11 | -8.5168e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0937 | 1.1 | 1.0978 | 1.0937 | 1.0759e-14 | -120.3121 | 119.9447 | 1.07e-14 | -120.3121 | 119.9447
Line4_2_6 | 0 | 0.060452 | 0.060452 | 0 | 0.060452 | 0.060452 | 0 | 0.013961 | 0.013961 | 0 | 0.013961 | 0.013961 | 2.2898e-17 | 0.01474 | 0.0037509 | -2.1626e-17 | -0.014704 | -0.0037143 | 2.5443e-18 | 0.0039919 | 0.014719 | -2.5443e-18 | -0.0039188 | -0.014646 | 0 | -135.6932 | 44.3068 | 0 | 44.3068 | -135.6932 | 1.1 | 1.0939 | 1.088 | 1.1 | 1.09 | 1.0823 | 1.0454e-14 | -120.5402 | 120.0098 | 1.0126e-14 | -120.7698 | 120.0757
Line5_6_7 | 0 | 0.060452 | 0.060452 | 0 | 0.060452 | 0.060452 | 0 | 0.013961 | 0.013961 | 0 | 0.013961 | 0.013961 | 1.781e-17 | 0.014704 | 0.0037143 | -1.781e-17 | -0.014667 | -0.0036778 | 2.5443e-18 | 0.0039188 | 0.014646 | -3.0796e-33 | -0.0038457 | -0.014572 | 0 | -135.6932 | 44.3068 | 0 | 44.3068 | -135.6932 | 1.1 | 1.09 | 1.0823 | 1.1 | 1.0861 | 1.0765 | 1.0126e-14 | -120.7698 | 120.0757 | 9.9075e-15 | -121.0011 | 120.1422
Line6_7_8 | 0 | 0.060452 | 0.060452 | 0 | 0.060452 | 0.060452 | 0 | 0.013961 | 0.013961 | 0 | 0.013961 | 0.013961 | 1.5266e-17 | 0.014667 | 0.0036778 | -2.0354e-17 | -0.014631 | -0.0036413 | -2.5443e-18 | 0.0038457 | 0.014572 | -3.4279e-33 | -0.0037726 | -0.014499 | 0 | -135.6932 | 44.3068 | 0 | 44.3068 | -135.6932 | 1.1 | 1.0861 | 1.0765 | 1.1 | 1.0823 | 1.0708 | 9.9075e-15 | -121.0011 | 120.1422 | 9.6495e-15 | -121.2341 | 120.2095
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5443e-18 | -6.9334e-11 | -1.1449e-10 | 2.5443e-18 | 6.9334e-11 | 1.1449e-10 | -4.2849e-34 | 9.4011e-11 | -1.5791e-11 | 2.5443e-18 | -9.4011e-11 | 1.5791e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0823 | 1.0708 | 1.1 | 1.0823 | 1.0708 | 9.6495e-15 | -121.2341 | 120.2095 | 9.5625e-15 | -121.2341 | 120.2095
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.5699e-34 | -6.9334e-11 | -1.1449e-10 | -2.5443e-18 | 6.9334e-11 | 1.1449e-10 | -5.0885e-18 | 9.4011e-11 | -1.5791e-11 | 2.5443e-18 | -9.4011e-11 | 1.5791e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0823 | 1.0708 | 1.1 | 1.0823 | 1.0708 | 9.6495e-15 | -121.2341 | 120.2095 | 9.5728e-15 | -121.2341 | 120.2095
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3675e-17 | -6.2015e-11 | -1.7671e-10 | -1.3675e-17 | 6.2015e-11 | 1.7671e-10 | 8.2688e-18 | 1.6884e-10 | 2.9809e-11 | -7.6328e-18 | -1.6884e-10 | -2.9809e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0937 | 1.1 | 1.0978 | 1.0937 | 1.0576e-14 | -120.3121 | 119.9447 | 1.0424e-14 | -120.3121 | 119.9447

## LL_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 1.455 | 1.455 | 0 | 1.455 | 1.455 | 0 | 0.33601 | 0.33601 | 0 | 0.33601 | 0.33601 | -1.7579e-16 | 0.28984 | 0.03533 | 1.5821e-16 | -0.24919 | 0.005316 | 4.3946e-16 | 0.073022 | 0.26569 | -4.5704e-16 | -0.030682 | -0.22336 | 0 | -142.8727 | 37.1273 | 0 | 37.1273 | -142.8727 | 0.95 | 0.88953 | 0.79769 | 0.95 | 0.74721 | 0.66491 | 1.1607e-12 | -128.7319 | 119.553 | 1.1717e-12 | -135.8534 | 128.4907
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8018e-16 | -9.6789e-10 | -2.6725e-09 | -1.8897e-16 | 9.6789e-10 | 2.6725e-09 | 2.1094e-16 | 2.8224e-09 | 1.3007e-10 | -2.1094e-16 | -2.8224e-09 | -1.3007e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.88953 | 0.79769 | 0.95 | 0.88953 | 0.79769 | 1.1638e-12 | -128.7319 | 119.553 | 1.1653e-12 | -128.7319 | 119.553
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7579e-16 | -8.0657e-10 | -2.2271e-09 | -1.7579e-16 | 8.0657e-10 | 2.2271e-09 | 2.461e-16 | 2.352e-09 | 1.0839e-10 | -2.461e-16 | -2.352e-09 | -1.0839e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.88953 | 0.79769 | 0.95 | 0.88953 | 0.79769 | 1.1653e-12 | -128.7319 | 119.553 | 1.1677e-12 | -128.7319 | 119.553
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.1648e-31 | -4.8394e-10 | -1.3362e-09 | 7.1684e-31 | 4.8394e-10 | 1.3362e-09 | 3.5157e-17 | 1.4112e-09 | 6.5035e-11 | -3.5157e-17 | -1.4112e-09 | -6.5035e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.88953 | 0.79769 | 0.95 | 0.88953 | 0.79769 | 1.1677e-12 | -128.7319 | 119.553 | 1.1682e-12 | -128.7319 | 119.553
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821e-16 | -1.6131e-10 | -4.4541e-10 | -1.4942e-16 | 1.6131e-10 | 4.4541e-10 | 1.7579e-16 | 4.7039e-10 | 2.1679e-11 | -1.7579e-16 | -4.7039e-10 | -2.1679e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.88953 | 0.79769 | 0.95 | 0.88953 | 0.79769 | 1.1677e-12 | -128.7319 | 119.553 | 1.169e-12 | -128.7319 | 119.553
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.1973e-17 | -3.2263e-10 | -8.9083e-10 | 2.1973e-17 | 3.2263e-10 | 8.9083e-10 | 3.5157e-17 | 9.4079e-10 | 4.3357e-11 | -1.7579e-17 | -9.4079e-10 | -4.3357e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.88953 | 0.79769 | 0.95 | 0.88953 | 0.79769 | 1.1682e-12 | -128.7319 | 119.553 | 1.1687e-12 | -128.7319 | 119.553
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3946e-17 | -1.6131e-10 | -4.4541e-10 | -4.3946e-17 | 1.6131e-10 | 4.4541e-10 | 8.9637e-31 | 4.7039e-10 | 2.1678e-11 | -8.9621e-31 | -4.7039e-10 | -2.1678e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.88953 | 0.79769 | 0.95 | 0.88953 | 0.79769 | 1.1687e-12 | -128.7319 | 119.553 | 1.1684e-12 | -128.7319 | 119.553
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7579e-17 | -1.6131e-10 | -4.4541e-10 | -2.6368e-17 | 1.6131e-10 | 4.4541e-10 | 3.5615e-31 | 4.7039e-10 | 2.1679e-11 | -5.3413e-31 | -4.7039e-10 | -2.1679e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.88953 | 0.79769 | 0.95 | 0.88953 | 0.79769 | 1.1609e-12 | -128.7319 | 119.553 | 1.1606e-12 | -128.7319 | 119.553
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8457e-16 | -1.6131e-10 | -4.4541e-10 | -1.8457e-16 | 1.6131e-10 | 4.4541e-10 | 1.4063e-16 | 4.7039e-10 | 2.1679e-11 | -1.5821e-16 | -4.7039e-10 | -2.1679e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.88953 | 0.79769 | 0.95 | 0.88953 | 0.79769 | 1.1612e-12 | -128.7319 | 119.553 | 1.161e-12 | -128.7319 | 119.553
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2413e-16 | -1.2905e-09 | -3.5633e-09 | -2.2413e-16 | 1.2905e-09 | 3.5633e-09 | 1.7579e-16 | 3.7632e-09 | 1.7343e-10 | -1.7579e-16 | -3.7632e-09 | -1.7343e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.88953 | 0.79769 | 0.95 | 0.88953 | 0.79769 | 1.1607e-12 | -128.7319 | 119.553 | 1.1624e-12 | -128.7319 | 119.553
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8457e-16 | -3.2263e-10 | -8.9083e-10 | -1.9336e-16 | 3.2263e-10 | 8.9083e-10 | 1.9336e-16 | 9.4079e-10 | 4.3357e-11 | -2.1094e-16 | -9.4079e-10 | -4.3357e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.88953 | 0.79769 | 0.95 | 0.88953 | 0.79769 | 1.1607e-12 | -128.7319 | 119.553 | 1.1609e-12 | -128.7319 | 119.553
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7579e-16 | -3.2263e-10 | -8.9083e-10 | -1.7579e-16 | 3.2263e-10 | 8.9083e-10 | 1.7579e-16 | 9.4079e-10 | 4.3357e-11 | -1.7579e-16 | -9.4079e-10 | -4.3357e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.88953 | 0.79769 | 0.95 | 0.88953 | 0.79769 | 1.1607e-12 | -128.7319 | 119.553 | 1.1612e-12 | -128.7319 | 119.553
Line4_2_6 | 0 | 1.455 | 1.455 | 0 | 1.455 | 1.455 | 0 | 0.33601 | 0.33601 | 0 | 0.33601 | 0.33601 | -1.4063e-16 | 0.24919 | -0.005316 | 1.7579e-16 | -0.20855 | 0.045962 | 4.5704e-16 | 0.030682 | 0.22336 | -4.5704e-16 | 0.011658 | -0.18102 | 0 | -142.8727 | 37.1273 | 0 | 37.1273 | -142.8727 | 0.95 | 0.74721 | 0.66491 | 0.95 | 0.62161 | 0.55581 | 1.1717e-12 | -135.8534 | 128.4907 | 1.1802e-12 | -146.0722 | 141.3743
Line5_6_7 | 0 | 1.455 | 1.455 | 0 | 1.455 | 1.455 | 0 | 0.33601 | 0.33601 | 0 | 0.33601 | 0.33601 | -1.4063e-16 | 0.20855 | -0.045962 | 1.0547e-16 | -0.1679 | 0.086608 | 4.2188e-16 | -0.011658 | 0.18102 | -4.2188e-16 | 0.053997 | -0.13868 | 0 | -142.8727 | 37.1273 | 0 | 37.1273 | -142.8727 | 0.95 | 0.62161 | 0.55581 | 0.95 | 0.52489 | 0.48658 | 1.1802e-12 | -146.0722 | 141.3743 | 1.1905e-12 | -160.7007 | 159.1134
Line6_7_8 | 0 | 1.455 | 1.455 | 0 | 1.455 | 1.455 | 0 | 0.33601 | 0.33601 | 0 | 0.33601 | 0.33601 | -1.4063e-16 | 0.1679 | -0.086608 | 2.1094e-16 | -0.12725 | 0.12725 | 2.8126e-16 | -0.053997 | 0.13868 | -2.8126e-16 | 0.096337 | -0.096337 | 0 | -142.8727 | 37.1273 | 0 | 37.1273 | -142.8727 | 0.95 | 0.52489 | 0.48658 | 0.95 | 0.475 | 0.475 | 1.1905e-12 | -160.7007 | 159.1134 | 1.1961e-12 | 180 | 180
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.9356e-30 | 1.7579e-16 | -1.0784e-22 | -7.0314e-17 | -1.7251e-16 | 3.2762e-18 | 1.4063e-16 | 1.4329e-09 | -1.4329e-09 | -1.4063e-16 | -1.4329e-09 | 1.4329e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.475 | 0.475 | 0.95 | 0.475 | 0.475 | 1.1961e-12 | 180 | 180 | 1.195e-12 | -180 | 180
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.9356e-30 | -7.0314e-17 | 1.4063e-16 | 2.9379e-30 | 3.8433e-17 | -1.3735e-16 | 1.4063e-16 | 1.4329e-09 | -1.4329e-09 | -1.4063e-16 | -1.4329e-09 | 1.4329e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.475 | 0.475 | 0.95 | 0.475 | 0.475 | 1.1961e-12 | 180 | 180 | 1.197e-12 | -180 | 180
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8897e-16 | -1.1292e-09 | -3.1179e-09 | -1.9776e-16 | 1.1292e-09 | 3.1179e-09 | 2.1094e-16 | 3.2928e-09 | 1.5175e-10 | -2.1094e-16 | -3.2928e-09 | -1.5175e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.88953 | 0.79769 | 0.95 | 0.88953 | 0.79769 | 1.1624e-12 | -128.7319 | 119.553 | 1.1638e-12 | -128.7319 | 119.553

## LL_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 1.3784 | 1.3784 | 0 | 1.3784 | 1.3784 | 0 | 0.31833 | 0.31833 | 0 | 0.31833 | 0.31833 | -1.4988e-16 | 0.26013 | 0.031709 | 1.3323e-16 | -0.22365 | 0.0047711 | 3.9968e-16 | 0.065537 | 0.23846 | -3.9968e-16 | -0.027537 | -0.20046 | 0 | -142.8727 | 37.1273 | 0 | 37.1273 | -142.8727 | 0.9 | 0.84271 | 0.7557 | 0.9 | 0.70788 | 0.62991 | 1.1631e-12 | -128.7319 | 119.553 | 1.1741e-12 | -135.8534 | 128.4907
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9984e-16 | -8.6869e-10 | -2.3986e-09 | -1.9151e-16 | 8.6869e-10 | 2.3986e-09 | 1.9984e-16 | 2.5331e-09 | 1.1674e-10 | -1.8319e-16 | -2.5331e-09 | -1.1674e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.84271 | 0.7557 | 0.9 | 0.84271 | 0.7557 | 1.1662e-12 | -128.7319 | 119.553 | 1.1676e-12 | -128.7319 | 119.553
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6237e-16 | -7.2391e-10 | -1.9988e-09 | -1.5404e-16 | 7.2391e-10 | 1.9988e-09 | 2.1649e-16 | 2.1109e-09 | 9.7283e-11 | -2.1649e-16 | -2.1109e-09 | -9.7283e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.84271 | 0.7557 | 0.9 | 0.84271 | 0.7557 | 1.1676e-12 | -128.7319 | 119.553 | 1.17e-12 | -128.7319 | 119.553
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3267e-18 | -4.3434e-10 | -1.1993e-09 | -8.3267e-18 | 4.3434e-10 | 1.1993e-09 | -1.6653e-17 | 1.2665e-09 | 5.837e-11 | -1.7011e-31 | -1.2665e-09 | -5.837e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.84271 | 0.7557 | 0.9 | 0.84271 | 0.7557 | 1.17e-12 | -128.7319 | 119.553 | 1.1706e-12 | -128.7319 | 119.553
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4155e-16 | -1.4478e-10 | -3.9976e-10 | -1.4155e-16 | 1.4478e-10 | 3.9976e-10 | 1.4988e-16 | 4.2218e-10 | 1.9457e-11 | -1.4988e-16 | -4.2218e-10 | -1.9457e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.84271 | 0.7557 | 0.9 | 0.84271 | 0.7557 | 1.17e-12 | -128.7319 | 119.553 | 1.1711e-12 | -128.7319 | 119.553
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1633e-18 | -2.8956e-10 | -7.9952e-10 | 4.1633e-18 | 2.8956e-10 | 7.9952e-10 | 4.996e-17 | 8.4436e-10 | 3.8913e-11 | -4.996e-17 | -8.4436e-10 | -3.8913e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.84271 | 0.7557 | 0.9 | 0.84271 | 0.7557 | 1.1706e-12 | -128.7319 | 119.553 | 1.171e-12 | -128.7319 | 119.553
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3267e-18 | -1.4478e-10 | -3.9976e-10 | 0 | 1.4478e-10 | 3.9976e-10 | 1.7017e-31 | 4.2218e-10 | 1.9457e-11 | 0 | -4.2218e-10 | -1.9457e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.84271 | 0.7557 | 0.9 | 0.84271 | 0.7557 | 1.171e-12 | -128.7319 | 119.553 | 1.1708e-12 | -128.7319 | 119.553
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0817e-17 | -1.4478e-10 | -3.9976e-10 | -2.0817e-17 | 1.4478e-10 | 3.9976e-10 | 4.2261e-31 | 4.2218e-10 | 1.9457e-11 | -4.2254e-31 | -4.2218e-10 | -1.9457e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.84271 | 0.7557 | 0.9 | 0.84271 | 0.7557 | 1.1632e-12 | -128.7319 | 119.553 | 1.163e-12 | -128.7319 | 119.553
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821e-16 | -1.4478e-10 | -3.9976e-10 | -1.5821e-16 | 1.4478e-10 | 3.9976e-10 | 1.1657e-16 | 4.2218e-10 | 1.9457e-11 | -1.3323e-16 | -4.2218e-10 | -1.9457e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.84271 | 0.7557 | 0.9 | 0.84271 | 0.7557 | 1.1635e-12 | -128.7319 | 119.553 | 1.1636e-12 | -128.7319 | 119.553
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.04e-16 | -1.1582e-09 | -3.1981e-09 | -2.04e-16 | 1.1582e-09 | 3.1981e-09 | 1.4988e-16 | 3.3775e-09 | 1.5565e-10 | -1.4988e-16 | -3.3775e-09 | -1.5565e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.84271 | 0.7557 | 0.9 | 0.84271 | 0.7557 | 1.1631e-12 | -128.7319 | 119.553 | 1.1647e-12 | -128.7319 | 119.553
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5404e-16 | -2.8956e-10 | -7.9952e-10 | -1.5404e-16 | 2.8956e-10 | 7.9952e-10 | 1.6653e-16 | 8.4436e-10 | 3.8913e-11 | -1.4988e-16 | -8.4436e-10 | -3.8913e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.84271 | 0.7557 | 0.9 | 0.84271 | 0.7557 | 1.1631e-12 | -128.7319 | 119.553 | 1.1632e-12 | -128.7319 | 119.553
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.707e-16 | -2.8956e-10 | -7.9952e-10 | -1.707e-16 | 2.8956e-10 | 7.9952e-10 | 1.4988e-16 | 8.4436e-10 | 3.8913e-11 | -1.4988e-16 | -8.4436e-10 | -3.8913e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.84271 | 0.7557 | 0.9 | 0.84271 | 0.7557 | 1.1631e-12 | -128.7319 | 119.553 | 1.1635e-12 | -128.7319 | 119.553
Line4_2_6 | 0 | 1.3784 | 1.3784 | 0 | 1.3784 | 1.3784 | 0 | 0.31833 | 0.31833 | 0 | 0.31833 | 0.31833 | -1.9984e-16 | 0.22365 | -0.0047711 | 1.6653e-16 | -0.18717 | 0.041251 | 3.9968e-16 | 0.027537 | 0.20046 | -3.9968e-16 | 0.010463 | -0.16246 | 0 | -142.8727 | 37.1273 | 0 | 37.1273 | -142.8727 | 0.9 | 0.70788 | 0.62991 | 0.9 | 0.5889 | 0.52656 | 1.1741e-12 | -135.8534 | 128.4907 | 1.1828e-12 | -146.0722 | 141.3743
Line5_6_7 | 0 | 1.3784 | 1.3784 | 0 | 1.3784 | 1.3784 | 0 | 0.31833 | 0.31833 | 0 | 0.31833 | 0.31833 | -1.9984e-16 | 0.18717 | -0.041251 | 1.9984e-16 | -0.15069 | 0.077731 | 3.9968e-16 | -0.010463 | 0.16246 | -3.9968e-16 | 0.048463 | -0.12446 | 0 | -142.8727 | 37.1273 | 0 | 37.1273 | -142.8727 | 0.9 | 0.5889 | 0.52656 | 0.9 | 0.49726 | 0.46097 | 1.1828e-12 | -146.0722 | 141.3743 | 1.1931e-12 | -160.7007 | 159.1134
Line6_7_8 | 0 | 1.3784 | 1.3784 | 0 | 1.3784 | 1.3784 | 0 | 0.31833 | 0.31833 | 0 | 0.31833 | 0.31833 | -6.9354e-30 | 0.15069 | -0.077731 | 5.5708e-30 | -0.11421 | 0.11421 | 3.3307e-16 | -0.048463 | 0.12446 | -2.6645e-16 | 0.086463 | -0.086463 | 0 | -142.8727 | 37.1273 | 0 | 37.1273 | -142.8727 | 0.9 | 0.49726 | 0.46097 | 0.9 | 0.45 | 0.45 | 1.1931e-12 | -160.7007 | 159.1134 | 1.1979e-12 | 180 | 180
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.6613e-17 | 1.9984e-16 | 1.3323e-16 | 6.6613e-17 | -1.969e-16 | -1.3029e-16 | -1.3927e-30 | 1.286e-09 | -1.286e-09 | 6.6613e-17 | -1.286e-09 | 1.286e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.45 | 0.45 | 0.9 | 0.45 | 0.45 | 1.1979e-12 | 180 | 180 | 1.1968e-12 | -180 | 180
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.3323e-16 | 9.992e-17 | 2.6645e-16 | 6.6613e-17 | -6.3673e-17 | -1.3029e-16 | -2.7854e-30 | 1.286e-09 | -1.286e-09 | 1.3935e-30 | -1.286e-09 | 1.286e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.45 | 0.45 | 0.9 | 0.45 | 0.45 | 1.1979e-12 | 180 | 180 | 1.1986e-12 | -180 | 180
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8319e-16 | -1.0135e-09 | -2.7983e-09 | -1.8319e-16 | 1.0135e-09 | 2.7983e-09 | 1.8319e-16 | 2.9553e-09 | 1.362e-10 | -1.8319e-16 | -2.9553e-09 | -1.362e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.84271 | 0.7557 | 0.9 | 0.84271 | 0.7557 | 1.1647e-12 | -128.7319 | 119.553 | 1.1662e-12 | -128.7319 | 119.553

## LL_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0.051843 | 0.051843 | 0 | 0.051843 | 0.051843 | 0 | 0.011973 | 0.011973 | 0 | 0.011973 | 0.011973 | -1.0987e-18 | 0.010966 | 0.0028847 | 1.648e-18 | -0.010915 | -0.0028331 | 1.5381e-17 | 0.0029326 | 0.010936 | -1.5381e-17 | -0.0028788 | -0.010882 | 0 | -135.2796 | 44.7204 | 0 | 44.7204 | -135.2796 | 0.95 | 0.94815 | 0.94465 | 0.95 | 0.94283 | 0.93921 | 4.0585e-14 | -120.3084 | 119.9432 | 4.085e-14 | -120.5043 | 120.1275
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.2786e-18 | -3.8309e-11 | -1.1119e-10 | -7.0039e-18 | 3.8309e-11 | 1.1119e-10 | 8.7893e-18 | 1.0665e-10 | 1.9584e-11 | -8.7893e-18 | -1.0665e-10 | -1.9584e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94815 | 0.94465 | 0.95 | 0.94815 | 0.94465 | 4.0693e-14 | -120.3084 | 119.9432 | 4.0747e-14 | -120.3084 | 119.9432
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.18e-18 | -3.1925e-11 | -9.2658e-11 | -6.18e-18 | 3.1925e-11 | 9.2658e-11 | 9.3386e-18 | 8.8872e-11 | 1.632e-11 | -8.7893e-18 | -8.8872e-11 | -1.632e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94815 | 0.94465 | 0.95 | 0.94815 | 0.94465 | 4.0747e-14 | -120.3084 | 119.9432 | 4.0833e-14 | -120.3084 | 119.9432
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.2399e-19 | -1.9155e-11 | -5.5595e-11 | -8.2399e-19 | 1.9155e-11 | 5.5595e-11 | 5.4933e-19 | 5.3323e-11 | 9.7921e-12 | -5.4933e-19 | -5.3323e-11 | -9.7921e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94815 | 0.94465 | 0.95 | 0.94815 | 0.94465 | 4.0833e-14 | -120.3084 | 119.9432 | 4.0853e-14 | -120.3084 | 119.9432
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7293e-18 | -6.3849e-12 | -1.8532e-11 | -6.4546e-18 | 6.3849e-12 | 1.8532e-11 | 5.4933e-18 | 1.7774e-11 | 3.264e-12 | -4.944e-18 | -1.7774e-11 | -3.264e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94815 | 0.94465 | 0.95 | 0.94815 | 0.94465 | 4.0833e-14 | -120.3084 | 119.9432 | 4.0872e-14 | -120.3084 | 119.9432
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4933e-19 | -1.277e-11 | -3.7063e-11 | -5.4933e-19 | 1.277e-11 | 3.7063e-11 | 1.0987e-18 | 3.5549e-11 | 6.5281e-12 | -1.0987e-18 | -3.5549e-11 | -6.5281e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94815 | 0.94465 | 0.95 | 0.94815 | 0.94465 | 4.0853e-14 | -120.3084 | 119.9432 | 4.0869e-14 | -120.3084 | 119.9432
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.8666e-20 | -6.3849e-12 | -1.8532e-11 | 6.8666e-20 | 6.3849e-12 | 1.8532e-11 | 5.4933e-19 | 1.7774e-11 | 3.264e-12 | 4.8971e-35 | -1.7774e-11 | -3.264e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94815 | 0.94465 | 0.95 | 0.94815 | 0.94465 | 4.0869e-14 | -120.3084 | 119.9432 | 4.0862e-14 | -120.3084 | 119.9432
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.7837e-34 | -6.3849e-12 | -1.8532e-11 | 3.8912e-34 | 6.3849e-12 | 1.8532e-11 | 1.0987e-18 | 1.7774e-11 | 3.264e-12 | -5.4933e-19 | -1.7774e-11 | -3.264e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94815 | 0.94465 | 0.95 | 0.94815 | 0.94465 | 4.0593e-14 | -120.3084 | 119.9432 | 4.0586e-14 | -120.3084 | 119.9432
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.9353e-18 | -6.3849e-12 | -1.8532e-11 | -6.9353e-18 | 6.3849e-12 | 1.8532e-11 | 6.0426e-18 | 1.7774e-11 | 3.264e-12 | -4.944e-18 | -1.7774e-11 | -3.264e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94815 | 0.94465 | 0.95 | 0.94815 | 0.94465 | 4.0607e-14 | -120.3084 | 119.9432 | 4.061e-14 | -120.3084 | 119.9432
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0639e-18 | -5.1079e-11 | -1.4825e-10 | -8.7893e-18 | 5.1079e-11 | 1.4825e-10 | 8.2399e-18 | 1.422e-10 | 2.6112e-11 | -6.5919e-18 | -1.422e-10 | -2.6112e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94815 | 0.94465 | 0.95 | 0.94815 | 0.94465 | 4.0585e-14 | -120.3084 | 119.9432 | 4.0639e-14 | -120.3084 | 119.9432
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.9353e-18 | -1.277e-11 | -3.7063e-11 | -6.6606e-18 | 1.277e-11 | 3.7063e-11 | 7.6906e-18 | 3.5549e-11 | 6.5281e-12 | -7.6906e-18 | -3.5549e-11 | -6.5281e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94815 | 0.94465 | 0.95 | 0.94815 | 0.94465 | 4.0585e-14 | -120.3084 | 119.9432 | 4.0593e-14 | -120.3084 | 119.9432
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.3173e-18 | -1.277e-11 | -3.7063e-11 | -6.0426e-18 | 1.277e-11 | 3.7063e-11 | 7.1413e-18 | 3.5549e-11 | 6.5281e-12 | -7.1413e-18 | -3.5549e-11 | -6.5281e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94815 | 0.94465 | 0.95 | 0.94815 | 0.94465 | 4.0585e-14 | -120.3084 | 119.9432 | 4.0607e-14 | -120.3084 | 119.9432
Line4_2_6 | 0 | 0.051843 | 0.051843 | 0 | 0.051843 | 0.051843 | 0 | 0.011973 | 0.011973 | 0 | 0.011973 | 0.011973 | -8.6165e-33 | 0.010915 | 0.0028331 | 9.45e-33 | -0.010863 | -0.0027815 | 1.2085e-17 | 0.0028788 | 0.010882 | -1.3184e-17 | -0.0028251 | -0.010828 | 0 | -135.2796 | 44.7204 | 0 | 44.7204 | -135.2796 | 0.95 | 0.94283 | 0.93921 | 0.95 | 0.93752 | 0.93379 | 4.085e-14 | -120.5043 | 120.1275 | 4.1068e-14 | -120.7024 | 120.3141
Line5_6_7 | 0 | 0.051843 | 0.051843 | 0 | 0.051843 | 0.051843 | 0 | 0.011973 | 0.011973 | 0 | 0.011973 | 0.011973 | -2.1973e-18 | 0.010863 | 0.0027815 | 2.1973e-18 | -0.010812 | -0.0027299 | 1.5381e-17 | 0.0028251 | 0.010828 | -1.7579e-17 | -0.0027713 | -0.010775 | 0 | -135.2796 | 44.7204 | 0 | 44.7204 | -135.2796 | 0.95 | 0.93752 | 0.93379 | 0.95 | 0.93223 | 0.92837 | 4.1068e-14 | -120.7024 | 120.3141 | 4.1364e-14 | -120.9028 | 120.5028
Line6_7_8 | 0 | 0.051843 | 0.051843 | 0 | 0.051843 | 0.051843 | 0 | 0.011973 | 0.011973 | 0 | 0.011973 | 0.011973 | 2.1973e-18 | 0.010812 | 0.0027299 | -2.1973e-18 | -0.01076 | -0.0026783 | 8.7893e-18 | 0.0027713 | 0.010775 | -8.7893e-18 | -0.0027175 | -0.010721 | 0 | -135.2796 | 44.7204 | 0 | 44.7204 | -135.2796 | 0.95 | 0.93223 | 0.92837 | 0.95 | 0.92694 | 0.92297 | 4.1364e-14 | -120.9028 | 120.5028 | 4.1564e-14 | -121.1055 | 120.6937
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.3946e-18 | -7.7759e-11 | -9.1252e-11 | 4.3946e-18 | 7.7759e-11 | 9.1252e-11 | 4.3946e-18 | 6.2294e-11 | -3.8923e-11 | -4.3946e-18 | -6.2294e-11 | 3.8923e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.92694 | 0.92297 | 0.95 | 0.92694 | 0.92297 | 4.1564e-14 | -121.1055 | 120.6937 | 4.153e-14 | -121.1055 | 120.6937
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.1973e-18 | -7.7759e-11 | -9.1252e-11 | 2.1973e-18 | 7.7759e-11 | 9.1252e-11 | -1.594e-33 | 6.2294e-11 | -3.8923e-11 | 1.5941e-33 | -6.2294e-11 | 3.8923e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.92694 | 0.92297 | 0.95 | 0.92694 | 0.92297 | 4.1564e-14 | -121.1055 | 120.6937 | 4.1566e-14 | -121.1055 | 120.6937
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6219e-18 | -4.4694e-11 | -1.2972e-10 | -7.6219e-18 | 4.4694e-11 | 1.2972e-10 | 7.1413e-18 | 1.2442e-10 | 2.2848e-11 | -7.1413e-18 | -1.2442e-10 | -2.2848e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94815 | 0.94465 | 0.95 | 0.94815 | 0.94465 | 4.0639e-14 | -120.3084 | 119.9432 | 4.0693e-14 | -120.3084 | 119.9432

## LL_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0.049114 | 0.049114 | 0 | 0.049114 | 0.049114 | 0 | 0.011342 | 0.011342 | 0 | 0.011342 | 0.011342 | -1.5613e-18 | 0.0098425 | 0.002589 | 1.5613e-18 | -0.0097961 | -0.0025427 | 1.4572e-17 | 0.002632 | 0.009815 | -1.3531e-17 | -0.0025837 | -0.0097667 | 0 | -135.2796 | 44.7204 | 0 | 44.7204 | -135.2796 | 0.9 | 0.89825 | 0.89493 | 0.9 | 0.89321 | 0.88978 | 4.2227e-14 | -120.3084 | 119.9432 | 4.2553e-14 | -120.5043 | 120.1275
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7004e-18 | -3.4383e-11 | -9.9793e-11 | -6.4402e-18 | 3.4383e-11 | 9.9793e-11 | 6.7654e-18 | 9.5716e-11 | 1.7577e-11 | -6.245e-18 | -9.5716e-11 | -1.7577e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89825 | 0.89493 | 0.9 | 0.89825 | 0.89493 | 4.233e-14 | -120.3084 | 119.9432 | 4.2382e-14 | -120.3084 | 119.9432
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0498e-18 | -2.8652e-11 | -8.3161e-11 | -5.7896e-18 | 2.8652e-11 | 8.3161e-11 | 7.8063e-18 | 7.9764e-11 | 1.4648e-11 | -7.8063e-18 | -7.9764e-11 | -1.4648e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89825 | 0.89493 | 0.9 | 0.89825 | 0.89493 | 4.2382e-14 | -120.3084 | 119.9432 | 4.2466e-14 | -120.3084 | 119.9432
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4962e-18 | -1.7192e-11 | -4.9896e-11 | -1.4962e-18 | 1.7191e-11 | 4.9896e-11 | 5.2042e-19 | 4.7858e-11 | 8.7885e-12 | -1.1095e-33 | -4.7858e-11 | -8.7885e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89825 | 0.89493 | 0.9 | 0.89825 | 0.89493 | 4.2466e-14 | -120.3084 | 119.9432 | 4.2486e-14 | -120.3084 | 119.9432
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.18e-18 | -5.7305e-12 | -1.6632e-11 | -6.4402e-18 | 5.7305e-12 | 1.6632e-11 | 5.7246e-18 | 1.5953e-11 | 2.9295e-12 | -5.2042e-18 | -1.5953e-11 | -2.9295e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89825 | 0.89493 | 0.9 | 0.89825 | 0.89493 | 4.2466e-14 | -120.3084 | 119.9432 | 4.251e-14 | -120.3084 | 119.9432
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5536e-19 | -1.1461e-11 | -3.3264e-11 | -4.5536e-19 | 1.1461e-11 | 3.3264e-11 | 1.0408e-18 | 3.1905e-11 | 5.859e-12 | -1.5613e-18 | -3.1905e-11 | -5.859e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89825 | 0.89493 | 0.9 | 0.89825 | 0.89493 | 4.2486e-14 | -120.3084 | 119.9432 | 4.2501e-14 | -120.3084 | 119.9432
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.7578e-19 | -5.7305e-12 | -1.6632e-11 | -7.1557e-19 | 5.7305e-12 | 1.6632e-11 | 1.0408e-18 | 1.5953e-11 | 2.9295e-12 | -5.3072e-34 | -1.5953e-11 | -2.9295e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89825 | 0.89493 | 0.9 | 0.89825 | 0.89493 | 4.2501e-14 | -120.3084 | 119.9432 | 4.2494e-14 | -120.3084 | 119.9432
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9516e-19 | -5.7305e-12 | -1.6632e-11 | -7.1557e-19 | 5.7305e-12 | 1.6632e-11 | -1.0408e-18 | 1.5953e-11 | 2.9295e-12 | 1.0408e-18 | -1.5953e-11 | -2.9295e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89825 | 0.89493 | 0.9 | 0.89825 | 0.89493 | 4.2232e-14 | -120.3084 | 119.9432 | 4.2225e-14 | -120.3084 | 119.9432
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3993e-18 | -5.7305e-12 | -1.6632e-11 | -5.3993e-18 | 5.7305e-12 | 1.6632e-11 | 5.2042e-18 | 1.5953e-11 | 2.9295e-12 | -5.7246e-18 | -1.5953e-11 | -2.9295e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89825 | 0.89493 | 0.9 | 0.89825 | 0.89493 | 4.2247e-14 | -120.3084 | 119.9432 | 4.2256e-14 | -120.3084 | 119.9432
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.546e-18 | -4.5844e-11 | -1.3306e-10 | -7.546e-18 | 4.5844e-11 | 1.3306e-10 | 6.245e-18 | 1.2762e-10 | 2.3436e-11 | -6.7654e-18 | -1.2762e-10 | -2.3436e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89825 | 0.89493 | 0.9 | 0.89825 | 0.89493 | 4.2227e-14 | -120.3084 | 119.9432 | 4.2279e-14 | -120.3084 | 119.9432
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.9197e-18 | -1.1461e-11 | -3.3264e-11 | -6.18e-18 | 1.1461e-11 | 3.3264e-11 | 6.7654e-18 | 3.1905e-11 | 5.859e-12 | -6.7654e-18 | -3.1905e-11 | -5.859e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89825 | 0.89493 | 0.9 | 0.89825 | 0.89493 | 4.2227e-14 | -120.3084 | 119.9432 | 4.2232e-14 | -120.3084 | 119.9432
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.9197e-18 | -1.1461e-11 | -3.3264e-11 | -5.9197e-18 | 1.1461e-11 | 3.3264e-11 | 5.7246e-18 | 3.1905e-11 | 5.859e-12 | -6.245e-18 | -3.1905e-11 | -5.859e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89825 | 0.89493 | 0.9 | 0.89825 | 0.89493 | 4.2227e-14 | -120.3084 | 119.9432 | 4.2247e-14 | -120.3084 | 119.9432
Line4_2_6 | 0 | 0.049114 | 0.049114 | 0 | 0.049114 | 0.049114 | 0 | 0.011342 | 0.011342 | 0 | 0.011342 | 0.011342 | -4.1633e-18 | 0.0097961 | 0.0025427 | 4.1633e-18 | -0.0097498 | -0.0024964 | 1.4572e-17 | 0.0025837 | 0.0097667 | -1.4572e-17 | -0.0025355 | -0.0097185 | 0 | -135.2796 | 44.7204 | 0 | 44.7204 | -135.2796 | 0.9 | 0.89321 | 0.88978 | 0.9 | 0.88818 | 0.88464 | 4.2553e-14 | -120.5043 | 120.1275 | 4.28e-14 | -120.7024 | 120.3141
Line5_6_7 | 0 | 0.049114 | 0.049114 | 0 | 0.049114 | 0.049114 | 0 | 0.011342 | 0.011342 | 0 | 0.011342 | 0.011342 | -1.244e-32 | 0.0097498 | 0.0024964 | 1.0965e-32 | -0.0097035 | -0.0024501 | 1.6653e-17 | 0.0025355 | 0.0097185 | -1.4572e-17 | -0.0024873 | -0.0096702 | 0 | -135.2796 | 44.7204 | 0 | 44.7204 | -135.2796 | 0.9 | 0.88818 | 0.88464 | 0.9 | 0.88316 | 0.87951 | 4.28e-14 | -120.7024 | 120.3141 | 4.3116e-14 | -120.9028 | 120.5028
Line6_7_8 | 0 | 0.049114 | 0.049114 | 0 | 0.049114 | 0.049114 | 0 | 0.011342 | 0.011342 | 0 | 0.011342 | 0.011342 | -6.266e-33 | 0.0097035 | 0.0024501 | 2.0817e-18 | -0.0096572 | -0.0024038 | 8.3267e-18 | 0.0024873 | 0.0096702 | -1.0408e-17 | -0.002439 | -0.009622 | 0 | -135.2796 | 44.7204 | 0 | 44.7204 | -135.2796 | 0.9 | 0.88316 | 0.87951 | 0.9 | 0.87816 | 0.87439 | 4.3116e-14 | -120.9028 | 120.5028 | 4.3328e-14 | -121.1055 | 120.6937
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.5742e-33 | -6.9789e-11 | -8.1899e-11 | -4.1633e-18 | 6.9789e-11 | 8.1899e-11 | 2.0817e-18 | 5.5909e-11 | -3.4934e-11 | -4.1633e-18 | -5.5909e-11 | 3.4934e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.87816 | 0.87439 | 0.9 | 0.87816 | 0.87439 | 4.3328e-14 | -121.1055 | 120.6937 | 4.3295e-14 | -121.1055 | 120.6937
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.5742e-33 | -6.9789e-11 | -8.1899e-11 | 3.1539e-33 | 6.9789e-11 | 8.1899e-11 | 2.0817e-18 | 5.5909e-11 | -3.4934e-11 | -4.1633e-18 | -5.5909e-11 | 3.4934e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.87816 | 0.87439 | 0.9 | 0.87816 | 0.87439 | 4.3328e-14 | -121.1055 | 120.6937 | 4.3404e-14 | -121.1055 | 120.6937
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.0256e-18 | -4.0113e-11 | -1.1643e-10 | -7.0256e-18 | 4.0113e-11 | 1.1643e-10 | 6.7654e-18 | 1.1167e-10 | 2.0507e-11 | -6.7654e-18 | -1.1167e-10 | -2.0507e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89825 | 0.89493 | 0.9 | 0.89825 | 0.89493 | 4.2279e-14 | -120.3084 | 119.9432 | 4.233e-14 | -120.3084 | 119.9432

## LG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.44637 | 0.041352 | 0.041352 | 0.44637 | 0.041352 | 0.041352 | 0.10308 | 0.0095498 | 0.0095498 | 0.10308 | 0.0095499 | 0.0095499 | 0.0069861 | -0.0084617 | 0.0088765 | -0.0052631 | 0.0085034 | -0.008835 | 0.013957 | 0.013755 | 0.012741 | -0.010513 | -0.01367 | -0.012657 | -86.1227 | 93.3457 | 93.3457 | 93.8773 | -86.6543 | -86.6543 |  | 0.1514 | 1.6911 | 1.626 | 0.11405 | 1.6858 | 1.6163 | -22.7135 | -145.0554 | 148.4819 | -22.7157 | -144.7715 | 148.429
Line10_11_12 | 0.040219 | 0.040219 | 0.040219 | 0.04022 | 0.04022 | 0.04022 | 0.0092883 | 0.0092883 | 0.0092883 | 0.0092884 | 0.0092884 | 0.0092884 | -0.00065121 | -0.0080621 | 0.0087862 | 0.0006593 | 0.0080703 | -0.0087782 | -0.0012871 | 0.013457 | 0.012241 | 0.0013033 | -0.013441 | -0.012225 | 94.1306 | 94.1306 | 94.1306 | -85.8694 | -85.8694 | -85.8694 |  | 0.1553 | 1.689 | 1.6222 | 0.15725 | 1.6879 | 1.6203 | -22.7065 | -144.9441 | 148.4602 | -22.7031 | -144.8884 | 148.4493
Line11_12_13 | 0.04022 | 0.04022 | 0.04022 | 0.04022 | 0.04022 | 0.04022 | 0.0092884 | 0.0092884 | 0.0092884 | 0.0092884 | 0.0092884 | 0.0092884 | -0.0006593 | -0.0080703 | 0.0087782 | 0.00066739 | 0.0080784 | -0.0087701 | -0.0013033 | 0.013441 | 0.012225 | 0.0013195 | -0.013425 | -0.012208 | 94.1305 | 94.1305 | 94.1305 | -85.8695 | -85.8695 | -85.8695 |  | 0.15725 | 1.6879 | 1.6203 | 0.15919 | 1.6869 | 1.6184 | -22.7031 | -144.8884 | 148.4493 | -22.6999 | -144.8326 | 148.4383
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4308e-08 | 2.0467e-07 | -1.944e-07 | -9.0664e-09 | -1.4098e-07 | 1.2548e-07 | 3.1878e-08 | -3.0859e-07 | -2.9735e-07 | -2.1488e-08 | 2.03e-07 | 2.012e-07 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.15919 | 1.6869 | 1.6184 | 0.15919 | 1.6869 | 1.6184 | -22.6999 | -144.8326 | 148.4383 | -22.6998 | -144.8326 | 148.4383
Line13_13_14 | 0.040221 | 0.040221 | 0.040221 | 0.040221 | 0.040221 | 0.040221 | 0.0092887 | 0.0092887 | 0.0092887 | 0.0092887 | 0.0092887 | 0.0092887 | -0.00066741 | -0.0080786 | 0.0087703 | 0.0006755 | 0.0080868 | -0.0087623 | -0.0013195 | 0.013426 | 0.012209 | 0.0013357 | -0.013409 | -0.012193 | 94.1305 | 94.1305 | 94.1305 | -85.8695 | -85.8695 | -85.8695 |  | 0.15919 | 1.6869 | 1.6184 | 0.16114 | 1.6858 | 1.6164 | -22.6999 | -144.8326 | 148.4383 | -22.6966 | -144.7767 | 148.4274
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.5389e-09 | 1.3644e-07 | -1.296e-07 | -4.297e-09 | -7.2762e-08 | 6.0675e-08 | 2.1252e-08 | -2.0573e-07 | -1.9823e-07 | -1.0862e-08 | 1.0014e-07 | 1.0208e-07 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.15919 | 1.6869 | 1.6184 | 0.15919 | 1.6869 | 1.6184 | -22.6998 | -144.8326 | 148.4383 | -22.6998 | -144.8326 | 148.4383
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7695e-09 | 6.8222e-08 | -6.48e-08 | 4.725e-10 | -4.5396e-09 | -4.1245e-09 | 1.0626e-08 | -1.0286e-07 | -9.9116e-08 | -2.3652e-10 | -2.7275e-09 | 2.9671e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.15919 | 1.6869 | 1.6184 | 0.15919 | 1.6869 | 1.6184 | -22.6998 | -144.8326 | 148.4383 | -22.6998 | -144.8326 | 148.4383
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5944e-09 | 6.8763e-08 | -6.5065e-08 | 4.5843e-10 | -4.5754e-09 | -4.1751e-09 | 1.0311e-08 | -1.0367e-07 | -1.0029e-07 | -2.2799e-10 | -2.7497e-09 | 2.9808e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.15337 | 1.69 | 1.6241 | 0.15337 | 1.69 | 1.6241 | -22.7128 | -144.9992 | 148.4712 | -22.7128 | -144.9992 | 148.4712
Line17_5_19 | 0.040462 | 0.040462 | 0.040462 | 0.040462 | 0.040462 | 0.040462 | 0.0093443 | 0.0093443 | 0.0093443 | 0.0093443 | 0.0093443 | 0.0093443 | -0.0006433 | -0.0081428 | 0.0088106 | 0.00065149 | 0.008151 | -0.0088025 | -0.0012806 | 0.013531 | 0.012357 | 0.0012969 | -0.013514 | -0.01234 | 93.961 | 93.961 | 93.961 | -86.039 | -86.039 | -86.039 |  | 0.15336 | 1.69 | 1.6241 | 0.15532 | 1.689 | 1.6222 | -22.7121 | -144.9994 | 148.4712 | -22.7107 | -144.9432 | 148.4604
Line1_1_3 | 0.040219 | 0.040219 | 0.040219 | 0.040219 | 0.040219 | 0.040219 | 0.0092881 | 0.0092881 | 0.0092881 | 0.0092882 | 0.0092882 | 0.0092882 | -0.00063502 | -0.0080458 | 0.0088022 | 0.00064311 | 0.008054 | -0.0087942 | -0.0012547 | 0.013489 | 0.012273 | 0.0012709 | -0.013473 | -0.012257 | 94.1306 | 94.1306 | 94.1306 | -85.8694 | -85.8694 | -85.8694 |  | 0.1514 | 1.6911 | 1.626 | 0.15335 | 1.69 | 1.6241 | -22.7135 | -145.0554 | 148.4819 | -22.71 | -144.9998 | 148.471
Line2_1_4 | 0.040542 | 0.040542 | 0.040542 | 0.040543 | 0.040543 | 0.040543 | 0.0093629 | 0.0093629 | 0.0093629 | 0.0093629 | 0.0093629 | 0.0093629 | -0.00063512 | -0.0081642 | 0.008824 | 0.00064335 | 0.0081725 | -0.0088159 | -0.0012673 | 0.013566 | 0.012406 | 0.0012838 | -0.013549 | -0.01239 | 93.904 | 93.904 | 93.904 | -86.096 | -86.096 | -86.096 |  | 0.1514 | 1.6911 | 1.626 | 0.15337 | 1.69 | 1.6241 | -22.7135 | -145.0554 | 148.4819 | -22.7128 | -144.9992 | 148.4712
Line3_1_5 | 0.040462 | 0.040462 | 0.040462 | 0.040462 | 0.040462 | 0.040462 | 0.0093442 | 0.0093442 | 0.0093442 | 0.0093443 | 0.0093443 | 0.0093443 | -0.00063511 | -0.0081345 | 0.0088187 | 0.0006433 | 0.0081428 | -0.0088106 | -0.0012642 | 0.013547 | 0.012373 | 0.0012806 | -0.013531 | -0.012357 | 93.961 | 93.961 | 93.961 | -86.039 | -86.039 | -86.039 |  | 0.1514 | 1.6911 | 1.626 | 0.15336 | 1.69 | 1.6241 | -22.7135 | -145.0554 | 148.4819 | -22.7121 | -144.9994 | 148.4712
Line4_2_6 | 0.44637 | 0.041352 | 0.041352 | 0.44637 | 0.041353 | 0.041353 | 0.10308 | 0.0095499 | 0.0095499 | 0.10308 | 0.00955 | 0.00955 | 0.0052631 | -0.0085034 | 0.008835 | -0.0035401 | 0.008545 | -0.0087935 | 0.010513 | 0.01367 | 0.012657 | -0.0070701 | -0.013586 | -0.012572 | -86.1227 | 93.3457 | 93.3457 | 93.8773 | -86.6543 | -86.6543 |  | 0.11405 | 1.6858 | 1.6163 | 0.076703 | 1.6806 | 1.6065 | -22.7157 | -144.7715 | 148.429 | -22.7201 | -144.4859 | 148.3755
Line5_6_7 | 0.44637 | 0.041353 | 0.041353 | 0.44637 | 0.041353 | 0.041353 | 0.10308 | 0.00955 | 0.00955 | 0.10308 | 0.0095501 | 0.0095501 | 0.0035401 | -0.008545 | 0.0087935 | -0.001817 | 0.0085867 | -0.0087519 | 0.0070701 | 0.013586 | 0.012572 | -0.0036269 | -0.013501 | -0.012488 | -86.1227 | 93.3457 | 93.3457 | 93.8773 | -86.6543 | -86.6543 |  | 0.076703 | 1.6806 | 1.6065 | 0.039353 | 1.6754 | 1.5968 | -22.7201 | -144.4859 | 148.3755 | -22.7328 | -144.1985 | 148.3214
Line6_7_8 | 0.48772 | 0 | 0 | 0.48772 | 0 | 0 | 0.11263 | 0 | 0 | 0.11263 | 0 | 0 | 0.0019822 | 2.1783e-07 | -1.9495e-07 | -2.3359e-14 | -1.5037e-07 | 1.2568e-07 | 0.0039645 | -3.1176e-07 | -3.0557e-07 | 9.4103e-15 | 2.0432e-07 | 2.0587e-07 | -86.1678 | 0 | 0 | 93.8322 | 0 | 0 |  | 0.039353 | 1.6754 | 1.5968 | 0 | 1.6714 | 1.589 | -22.7328 | -144.1985 | 148.3214 | 0 | -143.9684 | 148.2772
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6023e-20 | 7.3006e-08 | -6.4773e-08 | -2.6274e-17 | -4.3627e-09 | -3.8705e-09 | -5.3043e-21 | -1.0347e-07 | -1.0148e-07 | 1.5243e-17 | -2.614e-09 | 2.8982e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 1.6714 | 1.589 | 0 | 1.6714 | 1.589 | 0 | -143.9684 | 148.2772 | 0 | -143.9684 | 148.2772
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6023e-20 | 7.3006e-08 | -6.4773e-08 | -2.6274e-17 | -4.3627e-09 | -3.8705e-09 | -5.3043e-21 | -1.0347e-07 | -1.0148e-07 | 1.5243e-17 | -2.614e-09 | 2.8982e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 1.6714 | 1.589 | 0 | 1.6714 | 1.589 | 0 | -143.9684 | 148.2772 | 0 | -143.9684 | 148.2772
Line9_3_11 | 0.040219 | 0.040219 | 0.040219 | 0.040219 | 0.040219 | 0.040219 | 0.0092882 | 0.0092882 | 0.0092882 | 0.0092883 | 0.0092883 | 0.0092883 | -0.00064311 | -0.008054 | 0.0087942 | 0.00065121 | 0.0080621 | -0.0087862 | -0.0012709 | 0.013473 | 0.012257 | 0.0012871 | -0.013457 | -0.012241 | 94.1306 | 94.1306 | 94.1306 | -85.8694 | -85.8694 | -85.8694 |  | 0.15335 | 1.69 | 1.6241 | 0.1553 | 1.689 | 1.6222 | -22.71 | -144.9998 | 148.471 | -22.7065 | -144.9441 | 148.4602

## LG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.46693 | 0.043257 | 0.043257 | 0.46693 | 0.043258 | 0.043258 | 0.10783 | 0.0099899 | 0.0099899 | 0.10783 | 0.0099899 | 0.0099899 | 0.0076447 | -0.0092734 | 0.0097273 | -0.0057593 | 0.009319 | -0.0096819 | 0.015272 | 0.015053 | 0.013941 | -0.011504 | -0.01496 | -0.013849 | -86.1213 | 93.3471 | 93.3471 | 93.8787 | -86.6529 | -86.6529 |  | 0.15838 | 1.7698 | 1.7017 | 0.11931 | 1.7643 | 1.6915 | -22.7121 | -145.0172 | 148.4426 | -22.7143 | -144.7334 | 148.3895
Line10_11_12 | 0.042073 | 0.042073 | 0.042073 | 0.042073 | 0.042073 | 0.042073 | 0.0097163 | 0.0097163 | 0.0097163 | 0.0097163 | 0.0097163 | 0.0097163 | -0.0007126 | -0.0088358 | 0.0096281 | 0.00072145 | 0.0088447 | -0.0096193 | -0.0014084 | 0.014727 | 0.013393 | 0.0014262 | -0.01471 | -0.013376 | 94.132 | 94.132 | 94.132 | -85.868 | -85.8681 | -85.8681 |  | 0.16245 | 1.7676 | 1.6977 | 0.16449 | 1.7665 | 1.6957 | -22.7051 | -144.9059 | 148.4208 | -22.7017 | -144.8502 | 148.4098
Line11_12_13 | 0.042073 | 0.042073 | 0.042073 | 0.042073 | 0.042073 | 0.042073 | 0.0097163 | 0.0097163 | 0.0097163 | 0.0097164 | 0.0097164 | 0.0097164 | -0.00072145 | -0.0088447 | 0.0096193 | 0.00073031 | 0.0088536 | -0.0096105 | -0.0014262 | 0.01471 | 0.013376 | 0.0014439 | -0.014692 | -0.013358 | 94.1319 | 94.1319 | 94.1319 | -85.8681 | -85.8681 | -85.8681 |  | 0.16449 | 1.7665 | 1.6957 | 0.16653 | 1.7654 | 1.6936 | -22.7017 | -144.8502 | 148.4098 | -22.6985 | -144.7944 | 148.3989
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5655e-08 | 2.2427e-07 | -2.1306e-07 | -9.9184e-09 | -1.5448e-07 | 1.3753e-07 | 3.4884e-08 | -3.3771e-07 | -3.2536e-07 | -2.3515e-08 | 2.2215e-07 | 2.2015e-07 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.16653 | 1.7654 | 1.6936 | 0.16653 | 1.7654 | 1.6936 | -22.6985 | -144.7944 | 148.3989 | -22.6985 | -144.7944 | 148.3989
Line13_13_14 | 0.042074 | 0.042074 | 0.042074 | 0.042075 | 0.042075 | 0.042075 | 0.0097166 | 0.0097166 | 0.0097166 | 0.0097167 | 0.0097167 | 0.0097167 | -0.00073033 | -0.0088538 | 0.0096107 | 0.00073918 | 0.0088628 | -0.009602 | -0.0014439 | 0.014692 | 0.013359 | 0.0014616 | -0.014675 | -0.013341 | 94.1319 | 94.1319 | 94.1319 | -85.8681 | -85.8681 | -85.8681 |  | 0.16653 | 1.7654 | 1.6936 | 0.16856 | 1.7643 | 1.6916 | -22.6985 | -144.7944 | 148.3989 | -22.6952 | -144.7385 | 148.3879
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0436e-08 | 1.4951e-07 | -1.4204e-07 | -4.7002e-09 | -7.972e-08 | 6.6512e-08 | 2.3256e-08 | -2.2514e-07 | -2.1691e-07 | -1.1887e-08 | 1.0958e-07 | 1.117e-07 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.16653 | 1.7654 | 1.6936 | 0.16653 | 1.7654 | 1.6936 | -22.6985 | -144.7944 | 148.3989 | -22.6985 | -144.7944 | 148.3989
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2182e-09 | 7.4757e-08 | -7.1021e-08 | 5.1796e-10 | -4.9637e-09 | -4.5086e-09 | 1.1628e-08 | -1.1257e-07 | -1.0845e-07 | -2.5918e-10 | -2.9861e-09 | 3.2489e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.16653 | 1.7654 | 1.6936 | 0.16653 | 1.7654 | 1.6936 | -22.6985 | -144.7944 | 148.3989 | -22.6985 | -144.7944 | 148.3989
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.0267e-09 | 7.5349e-08 | -7.1311e-08 | 5.0253e-10 | -5.0029e-09 | -4.5639e-09 | 1.1283e-08 | -1.1345e-07 | -1.0974e-07 | -2.4983e-10 | -3.0104e-09 | 3.2639e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.16043 | 1.7687 | 1.6997 | 0.16043 | 1.7687 | 1.6997 | -22.7114 | -144.961 | 148.4319 | -22.7114 | -144.961 | 148.4319
Line17_5_19 | 0.042326 | 0.042326 | 0.042326 | 0.042326 | 0.042326 | 0.042326 | 0.0097748 | 0.0097748 | 0.0097748 | 0.0097749 | 0.0097749 | 0.0097749 | -0.00070395 | -0.0089241 | 0.0096549 | 0.00071291 | 0.0089331 | -0.009646 | -0.0014013 | 0.014807 | 0.01352 | 0.0014192 | -0.01479 | -0.013503 | 93.9624 | 93.9624 | 93.9624 | -86.0376 | -86.0376 | -86.0376 |  | 0.16043 | 1.7687 | 1.6997 | 0.16248 | 1.7676 | 1.6976 | -22.7107 | -144.9611 | 148.4318 | -22.7093 | -144.905 | 148.4211
Line1_1_3 | 0.042072 | 0.042072 | 0.042072 | 0.042072 | 0.042072 | 0.042072 | 0.0097161 | 0.0097161 | 0.0097161 | 0.0097162 | 0.0097162 | 0.0097162 | -0.00069489 | -0.0088179 | 0.0096456 | 0.00070374 | 0.0088268 | -0.0096369 | -0.001373 | 0.014762 | 0.013429 | 0.0013907 | -0.014745 | -0.013411 | 94.132 | 94.132 | 94.132 | -85.868 | -85.868 | -85.868 |  | 0.15838 | 1.7698 | 1.7017 | 0.16042 | 1.7687 | 1.6997 | -22.7121 | -145.0172 | 148.4426 | -22.7086 | -144.9616 | 148.4317
Line2_1_4 | 0.04241 | 0.04241 | 0.04241 | 0.042411 | 0.042411 | 0.042411 | 0.0097943 | 0.0097943 | 0.0097943 | 0.0097943 | 0.0097943 | 0.0097943 | -0.000695 | -0.0089476 | 0.0096696 | 0.000704 | 0.0089567 | -0.0096607 | -0.0013868 | 0.014846 | 0.013575 | 0.0014048 | -0.014828 | -0.013557 | 93.9054 | 93.9054 | 93.9054 | -86.0946 | -86.0946 | -86.0946 |  | 0.15838 | 1.7698 | 1.7017 | 0.16043 | 1.7687 | 1.6997 | -22.7121 | -145.0172 | 148.4426 | -22.7114 | -144.961 | 148.4319
Line3_1_5 | 0.042326 | 0.042326 | 0.042326 | 0.042326 | 0.042326 | 0.042326 | 0.0097747 | 0.0097747 | 0.0097747 | 0.0097748 | 0.0097748 | 0.0097748 | -0.00069499 | -0.008915 | 0.0096638 | 0.00070395 | 0.0089241 | -0.0096549 | -0.0013834 | 0.014825 | 0.013538 | 0.0014013 | -0.014807 | -0.01352 | 93.9624 | 93.9624 | 93.9624 | -86.0376 | -86.0376 | -86.0376 |  | 0.15838 | 1.7698 | 1.7017 | 0.16043 | 1.7687 | 1.6997 | -22.7121 | -145.0172 | 148.4426 | -22.7107 | -144.9611 | 148.4318
Line4_2_6 | 0.46693 | 0.043258 | 0.043258 | 0.46693 | 0.043258 | 0.043258 | 0.10783 | 0.0099899 | 0.0099899 | 0.10783 | 0.00999 | 0.00999 | 0.0057593 | -0.009319 | 0.0096819 | -0.0038738 | 0.0093646 | -0.0096365 | 0.011504 | 0.01496 | 0.013849 | -0.0077367 | -0.014868 | -0.013757 | -86.1213 | 93.3471 | 93.3471 | 93.8787 | -86.6529 | -86.6529 |  | 0.11931 | 1.7643 | 1.6915 | 0.080237 | 1.7589 | 1.6813 | -22.7143 | -144.7334 | 148.3895 | -22.7187 | -144.4478 | 148.3358
Line5_6_7 | 0.46693 | 0.043258 | 0.043258 | 0.46693 | 0.043258 | 0.043258 | 0.10783 | 0.00999 | 0.00999 | 0.10783 | 0.0099901 | 0.0099901 | 0.0038738 | -0.0093646 | 0.0096365 | -0.0019883 | 0.0094102 | -0.009591 | 0.0077367 | 0.014868 | 0.013757 | -0.0039688 | -0.014775 | -0.013664 | -86.1213 | 93.3471 | 93.3471 | 93.8787 | -86.6529 | -86.6529 |  | 0.080237 | 1.7589 | 1.6813 | 0.041166 | 1.7535 | 1.6711 | -22.7187 | -144.4478 | 148.3358 | -22.7314 | -144.1604 | 148.2814
Line6_7_8 | 0.51019 | 1.0282e-06 | 1.0282e-06 | 0.51019 | 0 | 0 | 0.11782 | 2.3746e-07 | 2.3746e-07 | 0.11782 | 0 | 0 | 0.0021691 | 2.3869e-07 | -2.1368e-07 | -1.7742e-14 | -1.6476e-07 | 1.3776e-07 | 0.0043382 | -3.4117e-07 | -3.3436e-07 | 1.3382e-14 | 2.236e-07 | 2.2526e-07 | -86.1664 | -89.1376 | -89.1376 | 93.8336 | 0 | 0 |  | 0.041166 | 1.7535 | 1.6711 | 0 | 1.7492 | 1.6629 | -22.7314 | -144.1604 | 148.2814 | 0 | -143.9303 | 148.2371
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2435e-20 | 7.9996e-08 | -7.0995e-08 | -2.8789e-17 | -4.7703e-09 | -4.2306e-09 | -8.1977e-21 | -1.1323e-07 | -1.1105e-07 | 1.6713e-17 | -2.8617e-09 | 3.1733e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 1.7492 | 1.6629 | 0 | 1.7492 | 1.6629 | 0 | -143.9303 | 148.2371 | 0 | -143.9303 | 148.2371
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2435e-20 | 7.9996e-08 | -7.0995e-08 | -2.8789e-17 | -4.7703e-09 | -4.2306e-09 | -8.1977e-21 | -1.1323e-07 | -1.1105e-07 | 1.6713e-17 | -2.8617e-09 | 3.1733e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 1.7492 | 1.6629 | 0 | 1.7492 | 1.6629 | 0 | -143.9303 | 148.2371 | 0 | -143.9303 | 148.2371
Line9_3_11 | 0.042072 | 0.042072 | 0.042072 | 0.042073 | 0.042073 | 0.042073 | 0.0097162 | 0.0097162 | 0.0097162 | 0.0097163 | 0.0097163 | 0.0097163 | -0.00070374 | -0.0088268 | 0.0096369 | 0.0007126 | 0.0088358 | -0.0096281 | -0.0013907 | 0.014745 | 0.013411 | 0.0014084 | -0.014727 | -0.013393 | 94.132 | 94.132 | 94.132 | -85.868 | -85.868 | -85.868 |  | 0.16042 | 1.7687 | 1.6997 | 0.16245 | 1.7676 | 1.6977 | -22.7086 | -144.9616 | 148.4317 | -22.7051 | -144.9059 | 148.4208

## LG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.029779 | 0.0027588 | 0.0027588 | 0.029779 | 0.0027588 | 0.0027588 | 0.0068771 | 0.00063711 | 0.00063711 | 0.0068771 | 0.00063711 | 0.00063711 | 0.0048796 | -0.00020714 | 0.00065397 | -0.0048719 | 0.00020733 | -0.00065379 | 0.004903 | 0.0006729 | -0.00010236 | -0.0048876 | -0.00067252 | 0.00010273 | -47.4719 | 131.9965 | 131.9965 | 132.5281 | -48.0035 | -48.0035 |  | 1.0058 | 1.1051 | 1.039 | 1.0035 | 1.1046 | 1.0388 | -2.3348 | -120.8935 | 123.1009 | -2.3795 | -120.87 | 123.0662
Line10_11_12 | 0.0026832 | 0.0026832 | 0.0026832 | 0.0026832 | 0.0026832 | 0.0026832 | 0.00061966 | 0.00061966 | 0.00061966 | 0.00061966 | 0.00061966 | 0.00061966 | -0.00044169 | -0.00019255 | 0.00063457 | 0.00044173 | 0.00019259 | -0.00063454 | -0.00043997 | 0.00065702 | -0.0001084 | 0.00044005 | -0.00065695 | 0.00010847 | 132.7813 | 132.7813 | 132.7813 | -47.2187 | -47.2187 | -47.2187 |  | 1.0061 | 1.1049 | 1.0389 | 1.0062 | 1.1048 | 1.0389 | -2.3301 | -120.8843 | 123.0872 | -2.3278 | -120.8797 | 123.0804
Line11_12_13 | 0.0026832 | 0.0026832 | 0.0026832 | 0.0026832 | 0.0026832 | 0.0026832 | 0.00061966 | 0.00061966 | 0.00061966 | 0.00061967 | 0.00061967 | 0.00061967 | -0.00044173 | -0.00019259 | 0.00063454 | 0.00044177 | 0.00019263 | -0.00063451 | -0.00044005 | 0.00065695 | -0.00010847 | 0.00044012 | -0.00065689 | 0.00010855 | 132.7813 | 132.7813 | 132.7813 | -47.2187 | -47.2187 | -47.2187 |  | 1.0062 | 1.1048 | 1.0389 | 1.0063 | 1.1047 | 1.0388 | -2.3278 | -120.8797 | 123.0804 | -2.3254 | -120.8751 | 123.0735
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.9459e-09 | 5.2297e-09 | -1.5094e-08 | -6.4726e-09 | -3.7085e-09 | 1.0099e-08 | 1.0873e-08 | -1.531e-08 | 1.9045e-09 | -7.4061e-09 | 1.0141e-08 | -1.0552e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0063 | 1.1047 | 1.0388 | 1.0063 | 1.1047 | 1.0388 | -2.3254 | -120.8751 | 123.0735 | -2.3254 | -120.8751 | 123.0735
Line13_13_14 | 0.0026833 | 0.0026833 | 0.0026833 | 0.0026833 | 0.0026833 | 0.0026833 | 0.00061968 | 0.00061968 | 0.00061968 | 0.00061969 | 0.00061969 | 0.00061969 | -0.00044178 | -0.00019264 | 0.00063452 | 0.00044182 | 0.00019267 | -0.00063449 | -0.00044014 | 0.0006569 | -0.00010855 | 0.00044021 | -0.00065684 | 0.00010862 | 132.7812 | 132.7812 | 132.7812 | -47.2188 | -47.2188 | -47.2188 |  | 1.0063 | 1.1047 | 1.0388 | 1.0065 | 1.1046 | 1.0388 | -2.3254 | -120.8751 | 123.0735 | -2.3231 | -120.8705 | 123.0667
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.6306e-09 | 3.4865e-09 | -1.0062e-08 | -3.1574e-09 | -1.9653e-09 | 5.068e-09 | 7.2489e-09 | -1.0206e-08 | 1.2696e-09 | -3.7816e-09 | 5.0382e-09 | -4.2038e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0063 | 1.1047 | 1.0388 | 1.0063 | 1.1047 | 1.0388 | -2.3254 | -120.8751 | 123.0735 | -2.3254 | -120.8751 | 123.0735
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3153e-09 | 1.7432e-09 | -5.0312e-09 | 1.5793e-10 | -2.2207e-10 | 3.6835e-11 | 3.6244e-09 | -5.1032e-09 | 6.3482e-10 | -1.572e-10 | -6.4959e-11 | 2.1444e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0063 | 1.1047 | 1.0388 | 1.0063 | 1.1047 | 1.0388 | -2.3254 | -120.8751 | 123.0735 | -2.3254 | -120.8751 | 123.0735
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3236e-09 | 1.7681e-09 | -5.0639e-09 | 1.5921e-10 | -2.233e-10 | 3.6334e-11 | 3.6542e-09 | -5.1302e-09 | 6.219e-10 | -1.5762e-10 | -6.5993e-11 | 2.1589e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.006 | 1.105 | 1.0389 | 1.006 | 1.105 | 1.0389 | -2.3325 | -120.8888 | 123.094 | -2.3325 | -120.8888 | 123.094
Line17_5_19 | 0.0026994 | 0.0026994 | 0.0026994 | 0.0026994 | 0.0026994 | 0.0026994 | 0.00062339 | 0.00062339 | 0.00062339 | 0.0006234 | 0.0006234 | 0.0006234 | -0.000443 | -0.00019563 | 0.00063875 | 0.00044304 | 0.00019567 | -0.00063871 | -0.00044387 | 0.00066048 | -0.00010709 | 0.00044394 | -0.00066041 | 0.00010717 | 132.6117 | 132.6117 | 132.6117 | -47.3883 | -47.3883 | -47.3883 |  | 1.006 | 1.105 | 1.0389 | 1.0061 | 1.1049 | 1.0389 | -2.3325 | -120.8888 | 123.094 | -2.3302 | -120.8842 | 123.0872
Line1_1_3 | 0.0026832 | 0.0026832 | 0.0026832 | 0.0026832 | 0.0026832 | 0.0026832 | 0.00061965 | 0.00061965 | 0.00061965 | 0.00061965 | 0.00061965 | 0.00061965 | -0.00044161 | -0.00019248 | 0.00063463 | 0.00044165 | 0.00019252 | -0.0006346 | -0.00043982 | 0.00065715 | -0.00010826 | 0.0004399 | -0.00065709 | 0.00010833 | 132.7814 | 132.7814 | 132.7814 | -47.2186 | -47.2186 | -47.2186 |  | 1.0058 | 1.1051 | 1.039 | 1.006 | 1.105 | 1.0389 | -2.3348 | -120.8935 | 123.1009 | -2.3325 | -120.8889 | 123.0941
Line2_1_4 | 0.0027047 | 0.0027047 | 0.0027047 | 0.0027048 | 0.0027048 | 0.0027048 | 0.00062463 | 0.00062463 | 0.00062463 | 0.00062464 | 0.00062464 | 0.00062464 | -0.00044341 | -0.00019665 | 0.00064016 | 0.00044345 | 0.00019668 | -0.00064013 | -0.00044512 | 0.00066167 | -0.0001066 | 0.00044519 | -0.0006616 | 0.00010667 | 132.5548 | 132.5548 | 132.5548 | -47.4452 | -47.4452 | -47.4452 |  | 1.0058 | 1.1051 | 1.039 | 1.006 | 1.105 | 1.0389 | -2.3348 | -120.8935 | 123.1009 | -2.3325 | -120.8888 | 123.094
Line3_1_5 | 0.0026993 | 0.0026993 | 0.0026993 | 0.0026994 | 0.0026994 | 0.0026994 | 0.00062339 | 0.00062339 | 0.00062339 | 0.00062339 | 0.00062339 | 0.00062339 | -0.00044296 | -0.0001956 | 0.00063878 | 0.000443 | 0.00019563 | -0.00063875 | -0.00044379 | 0.00066054 | -0.00010702 | 0.00044387 | -0.00066048 | 0.00010709 | 132.6117 | 132.6117 | 132.6117 | -47.3883 | -47.3883 | -47.3883 |  | 1.0058 | 1.1051 | 1.039 | 1.006 | 1.105 | 1.0389 | -2.3348 | -120.8935 | 123.1009 | -2.3325 | -120.8888 | 123.094
Line4_2_6 | 0.029779 | 0.0027588 | 0.0027588 | 0.029779 | 0.0027588 | 0.0027588 | 0.0068771 | 0.00063711 | 0.00063711 | 0.0068771 | 0.00063712 | 0.00063712 | 0.0048719 | -0.00020733 | 0.00065379 | -0.0048642 | 0.00020751 | -0.00065361 | 0.0048876 | 0.00067252 | -0.00010273 | -0.0048723 | -0.00067215 | 0.00010311 | -47.4719 | 131.9965 | 131.9965 | 132.5281 | -48.0035 | -48.0035 |  | 1.0035 | 1.1046 | 1.0388 | 1.0011 | 1.1041 | 1.0386 | -2.3795 | -120.87 | 123.0662 | -2.4243 | -120.8466 | 123.0315
Line5_6_7 | 0.029779 | 0.0027588 | 0.0027588 | 0.029779 | 0.0027588 | 0.0027588 | 0.0068771 | 0.00063712 | 0.00063712 | 0.0068771 | 0.00063712 | 0.00063712 | 0.0048642 | -0.00020751 | 0.00065361 | -0.0048565 | 0.0002077 | -0.00065343 | 0.0048723 | 0.00067215 | -0.00010311 | -0.004857 | -0.00067178 | 0.00010349 | -47.4719 | 131.9965 | 131.9965 | 132.5281 | -48.0035 | -48.0035 |  | 1.0011 | 1.1041 | 1.0386 | 0.99875 | 1.1036 | 1.0384 | -2.4243 | -120.8466 | 123.0315 | -2.4694 | -120.8231 | 122.9968
Line6_7_8 | 0.032538 | 0 | 0 | 0.032538 | 0 | 0 | 0.0075142 | 0 | 0 | 0.0075142 | 0 | 0 | 0.0053023 | 5.6251e-09 | -1.5624e-08 | -0.0052935 | -3.9791e-09 | 1.0468e-08 | 0.0053111 | -1.5738e-08 | 1.7836e-09 | -0.0052935 | 1.044e-08 | -9.8243e-10 | -47.517 | 0 | 0 | 132.483 | 0 | 0 |  | 0.99875 | 1.1036 | 1.0384 | 0.99625 | 1.1033 | 1.0382 | -2.4694 | -120.8231 | 122.9968 | -2.517 | -120.8044 | 122.9691
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3163e-09 | 1.8816e-09 | -5.2141e-09 | 1.9263e-10 | -2.1589e-10 | 3.9438e-11 | 3.765e-09 | -5.2496e-09 | 5.9474e-10 | -1.6844e-10 | -5.9635e-11 | 2.0705e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.99625 | 1.1033 | 1.0382 | 0.99625 | 1.1033 | 1.0382 | -2.517 | -120.8044 | 122.9691 | -2.517 | -120.8044 | 122.9691
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3163e-09 | 1.8816e-09 | -5.2141e-09 | 1.9263e-10 | -2.1589e-10 | 3.9438e-11 | 3.765e-09 | -5.2496e-09 | 5.9474e-10 | -1.6844e-10 | -5.9635e-11 | 2.0705e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.99625 | 1.1033 | 1.0382 | 0.99625 | 1.1033 | 1.0382 | -2.517 | -120.8044 | 122.9691 | -2.517 | -120.8044 | 122.9691
Line9_3_11 | 0.0026832 | 0.0026832 | 0.0026832 | 0.0026832 | 0.0026832 | 0.0026832 | 0.00061965 | 0.00061965 | 0.00061965 | 0.00061966 | 0.00061966 | 0.00061966 | -0.00044165 | -0.00019252 | 0.0006346 | 0.00044169 | 0.00019255 | -0.00063457 | -0.0004399 | 0.00065709 | -0.00010833 | 0.00043997 | -0.00065702 | 0.0001084 | 132.7814 | 132.7813 | 132.7813 | -47.2187 | -47.2187 | -47.2187 |  | 1.006 | 1.105 | 1.0389 | 1.0061 | 1.1049 | 1.0389 | -2.3325 | -120.8889 | 123.0941 | -2.3301 | -120.8843 | 123.0872

## LG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.031195 | 0.0028899 | 0.0028899 | 0.031194 | 0.0028899 | 0.0028899 | 0.0072041 | 0.00066739 | 0.00066739 | 0.0072041 | 0.0006674 | 0.0006674 | 0.0053545 | -0.00022736 | 0.00071769 | -0.0053461 | 0.00022757 | -0.00071749 | 0.0053802 | 0.0007384 | -0.00011233 | -0.0053634 | -0.00073799 | 0.00011274 | -47.4754 | 131.993 | 131.993 | 132.5246 | -48.007 | -48.007 |  | 1.0537 | 1.1577 | 1.0885 | 1.0512 | 1.1571 | 1.0882 | -2.3383 | -120.8926 | 123.0979 | -2.3829 | -120.8692 | 123.0632
Line10_11_12 | 0.0028108 | 0.0028108 | 0.0028108 | 0.0028108 | 0.0028108 | 0.0028108 | 0.00064912 | 0.00064912 | 0.00064912 | 0.00064912 | 0.00064912 | 0.00064912 | -0.00048468 | -0.00021136 | 0.00069639 | 0.00048472 | 0.0002114 | -0.00069636 | -0.0004828 | 0.00072098 | -0.00011896 | 0.00048288 | -0.0007209 | 0.00011904 | 132.7779 | 132.7779 | 132.7779 | -47.2221 | -47.2221 | -47.2221 |  | 1.0539 | 1.1575 | 1.0884 | 1.054 | 1.1574 | 1.0883 | -2.3336 | -120.8834 | 123.0842 | -2.3312 | -120.8788 | 123.0773
Line11_12_13 | 0.0028108 | 0.0028108 | 0.0028108 | 0.0028108 | 0.0028108 | 0.0028108 | 0.00064912 | 0.00064912 | 0.00064912 | 0.00064913 | 0.00064913 | 0.00064913 | -0.00048472 | -0.0002114 | 0.00069636 | 0.00048477 | 0.00021144 | -0.00069633 | -0.00048288 | 0.0007209 | -0.00011904 | 0.00048296 | -0.00072083 | 0.00011912 | 132.7779 | 132.7779 | 132.7779 | -47.2221 | -47.2221 | -47.2221 |  | 1.054 | 1.1574 | 1.0883 | 1.0542 | 1.1573 | 1.0883 | -2.3312 | -120.8788 | 123.0773 | -2.3289 | -120.8743 | 123.0705
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0913e-08 | 5.7395e-09 | -1.6564e-08 | -7.1017e-09 | -4.0698e-09 | 1.1083e-08 | 1.1932e-08 | -1.68e-08 | 2.0906e-09 | -8.1277e-09 | 1.1129e-08 | -1.1586e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0542 | 1.1573 | 1.0883 | 1.0542 | 1.1573 | 1.0883 | -2.3289 | -120.8743 | 123.0705 | -2.3289 | -120.8743 | 123.0705
Line13_13_14 | 0.0028109 | 0.0028109 | 0.0028109 | 0.0028109 | 0.0028109 | 0.0028109 | 0.00064914 | 0.00064914 | 0.00064914 | 0.00064915 | 0.00064915 | 0.00064915 | -0.00048478 | -0.00021145 | 0.00069634 | 0.00048482 | 0.00021149 | -0.00069631 | -0.00048298 | 0.00072085 | -0.00011912 | 0.00048306 | -0.00072077 | 0.0001192 | 132.7778 | 132.7778 | 132.7778 | -47.2222 | -47.2222 | -47.2222 |  | 1.0542 | 1.1573 | 1.0883 | 1.0543 | 1.1572 | 1.0883 | -2.3289 | -120.8743 | 123.0705 | -2.3265 | -120.8697 | 123.0636
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.2753e-09 | 3.8263e-09 | -1.1043e-08 | -3.464e-09 | -2.1566e-09 | 5.5618e-09 | 7.955e-09 | -1.12e-08 | 1.3937e-09 | -4.1503e-09 | 5.5288e-09 | -4.6173e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0542 | 1.1573 | 1.0883 | 1.0542 | 1.1573 | 1.0883 | -2.3289 | -120.8743 | 123.0705 | -2.3289 | -120.8743 | 123.0705
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6377e-09 | 1.9132e-09 | -5.5214e-09 | 1.7363e-10 | -2.4348e-10 | 4.0404e-11 | 3.9775e-09 | -5.6e-09 | 6.9685e-10 | -1.7278e-10 | -7.1218e-11 | 2.3512e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0542 | 1.1573 | 1.0883 | 1.0542 | 1.1573 | 1.0883 | -2.3289 | -120.8743 | 123.0705 | -2.3289 | -120.8743 | 123.0705
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6468e-09 | 1.9404e-09 | -5.5573e-09 | 1.7503e-10 | -2.4482e-10 | 3.9855e-11 | 4.0101e-09 | -5.6297e-09 | 6.8266e-10 | -1.7324e-10 | -7.2353e-11 | 2.3671e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0538 | 1.1576 | 1.0884 | 1.0538 | 1.1576 | 1.0884 | -2.336 | -120.888 | 123.091 | -2.336 | -120.888 | 123.091
Line17_5_19 | 0.0028277 | 0.0028277 | 0.0028277 | 0.0028277 | 0.0028277 | 0.0028277 | 0.00065303 | 0.00065303 | 0.00065303 | 0.00065303 | 0.00065303 | 0.00065303 | -0.00048612 | -0.00021474 | 0.00070098 | 0.00048617 | 0.00021478 | -0.00070095 | -0.00048707 | 0.00072477 | -0.00011752 | 0.00048715 | -0.00072469 | 0.0001176 | 132.6083 | 132.6083 | 132.6083 | -47.3917 | -47.3917 | -47.3917 |  | 1.0538 | 1.1576 | 1.0884 | 1.0539 | 1.1575 | 1.0884 | -2.3359 | -120.888 | 123.091 | -2.3336 | -120.8833 | 123.0841
Line1_1_3 | 0.0028107 | 0.0028107 | 0.0028107 | 0.0028107 | 0.0028107 | 0.0028107 | 0.0006491 | 0.0006491 | 0.0006491 | 0.00064911 | 0.00064911 | 0.00064911 | -0.00048459 | -0.00021127 | 0.00069646 | 0.00048464 | 0.00021132 | -0.00069643 | -0.00048263 | 0.00072112 | -0.0001188 | 0.00048271 | -0.00072105 | 0.00011888 | 132.7779 | 132.7779 | 132.7779 | -47.2221 | -47.2221 | -47.2221 |  | 1.0537 | 1.1577 | 1.0885 | 1.0538 | 1.1576 | 1.0884 | -2.3383 | -120.8926 | 123.0979 | -2.3359 | -120.888 | 123.091
Line2_1_4 | 0.0028333 | 0.0028333 | 0.0028333 | 0.0028333 | 0.0028333 | 0.0028333 | 0.00065433 | 0.00065433 | 0.00065433 | 0.00065433 | 0.00065433 | 0.00065433 | -0.00048656 | -0.00021585 | 0.00070253 | 0.00048661 | 0.00021589 | -0.0007025 | -0.00048844 | 0.00072608 | -0.00011698 | 0.00048853 | -0.000726 | 0.00011706 | 132.5513 | 132.5513 | 132.5513 | -47.4487 | -47.4487 | -47.4487 |  | 1.0537 | 1.1577 | 1.0885 | 1.0538 | 1.1576 | 1.0884 | -2.3383 | -120.8926 | 123.0979 | -2.336 | -120.888 | 123.091
Line3_1_5 | 0.0028277 | 0.0028277 | 0.0028277 | 0.0028277 | 0.0028277 | 0.0028277 | 0.00065302 | 0.00065302 | 0.00065302 | 0.00065303 | 0.00065303 | 0.00065303 | -0.00048608 | -0.0002147 | 0.00070101 | 0.00048612 | 0.00021474 | -0.00070098 | -0.00048699 | 0.00072484 | -0.00011744 | 0.00048707 | -0.00072477 | 0.00011752 | 132.6083 | 132.6083 | 132.6083 | -47.3917 | -47.3917 | -47.3917 |  | 1.0537 | 1.1577 | 1.0885 | 1.0538 | 1.1576 | 1.0884 | -2.3383 | -120.8926 | 123.0979 | -2.3359 | -120.888 | 123.091
Line4_2_6 | 0.031194 | 0.0028899 | 0.0028899 | 0.031194 | 0.0028899 | 0.0028899 | 0.0072041 | 0.0006674 | 0.0006674 | 0.0072041 | 0.0006674 | 0.0006674 | 0.0053461 | -0.00022757 | 0.00071749 | -0.0053377 | 0.00022777 | -0.00071729 | 0.0053634 | 0.00073799 | -0.00011274 | -0.0053466 | -0.00073758 | 0.00011315 | -47.4754 | 131.993 | 131.993 | 132.5246 | -48.007 | -48.007 |  | 1.0512 | 1.1571 | 1.0882 | 1.0487 | 1.1566 | 1.088 | -2.3829 | -120.8692 | 123.0632 | -2.4278 | -120.8457 | 123.0285
Line5_6_7 | 0.031194 | 0.0028899 | 0.0028899 | 0.031194 | 0.00289 | 0.00289 | 0.0072041 | 0.0006674 | 0.0006674 | 0.007204 | 0.00066741 | 0.00066741 | 0.0053377 | -0.00022777 | 0.00071729 | -0.0053293 | 0.00022798 | -0.0007171 | 0.0053466 | 0.00073758 | -0.00011315 | -0.0053297 | -0.00073717 | 0.00011357 | -47.4754 | 131.993 | 131.993 | 132.5246 | -48.007 | -48.007 |  | 1.0487 | 1.1566 | 1.088 | 1.0462 | 1.1561 | 1.0878 | -2.4278 | -120.8457 | 123.0285 | -2.4728 | -120.8223 | 122.9938
Line6_7_8 | 0.034084 | 0 | 0 | 0.034084 | 0 | 0 | 0.0078714 | 0 | 0 | 0.0078714 | 0 | 0 | 0.0058184 | 6.1734e-09 | -1.7146e-08 | -0.0058087 | -4.3668e-09 | 1.1487e-08 | 0.0058281 | -1.7271e-08 | 1.9579e-09 | -0.0058087 | 1.1456e-08 | -1.0787e-09 | -47.5204 | 0 | 0 | 132.4796 | 0 | 0 |  | 1.0462 | 1.1561 | 1.0878 | 1.0436 | 1.1557 | 1.0877 | -2.4728 | -120.8223 | 122.9938 | -2.5204 | -120.8036 | 122.9661
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6388e-09 | 2.0651e-09 | -5.7221e-09 | 2.1169e-10 | -2.3669e-10 | 4.3261e-11 | 4.1317e-09 | -5.7607e-09 | 6.5286e-10 | -1.851e-10 | -6.5375e-11 | 2.27e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0436 | 1.1557 | 1.0877 | 1.0436 | 1.1557 | 1.0877 | -2.5204 | -120.8036 | 122.9661 | -2.5204 | -120.8036 | 122.9661
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6388e-09 | 2.0651e-09 | -5.7221e-09 | 2.1169e-10 | -2.3669e-10 | 4.3261e-11 | 4.1317e-09 | -5.7607e-09 | 6.5286e-10 | -1.851e-10 | -6.5375e-11 | 2.27e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0436 | 1.1557 | 1.0877 | 1.0436 | 1.1557 | 1.0877 | -2.5204 | -120.8036 | 122.9661 | -2.5204 | -120.8036 | 122.9661
Line9_3_11 | 0.0028107 | 0.0028107 | 0.0028107 | 0.0028108 | 0.0028108 | 0.0028108 | 0.00064911 | 0.00064911 | 0.00064911 | 0.00064912 | 0.00064912 | 0.00064912 | -0.00048464 | -0.00021132 | 0.00069643 | 0.00048468 | 0.00021136 | -0.00069639 | -0.00048272 | 0.00072105 | -0.00011888 | 0.0004828 | -0.00072098 | 0.00011896 | 132.7779 | 132.7779 | 132.7779 | -47.2221 | -47.2221 | -47.2221 |  | 1.0538 | 1.1576 | 1.0884 | 1.0539 | 1.1575 | 1.0884 | -2.3359 | -120.888 | 123.091 | -2.3336 | -120.8834 | 123.0842

## LG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.40106 | 0.037161 | 0.037161 | 0.40106 | 0.037162 | 0.037162 | 0.092621 | 0.008582 | 0.008582 | 0.092621 | 0.0085821 | 0.0085821 | 0.010829 | -0.0066971 | 0.0073401 | -0.0081579 | 0.0067616 | -0.0072757 | 0.01126 | 0.011472 | 0.0099329 | -0.0084819 | -0.011403 | -0.0098641 | -82.7237 | 96.2558 | 96.2558 | 97.2763 | -83.7442 | -83.7442 |  | 0.16867 | 1.5478 | 1.4391 | 0.12706 | 1.5447 | 1.4282 | -36.604 | -143.4681 | 149.7926 | -36.6083 | -143.0772 | 149.8435
Line10_11_12 | 0.036136 | 0.036136 | 0.036136 | 0.036137 | 0.036137 | 0.036137 | 0.0083453 | 0.0083453 | 0.0083453 | 0.0083454 | 0.0083454 | 0.0083454 | -0.0010093 | -0.0062419 | 0.0073641 | 0.0010219 | 0.0062545 | -0.0073516 | -0.0010324 | 0.011297 | 0.0094419 | 0.0010455 | -0.011284 | -0.0094289 | 97.7625 | 97.7625 | 97.7625 | -82.2375 | -82.2375 | -82.2375 |  | 0.17301 | 1.5465 | 1.4348 | 0.17518 | 1.5459 | 1.4327 | -36.5906 | -143.3147 | 149.8103 | -36.5841 | -143.238 | 149.8192
Line11_12_13 | 0.036137 | 0.036137 | 0.036137 | 0.036137 | 0.036137 | 0.036137 | 0.0083454 | 0.0083454 | 0.0083454 | 0.0083455 | 0.0083455 | 0.0083455 | -0.0010219 | -0.0062545 | 0.0073516 | 0.0010344 | 0.0062671 | -0.0073391 | -0.0010455 | 0.011284 | 0.0094289 | 0.0010585 | -0.011271 | -0.0094159 | 97.7625 | 97.7625 | 97.7625 | -82.2375 | -82.2375 | -82.2375 |  | 0.17518 | 1.5459 | 1.4327 | 0.17734 | 1.5453 | 1.4305 | -36.5841 | -143.238 | 149.8192 | -36.5778 | -143.1611 | 149.8281
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3232e-08 | 1.5989e-07 | -1.6331e-07 | -1.5107e-08 | -1.104e-07 | 1.0569e-07 | 2.6143e-08 | -2.5946e-07 | -2.3008e-07 | -1.7797e-08 | 1.7086e-07 | 1.5586e-07 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.17734 | 1.5453 | 1.4305 | 0.17734 | 1.5453 | 1.4305 | -36.5778 | -143.1611 | 149.8281 | -36.5778 | -143.1611 | 149.8281
Line13_13_14 | 0.036138 | 0.036138 | 0.036138 | 0.036138 | 0.036138 | 0.036138 | 0.0083457 | 0.0083457 | 0.0083457 | 0.0083457 | 0.0083457 | 0.0083457 | -0.0010344 | -0.0062672 | 0.0073393 | 0.001047 | 0.0062798 | -0.0073268 | -0.0010585 | 0.011271 | 0.0094161 | 0.0010716 | -0.011258 | -0.0094031 | 97.7624 | 97.7624 | 97.7624 | -82.2376 | -82.2376 | -82.2376 |  | 0.17734 | 1.5453 | 1.4305 | 0.17951 | 1.5446 | 1.4283 | -36.5778 | -143.1611 | 149.8281 | -36.5717 | -143.0842 | 149.8371
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5488e-08 | 1.066e-07 | -1.0887e-07 | -7.3633e-09 | -5.7105e-08 | 5.1255e-08 | 1.7428e-08 | -1.7297e-07 | -1.5338e-07 | -9.0823e-09 | 8.437e-08 | 7.917e-08 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.17734 | 1.5453 | 1.4305 | 0.17734 | 1.5453 | 1.4305 | -36.5778 | -143.1611 | 149.8281 | -36.5778 | -143.1611 | 149.8281
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7441e-09 | 5.3298e-08 | -5.4436e-08 | 3.8076e-10 | -3.8065e-09 | -3.1805e-09 | 8.7142e-09 | -8.6487e-08 | -7.6692e-08 | -3.6813e-10 | -2.1171e-09 | 2.4785e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.17734 | 1.5453 | 1.4305 | 0.17734 | 1.5453 | 1.4305 | -36.5778 | -143.1611 | 149.8281 | -36.5778 | -143.1611 | 149.8281
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4614e-09 | 5.3831e-08 | -5.4605e-08 | 3.7074e-10 | -3.8308e-09 | -3.2277e-09 | 8.485e-09 | -8.7026e-08 | -7.7787e-08 | -3.5486e-10 | -2.1396e-09 | 2.4877e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.17086 | 1.5472 | 1.437 | 0.17086 | 1.5472 | 1.437 | -36.6027 | -143.3907 | 149.8022 | -36.6027 | -143.3907 | 149.8022
Line17_5_19 | 0.036355 | 0.036355 | 0.036355 | 0.036355 | 0.036355 | 0.036355 | 0.0083959 | 0.0083959 | 0.0083959 | 0.0083959 | 0.0083959 | 0.0083959 | -0.00099714 | -0.0063318 | 0.007367 | 0.0010098 | 0.0063445 | -0.0073543 | -0.0010312 | 0.011342 | 0.0095541 | 0.0010444 | -0.011329 | -0.009541 | 97.437 | 97.437 | 97.437 | -82.563 | -82.563 | -82.563 |  | 0.17085 | 1.5472 | 1.437 | 0.17303 | 1.5465 | 1.4348 | -36.6013 | -143.3909 | 149.802 | -36.5987 | -143.3135 | 149.8114
Line1_1_3 | 0.036136 | 0.036136 | 0.036136 | 0.036136 | 0.036136 | 0.036136 | 0.0083452 | 0.0083452 | 0.0083452 | 0.0083453 | 0.0083453 | 0.0083453 | -0.00098424 | -0.0062167 | 0.0073891 | 0.00099679 | 0.0062293 | -0.0073766 | -0.0010063 | 0.011323 | 0.0094678 | 0.0010193 | -0.01131 | -0.0094548 | 97.7625 | 97.7625 | 97.7625 | -82.2375 | -82.2375 | -82.2375 |  | 0.16867 | 1.5478 | 1.4391 | 0.17084 | 1.5472 | 1.437 | -36.604 | -143.4681 | 149.7926 | -36.5972 | -143.3915 | 149.8015
Line2_1_4 | 0.036428 | 0.036428 | 0.036428 | 0.036428 | 0.036428 | 0.036428 | 0.0084126 | 0.0084126 | 0.0084126 | 0.0084127 | 0.0084127 | 0.0084127 | -0.00098446 | -0.0063534 | 0.0073761 | 0.00099721 | 0.0063662 | -0.0073634 | -0.0010219 | 0.011366 | 0.0096005 | 0.0010352 | -0.011353 | -0.0095873 | 97.3276 | 97.3276 | 97.3276 | -82.6724 | -82.6724 | -82.6724 |  | 0.16867 | 1.5478 | 1.4391 | 0.17086 | 1.5472 | 1.437 | -36.604 | -143.4681 | 149.7926 | -36.6027 | -143.3907 | 149.8022
Line3_1_5 | 0.036355 | 0.036355 | 0.036355 | 0.036355 | 0.036355 | 0.036355 | 0.0083958 | 0.0083958 | 0.0083958 | 0.0083959 | 0.0083959 | 0.0083959 | -0.00098444 | -0.006319 | 0.0073796 | 0.00099714 | 0.0063318 | -0.007367 | -0.001018 | 0.011355 | 0.0095673 | 0.0010312 | -0.011342 | -0.0095541 | 97.437 | 97.437 | 97.437 | -82.563 | -82.563 | -82.563 |  | 0.16867 | 1.5478 | 1.4391 | 0.17085 | 1.5472 | 1.437 | -36.604 | -143.4681 | 149.7926 | -36.6013 | -143.3909 | 149.802
Line4_2_6 | 0.40106 | 0.037162 | 0.037162 | 0.40106 | 0.037162 | 0.037162 | 0.092621 | 0.0085821 | 0.0085821 | 0.092621 | 0.0085822 | 0.0085822 | 0.0081579 | -0.0067616 | 0.0072757 | -0.0054872 | 0.0068262 | -0.0072113 | 0.0084819 | 0.011403 | 0.0098641 | -0.0057034 | -0.011334 | -0.0097952 | -82.7237 | 96.2558 | 96.2558 | 97.2763 | -83.7442 | -83.7442 |  | 0.12706 | 1.5447 | 1.4282 | 0.08545 | 1.5417 | 1.4173 | -36.6083 | -143.0772 | 149.8435 | -36.6167 | -142.6848 | 149.8952
Line5_6_7 | 0.40106 | 0.037162 | 0.037162 | 0.40106 | 0.037162 | 0.037162 | 0.092621 | 0.0085822 | 0.0085822 | 0.092621 | 0.0085822 | 0.0085822 | 0.0054872 | -0.0068262 | 0.0072113 | -0.0028164 | 0.0068907 | -0.0071468 | 0.0057034 | 0.011334 | 0.0097952 | -0.0029249 | -0.011265 | -0.0097264 | -82.7237 | 96.2557 | 96.2557 | 97.2763 | -83.7443 | -83.7443 |  | 0.08545 | 1.5417 | 1.4173 | 0.04384 | 1.5387 | 1.4064 | -36.6167 | -142.6848 | 149.8952 | -36.6411 | -142.2908 | 149.9477
Line6_7_8 | 0.43822 | 0 | 0 | 0.43822 | 0 | 0 | 0.1012 | 0 | 0 | 0.1012 | 0 | 0 | 0.0030726 | 1.7621e-07 | -1.5921e-07 | 4.7324e-16 | -1.223e-07 | 1.0239e-07 | 0.0032006 | -2.6024e-07 | -2.391e-07 | 2.3751e-15 | 1.7068e-07 | 1.6126e-07 | -82.8102 | 0 | 0 | 97.1898 | 0 | 0 |  | 0.04384 | 1.5387 | 1.4064 | 0 | 1.5364 | 1.3977 | -36.6411 | -142.2908 | 149.9477 | 0 | -141.976 | 149.9889
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.9676e-22 | 5.9303e-08 | -5.2666e-08 | -2.1528e-17 | -3.692e-09 | -2.9459e-09 | -1.6076e-21 | -8.6341e-08 | -7.9413e-08 | 2.1364e-17 | -2.0027e-09 | 2.4334e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 1.5364 | 1.3977 | 0 | 1.5364 | 1.3977 | 0 | -141.976 | 149.9889 | 0 | -141.976 | 149.9889
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.9676e-22 | 5.9303e-08 | -5.2666e-08 | -2.1528e-17 | -3.692e-09 | -2.9459e-09 | -1.6076e-21 | -8.6341e-08 | -7.9413e-08 | 2.1364e-17 | -2.0027e-09 | 2.4334e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 1.5364 | 1.3977 | 0 | 1.5364 | 1.3977 | 0 | -141.976 | 149.9889 | 0 | -141.976 | 149.9889
Line9_3_11 | 0.036136 | 0.036136 | 0.036136 | 0.036136 | 0.036136 | 0.036136 | 0.0083453 | 0.0083453 | 0.0083453 | 0.0083453 | 0.0083453 | 0.0083453 | -0.00099679 | -0.0062293 | 0.0073766 | 0.0010093 | 0.0062419 | -0.0073641 | -0.0010193 | 0.01131 | 0.0094548 | 0.0010324 | -0.011297 | -0.0094419 | 97.7625 | 97.7625 | 97.7625 | -82.2375 | -82.2375 | -82.2375 |  | 0.17084 | 1.5472 | 1.437 | 0.17301 | 1.5465 | 1.4348 | -36.5972 | -143.3915 | 149.8015 | -36.5906 | -143.3147 | 149.8103

## LG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.37995 | 0.035205 | 0.035205 | 0.37995 | 0.035206 | 0.035206 | 0.087746 | 0.0081303 | 0.0081303 | 0.087746 | 0.0081304 | 0.0081304 | 0.0097188 | -0.0060107 | 0.0065878 | -0.0073218 | 0.0060686 | -0.00653 | 0.010106 | 0.010296 | 0.0089149 | -0.0076126 | -0.010234 | -0.0088531 | -82.7237 | 96.2558 | 96.2558 | 97.2763 | -83.7442 | -83.7442 |  | 0.15979 | 1.4664 | 1.3634 | 0.12037 | 1.4634 | 1.353 | -36.604 | -143.4681 | 149.7926 | -36.6083 | -143.0772 | 149.8435
Line10_11_12 | 0.034234 | 0.034234 | 0.034234 | 0.034235 | 0.034235 | 0.034235 | 0.0079061 | 0.0079061 | 0.0079061 | 0.0079062 | 0.0079062 | 0.0079062 | -0.00090588 | -0.0056021 | 0.0066093 | 0.00091714 | 0.0056134 | -0.0065981 | -0.00092657 | 0.010139 | 0.0084741 | 0.0009383 | -0.010127 | -0.0084625 | 97.7625 | 97.7625 | 97.7625 | -82.2375 | -82.2375 | -82.2375 |  | 0.1639 | 1.4651 | 1.3593 | 0.16596 | 1.4645 | 1.3573 | -36.5906 | -143.3147 | 149.8103 | -36.5841 | -143.238 | 149.8192
Line11_12_13 | 0.034235 | 0.034235 | 0.034235 | 0.034235 | 0.034235 | 0.034235 | 0.0079062 | 0.0079062 | 0.0079062 | 0.0079062 | 0.0079062 | 0.0079062 | -0.00091714 | -0.0056134 | 0.0065981 | 0.0009284 | 0.0056247 | -0.0065869 | -0.0009383 | 0.010127 | 0.0084625 | 0.00095003 | -0.010115 | -0.0084508 | 97.7625 | 97.7625 | 97.7625 | -82.2375 | -82.2375 | -82.2375 |  | 0.16596 | 1.4645 | 1.3573 | 0.16801 | 1.4639 | 1.3552 | -36.5841 | -143.238 | 149.8192 | -36.5778 | -143.1611 | 149.8281
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0851e-08 | 1.4351e-07 | -1.4657e-07 | -1.3559e-08 | -9.9087e-08 | 9.4859e-08 | 2.3463e-08 | -2.3287e-07 | -2.0649e-07 | -1.5973e-08 | 1.5335e-07 | 1.3989e-07 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.16801 | 1.4639 | 1.3552 | 0.16801 | 1.4639 | 1.3552 | -36.5778 | -143.1611 | 149.8281 | -36.5778 | -143.1611 | 149.8281
Line13_13_14 | 0.034236 | 0.034236 | 0.034236 | 0.034236 | 0.034236 | 0.034236 | 0.0079064 | 0.0079064 | 0.0079064 | 0.0079065 | 0.0079065 | 0.0079065 | -0.00092842 | -0.0056249 | 0.0065871 | 0.00093968 | 0.0056362 | -0.0065759 | -0.00095005 | 0.010116 | 0.008451 | 0.00096178 | -0.010104 | -0.0084394 | 97.7624 | 97.7624 | 97.7624 | -82.2376 | -82.2376 | -82.2376 |  | 0.16801 | 1.4639 | 1.3552 | 0.17007 | 1.4633 | 1.3532 | -36.5778 | -143.1611 | 149.8281 | -36.5717 | -143.0842 | 149.8371
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3901e-08 | 9.5671e-08 | -9.7713e-08 | -6.6086e-09 | -5.1252e-08 | 4.6002e-08 | 1.5642e-08 | -1.5525e-07 | -1.3766e-07 | -8.1515e-09 | 7.5723e-08 | 7.1056e-08 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.16801 | 1.4639 | 1.3552 | 0.16801 | 1.4639 | 1.3552 | -36.5778 | -143.1611 | 149.8281 | -36.5778 | -143.1611 | 149.8281
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.9504e-09 | 4.7835e-08 | -4.8857e-08 | 3.4174e-10 | -3.4163e-09 | -2.8545e-09 | 7.8211e-09 | -7.7623e-08 | -6.8831e-08 | -3.304e-10 | -1.9001e-09 | 2.2245e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.16801 | 1.4639 | 1.3552 | 0.16801 | 1.4639 | 1.3552 | -36.5778 | -143.1611 | 149.8281 | -36.5778 | -143.1611 | 149.8281
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.6966e-09 | 4.8314e-08 | -4.9008e-08 | 3.3274e-10 | -3.4381e-09 | -2.8969e-09 | 7.6154e-09 | -7.8107e-08 | -6.9814e-08 | -3.1849e-10 | -1.9203e-09 | 2.2328e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.16186 | 1.4658 | 1.3613 | 0.16186 | 1.4658 | 1.3613 | -36.6027 | -143.3907 | 149.8022 | -36.6027 | -143.3907 | 149.8022
Line17_5_19 | 0.034442 | 0.034442 | 0.034442 | 0.034442 | 0.034442 | 0.034442 | 0.007954 | 0.007954 | 0.007954 | 0.007954 | 0.007954 | 0.007954 | -0.00089494 | -0.0056828 | 0.0066119 | 0.00090633 | 0.0056942 | -0.0066006 | -0.0009255 | 0.01018 | 0.0085749 | 0.00093737 | -0.010168 | -0.0085631 | 97.437 | 97.437 | 97.437 | -82.563 | -82.563 | -82.563 |  | 0.16186 | 1.4658 | 1.3613 | 0.16393 | 1.4652 | 1.3593 | -36.6013 | -143.3909 | 149.802 | -36.5987 | -143.3135 | 149.8114
Line1_1_3 | 0.034234 | 0.034234 | 0.034234 | 0.034234 | 0.034234 | 0.034234 | 0.007906 | 0.007906 | 0.007906 | 0.0079061 | 0.0079061 | 0.0079061 | -0.00088337 | -0.0055795 | 0.0066317 | 0.00089462 | 0.0055908 | -0.0066205 | -0.00090312 | 0.010162 | 0.0084974 | 0.00091484 | -0.01015 | -0.0084858 | 97.7625 | 97.7625 | 97.7625 | -82.2375 | -82.2375 | -82.2375 |  | 0.15979 | 1.4664 | 1.3634 | 0.16185 | 1.4657 | 1.3613 | -36.604 | -143.4681 | 149.7926 | -36.5972 | -143.3915 | 149.8015
Line2_1_4 | 0.03451 | 0.03451 | 0.03451 | 0.034511 | 0.034511 | 0.034511 | 0.0079698 | 0.0079698 | 0.0079698 | 0.0079699 | 0.0079699 | 0.0079699 | -0.00088356 | -0.0057022 | 0.0066201 | 0.000895 | 0.0057137 | -0.0066087 | -0.00091714 | 0.010201 | 0.0086165 | 0.00092906 | -0.010189 | -0.0086047 | 97.3276 | 97.3276 | 97.3276 | -82.6724 | -82.6724 | -82.6724 |  | 0.15979 | 1.4664 | 1.3634 | 0.16186 | 1.4658 | 1.3613 | -36.604 | -143.4681 | 149.7926 | -36.6027 | -143.3907 | 149.8022
Line3_1_5 | 0.034441 | 0.034441 | 0.034441 | 0.034442 | 0.034442 | 0.034442 | 0.0079539 | 0.0079539 | 0.0079539 | 0.007954 | 0.007954 | 0.007954 | -0.00088354 | -0.0056714 | 0.0066232 | 0.00089494 | 0.0056828 | -0.0066119 | -0.00091363 | 0.010192 | 0.0085867 | 0.0009255 | -0.01018 | -0.0085749 | 97.437 | 97.437 | 97.437 | -82.563 | -82.563 | -82.563 |  | 0.15979 | 1.4664 | 1.3634 | 0.16186 | 1.4658 | 1.3613 | -36.604 | -143.4681 | 149.7926 | -36.6013 | -143.3909 | 149.802
Line4_2_6 | 0.37995 | 0.035206 | 0.035206 | 0.37995 | 0.035206 | 0.035206 | 0.087746 | 0.0081304 | 0.0081304 | 0.087746 | 0.0081305 | 0.0081305 | 0.0073218 | -0.0060686 | 0.00653 | -0.0049248 | 0.0061265 | -0.0064722 | 0.0076126 | 0.010234 | 0.0088531 | -0.0051189 | -0.010172 | -0.0087913 | -82.7237 | 96.2558 | 96.2558 | 97.2763 | -83.7442 | -83.7442 |  | 0.12037 | 1.4634 | 1.353 | 0.080952 | 1.4605 | 1.3427 | -36.6083 | -143.0772 | 149.8435 | -36.6167 | -142.6848 | 149.8952
Line5_6_7 | 0.37995 | 0.035206 | 0.035206 | 0.37995 | 0.035206 | 0.035206 | 0.087746 | 0.0081305 | 0.0081305 | 0.087746 | 0.0081305 | 0.0081305 | 0.0049248 | -0.0061265 | 0.0064721 | -0.0025278 | 0.0061844 | -0.0064143 | 0.0051189 | 0.010172 | 0.0087913 | -0.0026252 | -0.010111 | -0.0087295 | -82.7237 | 96.2557 | 96.2557 | 97.2763 | -83.7443 | -83.7443 |  | 0.080952 | 1.4605 | 1.3427 | 0.041533 | 1.4577 | 1.3323 | -36.6167 | -142.6848 | 149.8952 | -36.6411 | -142.2908 | 149.9477
Line6_7_8 | 0.41515 | 0 | 0 | 0.41515 | 0 | 0 | 0.095876 | 0 | 0 | 0.095876 | 0 | 0 | 0.0027576 | 1.5815e-07 | -1.4289e-07 | 4.2886e-16 | -1.0976e-07 | 9.1891e-08 | 0.0028725 | -2.3357e-07 | -2.1459e-07 | 2.1453e-15 | 1.5319e-07 | 1.4473e-07 | -82.8102 | 0 | 0 | 97.1898 | 0 | 0 |  | 0.041533 | 1.4577 | 1.3323 | 0 | 1.4555 | 1.3241 | -36.6411 | -142.2908 | 149.9477 | 0 | -141.976 | 149.9889
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.7867e-22 | 5.3225e-08 | -4.7268e-08 | -1.9322e-17 | -3.3136e-09 | -2.644e-09 | -1.4521e-21 | -7.7492e-08 | -7.1274e-08 | 1.9174e-17 | -1.7974e-09 | 2.184e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 1.4555 | 1.3241 | 0 | 1.4555 | 1.3241 | 0 | -141.976 | 149.9889 | 0 | -141.976 | 149.9889
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.7867e-22 | 5.3225e-08 | -4.7268e-08 | -1.9322e-17 | -3.3136e-09 | -2.644e-09 | -1.4521e-21 | -7.7492e-08 | -7.1274e-08 | 1.9174e-17 | -1.7974e-09 | 2.184e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 1.4555 | 1.3241 | 0 | 1.4555 | 1.3241 | 0 | -141.976 | 149.9889 | 0 | -141.976 | 149.9889
Line9_3_11 | 0.034234 | 0.034234 | 0.034234 | 0.034234 | 0.034234 | 0.034234 | 0.0079061 | 0.0079061 | 0.0079061 | 0.0079061 | 0.0079061 | 0.0079061 | -0.00089462 | -0.0055908 | 0.0066205 | 0.00090588 | 0.0056021 | -0.0066093 | -0.00091484 | 0.01015 | 0.0084858 | 0.00092657 | -0.010139 | -0.0084741 | 97.7625 | 97.7625 | 97.7625 | -82.2375 | -82.2375 | -82.2375 |  | 0.16185 | 1.4657 | 1.3613 | 0.1639 | 1.4651 | 1.3593 | -36.5972 | -143.3915 | 149.8015 | -36.5906 | -143.3147 | 149.8103

## LG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.026869 | 0.0024896 | 0.0024896 | 0.026869 | 0.0024896 | 0.0024896 | 0.0062052 | 0.00057496 | 0.00057496 | 0.0062052 | 0.00057496 | 0.00057496 | 0.0039987 | -0.00017195 | 0.00053428 | -0.0039868 | 0.00017224 | -0.000534 | 0.0039888 | 0.00054847 | -8.1029e-05 | -0.0039763 | -0.00054816 | 8.1339e-05 | -47.2673 | 131.7121 | 131.7121 | 132.7327 | -48.2879 | -48.2879 |  | 0.91021 | 0.99971 | 0.93989 | 0.90743 | 0.99935 | 0.93947 | -2.3389 | -120.8815 | 123.0884 | -2.3426 | -120.8448 | 123.0514
Line10_11_12 | 0.002421 | 0.002421 | 0.002421 | 0.002421 | 0.002421 | 0.002421 | 0.0005591 | 0.0005591 | 0.0005591 | 0.0005591 | 0.0005591 | 0.0005591 | -0.00036344 | -0.00015323 | 0.00051719 | 0.0003635 | 0.00015329 | -0.00051713 | -0.00035644 | 0.00053744 | -9.2545e-05 | 0.0003565 | -0.00053738 | 9.2605e-05 | 133.2188 | 133.2188 | 133.2188 | -46.7812 | -46.7812 | -46.7812 |  | 0.9105 | 0.99956 | 0.93973 | 0.91065 | 0.99949 | 0.93965 | -2.3383 | -120.8671 | 123.0737 | -2.3381 | -120.86 | 123.0663
Line11_12_13 | 0.002421 | 0.002421 | 0.002421 | 0.002421 | 0.002421 | 0.002421 | 0.0005591 | 0.0005591 | 0.0005591 | 0.00055911 | 0.00055911 | 0.00055911 | -0.0003635 | -0.00015329 | 0.00051713 | 0.00036356 | 0.00015335 | -0.00051708 | -0.0003565 | 0.00053738 | -9.2604e-05 | 0.00035657 | -0.00053733 | 9.2664e-05 | 133.2188 | 133.2188 | 133.2188 | -46.7812 | -46.7812 | -46.7812 |  | 0.91065 | 0.99949 | 0.93965 | 0.91079 | 0.99942 | 0.93957 | -2.3381 | -120.86 | 123.0663 | -2.3378 | -120.8528 | 123.0589
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.1826e-09 | 4.1893e-09 | -1.2306e-08 | -5.3268e-09 | -2.9744e-09 | 8.2354e-09 | 8.8232e-09 | -1.2524e-08 | 1.6404e-09 | -6.0115e-09 | 8.2974e-09 | -9.1896e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.91079 | 0.99942 | 0.93957 | 0.91079 | 0.99942 | 0.93957 | -2.3378 | -120.8528 | 123.0589 | -2.3378 | -120.8528 | 123.0589
Line13_13_14 | 0.0024211 | 0.0024211 | 0.0024211 | 0.0024211 | 0.0024211 | 0.0024211 | 0.00055912 | 0.00055912 | 0.00055912 | 0.00055912 | 0.00055912 | 0.00055912 | -0.00036357 | -0.00015335 | 0.00051709 | 0.00036363 | 0.00015341 | -0.00051704 | -0.00035657 | 0.00053734 | -9.2665e-05 | 0.00035664 | -0.00053729 | 9.2725e-05 | 133.2187 | 133.2187 | 133.2187 | -46.7813 | -46.7813 | -46.7813 |  | 0.91079 | 0.99942 | 0.93957 | 0.91094 | 0.99934 | 0.93949 | -2.3378 | -120.8528 | 123.0589 | -2.3375 | -120.8456 | 123.0516
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4551e-09 | 2.7929e-09 | -8.2041e-09 | -2.5992e-09 | -1.5779e-09 | 4.1334e-09 | 5.8821e-09 | -8.3492e-09 | 1.0936e-09 | -3.0705e-09 | 4.1228e-09 | -3.7216e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.91079 | 0.99942 | 0.93957 | 0.91079 | 0.99942 | 0.93957 | -2.3378 | -120.8528 | 123.0589 | -2.3378 | -120.8528 | 123.0589
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7275e-09 | 1.3964e-09 | -4.1021e-09 | 1.2829e-10 | -1.8148e-10 | 3.1281e-11 | 2.9411e-09 | -4.1746e-09 | 5.468e-10 | -1.2941e-10 | -5.1812e-11 | 1.7465e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.91079 | 0.99942 | 0.93957 | 0.91079 | 0.99942 | 0.93957 | -2.3378 | -120.8528 | 123.0589 | -2.3378 | -120.8528 | 123.0589
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7259e-09 | 1.4274e-09 | -4.131e-09 | 1.2968e-10 | -1.8234e-10 | 3.0393e-11 | 2.9728e-09 | -4.1931e-09 | 5.252e-10 | -1.294e-10 | -5.3129e-11 | 1.7595e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.91036 | 0.99964 | 0.93981 | 0.91036 | 0.99964 | 0.93981 | -2.3387 | -120.8743 | 123.081 | -2.3387 | -120.8743 | 123.081
Line17_5_19 | 0.0024356 | 0.0024356 | 0.0024356 | 0.0024356 | 0.0024356 | 0.0024356 | 0.00056248 | 0.00056248 | 0.00056248 | 0.00056249 | 0.00056249 | 0.00056249 | -0.00036355 | -0.00015718 | 0.00052089 | 0.0003636 | 0.00015723 | -0.00052084 | -0.00036061 | 0.00053986 | -9.0089e-05 | 0.00036068 | -0.00053981 | 9.0149e-05 | 132.8933 | 132.8933 | 132.8933 | -47.1067 | -47.1067 | -47.1067 |  | 0.91036 | 0.99964 | 0.93981 | 0.91051 | 0.99956 | 0.93973 | -2.3387 | -120.8743 | 123.081 | -2.3385 | -120.867 | 123.0737
Line1_1_3 | 0.0024209 | 0.0024209 | 0.0024209 | 0.0024209 | 0.0024209 | 0.0024209 | 0.00055909 | 0.00055909 | 0.00055909 | 0.00055909 | 0.00055909 | 0.00055909 | -0.00036333 | -0.00015312 | 0.00051729 | 0.00036339 | 0.00015318 | -0.00051724 | -0.00035632 | 0.00053754 | -9.2427e-05 | 0.00035638 | -0.00053749 | 9.2486e-05 | 133.2189 | 133.2189 | 133.2189 | -46.7811 | -46.7811 | -46.7811 |  | 0.91021 | 0.99971 | 0.93989 | 0.91036 | 0.99964 | 0.93981 | -2.3389 | -120.8815 | 123.0884 | -2.3386 | -120.8743 | 123.0811
Line2_1_4 | 0.0024405 | 0.0024405 | 0.0024405 | 0.0024405 | 0.0024405 | 0.0024405 | 0.0005636 | 0.0005636 | 0.0005636 | 0.00056361 | 0.00056361 | 0.00056361 | -0.00036352 | -0.00015846 | 0.00052216 | 0.00036358 | 0.00015852 | -0.00052211 | -0.00036197 | 0.0005407 | -8.9213e-05 | 0.00036203 | -0.00054064 | 8.9273e-05 | 132.784 | 132.784 | 132.784 | -47.216 | -47.216 | -47.216 |  | 0.91021 | 0.99971 | 0.93989 | 0.91036 | 0.99964 | 0.93981 | -2.3389 | -120.8815 | 123.0884 | -2.3387 | -120.8743 | 123.081
Line3_1_5 | 0.0024356 | 0.0024356 | 0.0024356 | 0.0024356 | 0.0024356 | 0.0024356 | 0.00056248 | 0.00056248 | 0.00056248 | 0.00056248 | 0.00056248 | 0.00056248 | -0.00036349 | -0.00015712 | 0.00052094 | 0.00036355 | 0.00015718 | -0.00052089 | -0.00036055 | 0.00053992 | -9.0029e-05 | 0.00036061 | -0.00053986 | 9.0089e-05 | 132.8933 | 132.8933 | 132.8933 | -47.1067 | -47.1067 | -47.1067 |  | 0.91021 | 0.99971 | 0.93989 | 0.91036 | 0.99964 | 0.93981 | -2.3389 | -120.8815 | 123.0884 | -2.3387 | -120.8743 | 123.081
Line4_2_6 | 0.026869 | 0.0024896 | 0.0024896 | 0.026869 | 0.0024897 | 0.0024897 | 0.0062052 | 0.00057496 | 0.00057496 | 0.0062052 | 0.00057496 | 0.00057496 | 0.0039868 | -0.00017224 | 0.000534 | -0.0039748 | 0.00017253 | -0.00053371 | 0.0039763 | 0.00054816 | -8.1339e-05 | -0.0039638 | -0.00054786 | 8.1649e-05 | -47.2673 | 131.7121 | 131.7121 | 132.7327 | -48.2879 | -48.2879 |  | 0.90743 | 0.99935 | 0.93947 | 0.90464 | 0.99899 | 0.93906 | -2.3426 | -120.8448 | 123.0514 | -2.3463 | -120.808 | 123.0143
Line5_6_7 | 0.026869 | 0.0024897 | 0.0024897 | 0.026869 | 0.0024897 | 0.0024897 | 0.0062052 | 0.00057496 | 0.00057496 | 0.0062052 | 0.00057497 | 0.00057497 | 0.0039748 | -0.00017253 | 0.00053371 | -0.0039628 | 0.00017282 | -0.00053343 | 0.0039638 | 0.00054786 | -8.1649e-05 | -0.0039513 | -0.00054755 | 8.1959e-05 | -47.2673 | 131.7121 | 131.7121 | 132.7327 | -48.2879 | -48.2879 |  | 0.90464 | 0.99899 | 0.93906 | 0.90185 | 0.99862 | 0.93864 | -2.3463 | -120.808 | 123.0143 | -2.3501 | -120.7712 | 122.9772
Line6_7_8 | 0.029359 | 0 | 0 | 0.029358 | 0 | 0 | 0.0067801 | 0 | 0 | 0.0067801 | 0 | 0 | 0.0043234 | 4.7108e-09 | -1.2772e-08 | -0.0043096 | -3.3354e-09 | 8.5598e-09 | 0.004324 | -1.2828e-08 | 1.3619e-09 | -0.0043096 | 8.5106e-09 | -7.3529e-10 | -47.3539 | 0 | 0 | 132.6461 | 0 | 0 |  | 0.90185 | 0.99862 | 0.93864 | 0.89892 | 0.99833 | 0.93831 | -2.3501 | -120.7712 | 122.9772 | -2.3539 | -120.7418 | 122.9475
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6584e-09 | 1.5791e-09 | -4.262e-09 | 1.6573e-10 | -1.7722e-10 | 3.5895e-11 | 3.0897e-09 | -4.2778e-09 | 4.5168e-10 | -1.286e-10 | -4.5024e-11 | 1.6807e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.89892 | 0.99833 | 0.93831 | 0.89892 | 0.99833 | 0.93831 | -2.3539 | -120.7418 | 122.9475 | -2.3539 | -120.7418 | 122.9475
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6584e-09 | 1.5791e-09 | -4.262e-09 | 1.6573e-10 | -1.7722e-10 | 3.5895e-11 | 3.0897e-09 | -4.2778e-09 | 4.5168e-10 | -1.286e-10 | -4.5024e-11 | 1.6807e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.89892 | 0.99833 | 0.93831 | 0.89892 | 0.99833 | 0.93831 | -2.3539 | -120.7418 | 122.9475 | -2.3539 | -120.7418 | 122.9475
Line9_3_11 | 0.0024209 | 0.0024209 | 0.0024209 | 0.002421 | 0.002421 | 0.002421 | 0.00055909 | 0.00055909 | 0.00055909 | 0.0005591 | 0.0005591 | 0.0005591 | -0.00036338 | -0.00015318 | 0.00051724 | 0.00036344 | 0.00015323 | -0.00051719 | -0.00035638 | 0.00053749 | -9.2486e-05 | 0.00035644 | -0.00053744 | 9.2545e-05 | 133.2189 | 133.2189 | 133.2189 | -46.7811 | -46.7811 | -46.7811 |  | 0.91036 | 0.99964 | 0.93981 | 0.9105 | 0.99956 | 0.93973 | -2.3386 | -120.8743 | 123.0811 | -2.3383 | -120.8671 | 123.0737

## LG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.025455 | 0.0023586 | 0.0023586 | 0.025455 | 0.0023586 | 0.0023586 | 0.0058786 | 0.00054469 | 0.00054469 | 0.0058786 | 0.0005447 | 0.0005447 | 0.0035889 | -0.00015432 | 0.00047952 | -0.0035781 | 0.00015458 | -0.00047927 | 0.0035799 | 0.00049225 | -7.2724e-05 | -0.0035688 | -0.00049198 | 7.3002e-05 | -47.2673 | 131.7121 | 131.7121 | 132.7327 | -48.2879 | -48.2879 |  | 0.86231 | 0.94709 | 0.89042 | 0.85967 | 0.94675 | 0.89003 | -2.3389 | -120.8815 | 123.0884 | -2.3426 | -120.8448 | 123.0514
Line10_11_12 | 0.0022935 | 0.0022935 | 0.0022935 | 0.0022936 | 0.0022936 | 0.0022936 | 0.00052967 | 0.00052967 | 0.00052967 | 0.00052968 | 0.00052968 | 0.00052968 | -0.00032619 | -0.00013753 | 0.00046418 | 0.00032625 | 0.00013758 | -0.00046413 | -0.00031991 | 0.00048235 | -8.306e-05 | 0.00031997 | -0.0004823 | 8.3113e-05 | 133.2188 | 133.2188 | 133.2188 | -46.7812 | -46.7812 | -46.7812 |  | 0.86258 | 0.94696 | 0.89027 | 0.86272 | 0.94689 | 0.89019 | -2.3383 | -120.8671 | 123.0737 | -2.3381 | -120.86 | 123.0663
Line11_12_13 | 0.0022936 | 0.0022936 | 0.0022936 | 0.0022936 | 0.0022936 | 0.0022936 | 0.00052968 | 0.00052968 | 0.00052968 | 0.00052968 | 0.00052968 | 0.00052968 | -0.00032625 | -0.00013758 | 0.00046413 | 0.0003263 | 0.00013763 | -0.00046408 | -0.00031997 | 0.0004823 | -8.3113e-05 | 0.00032002 | -0.00048225 | 8.3166e-05 | 133.2188 | 133.2188 | 133.2188 | -46.7812 | -46.7812 | -46.7812 |  | 0.86272 | 0.94689 | 0.89019 | 0.86286 | 0.94682 | 0.89012 | -2.3381 | -120.86 | 123.0663 | -2.3378 | -120.8528 | 123.0589
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.344e-09 | 3.76e-09 | -1.1045e-08 | -4.7808e-09 | -2.6695e-09 | 7.3914e-09 | 7.9188e-09 | -1.124e-08 | 1.4723e-09 | -5.3954e-09 | 7.447e-09 | -8.2477e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.86286 | 0.94682 | 0.89012 | 0.86286 | 0.94682 | 0.89012 | -2.3378 | -120.8528 | 123.0589 | -2.3378 | -120.8528 | 123.0589
Line13_13_14 | 0.0022936 | 0.0022936 | 0.0022936 | 0.0022937 | 0.0022937 | 0.0022937 | 0.00052969 | 0.00052969 | 0.00052969 | 0.0005297 | 0.0005297 | 0.0005297 | -0.00032631 | -0.00013764 | 0.00046409 | 0.00032636 | 0.00013769 | -0.00046405 | -0.00032003 | 0.00048227 | -8.3168e-05 | 0.00032008 | -0.00048222 | 8.3221e-05 | 133.2187 | 133.2187 | 133.2187 | -46.7813 | -46.7813 | -46.7813 |  | 0.86286 | 0.94682 | 0.89012 | 0.863 | 0.94675 | 0.89004 | -2.3378 | -120.8528 | 123.0589 | -2.3375 | -120.8456 | 123.0516
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.896e-09 | 2.5066e-09 | -7.3633e-09 | -2.3328e-09 | -1.4162e-09 | 3.7097e-09 | 5.2792e-09 | -7.4935e-09 | 9.8152e-10 | -2.7558e-09 | 3.7002e-09 | -3.3401e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.86286 | 0.94682 | 0.89012 | 0.86286 | 0.94682 | 0.89012 | -2.3378 | -120.8528 | 123.0589 | -2.3378 | -120.8528 | 123.0589
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.448e-09 | 1.2533e-09 | -3.6816e-09 | 1.1514e-10 | -1.6288e-10 | 2.8075e-11 | 2.6396e-09 | -3.7467e-09 | 4.9076e-10 | -1.1615e-10 | -4.6501e-11 | 1.5675e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.86286 | 0.94682 | 0.89012 | 0.86286 | 0.94682 | 0.89012 | -2.3378 | -120.8528 | 123.0589 | -2.3378 | -120.8528 | 123.0589
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4465e-09 | 1.2811e-09 | -3.7076e-09 | 1.1639e-10 | -1.6366e-10 | 2.7278e-11 | 2.6681e-09 | -3.7633e-09 | 4.7137e-10 | -1.1614e-10 | -4.7684e-11 | 1.5792e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.86245 | 0.94703 | 0.89034 | 0.86245 | 0.94703 | 0.89034 | -2.3387 | -120.8743 | 123.081 | -2.3387 | -120.8743 | 123.081
Line17_5_19 | 0.0023074 | 0.0023074 | 0.0023074 | 0.0023074 | 0.0023074 | 0.0023074 | 0.00053288 | 0.00053288 | 0.00053288 | 0.00053288 | 0.00053288 | 0.00053288 | -0.00032628 | -0.00014107 | 0.0004675 | 0.00032634 | 0.00014112 | -0.00046746 | -0.00032365 | 0.00048453 | -8.0855e-05 | 0.00032371 | -0.00048448 | 8.0909e-05 | 132.8933 | 132.8933 | 132.8933 | -47.1067 | -47.1067 | -47.1067 |  | 0.86245 | 0.94703 | 0.89034 | 0.86258 | 0.94696 | 0.89027 | -2.3387 | -120.8743 | 123.081 | -2.3385 | -120.867 | 123.0737
Line1_1_3 | 0.0022935 | 0.0022935 | 0.0022935 | 0.0022935 | 0.0022935 | 0.0022935 | 0.00052966 | 0.00052966 | 0.00052966 | 0.00052967 | 0.00052967 | 0.00052967 | -0.00032609 | -0.00013743 | 0.00046427 | 0.00032614 | 0.00013748 | -0.00046422 | -0.0003198 | 0.00048245 | -8.2954e-05 | 0.00031985 | -0.0004824 | 8.3007e-05 | 133.2189 | 133.2189 | 133.2189 | -46.7811 | -46.7811 | -46.7811 |  | 0.86231 | 0.94709 | 0.89042 | 0.86244 | 0.94702 | 0.89034 | -2.3389 | -120.8815 | 123.0884 | -2.3386 | -120.8743 | 123.0811
Line2_1_4 | 0.002312 | 0.002312 | 0.002312 | 0.002312 | 0.002312 | 0.002312 | 0.00053394 | 0.00053394 | 0.00053394 | 0.00053394 | 0.00053394 | 0.00053394 | -0.00032626 | -0.00014222 | 0.00046864 | 0.00032632 | 0.00014228 | -0.00046859 | -0.00032487 | 0.00048528 | -8.0069e-05 | 0.00032492 | -0.00048523 | 8.0123e-05 | 132.784 | 132.784 | 132.784 | -47.216 | -47.216 | -47.216 |  | 0.86231 | 0.94709 | 0.89042 | 0.86245 | 0.94703 | 0.89034 | -2.3389 | -120.8815 | 123.0884 | -2.3387 | -120.8743 | 123.081
Line3_1_5 | 0.0023074 | 0.0023074 | 0.0023074 | 0.0023074 | 0.0023074 | 0.0023074 | 0.00053287 | 0.00053287 | 0.00053287 | 0.00053288 | 0.00053288 | 0.00053288 | -0.00032623 | -0.00014101 | 0.00046755 | 0.00032628 | 0.00014107 | -0.0004675 | -0.0003236 | 0.00048458 | -8.0801e-05 | 0.00032365 | -0.00048453 | 8.0855e-05 | 132.8933 | 132.8933 | 132.8933 | -47.1067 | -47.1067 | -47.1067 |  | 0.86231 | 0.94709 | 0.89042 | 0.86245 | 0.94703 | 0.89034 | -2.3389 | -120.8815 | 123.0884 | -2.3387 | -120.8743 | 123.081
Line4_2_6 | 0.025455 | 0.0023586 | 0.0023586 | 0.025455 | 0.0023586 | 0.0023586 | 0.0058786 | 0.0005447 | 0.0005447 | 0.0058786 | 0.0005447 | 0.0005447 | 0.0035781 | -0.00015458 | 0.00047927 | -0.0035674 | 0.00015484 | -0.00047901 | 0.0035688 | 0.00049198 | -7.3002e-05 | -0.0035576 | -0.00049171 | 7.328e-05 | -47.2673 | 131.7121 | 131.7121 | 132.7327 | -48.2879 | -48.2879 |  | 0.85967 | 0.94675 | 0.89003 | 0.85703 | 0.94641 | 0.88963 | -2.3426 | -120.8448 | 123.0514 | -2.3463 | -120.808 | 123.0143
Line5_6_7 | 0.025455 | 0.0023586 | 0.0023586 | 0.025455 | 0.0023587 | 0.0023587 | 0.0058786 | 0.0005447 | 0.0005447 | 0.0058786 | 0.00054471 | 0.00054471 | 0.0035674 | -0.00015484 | 0.00047901 | -0.0035566 | 0.00015511 | -0.00047876 | 0.0035576 | 0.00049171 | -7.328e-05 | -0.0035464 | -0.00049143 | 7.3559e-05 | -47.2673 | 131.7121 | 131.7121 | 132.7327 | -48.2879 | -48.2879 |  | 0.85703 | 0.94641 | 0.88963 | 0.85439 | 0.94606 | 0.88924 | -2.3463 | -120.808 | 123.0143 | -2.3501 | -120.7712 | 122.9772
Line6_7_8 | 0.027813 | 0 | 0 | 0.027813 | 0 | 0 | 0.0064232 | 0 | 0 | 0.0064232 | 0 | 0 | 0.0038803 | 4.228e-09 | -1.1463e-08 | -0.0038679 | -2.9936e-09 | 7.6825e-09 | 0.0038808 | -1.1513e-08 | 1.2223e-09 | -0.0038679 | 7.6384e-09 | -6.5993e-10 | -47.3539 | 0 | 0 | 132.6461 | 0 | 0 |  | 0.85439 | 0.94606 | 0.88924 | 0.8516 | 0.94579 | 0.88893 | -2.3501 | -120.7712 | 122.9772 | -2.3539 | -120.7418 | 122.9475
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.386e-09 | 1.4173e-09 | -3.8251e-09 | 1.4875e-10 | -1.5906e-10 | 3.2216e-11 | 2.773e-09 | -3.8394e-09 | 4.0539e-10 | -1.1542e-10 | -4.041e-11 | 1.5084e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.8516 | 0.94579 | 0.88893 | 0.8516 | 0.94579 | 0.88893 | -2.3539 | -120.7418 | 122.9475 | -2.3539 | -120.7418 | 122.9475
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.386e-09 | 1.4173e-09 | -3.8251e-09 | 1.4875e-10 | -1.5906e-10 | 3.2216e-11 | 2.773e-09 | -3.8394e-09 | 4.0539e-10 | -1.1542e-10 | -4.041e-11 | 1.5084e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.8516 | 0.94579 | 0.88893 | 0.8516 | 0.94579 | 0.88893 | -2.3539 | -120.7418 | 122.9475 | -2.3539 | -120.7418 | 122.9475
Line9_3_11 | 0.0022935 | 0.0022935 | 0.0022935 | 0.0022935 | 0.0022935 | 0.0022935 | 0.00052967 | 0.00052967 | 0.00052967 | 0.00052967 | 0.00052967 | 0.00052967 | -0.00032614 | -0.00013748 | 0.00046422 | 0.00032619 | 0.00013753 | -0.00046418 | -0.00031985 | 0.0004824 | -8.3007e-05 | 0.00031991 | -0.00048235 | 8.306e-05 | 133.2189 | 133.2189 | 133.2189 | -46.7811 | -46.7811 | -46.7811 |  | 0.86244 | 0.94702 | 0.89034 | 0.86258 | 0.94696 | 0.89027 | -2.3386 | -120.8743 | 123.0811 | -2.3383 | -120.8671 | 123.0737

## LLG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.023119 | 1.8486 | 1.9275 | 0.02312 | 1.8486 | 1.9275 | 0.0053392 | 0.42691 | 0.44514 | 0.0053392 | 0.42691 | 0.44514 | 8.0329e-05 | 0.13297 | 0.15204 | -6.733e-05 | -0.099816 | -0.11395 | 0.0081817 | 0.27691 | 0.29313 | -0.0081553 | -0.2076 | -0.21994 | -88.9068 | -161.173 | 25.2724 | 91.0932 | 18.827 | -154.7276 |  | 1.5325 | 0.71955 | 0.74182 | 1.5275 | 0.53957 | 0.55648 | 0.5307 | -96.8239 | 87.8567 | 0.6202 | -96.8521 | 87.8832
Line10_11_12 | 0.022486 | 0.022486 | 0.022486 | 0.022486 | 0.022486 | 0.022486 | 0.005193 | 0.005193 | 0.005193 | 0.005193 | 0.005193 | 0.005193 | 0.00018207 | 0.0036885 | -0.0038478 | -0.00017954 | -0.003686 | 0.0038504 | 0.0079457 | -0.00057544 | 0.00026004 | -0.0079407 | 0.0005805 | -0.00025498 | -88.1219 | -88.122 | -88.1219 | 91.8781 | 91.878 | 91.8781 |  | 1.5305 | 0.71888 | 0.74266 | 1.5295 | 0.71855 | 0.74308 | 0.56542 | -96.9891 | 88.0119 | 0.58282 | -97.0718 | 88.0893
Line11_12_13 | 0.022486 | 0.022486 | 0.022486 | 0.022487 | 0.022487 | 0.022487 | 0.005193 | 0.005193 | 0.005193 | 0.0051931 | 0.005193 | 0.0051931 | 0.00017954 | 0.003686 | -0.0038504 | -0.00017701 | -0.0036835 | 0.0038529 | 0.0079407 | -0.0005805 | 0.00025498 | -0.0079357 | 0.00058556 | -0.00024993 | -88.122 | -88.122 | -88.1219 | 91.878 | 91.878 | 91.878 |  | 1.5295 | 0.71855 | 0.74308 | 1.5285 | 0.71822 | 0.7435 | 0.58282 | -97.0718 | 88.0893 | 0.60024 | -97.1546 | 88.1667
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0549e-09 | -8.8952e-08 | 8.9758e-08 | -5.3855e-09 | 5.9958e-08 | -5.9434e-08 | -1.8755e-07 | 1.0517e-08 | -1.2803e-09 | 1.251e-07 | -5.938e-09 | -6.5626e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.5285 | 0.71822 | 0.7435 | 1.5285 | 0.71823 | 0.7435 | 0.60024 | -97.1546 | 88.1667 | 0.60024 | -97.1546 | 88.1667
Line13_13_14 | 0.022487 | 0.022487 | 0.022487 | 0.022487 | 0.022487 | 0.022487 | 0.0051932 | 0.0051932 | 0.0051932 | 0.0051932 | 0.0051932 | 0.0051932 | 0.000177 | 0.0036836 | -0.003853 | -0.00017448 | -0.0036811 | 0.0038556 | 0.0079359 | -0.00058557 | 0.00024993 | -0.0079309 | 0.00059063 | -0.00024487 | -88.122 | -88.122 | -88.122 | 91.878 | 91.878 | 91.878 |  | 1.5285 | 0.71822 | 0.7435 | 1.5275 | 0.7179 | 0.74392 | 0.60024 | -97.1546 | 88.1667 | 0.61768 | -97.2374 | 88.2439
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7033e-09 | -5.9301e-08 | 5.9839e-08 | -4.0339e-09 | 3.0307e-08 | -2.9514e-08 | -1.2503e-07 | 7.0116e-09 | -8.5355e-10 | 6.2578e-08 | -2.4322e-09 | -1.083e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.5285 | 0.71823 | 0.7435 | 1.5285 | 0.71823 | 0.7435 | 0.60024 | -97.1546 | 88.1667 | 0.60024 | -97.1546 | 88.1667
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3516e-09 | -2.9651e-08 | 2.9919e-08 | -2.6823e-09 | 6.5681e-10 | 4.0501e-10 | -6.2517e-08 | 3.5058e-09 | -4.2678e-10 | 6.165e-11 | 1.0736e-09 | -1.5098e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.5285 | 0.71823 | 0.7435 | 1.5285 | 0.71823 | 0.7435 | 0.60024 | -97.1546 | 88.1667 | 0.60024 | -97.1546 | 88.1667
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4917e-09 | -2.989e-08 | 3.0051e-08 | -2.7039e-09 | 6.5045e-10 | 4.0163e-10 | -6.3009e-08 | 3.3144e-09 | -4.6106e-10 | 5.6427e-11 | 1.086e-09 | -1.5171e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.5315 | 0.71921 | 0.74225 | 1.5315 | 0.71921 | 0.74225 | 0.54834 | -96.907 | 87.9348 | 0.54834 | -96.907 | 87.9348
Line17_5_19 | 0.022622 | 0.022622 | 0.022622 | 0.022622 | 0.022622 | 0.022622 | 0.0052243 | 0.0052243 | 0.0052243 | 0.0052243 | 0.0052243 | 0.0052243 | 0.000162 | 0.0037149 | -0.0038693 | -0.00015944 | -0.0037124 | 0.0038719 | 0.0079992 | -0.00056285 | 0.00025522 | -0.0079941 | 0.00056797 | -0.0002501 | -88.2915 | -88.2915 | -88.2915 | 91.7085 | 91.7085 | 91.7085 |  | 1.5315 | 0.71921 | 0.74224 | 1.5305 | 0.71887 | 0.74267 | 0.54826 | -96.9069 | 87.9347 | 0.56585 | -96.9899 | 88.0126
Line1_1_3 | 0.022486 | 0.022486 | 0.022486 | 0.022486 | 0.022486 | 0.022486 | 0.0051929 | 0.0051929 | 0.0051929 | 0.0051929 | 0.0051929 | 0.0051929 | 0.00018713 | 0.0036935 | -0.0038427 | -0.0001846 | -0.003691 | 0.0038453 | 0.0079557 | -0.00056532 | 0.00027015 | -0.0079507 | 0.00057038 | -0.0002651 | -88.1219 | -88.1219 | -88.1219 | 91.8781 | 91.8781 | 91.8781 |  | 1.5325 | 0.71955 | 0.74182 | 1.5315 | 0.71922 | 0.74224 | 0.5307 | -96.8239 | 87.8567 | 0.54805 | -96.9065 | 87.9344
Line2_1_4 | 0.022667 | 0.022667 | 0.022667 | 0.022667 | 0.022667 | 0.022667 | 0.0052347 | 0.0052347 | 0.0052347 | 0.0052347 | 0.0052347 | 0.0052347 | 0.00015692 | 0.0037255 | -0.0038747 | -0.00015435 | -0.0037229 | 0.0038773 | 0.0080204 | -0.00055514 | 0.000257 | -0.0080153 | 0.00056028 | -0.00025187 | -88.3485 | -88.3485 | -88.3485 | 91.6515 | 91.6515 | 91.6515 |  | 1.5325 | 0.71955 | 0.74182 | 1.5315 | 0.71921 | 0.74225 | 0.5307 | -96.8239 | 87.8567 | 0.54834 | -96.907 | 87.9348
Line3_1_5 | 0.022622 | 0.022622 | 0.022622 | 0.022622 | 0.022622 | 0.022622 | 0.0052242 | 0.0052242 | 0.0052242 | 0.0052243 | 0.0052243 | 0.0052243 | 0.00016456 | 0.0037175 | -0.0038667 | -0.000162 | -0.0037149 | 0.0038693 | 0.0080042 | -0.00055773 | 0.00026033 | -0.0079992 | 0.00056285 | -0.00025522 | -88.2915 | -88.2915 | -88.2915 | 91.7085 | 91.7085 | 91.7085 |  | 1.5325 | 0.71955 | 0.74182 | 1.5315 | 0.71921 | 0.74224 | 0.5307 | -96.8239 | 87.8567 | 0.54826 | -96.9069 | 87.9347
Line4_2_6 | 0.02312 | 1.8486 | 1.9275 | 0.02312 | 1.8486 | 1.9275 | 0.0053392 | 0.42691 | 0.44514 | 0.0053393 | 0.42691 | 0.44514 | 6.7327e-05 | 0.099816 | 0.11395 | -5.4327e-05 | -0.066658 | -0.075864 | 0.0081553 | 0.2076 | 0.21994 | -0.008129 | -0.13829 | -0.14676 | -88.9068 | -161.173 | 25.2724 | 91.0932 | 18.827 | -154.7276 |  | 1.5275 | 0.53957 | 0.55648 | 1.5225 | 0.3596 | 0.37113 | 0.6202 | -96.8521 | 87.8832 | 0.71029 | -96.9084 | 87.9361
Line5_6_7 | 0.02312 | 1.8486 | 1.9275 | 0.02312 | 1.8486 | 1.9275 | 0.0053393 | 0.42691 | 0.44514 | 0.0053393 | 0.42691 | 0.44514 | 5.4325e-05 | 0.066658 | 0.075864 | -4.1324e-05 | -0.0335 | -0.037774 | 0.008129 | 0.13829 | 0.14676 | -0.0081026 | -0.068976 | -0.073571 | -88.9068 | -161.173 | 25.2724 | 91.0932 | 18.827 | -154.7276 |  | 1.5225 | 0.3596 | 0.37113 | 1.5175 | 0.17962 | 0.18579 | 0.71029 | -96.9084 | 87.9361 | 0.80097 | -97.0777 | 88.0945
Line6_7_8 | 0 | 1.8416 | 1.9371 | 0 | 1.8416 | 1.9371 | 0 | 0.42531 | 0.44735 | 0 | 0.42531 | 0.44735 | 7.3753e-09 | 0.032551 | 0.038765 | -7.7205e-09 | 5.7147e-14 | 1.0545e-14 | -1.9245e-07 | 0.069113 | 0.073519 | 1.2822e-07 | 1.1238e-14 | -1.4671e-14 | 0 | -161.8581 | 25.8962 | 0 | 18.1419 | -154.1038 |  | 1.5175 | 0.17962 | 0.18579 | 1.5136 | 0 | 0 | 0.80097 | -97.0777 | 88.0945 | 0.87343 | 0 | 0
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5735e-09 | 3.2055e-21 | 7.0219e-22 | -2.5735e-09 | 8.5657e-21 | -1.0468e-17 | -6.4064e-08 | -5.3612e-21 | 1.4076e-21 | 8.883e-11 | 2.2455e-17 | -5.2887e-18 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.5136 | 0 | 0 | 1.5136 | 0 | 0 | 0.87343 | 0 | 0 | 0.87343 | 0 | 0
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5735e-09 | 3.2055e-21 | 7.0219e-22 | -2.5735e-09 | 8.5659e-21 | -1.0468e-17 | -6.4064e-08 | -5.3612e-21 | 1.4076e-21 | 8.883e-11 | 2.2455e-17 | -5.2887e-18 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.5136 | 0 | 0 | 1.5136 | 0 | 0 | 0.87343 | 0 | 0 | 0.87343 | 0 | 0
Line9_3_11 | 0.022486 | 0.022486 | 0.022486 | 0.022486 | 0.022486 | 0.022486 | 0.0051929 | 0.0051929 | 0.0051929 | 0.005193 | 0.005193 | 0.005193 | 0.0001846 | 0.003691 | -0.0038453 | -0.00018207 | -0.0036885 | 0.0038478 | 0.0079507 | -0.00057038 | 0.00026509 | -0.0079457 | 0.00057544 | -0.00026004 | -88.1219 | -88.1219 | -88.1219 | 91.8781 | 91.8781 | 91.8781 |  | 1.5315 | 0.71922 | 0.74224 | 1.5305 | 0.71888 | 0.74266 | 0.54805 | -96.9065 | 87.9344 | 0.56542 | -96.9891 | 88.0119

## LLG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.02421 | 1.9185 | 2.0005 | 0.024211 | 1.9185 | 2.0005 | 0.0055911 | 0.44306 | 0.462 | 0.0055912 | 0.44306 | 0.462 | 8.8089e-05 | 0.14318 | 0.16383 | -7.3834e-05 | -0.10748 | -0.12278 | 0.0089721 | 0.29828 | 0.31572 | -0.0089432 | -0.22362 | -0.2369 | -88.9055 | -161.3734 | 25.1371 | 91.0945 | 18.6266 | -154.8629 |  | 1.6048 | 0.74677 | 0.76991 | 1.5996 | 0.55998 | 0.57755 | 0.53202 | -97.0151 | 87.7129 | 0.62152 | -97.0435 | 87.7396
Line10_11_12 | 0.023547 | 0.023547 | 0.023547 | 0.023547 | 0.023547 | 0.023547 | 0.005438 | 0.005438 | 0.005438 | 0.0054381 | 0.0054381 | 0.0054381 | 0.00019965 | 0.0040066 | -0.0041812 | -0.00019688 | -0.0040038 | 0.0041841 | 0.0087133 | -0.00063897 | 0.0002931 | -0.0087078 | 0.00064452 | -0.00028756 | -88.1206 | -88.1206 | -88.1206 | 91.8794 | 91.8794 | 91.8794 |  | 1.6027 | 0.74608 | 0.77078 | 1.6017 | 0.74574 | 0.77122 | 0.56674 | -97.1819 | 87.8696 | 0.58414 | -97.2655 | 87.9478
Line11_12_13 | 0.023547 | 0.023547 | 0.023547 | 0.023548 | 0.023548 | 0.023548 | 0.0054381 | 0.0054381 | 0.0054381 | 0.0054381 | 0.0054381 | 0.0054381 | 0.00019688 | 0.0040038 | -0.0041841 | -0.00019411 | -0.0040011 | 0.0041869 | 0.0087078 | -0.00064452 | 0.00028755 | -0.0087023 | 0.00065007 | -0.00028201 | -88.1206 | -88.1207 | -88.1206 | 91.8794 | 91.8793 | 91.8794 |  | 1.6017 | 0.74574 | 0.77122 | 1.6007 | 0.7454 | 0.77166 | 0.58414 | -97.2655 | 87.9478 | 0.60156 | -97.3491 | 88.0259
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4387e-09 | -9.6692e-08 | 9.7487e-08 | -5.8978e-09 | 6.5199e-08 | -6.4535e-08 | -2.0567e-07 | 1.178e-08 | -1.6151e-09 | 1.3718e-07 | -6.6956e-09 | -5.7136e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.6007 | 0.7454 | 0.77166 | 1.6007 | 0.7454 | 0.77166 | 0.60156 | -97.3491 | 88.0259 | 0.60156 | -97.3491 | 88.0259
Line13_13_14 | 0.023548 | 0.023548 | 0.023548 | 0.023548 | 0.023548 | 0.023548 | 0.0054382 | 0.0054382 | 0.0054382 | 0.0054383 | 0.0054383 | 0.0054383 | 0.0001941 | 0.0040012 | -0.004187 | -0.00019133 | -0.0039984 | 0.0041898 | 0.0087025 | -0.00065008 | 0.00028201 | -0.0086971 | 0.00065563 | -0.00027647 | -88.1207 | -88.1207 | -88.1207 | 91.8793 | 91.8793 | 91.8793 |  | 1.6007 | 0.7454 | 0.77166 | 1.5996 | 0.74506 | 0.7721 | 0.60156 | -97.3491 | 88.0259 | 0.619 | -97.4328 | 88.104
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9591e-09 | -6.4461e-08 | 6.4991e-08 | -4.4183e-09 | 3.2968e-08 | -3.2039e-08 | -1.3711e-07 | 7.8534e-09 | -1.0767e-09 | 6.8624e-08 | -2.7689e-09 | -1.1097e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.6007 | 0.7454 | 0.77166 | 1.6007 | 0.7454 | 0.77166 | 0.60156 | -97.3491 | 88.0259 | 0.60156 | -97.3491 | 88.0259
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4796e-09 | -3.2231e-08 | 3.2496e-08 | -2.9387e-09 | 7.3728e-10 | 4.5684e-10 | -6.8556e-08 | 3.9267e-09 | -5.3837e-10 | 6.7782e-11 | 1.1578e-09 | -1.6481e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.6007 | 0.7454 | 0.77166 | 1.6007 | 0.7454 | 0.77166 | 0.60156 | -97.3491 | 88.0259 | 0.60156 | -97.3491 | 88.0259
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6332e-09 | -3.2492e-08 | 3.2638e-08 | -2.9625e-09 | 7.3041e-10 | 4.5301e-10 | -6.9096e-08 | 3.7181e-09 | -5.7723e-10 | 6.2053e-11 | 1.1715e-09 | -1.6561e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.6037 | 0.74642 | 0.77035 | 1.6037 | 0.74642 | 0.77035 | 0.54966 | -97.099 | 87.7918 | 0.54966 | -97.099 | 87.7918
Line17_5_19 | 0.023689 | 0.023689 | 0.023689 | 0.023689 | 0.023689 | 0.023689 | 0.0054708 | 0.0054708 | 0.0054708 | 0.0054708 | 0.0054708 | 0.0054708 | 0.00017765 | 0.0040353 | -0.0042046 | -0.00017484 | -0.0040326 | 0.0042074 | 0.0087719 | -0.00062533 | 0.00028797 | -0.0087664 | 0.00063094 | -0.00028236 | -88.2902 | -88.2902 | -88.2902 | 91.7098 | 91.7098 | 91.7098 |  | 1.6037 | 0.74642 | 0.77035 | 1.6027 | 0.74607 | 0.77079 | 0.54958 | -97.0989 | 87.7917 | 0.56717 | -97.1828 | 87.8704
Line1_1_3 | 0.023547 | 0.023547 | 0.023547 | 0.023547 | 0.023547 | 0.023547 | 0.0054379 | 0.0054379 | 0.0054379 | 0.005438 | 0.005438 | 0.005438 | 0.0002052 | 0.004012 | -0.0041756 | -0.00020243 | -0.0040093 | 0.0041784 | 0.0087242 | -0.00062787 | 0.00030419 | -0.0087188 | 0.00063342 | -0.00029864 | -88.1206 | -88.1206 | -88.1206 | 91.8794 | 91.8794 | 91.8794 |  | 1.6048 | 0.74677 | 0.76991 | 1.6037 | 0.74642 | 0.77034 | 0.53202 | -97.0151 | 87.7129 | 0.54937 | -97.0985 | 87.7913
Line2_1_4 | 0.023736 | 0.023736 | 0.023736 | 0.023736 | 0.023736 | 0.023737 | 0.0054817 | 0.0054817 | 0.0054817 | 0.0054817 | 0.0054817 | 0.0054817 | 0.00017207 | 0.0040468 | -0.0042104 | -0.00016926 | -0.004044 | 0.0042132 | 0.0087952 | -0.00061693 | 0.00028998 | -0.0087896 | 0.00062257 | -0.00028435 | -88.3472 | -88.3472 | -88.3471 | 91.6528 | 91.6528 | 91.6529 |  | 1.6048 | 0.74677 | 0.76991 | 1.6037 | 0.74642 | 0.77035 | 0.53202 | -97.0151 | 87.7129 | 0.54966 | -97.099 | 87.7918
Line3_1_5 | 0.023689 | 0.023689 | 0.023689 | 0.023689 | 0.023689 | 0.023689 | 0.0054707 | 0.0054707 | 0.0054707 | 0.0054708 | 0.0054708 | 0.0054708 | 0.00018046 | 0.0040381 | -0.0042017 | -0.00017765 | -0.0040353 | 0.0042046 | 0.0087775 | -0.00061971 | 0.00029358 | -0.0087719 | 0.00062533 | -0.00028797 | -88.2902 | -88.2902 | -88.2902 | 91.7098 | 91.7098 | 91.7098 |  | 1.6048 | 0.74677 | 0.76991 | 1.6037 | 0.74642 | 0.77035 | 0.53202 | -97.0151 | 87.7129 | 0.54958 | -97.0989 | 87.7917
Line4_2_6 | 0.024211 | 1.9185 | 2.0005 | 0.024211 | 1.9185 | 2.0005 | 0.0055912 | 0.44306 | 0.462 | 0.0055912 | 0.44306 | 0.462 | 7.3831e-05 | 0.10748 | 0.12278 | -5.9575e-05 | -0.071776 | -0.081741 | 0.0089432 | 0.22362 | 0.2369 | -0.0089142 | -0.14896 | -0.15807 | -88.9055 | -161.3734 | 25.1371 | 91.0945 | 18.6266 | -154.8629 |  | 1.5996 | 0.55998 | 0.57755 | 1.5944 | 0.3732 | 0.38518 | 0.62152 | -97.0435 | 87.7396 | 0.71161 | -97.1004 | 87.7931
Line5_6_7 | 0.024211 | 1.9185 | 2.0005 | 0.024211 | 1.9185 | 2.0005 | 0.0055912 | 0.44306 | 0.462 | 0.0055913 | 0.44306 | 0.462 | 5.9572e-05 | 0.071776 | 0.081741 | -4.5316e-05 | -0.036074 | -0.040699 | 0.0089142 | 0.14896 | 0.15807 | -0.0088853 | -0.074299 | -0.079245 | -88.9055 | -161.3734 | 25.1371 | 91.0945 | 18.6266 | -154.8629 |  | 1.5944 | 0.3732 | 0.38518 | 1.5892 | 0.18642 | 0.19282 | 0.71161 | -97.1004 | 87.7931 | 0.80229 | -97.2714 | 87.953
Line6_7_8 | 0 | 1.9114 | 2.0105 | 0 | 1.9114 | 2.0105 | 0 | 0.44141 | 0.46431 | 0 | 0.44141 | 0.46431 | 8.0799e-09 | 0.035043 | 0.041775 | -8.4584e-09 | 7.1082e-14 | 1.9269e-14 | -2.1105e-07 | 0.07445 | 0.079186 | 1.406e-07 | -1.528e-14 | -1.119e-14 | 0 | -162.0655 | 25.7672 | 0 | 17.9345 | -154.2328 |  | 1.5892 | 0.18642 | 0.19282 | 1.585 | 0 | 0 | 0.80229 | -97.2714 | 87.953 | 0.87475 | 0 | 0
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8195e-09 | 1.0149e-21 | 8.5183e-23 | -2.8195e-09 | 1.0331e-20 | -1.1483e-17 | -7.0253e-08 | -7.8024e-21 | 1.9555e-21 | 9.7599e-11 | 2.4637e-17 | -5.7997e-18 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.585 | 0 | 0 | 1.585 | 0 | 0 | 0.87475 | 0 | 0 | 0.87475 | 0 | 0
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8195e-09 | 1.0149e-21 | 8.5183e-23 | -2.8195e-09 | 1.0334e-20 | -1.1483e-17 | -7.0253e-08 | -7.8024e-21 | 1.9555e-21 | 9.7599e-11 | 2.4637e-17 | -5.7997e-18 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.585 | 0 | 0 | 1.585 | 0 | 0 | 0.87475 | 0 | 0 | 0.87475 | 0 | 0
Line9_3_11 | 0.023547 | 0.023547 | 0.023547 | 0.023547 | 0.023547 | 0.023547 | 0.005438 | 0.005438 | 0.005438 | 0.005438 | 0.005438 | 0.005438 | 0.00020243 | 0.0040093 | -0.0041784 | -0.00019966 | -0.0040066 | 0.0041812 | 0.0087188 | -0.00063342 | 0.00029864 | -0.0087133 | 0.00063897 | -0.0002931 | -88.1206 | -88.1206 | -88.1206 | 91.8794 | 91.8794 | 91.8794 |  | 1.6037 | 0.74642 | 0.77034 | 1.6027 | 0.74608 | 0.77078 | 0.54937 | -97.0985 | 87.7913 | 0.56674 | -97.1819 | 87.8696

## LLG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.0026559 | 0.031175 | 0.032868 | 0.0026559 | 0.031175 | 0.032868 | 0.00061335 | 0.0071995 | 0.0075905 | 0.00061336 | 0.0071995 | 0.0075905 | 0.00041348 | 0.0054185 | 0.0052696 | -0.00041332 | -0.0054115 | -0.0052571 | 0.00052746 | 0.0046899 | 0.0060695 | -0.00052712 | -0.0046702 | -0.0060502 | -50.0153 | -159.938 | 67.9021 | 129.9847 | 20.0621 | -112.0979 |  | 1.0927 | 0.99539 | 1.0589 | 1.0921 | 0.99286 | 1.0559 | 1.8913 | -119.0608 | 116.9374 | 1.8844 | -119.1435 | 116.9144
Line10_11_12 | 0.0025832 | 0.0025832 | 0.0025832 | 0.0025832 | 0.0025832 | 0.0025832 | 0.00059655 | 0.00059655 | 0.00059655 | 0.00059656 | 0.00059656 | 0.00059656 | 0.00040908 | 0.00020468 | -0.00061346 | -0.00040905 | -0.00020465 | 0.0006135 | 0.00050733 | -0.00055753 | 0.0001509 | -0.00050726 | 0.0005576 | -0.00015083 | -49.2305 | -49.2305 | -49.2305 | 130.7695 | 130.7695 | 130.7695 |  | 1.0925 | 0.99556 | 1.059 | 1.0923 | 0.99565 | 1.059 | 1.8885 | -119.0713 | 116.9506 | 1.8871 | -119.0766 | 116.9572
Line11_12_13 | 0.0025832 | 0.0025832 | 0.0025832 | 0.0025832 | 0.0025832 | 0.0025832 | 0.00059656 | 0.00059656 | 0.00059656 | 0.00059656 | 0.00059656 | 0.00059656 | 0.00040905 | 0.00020465 | -0.0006135 | -0.00040902 | -0.00020462 | 0.00061354 | 0.00050726 | -0.0005576 | 0.00015083 | -0.0005072 | 0.00055767 | -0.00015076 | -49.2305 | -49.2305 | -49.2305 | 130.7695 | 130.7695 | 130.7695 |  | 1.0923 | 0.99565 | 1.059 | 1.0922 | 0.99574 | 1.059 | 1.8871 | -119.0766 | 116.9572 | 1.8857 | -119.0818 | 116.9638
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -9.131e-09 | -5.437e-09 | 1.4612e-08 | 5.916e-09 | 3.8223e-09 | -9.782e-09 | -1.24e-08 | 1.2977e-08 | -2.8971e-09 | 8.4048e-09 | -8.5901e-09 | 1.7155e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0922 | 0.99574 | 1.059 | 1.0922 | 0.99574 | 1.059 | 1.8857 | -119.0818 | 116.9638 | 1.8857 | -119.0818 | 116.9638
Line13_13_14 | 0.0025833 | 0.0025833 | 0.0025833 | 0.0025833 | 0.0025833 | 0.0025833 | 0.00059658 | 0.00059658 | 0.00059658 | 0.00059658 | 0.00059658 | 0.00059658 | 0.00040903 | 0.00020462 | -0.00061355 | -0.000409 | -0.00020459 | 0.00061359 | 0.00050721 | -0.00055768 | 0.00015077 | -0.00050715 | 0.00055775 | -0.0001507 | -49.2306 | -49.2306 | -49.2306 | 130.7694 | 130.7694 | 130.7694 |  | 1.0922 | 0.99574 | 1.059 | 1.0921 | 0.99582 | 1.0591 | 1.8857 | -119.0818 | 116.9638 | 1.8843 | -119.087 | 116.9704
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.0873e-09 | -3.6246e-09 | 9.7411e-09 | 2.8723e-09 | 2.01e-09 | -4.9114e-09 | -8.2664e-09 | 8.6515e-09 | -1.9314e-09 | 4.2716e-09 | -4.2643e-09 | 7.4975e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0922 | 0.99574 | 1.059 | 1.0922 | 0.99574 | 1.059 | 1.8857 | -119.0818 | 116.9638 | 1.8857 | -119.0818 | 116.9638
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.0437e-09 | -1.8123e-09 | 4.8705e-09 | -1.7134e-10 | 1.9763e-10 | -4.0856e-11 | -4.1332e-09 | 4.3258e-09 | -9.6571e-10 | 1.3837e-10 | 6.1433e-11 | -2.1596e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0922 | 0.99574 | 1.059 | 1.0922 | 0.99574 | 1.059 | 1.8857 | -119.0818 | 116.9638 | 1.8857 | -119.0818 | 116.9638
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.0503e-09 | -1.8367e-09 | 4.9019e-09 | -1.7287e-10 | 1.985e-10 | -4.0609e-11 | -4.1686e-09 | 4.3446e-09 | -9.5862e-10 | 1.3872e-10 | 6.2464e-11 | -2.1735e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0926 | 0.99548 | 1.059 | 1.0926 | 0.99548 | 1.059 | 1.8899 | -119.0661 | 116.944 | 1.8899 | -119.0661 | 116.944
Line17_5_19 | 0.0025987 | 0.0025987 | 0.0025987 | 0.0025987 | 0.0025987 | 0.0025987 | 0.00060015 | 0.00060015 | 0.00060015 | 0.00060015 | 0.00060015 | 0.00060015 | 0.00041007 | 0.0002076 | -0.00061757 | -0.00041004 | -0.00020757 | 0.00061761 | 0.00051167 | -0.00056021 | 0.00015004 | -0.0005116 | 0.00056028 | -0.00014998 | -49.4001 | -49.4001 | -49.4001 | 130.5999 | 130.5999 | 130.5999 |  | 1.0926 | 0.99548 | 1.059 | 1.0925 | 0.99557 | 1.059 | 1.8899 | -119.0661 | 116.944 | 1.8885 | -119.0714 | 116.9507
Line1_1_3 | 0.0025831 | 0.0025831 | 0.0025831 | 0.0025831 | 0.0025831 | 0.0025831 | 0.00059655 | 0.00059655 | 0.00059655 | 0.00059655 | 0.00059655 | 0.00059655 | 0.00040914 | 0.00020474 | -0.00061338 | -0.00040911 | -0.00020471 | 0.00061342 | 0.00050745 | -0.00055738 | 0.00015103 | -0.00050739 | 0.00055745 | -0.00015096 | -49.2305 | -49.2305 | -49.2305 | 130.7695 | 130.7695 | 130.7695 |  | 1.0927 | 0.99539 | 1.0589 | 1.0926 | 0.99548 | 1.059 | 1.8913 | -119.0608 | 116.9374 | 1.8899 | -119.0661 | 116.944
Line2_1_4 | 0.0026039 | 0.0026039 | 0.0026039 | 0.0026039 | 0.0026039 | 0.0026039 | 0.00060134 | 0.00060134 | 0.00060134 | 0.00060135 | 0.00060135 | 0.00060135 | 0.00041041 | 0.00020861 | -0.00061892 | -0.00041038 | -0.00020858 | 0.00061895 | 0.00051316 | -0.00056105 | 0.0001498 | -0.0005131 | 0.00056112 | -0.00014973 | -49.457 | -49.457 | -49.457 | 130.543 | 130.543 | 130.543 |  | 1.0927 | 0.99539 | 1.0589 | 1.0926 | 0.99548 | 1.059 | 1.8913 | -119.0608 | 116.9374 | 1.8899 | -119.0661 | 116.944
Line3_1_5 | 0.0025987 | 0.0025987 | 0.0025987 | 0.0025987 | 0.0025987 | 0.0025987 | 0.00060014 | 0.00060014 | 0.00060014 | 0.00060015 | 0.00060015 | 0.00060015 | 0.0004101 | 0.00020764 | -0.00061753 | -0.00041007 | -0.0002076 | 0.00061757 | 0.00051173 | -0.00056013 | 0.00015011 | -0.00051167 | 0.00056021 | -0.00015004 | -49.4001 | -49.4001 | -49.4001 | 130.5999 | 130.5999 | 130.5999 |  | 1.0927 | 0.99539 | 1.0589 | 1.0926 | 0.99548 | 1.059 | 1.8913 | -119.0608 | 116.9374 | 1.8899 | -119.0661 | 116.944
Line4_2_6 | 0.0026559 | 0.031175 | 0.032868 | 0.0026559 | 0.031175 | 0.032868 | 0.00061336 | 0.0071995 | 0.0075905 | 0.00061336 | 0.0071995 | 0.0075905 | 0.00041332 | 0.0054115 | 0.0052571 | -0.00041315 | -0.0054045 | -0.0052446 | 0.00052712 | 0.0046702 | 0.0060502 | -0.00052677 | -0.0046505 | -0.0060309 | -50.0154 | -159.9379 | 67.9021 | 129.9846 | 20.0621 | -112.098 |  | 1.0921 | 0.99286 | 1.0559 | 1.0915 | 0.99034 | 1.0529 | 1.8844 | -119.1435 | 116.9144 | 1.8775 | -119.2266 | 116.8913
Line5_6_7 | 0.0026559 | 0.031175 | 0.032868 | 0.002656 | 0.031175 | 0.032868 | 0.00061336 | 0.0071995 | 0.0075905 | 0.00061337 | 0.0071995 | 0.0075905 | 0.00041315 | 0.0054045 | 0.0052446 | -0.00041298 | -0.0053975 | -0.0052321 | 0.00052677 | 0.0046505 | 0.0060309 | -0.00052643 | -0.0046307 | -0.0060116 | -50.0154 | -159.9379 | 67.902 | 129.9846 | 20.0621 | -112.098 |  | 1.0915 | 0.99034 | 1.0529 | 1.0908 | 0.98781 | 1.0499 | 1.8775 | -119.2266 | 116.8913 | 1.8706 | -119.3102 | 116.868
Line6_7_8 | 0 | 0.032177 | 0.034192 | 0 | 0.032177 | 0.034192 | 0 | 0.0074309 | 0.0078963 | 0 | 0.0074309 | 0.0078963 | -9.264e-09 | 0.0051833 | 0.0058593 | 6.0137e-09 | -0.0051767 | -0.0058455 | -1.2927e-08 | 0.0051975 | 0.0058655 | 8.7651e-09 | -0.0051767 | -0.0058455 | 0 | -164.3888 | 71.8378 | 0 | 15.6113 | -108.1622 |  | 1.0908 | 0.98781 | 1.0499 | 1.0903 | 0.9852 | 1.0469 | 1.8706 | -119.3102 | 116.868 | 1.8651 | -119.3887 | 116.8377
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.0886e-09 | -1.9362e-09 | 4.9488e-09 | -1.6354e-10 | 2.3386e-10 | 5.7069e-12 | -4.3143e-09 | 4.4301e-09 | -9.1486e-10 | 1.3662e-10 | 4.047e-11 | -2.2234e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0903 | 0.9852 | 1.0469 | 1.0903 | 0.9852 | 1.0469 | 1.8651 | -119.3887 | 116.8377 | 1.8651 | -119.3887 | 116.8377
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.0886e-09 | -1.9362e-09 | 4.9488e-09 | -1.6354e-10 | 2.3386e-10 | 5.707e-12 | -4.3143e-09 | 4.4301e-09 | -9.1486e-10 | 1.3662e-10 | 4.047e-11 | -2.2234e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0903 | 0.9852 | 1.0469 | 1.0903 | 0.9852 | 1.0469 | 1.8651 | -119.3887 | 116.8377 | 1.8651 | -119.3887 | 116.8377
Line9_3_11 | 0.0025831 | 0.0025831 | 0.0025831 | 0.0025832 | 0.0025832 | 0.0025832 | 0.00059655 | 0.00059655 | 0.00059655 | 0.00059655 | 0.00059655 | 0.00059656 | 0.00040911 | 0.00020471 | -0.00061342 | -0.00040908 | -0.00020468 | 0.00061346 | 0.00050739 | -0.00055745 | 0.00015096 | -0.00050733 | 0.00055753 | -0.0001509 | -49.2305 | -49.2305 | -49.2305 | 130.7695 | 130.7695 | 130.7695 |  | 1.0926 | 0.99548 | 1.059 | 1.0925 | 0.99556 | 1.059 | 1.8899 | -119.0661 | 116.944 | 1.8885 | -119.0713 | 116.9506

## LLG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.0027823 | 0.032657 | 0.034429 | 0.0027823 | 0.032657 | 0.034429 | 0.00064254 | 0.0075417 | 0.007951 | 0.00064254 | 0.0075417 | 0.007951 | 0.00045377 | 0.005946 | 0.0057819 | -0.00045358 | -0.0059383 | -0.0057682 | 0.00057885 | 0.0051464 | 0.0066597 | -0.00057847 | -0.0051248 | -0.0066385 | -50.0169 | -159.9448 | 67.8988 | 129.9831 | 20.0553 | -112.1012 |  | 1.1447 | 1.0427 | 1.1092 | 1.144 | 1.0401 | 1.1061 | 1.8897 | -119.0677 | 116.9345 | 1.8828 | -119.1503 | 116.9115
Line10_11_12 | 0.0027061 | 0.0027061 | 0.0027061 | 0.0027061 | 0.0027061 | 0.0027061 | 0.00062494 | 0.00062494 | 0.00062494 | 0.00062494 | 0.00062494 | 0.00062494 | 0.00044894 | 0.00022456 | -0.00067316 | -0.0004489 | -0.00022452 | 0.0006732 | 0.00055675 | -0.00061184 | 0.0001656 | -0.00055668 | 0.00061192 | -0.00016552 | -49.2321 | -49.2321 | -49.2321 | 130.7679 | 130.7679 | 130.7679 |  | 1.1444 | 1.0429 | 1.1093 | 1.1443 | 1.043 | 1.1093 | 1.8869 | -119.0781 | 116.9477 | 1.8855 | -119.0834 | 116.9543
Line11_12_13 | 0.0027061 | 0.0027061 | 0.0027061 | 0.0027061 | 0.0027061 | 0.0027061 | 0.00062494 | 0.00062494 | 0.00062494 | 0.00062495 | 0.00062495 | 0.00062495 | 0.0004489 | 0.00022452 | -0.0006732 | -0.00044887 | -0.00022449 | 0.00067325 | 0.00055668 | -0.00061192 | 0.00016552 | -0.00055661 | 0.000612 | -0.00016545 | -49.2321 | -49.2321 | -49.2321 | 130.7679 | 130.7679 | 130.7679 |  | 1.1443 | 1.043 | 1.1093 | 1.1442 | 1.0431 | 1.1093 | 1.8855 | -119.0834 | 116.9543 | 1.8841 | -119.0886 | 116.9609
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.0021e-08 | -5.966e-09 | 1.6032e-08 | 6.4928e-09 | 4.1945e-09 | -1.0732e-08 | -1.3607e-08 | 1.4243e-08 | -3.1788e-09 | 9.2233e-09 | -9.4285e-09 | 1.882e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1442 | 1.0431 | 1.1093 | 1.1442 | 1.0431 | 1.1093 | 1.8841 | -119.0886 | 116.9609 | 1.8841 | -119.0886 | 116.9609
Line13_13_14 | 0.0027062 | 0.0027062 | 0.0027062 | 0.0027062 | 0.0027062 | 0.0027062 | 0.00062496 | 0.00062496 | 0.00062496 | 0.00062497 | 0.00062497 | 0.00062497 | 0.00044888 | 0.00022449 | -0.00067326 | -0.00044885 | -0.00022446 | 0.0006733 | 0.00055663 | -0.00061201 | 0.00016546 | -0.00055656 | 0.00061209 | -0.00016538 | -49.2322 | -49.2322 | -49.2322 | 130.7678 | 130.7678 | 130.7678 |  | 1.1442 | 1.0431 | 1.1093 | 1.1441 | 1.0432 | 1.1094 | 1.8841 | -119.0886 | 116.9609 | 1.8827 | -119.0938 | 116.9675
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.6807e-09 | -3.9774e-09 | 1.0688e-08 | 3.1525e-09 | 2.2058e-09 | -5.3883e-09 | -9.0715e-09 | 9.4954e-09 | -2.1192e-09 | 4.6875e-09 | -4.6808e-09 | 8.2237e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1442 | 1.0431 | 1.1093 | 1.1442 | 1.0431 | 1.1093 | 1.8841 | -119.0886 | 116.9609 | 1.8841 | -119.0886 | 116.9609
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.3404e-09 | -1.9887e-09 | 5.344e-09 | -1.8785e-10 | 2.1717e-10 | -4.4276e-11 | -4.5358e-09 | 4.7477e-09 | -1.0596e-09 | 1.5173e-10 | 6.6918e-11 | -2.3722e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1442 | 1.0431 | 1.1093 | 1.1442 | 1.0431 | 1.1093 | 1.8841 | -119.0886 | 116.9609 | 1.8841 | -119.0886 | 116.9609
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.3476e-09 | -2.0154e-09 | 5.3784e-09 | -1.8953e-10 | 2.1813e-10 | -4.4004e-11 | -4.5746e-09 | 4.7683e-09 | -1.0518e-09 | 1.5212e-10 | 6.805e-11 | -2.3874e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1446 | 1.0428 | 1.1093 | 1.1446 | 1.0428 | 1.1093 | 1.8883 | -119.073 | 116.9411 | 1.8883 | -119.073 | 116.9411
Line17_5_19 | 0.0027224 | 0.0027224 | 0.0027224 | 0.0027224 | 0.0027224 | 0.0027224 | 0.0006287 | 0.0006287 | 0.0006287 | 0.00062871 | 0.00062871 | 0.00062871 | 0.00045002 | 0.00022777 | -0.00067767 | -0.00044998 | -0.00022773 | 0.00067772 | 0.00056151 | -0.00061478 | 0.00016466 | -0.00056144 | 0.00061486 | -0.00016459 | -49.4017 | -49.4017 | -49.4017 | 130.5983 | 130.5983 | 130.5983 |  | 1.1446 | 1.0428 | 1.1093 | 1.1444 | 1.0429 | 1.1093 | 1.8883 | -119.0729 | 116.9411 | 1.8869 | -119.0782 | 116.9478
Line1_1_3 | 0.002706 | 0.002706 | 0.002706 | 0.002706 | 0.002706 | 0.002706 | 0.00062493 | 0.00062493 | 0.00062493 | 0.00062493 | 0.00062493 | 0.00062493 | 0.000449 | 0.00022462 | -0.00067308 | -0.00044897 | -0.00022459 | 0.00067312 | 0.00055689 | -0.00061169 | 0.00016574 | -0.00055682 | 0.00061176 | -0.00016567 | -49.232 | -49.232 | -49.232 | 130.768 | 130.768 | 130.768 |  | 1.1447 | 1.0427 | 1.1092 | 1.1446 | 1.0428 | 1.1093 | 1.8897 | -119.0677 | 116.9345 | 1.8883 | -119.0729 | 116.9411
Line2_1_4 | 0.0027278 | 0.0027278 | 0.0027278 | 0.0027278 | 0.0027278 | 0.0027278 | 0.00062995 | 0.00062995 | 0.00062995 | 0.00062996 | 0.00062996 | 0.00062996 | 0.00045039 | 0.00022887 | -0.00067915 | -0.00045036 | -0.00022883 | 0.00067919 | 0.00056315 | -0.0006157 | 0.00016439 | -0.00056308 | 0.00061578 | -0.00016432 | -49.4586 | -49.4586 | -49.4586 | 130.5414 | 130.5414 | 130.5414 |  | 1.1447 | 1.0427 | 1.1092 | 1.1446 | 1.0428 | 1.1093 | 1.8897 | -119.0677 | 116.9345 | 1.8883 | -119.073 | 116.9411
Line3_1_5 | 0.0027223 | 0.0027223 | 0.0027223 | 0.0027224 | 0.0027224 | 0.0027224 | 0.0006287 | 0.0006287 | 0.0006287 | 0.0006287 | 0.0006287 | 0.0006287 | 0.00045005 | 0.0002278 | -0.00067763 | -0.00045002 | -0.00022777 | 0.00067767 | 0.00056158 | -0.0006147 | 0.00016474 | -0.00056151 | 0.00061478 | -0.00016466 | -49.4017 | -49.4017 | -49.4017 | 130.5983 | 130.5983 | 130.5983 |  | 1.1447 | 1.0427 | 1.1092 | 1.1446 | 1.0428 | 1.1093 | 1.8897 | -119.0677 | 116.9345 | 1.8883 | -119.0729 | 116.9411
Line4_2_6 | 0.0027823 | 0.032657 | 0.034429 | 0.0027823 | 0.032656 | 0.034429 | 0.00064254 | 0.0075417 | 0.007951 | 0.00064255 | 0.0075417 | 0.007951 | 0.00045358 | 0.0059383 | 0.0057682 | -0.0004534 | -0.0059306 | -0.0057545 | 0.00057847 | 0.0051248 | 0.0066385 | -0.00057809 | -0.0051031 | -0.0066173 | -50.0169 | -159.9447 | 67.8988 | 129.9831 | 20.0553 | -112.1013 |  | 1.144 | 1.0401 | 1.1061 | 1.1434 | 1.0374 | 1.1029 | 1.8828 | -119.1503 | 116.9115 | 1.8759 | -119.2335 | 116.8884
Line5_6_7 | 0.0027823 | 0.032656 | 0.034429 | 0.0027823 | 0.032656 | 0.034429 | 0.00064255 | 0.0075417 | 0.007951 | 0.00064255 | 0.0075417 | 0.007951 | 0.0004534 | 0.0059306 | 0.0057545 | -0.00045321 | -0.0059229 | -0.0057408 | 0.00057809 | 0.0051031 | 0.0066173 | -0.00057771 | -0.0050815 | -0.0065962 | -50.017 | -159.9447 | 67.8987 | 129.983 | 20.0553 | -112.1013 |  | 1.1434 | 1.0374 | 1.1029 | 1.1427 | 1.0348 | 1.0998 | 1.8759 | -119.2335 | 116.8884 | 1.869 | -119.317 | 116.8651
Line6_7_8 | 0 | 0.033706 | 0.035816 | 0 | 0.033706 | 0.035816 | 0 | 0.0077842 | 0.0082713 | 0 | 0.0077842 | 0.0082713 | -1.0167e-08 | 0.0056879 | 0.006429 | 6.6001e-09 | -0.0056806 | -0.0064139 | -1.4186e-08 | 0.0057035 | 0.0064358 | 9.6187e-09 | -0.0056806 | -0.0064138 | 0 | -164.3956 | 71.8349 | 0 | 15.6044 | -108.1651 |  | 1.1427 | 1.0348 | 1.0998 | 1.1422 | 1.032 | 1.0966 | 1.869 | -119.317 | 116.8651 | 1.8635 | -119.3955 | 116.8349
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.3897e-09 | -2.1246e-09 | 5.4299e-09 | -1.7929e-10 | 2.5692e-10 | 6.8081e-12 | -4.7344e-09 | 4.8622e-09 | -1.0038e-09 | 1.4981e-10 | 4.3918e-11 | -2.4422e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1422 | 1.032 | 1.0966 | 1.1422 | 1.032 | 1.0966 | 1.8635 | -119.3955 | 116.8349 | 1.8635 | -119.3955 | 116.8349
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.3897e-09 | -2.1246e-09 | 5.4299e-09 | -1.7929e-10 | 2.5692e-10 | 6.8081e-12 | -4.7344e-09 | 4.8622e-09 | -1.0038e-09 | 1.4981e-10 | 4.3918e-11 | -2.4422e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1422 | 1.032 | 1.0966 | 1.1422 | 1.032 | 1.0966 | 1.8635 | -119.3955 | 116.8349 | 1.8635 | -119.3955 | 116.8349
Line9_3_11 | 0.002706 | 0.002706 | 0.002706 | 0.0027061 | 0.0027061 | 0.0027061 | 0.00062493 | 0.00062493 | 0.00062493 | 0.00062494 | 0.00062494 | 0.00062494 | 0.00044897 | 0.00022459 | -0.00067312 | -0.00044894 | -0.00022456 | 0.00067316 | 0.00055682 | -0.00061176 | 0.00016567 | -0.00055675 | 0.00061184 | -0.0001656 | -49.2321 | -49.2321 | -49.2321 | 130.7679 | 130.7679 | 130.7679 |  | 1.1446 | 1.0428 | 1.1093 | 1.1444 | 1.0429 | 1.1093 | 1.8883 | -119.0729 | 116.9411 | 1.8869 | -119.0781 | 116.9477

## LLG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.020892 | 1.4004 | 1.5145 | 0.020892 | 1.4004 | 1.5145 | 0.0048248 | 0.32342 | 0.34975 | 0.0048248 | 0.32342 | 0.34975 | 0.0001259 | 0.14943 | 0.17691 | -0.00010553 | -0.1121 | -0.13267 | 0.0066824 | 0.16108 | 0.17885 | -0.0066607 | -0.12071 | -0.13425 | -87.9409 | -146.3468 | 40.3394 | 92.0591 | 33.6532 | -139.6606 |  | 1.3853 | 0.67936 | 0.71926 | 1.3807 | 0.50935 | 0.53963 | 0.97968 | -99.1976 | 85.652 | 1.1514 | -99.2273 | 85.6784
Line10_11_12 | 0.020316 | 0.020316 | 0.020316 | 0.020316 | 0.020316 | 0.020316 | 0.0046917 | 0.0046917 | 0.0046917 | 0.0046918 | 0.0046918 | 0.0046918 | 0.00028533 | 0.0031007 | -0.0033503 | -0.00028137 | -0.0030967 | 0.0033543 | 0.0064844 | -0.00071242 | 0.00045637 | -0.0064804 | 0.00071655 | -0.00045224 | -86.4342 | -86.4342 | -86.4342 | 93.5658 | 93.5658 | 93.5658 |  | 1.3834 | 0.6781 | 0.72069 | 1.3825 | 0.67748 | 0.72141 | 1.0463 | -99.3741 | 85.809 | 1.0796 | -99.4626 | 85.8873
Line11_12_13 | 0.020316 | 0.020316 | 0.020316 | 0.020316 | 0.020316 | 0.020316 | 0.0046918 | 0.0046918 | 0.0046918 | 0.0046918 | 0.0046918 | 0.0046918 | 0.00028137 | 0.0030967 | -0.0033543 | -0.00027741 | -0.0030928 | 0.0033583 | 0.0064804 | -0.00071655 | 0.00045224 | -0.0064763 | 0.00072069 | -0.00044812 | -86.4342 | -86.4343 | -86.4342 | 93.5658 | 93.5657 | 93.5658 |  | 1.3825 | 0.67748 | 0.72141 | 1.3816 | 0.67686 | 0.72213 | 1.0796 | -99.4626 | 85.8873 | 1.113 | -99.5512 | 85.9654
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0593e-10 | -7.4641e-08 | 7.8792e-08 | -2.3913e-09 | 5.029e-08 | -5.2356e-08 | -1.532e-07 | 1.4404e-08 | -6.2043e-09 | 1.0222e-07 | -8.779e-09 | 2.7283e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3816 | 0.67686 | 0.72213 | 1.3816 | 0.67686 | 0.72213 | 1.113 | -99.5512 | 85.9654 | 1.113 | -99.5512 | 85.9654
Line13_13_14 | 0.020317 | 0.020317 | 0.020317 | 0.020317 | 0.020317 | 0.020317 | 0.0046919 | 0.0046919 | 0.0046919 | 0.0046919 | 0.0046919 | 0.0046919 | 0.0002774 | 0.0030929 | -0.0033584 | -0.00027344 | -0.0030889 | 0.0033624 | 0.0064764 | -0.0007207 | 0.00044812 | -0.0064724 | 0.00072483 | -0.000444 | -86.4343 | -86.4343 | -86.4343 | 93.5657 | 93.5657 | 93.5657 |  | 1.3816 | 0.67686 | 0.72213 | 1.3807 | 0.67623 | 0.72285 | 1.113 | -99.5512 | 85.9654 | 1.1465 | -99.6401 | 86.0434
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0395e-10 | -4.9761e-08 | 5.2528e-08 | -2.2894e-09 | 2.541e-08 | -2.6092e-08 | -1.0213e-07 | 9.6027e-09 | -4.1362e-09 | 5.1159e-08 | -3.9776e-09 | 6.6023e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3816 | 0.67686 | 0.72213 | 1.3816 | 0.67686 | 0.72213 | 1.113 | -99.5512 | 85.9654 | 1.113 | -99.5512 | 85.9654
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0198e-10 | -2.488e-08 | 2.6264e-08 | -2.1874e-09 | 5.2932e-10 | 1.7247e-10 | -5.1066e-08 | 4.8014e-09 | -2.0681e-09 | 9.3485e-11 | 8.2371e-10 | -1.4079e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3816 | 0.67686 | 0.72213 | 1.3816 | 0.67686 | 0.72213 | 1.113 | -99.5512 | 85.9654 | 1.113 | -99.5512 | 85.9654
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0559e-10 | -2.5144e-08 | 2.635e-08 | -2.2055e-09 | 5.2229e-10 | 1.7185e-10 | -5.1474e-08 | 4.5849e-09 | -2.0325e-09 | 8.5296e-11 | 8.3623e-10 | -1.4122e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3844 | 0.67872 | 0.71999 | 1.3844 | 0.67872 | 0.71999 | 1.0135 | -99.286 | 85.7308 | 1.0135 | -99.286 | 85.7308
Line17_5_19 | 0.020439 | 0.020439 | 0.020439 | 0.020439 | 0.020439 | 0.020439 | 0.0047201 | 0.0047201 | 0.0047201 | 0.0047202 | 0.0047202 | 0.0047202 | 0.0002539 | 0.0031274 | -0.0033693 | -0.00024989 | -0.0031234 | 0.0033733 | 0.0065294 | -0.00069483 | 0.00044414 | -0.0065253 | 0.00069901 | -0.00043997 | -86.7597 | -86.7597 | -86.7597 | 93.2403 | 93.2403 | 93.2403 |  | 1.3844 | 0.67872 | 0.71998 | 1.3834 | 0.67809 | 0.72071 | 1.0134 | -99.286 | 85.7307 | 1.0471 | -99.3745 | 85.8093
Line1_1_3 | 0.020315 | 0.020315 | 0.020315 | 0.020316 | 0.020316 | 0.020316 | 0.0046916 | 0.0046916 | 0.0046916 | 0.0046917 | 0.0046917 | 0.0046917 | 0.00029325 | 0.0031086 | -0.0033424 | -0.00028929 | -0.0031046 | 0.0033464 | 0.0064926 | -0.00070416 | 0.00046462 | -0.0064885 | 0.00070829 | -0.00046049 | -86.4342 | -86.4342 | -86.4341 | 93.5658 | 93.5658 | 93.5659 |  | 1.3853 | 0.67936 | 0.71926 | 1.3844 | 0.67873 | 0.71997 | 0.97968 | -99.1976 | 85.652 | 1.013 | -99.2857 | 85.7306
Line2_1_4 | 0.020479 | 0.020479 | 0.020479 | 0.02048 | 0.02048 | 0.02048 | 0.0047295 | 0.0047295 | 0.0047295 | 0.0047296 | 0.0047296 | 0.0047296 | 0.00024593 | 0.003139 | -0.0033728 | -0.00024191 | -0.003135 | 0.0033769 | 0.0065471 | -0.00068604 | 0.00044278 | -0.0065429 | 0.00069024 | -0.00043859 | -86.8691 | -86.8691 | -86.8691 | 93.1309 | 93.1309 | 93.1309 |  | 1.3853 | 0.67936 | 0.71926 | 1.3844 | 0.67872 | 0.71999 | 0.97968 | -99.1976 | 85.652 | 1.0135 | -99.286 | 85.7308
Line3_1_5 | 0.020439 | 0.020439 | 0.020439 | 0.020439 | 0.020439 | 0.020439 | 0.0047201 | 0.0047201 | 0.0047201 | 0.0047201 | 0.0047201 | 0.0047201 | 0.00025791 | 0.0031314 | -0.0033652 | -0.0002539 | -0.0031274 | 0.0033693 | 0.0065335 | -0.00069065 | 0.00044832 | -0.0065294 | 0.00069483 | -0.00044414 | -86.7597 | -86.7597 | -86.7597 | 93.2403 | 93.2403 | 93.2403 |  | 1.3853 | 0.67936 | 0.71926 | 1.3844 | 0.67872 | 0.71998 | 0.97968 | -99.1976 | 85.652 | 1.0134 | -99.286 | 85.7307
Line4_2_6 | 0.020892 | 1.4004 | 1.5145 | 0.020892 | 1.4004 | 1.5145 | 0.0048248 | 0.32342 | 0.34975 | 0.0048249 | 0.32342 | 0.34975 | 0.00010552 | 0.1121 | 0.13267 | -8.5146e-05 | -0.074765 | -0.088424 | 0.0066607 | 0.12071 | 0.13425 | -0.006639 | -0.080344 | -0.089642 | -87.941 | -146.3468 | 40.3394 | 92.059 | 33.6532 | -139.6606 |  | 1.3807 | 0.50935 | 0.53963 | 1.3761 | 0.33934 | 0.36001 | 1.1514 | -99.2273 | 85.6784 | 1.3243 | -99.2868 | 85.7312
Line5_6_7 | 0.020892 | 1.4004 | 1.5145 | 0.020892 | 1.4004 | 1.5145 | 0.0048249 | 0.32342 | 0.34975 | 0.0048249 | 0.32342 | 0.34975 | 8.5144e-05 | 0.074765 | 0.088424 | -6.4765e-05 | -0.037433 | -0.044182 | 0.006639 | 0.080344 | 0.089642 | -0.0066172 | -0.039976 | -0.045038 | -87.941 | -146.3468 | 40.3394 | 92.059 | 33.6533 | -139.6606 |  | 1.3761 | 0.33934 | 0.36001 | 1.3715 | 0.16934 | 0.18039 | 1.3243 | -99.2868 | 85.7312 | 1.4983 | -99.4657 | 85.8892
Line6_7_8 | 0 | 1.3896 | 1.5275 | 0 | 1.3896 | 1.5275 | 0 | 0.32092 | 0.35276 | 0 | 0.32092 | 0.35276 | 5.7376e-09 | 0.036633 | 0.045047 | -6.294e-09 | 5.8992e-15 | -5.9225e-15 | -1.5739e-07 | 0.040139 | 0.044945 | 1.0491e-07 | -1.6849e-14 | 1.2296e-14 | 0 | -147.0805 | 40.9546 | 0 | 32.9195 | -139.0454 |  | 1.3715 | 0.16934 | 0.18039 | 1.3679 | 0 | 0 | 1.4983 | -99.4657 | 85.8892 | 1.6373 | 0 | 0
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.098e-09 | -1.3757e-21 | -5.1569e-22 | -2.098e-09 | 6.541e-18 | -1.1633e-17 | -5.2389e-08 | -1.8335e-21 | -1.2593e-21 | 1.3615e-10 | 2.1772e-17 | -2.1792e-18 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3679 | 0 | 0 | 1.3679 | 0 | 0 | 1.6373 | 0 | 0 | 1.6373 | 0 | 0
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.098e-09 | -1.3757e-21 | -5.1569e-22 | -2.098e-09 | 6.541e-18 | -1.1633e-17 | -5.2389e-08 | -1.8335e-21 | -1.2593e-21 | 1.3615e-10 | 2.1772e-17 | -2.1792e-18 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3679 | 0 | 0 | 1.3679 | 0 | 0 | 1.6373 | 0 | 0 | 1.6373 | 0 | 0
Line9_3_11 | 0.020316 | 0.020316 | 0.020316 | 0.020316 | 0.020316 | 0.020316 | 0.0046917 | 0.0046917 | 0.0046917 | 0.0046917 | 0.0046917 | 0.0046917 | 0.00028929 | 0.0031046 | -0.0033464 | -0.00028533 | -0.0031007 | 0.0033503 | 0.0064885 | -0.00070829 | 0.00046049 | -0.0064844 | 0.00071242 | -0.00045637 | -86.4342 | -86.4342 | -86.4342 | 93.5658 | 93.5658 | 93.5658 |  | 1.3844 | 0.67873 | 0.71997 | 1.3834 | 0.6781 | 0.72069 | 1.013 | -99.2857 | 85.7306 | 1.0463 | -99.3741 | 85.809

## LLG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.019792 | 1.3267 | 1.4348 | 0.019792 | 1.3267 | 1.4348 | 0.0045708 | 0.3064 | 0.33135 | 0.0045709 | 0.3064 | 0.33135 | 0.000113 | 0.13411 | 0.15878 | -9.471e-05 | -0.10061 | -0.11907 | 0.0059975 | 0.14457 | 0.16052 | -0.005978 | -0.10834 | -0.12049 | -87.9409 | -146.3468 | 40.3394 | 92.0591 | 33.6532 | -139.6606 |  | 1.3124 | 0.6436 | 0.6814 | 1.308 | 0.48254 | 0.51123 | 0.97968 | -99.1976 | 85.652 | 1.1514 | -99.2273 | 85.6784
Line10_11_12 | 0.019246 | 0.019246 | 0.019246 | 0.019247 | 0.019247 | 0.019247 | 0.0044448 | 0.0044448 | 0.0044448 | 0.0044448 | 0.0044448 | 0.0044448 | 0.00025608 | 0.0027829 | -0.003007 | -0.00025253 | -0.0027793 | 0.0030105 | 0.0058198 | -0.0006394 | 0.00040959 | -0.0058162 | 0.00064311 | -0.00040589 | -86.4342 | -86.4342 | -86.4342 | 93.5658 | 93.5658 | 93.5658 |  | 1.3106 | 0.64241 | 0.68276 | 1.3098 | 0.64182 | 0.68344 | 1.0463 | -99.3741 | 85.809 | 1.0796 | -99.4626 | 85.8873
Line11_12_13 | 0.019247 | 0.019247 | 0.019247 | 0.019247 | 0.019247 | 0.019247 | 0.0044448 | 0.0044448 | 0.0044448 | 0.0044449 | 0.0044449 | 0.0044449 | 0.00025253 | 0.0027793 | -0.0030105 | -0.00024897 | -0.0027758 | 0.0030141 | 0.0058162 | -0.00064311 | 0.00040589 | -0.0058125 | 0.00064682 | -0.00040219 | -86.4342 | -86.4343 | -86.4342 | 93.5658 | 93.5657 | 93.5658 |  | 1.3098 | 0.64182 | 0.68344 | 1.3089 | 0.64123 | 0.68412 | 1.0796 | -99.4626 | 85.8873 | 1.113 | -99.5512 | 85.9654
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7457e-10 | -6.6991e-08 | 7.0716e-08 | -2.1462e-09 | 4.5136e-08 | -4.699e-08 | -1.375e-07 | 1.2928e-08 | -5.5684e-09 | 9.1747e-08 | -7.8792e-09 | 2.4487e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3089 | 0.64123 | 0.68412 | 1.3089 | 0.64123 | 0.68412 | 1.113 | -99.5512 | 85.9654 | 1.113 | -99.5512 | 85.9654
Line13_13_14 | 0.019247 | 0.019247 | 0.019247 | 0.019247 | 0.019247 | 0.019247 | 0.004445 | 0.004445 | 0.004445 | 0.004445 | 0.004445 | 0.004445 | 0.00024897 | 0.0027759 | -0.0030142 | -0.00024542 | -0.0027723 | 0.0030178 | 0.0058126 | -0.00064683 | 0.00040219 | -0.005809 | 0.00065054 | -0.00039849 | -86.4343 | -86.4343 | -86.4343 | 93.5657 | 93.5657 | 93.5657 |  | 1.3089 | 0.64123 | 0.68412 | 1.308 | 0.64064 | 0.68481 | 1.113 | -99.5512 | 85.9654 | 1.1465 | -99.6401 | 86.0434
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8305e-10 | -4.4661e-08 | 4.7144e-08 | -2.0547e-09 | 2.2805e-08 | -2.3417e-08 | -9.1663e-08 | 8.6185e-09 | -3.7123e-09 | 4.5916e-08 | -3.57e-09 | 5.9256e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3089 | 0.64123 | 0.68412 | 1.3089 | 0.64123 | 0.68412 | 1.113 | -99.5512 | 85.9654 | 1.113 | -99.5512 | 85.9654
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.1525e-11 | -2.233e-08 | 2.3572e-08 | -1.9632e-09 | 4.7507e-10 | 1.5479e-10 | -4.5832e-08 | 4.3093e-09 | -1.8561e-09 | 8.3904e-11 | 7.3929e-10 | -1.2636e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3089 | 0.64123 | 0.68412 | 1.3089 | 0.64123 | 0.68412 | 1.113 | -99.5512 | 85.9654 | 1.113 | -99.5512 | 85.9654
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7427e-10 | -2.2567e-08 | 2.3649e-08 | -1.9795e-09 | 4.6876e-10 | 1.5423e-10 | -4.6198e-08 | 4.115e-09 | -1.8242e-09 | 7.6554e-11 | 7.5052e-10 | -1.2674e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3115 | 0.643 | 0.68209 | 1.3115 | 0.643 | 0.68209 | 1.0135 | -99.286 | 85.7308 | 1.0135 | -99.286 | 85.7308
Line17_5_19 | 0.019363 | 0.019363 | 0.019363 | 0.019363 | 0.019363 | 0.019363 | 0.0044717 | 0.0044717 | 0.0044717 | 0.0044717 | 0.0044717 | 0.0044717 | 0.00022788 | 0.0028069 | -0.0030239 | -0.00022428 | -0.0028033 | 0.0030276 | 0.0058602 | -0.00062361 | 0.00039862 | -0.0058565 | 0.00062737 | -0.00039488 | -86.7597 | -86.7597 | -86.7597 | 93.2403 | 93.2403 | 93.2403 |  | 1.3115 | 0.643 | 0.68209 | 1.3106 | 0.6424 | 0.68278 | 1.0134 | -99.286 | 85.7307 | 1.0471 | -99.3745 | 85.8093
Line1_1_3 | 0.019246 | 0.019246 | 0.019246 | 0.019246 | 0.019246 | 0.019246 | 0.0044447 | 0.0044447 | 0.0044447 | 0.0044447 | 0.0044447 | 0.0044448 | 0.0002632 | 0.00279 | -0.0029998 | -0.00025964 | -0.0027864 | 0.0030034 | 0.0058271 | -0.00063199 | 0.000417 | -0.0058235 | 0.00063569 | -0.0004133 | -86.4342 | -86.4342 | -86.4341 | 93.5658 | 93.5658 | 93.5659 |  | 1.3124 | 0.6436 | 0.6814 | 1.3115 | 0.64301 | 0.68208 | 0.97968 | -99.1976 | 85.652 | 1.013 | -99.2857 | 85.7306
Line2_1_4 | 0.019402 | 0.019402 | 0.019402 | 0.019402 | 0.019402 | 0.019402 | 0.0044806 | 0.0044806 | 0.0044806 | 0.0044806 | 0.0044806 | 0.0044806 | 0.00022073 | 0.0028172 | -0.0030271 | -0.00021712 | -0.0028136 | 0.0030308 | 0.005876 | -0.00061572 | 0.0003974 | -0.0058723 | 0.00061949 | -0.00039364 | -86.8691 | -86.8691 | -86.8691 | 93.1309 | 93.1309 | 93.1309 |  | 1.3124 | 0.6436 | 0.6814 | 1.3115 | 0.643 | 0.68209 | 0.97968 | -99.1976 | 85.652 | 1.0135 | -99.286 | 85.7308
Line3_1_5 | 0.019363 | 0.019363 | 0.019363 | 0.019363 | 0.019363 | 0.019363 | 0.0044717 | 0.0044717 | 0.0044717 | 0.0044717 | 0.0044717 | 0.0044717 | 0.00023148 | 0.0028104 | -0.0030203 | -0.00022788 | -0.0028069 | 0.0030239 | 0.0058639 | -0.00061986 | 0.00040237 | -0.0058602 | 0.00062361 | -0.00039862 | -86.7597 | -86.7597 | -86.7597 | 93.2403 | 93.2403 | 93.2403 |  | 1.3124 | 0.6436 | 0.6814 | 1.3115 | 0.643 | 0.68209 | 0.97968 | -99.1976 | 85.652 | 1.0134 | -99.286 | 85.7307
Line4_2_6 | 0.019792 | 1.3267 | 1.4348 | 0.019793 | 1.3267 | 1.4348 | 0.0045709 | 0.3064 | 0.33135 | 0.0045709 | 0.3064 | 0.33135 | 9.4708e-05 | 0.10061 | 0.11907 | -7.6419e-05 | -0.067102 | -0.079362 | 0.005978 | 0.10834 | 0.12049 | -0.0059585 | -0.072109 | -0.080454 | -87.941 | -146.3468 | 40.3394 | 92.059 | 33.6532 | -139.6606 |  | 1.308 | 0.48254 | 0.51123 | 1.3037 | 0.32148 | 0.34106 | 1.1514 | -99.2273 | 85.6784 | 1.3243 | -99.2868 | 85.7312
Line5_6_7 | 0.019793 | 1.3267 | 1.4348 | 0.019793 | 1.3267 | 1.4348 | 0.0045709 | 0.3064 | 0.33135 | 0.004571 | 0.3064 | 0.33135 | 7.6417e-05 | 0.067102 | 0.079362 | -5.8127e-05 | -0.033597 | -0.039654 | 0.0059585 | 0.072109 | 0.080454 | -0.005939 | -0.035878 | -0.040422 | -87.941 | -146.3468 | 40.3394 | 92.059 | 33.6533 | -139.6606 |  | 1.3037 | 0.32148 | 0.34106 | 1.2994 | 0.16042 | 0.17089 | 1.3243 | -99.2868 | 85.7312 | 1.4983 | -99.4657 | 85.8892
Line6_7_8 | 0 | 1.3165 | 1.4471 | 0 | 1.3165 | 1.4471 | 0 | 0.30403 | 0.3342 | 0 | 0.30403 | 0.3342 | 5.1495e-09 | 0.032878 | 0.04043 | -5.6489e-09 | 5.4923e-15 | -5.5626e-15 | -1.4126e-07 | 0.036025 | 0.040338 | 9.4161e-08 | -1.5056e-14 | 1.0969e-14 | 0 | -147.0805 | 40.9546 | 0 | 32.9195 | -139.0454 |  | 1.2994 | 0.16042 | 0.17089 | 1.2959 | 0 | 0 | 1.4983 | -99.4657 | 85.8892 | 1.6373 | 0 | 0
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.883e-09 | -1.2134e-21 | -4.4136e-22 | -1.883e-09 | 5.8706e-18 | -1.0441e-17 | -4.7019e-08 | -1.6619e-21 | -1.1441e-21 | 1.2219e-10 | 1.9541e-17 | -1.9558e-18 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.2959 | 0 | 0 | 1.2959 | 0 | 0 | 1.6373 | 0 | 0 | 1.6373 | 0 | 0
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.883e-09 | -1.2134e-21 | -4.4136e-22 | -1.883e-09 | 5.8706e-18 | -1.0441e-17 | -4.7019e-08 | -1.6619e-21 | -1.1441e-21 | 1.2219e-10 | 1.9541e-17 | -1.9558e-18 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.2959 | 0 | 0 | 1.2959 | 0 | 0 | 1.6373 | 0 | 0 | 1.6373 | 0 | 0
Line9_3_11 | 0.019246 | 0.019246 | 0.019246 | 0.019246 | 0.019246 | 0.019246 | 0.0044447 | 0.0044447 | 0.0044448 | 0.0044448 | 0.0044448 | 0.0044448 | 0.00025964 | 0.0027864 | -0.0030034 | -0.00025609 | -0.0027829 | 0.003007 | 0.0058235 | -0.00063569 | 0.00041329 | -0.0058198 | 0.0006394 | -0.00040959 | -86.4342 | -86.4342 | -86.4342 | 93.5658 | 93.5658 | 93.5658 |  | 1.3115 | 0.64301 | 0.68208 | 1.3106 | 0.64241 | 0.68276 | 1.013 | -99.2857 | 85.7306 | 1.0463 | -99.3741 | 85.809

## LLG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.0023988 | 0.028111 | 0.029636 | 0.0023989 | 0.028111 | 0.029636 | 0.00055399 | 0.0064919 | 0.0068441 | 0.00055399 | 0.0064919 | 0.0068441 | 0.00033538 | 0.0044326 | 0.0043194 | -0.00033511 | -0.00442 | -0.0043016 | 0.00043288 | 0.0038124 | 0.0049336 | -0.0004326 | -0.0037955 | -0.0049188 | -50.341 | -159.7735 | 68.144 | 129.659 | 20.2265 | -111.856 |  | 0.98846 | 0.9006 | 0.95809 | 0.98775 | 0.89743 | 0.95475 | 1.892 | -119.0756 | 116.9418 | 1.8958 | -119.1203 | 116.9735
Line10_11_12 | 0.0023327 | 0.0023327 | 0.0023327 | 0.0023327 | 0.0023327 | 0.0023327 | 0.00053871 | 0.00053871 | 0.00053871 | 0.00053872 | 0.00053872 | 0.00053872 | 0.00033698 | 0.00016391 | -0.00050042 | -0.00033693 | -0.00016386 | 0.00050047 | 0.00041211 | -0.00045671 | 0.00012671 | -0.00041206 | 0.00045677 | -0.00012666 | -48.8343 | -48.8343 | -48.8343 | 131.1657 | 131.1657 | 131.1657 |  | 0.98818 | 0.90072 | 0.95823 | 0.98804 | 0.90079 | 0.9583 | 1.8933 | -119.0915 | 116.9563 | 1.8939 | -119.0995 | 116.9636
Line11_12_13 | 0.0023327 | 0.0023327 | 0.0023327 | 0.0023327 | 0.0023327 | 0.0023327 | 0.00053872 | 0.00053872 | 0.00053872 | 0.00053872 | 0.00053872 | 0.00053872 | 0.00033693 | 0.00016386 | -0.00050047 | -0.00033688 | -0.00016381 | 0.00050053 | 0.00041206 | -0.00045677 | 0.00012666 | -0.00041201 | 0.00045682 | -0.00012661 | -48.8343 | -48.8343 | -48.8343 | 131.1657 | 131.1657 | 131.1657 |  | 0.98804 | 0.90079 | 0.9583 | 0.9879 | 0.90085 | 0.95837 | 1.8939 | -119.0995 | 116.9636 | 1.8946 | -119.1075 | 116.9709
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.5175e-09 | -4.3741e-09 | 1.1925e-08 | 4.8725e-09 | 3.078e-09 | -7.9843e-09 | -1.0084e-08 | 1.0631e-08 | -2.4372e-09 | 6.8364e-09 | -7.0388e-09 | 1.4484e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.9879 | 0.90085 | 0.95837 | 0.9879 | 0.90085 | 0.95837 | 1.8946 | -119.1075 | 116.9709 | 1.8946 | -119.1075 | 116.9709
Line13_13_14 | 0.0023328 | 0.0023328 | 0.0023328 | 0.0023328 | 0.0023328 | 0.0023328 | 0.00053873 | 0.00053873 | 0.00053873 | 0.00053874 | 0.00053874 | 0.00053874 | 0.00033689 | 0.00016381 | -0.00050054 | -0.00033684 | -0.00016376 | 0.0005006 | 0.00041202 | -0.00045683 | 0.00012661 | -0.00041197 | 0.00045689 | -0.00012655 | -48.8344 | -48.8344 | -48.8344 | 131.1656 | 131.1656 | 131.1656 |  | 0.9879 | 0.90085 | 0.95837 | 0.98776 | 0.90091 | 0.95844 | 1.8946 | -119.1075 | 116.9709 | 1.8952 | -119.1154 | 116.9782
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.0116e-09 | -2.9161e-09 | 7.9503e-09 | 2.3667e-09 | 1.62e-09 | -4.0092e-09 | -6.7227e-09 | 7.0876e-09 | -1.6248e-09 | 3.4751e-09 | -3.4949e-09 | 6.36e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.9879 | 0.90085 | 0.95837 | 0.9879 | 0.90085 | 0.95837 | 1.8946 | -119.1075 | 116.9709 | 1.8946 | -119.1075 | 116.9709
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5058e-09 | -1.458e-09 | 3.9751e-09 | -1.3917e-10 | 1.6197e-10 | -3.4081e-11 | -3.3613e-09 | 3.5438e-09 | -8.1241e-10 | 1.1377e-10 | 4.888e-11 | -1.7641e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.9879 | 0.90085 | 0.95837 | 0.9879 | 0.90085 | 0.95837 | 1.8946 | -119.1075 | 116.9709 | 1.8946 | -119.1075 | 116.9709
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5028e-09 | -1.4881e-09 | 4.0025e-09 | -1.4074e-10 | 1.6253e-10 | -3.3417e-11 | -3.3971e-09 | 3.5554e-09 | -7.9592e-10 | 1.137e-10 | 5.0175e-11 | -1.7764e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.98832 | 0.90066 | 0.95817 | 0.98832 | 0.90066 | 0.95817 | 1.8927 | -119.0836 | 116.9491 | 1.8927 | -119.0836 | 116.9491
Line17_5_19 | 0.0023468 | 0.0023468 | 0.0023468 | 0.0023468 | 0.0023468 | 0.0023468 | 0.00054197 | 0.00054197 | 0.00054197 | 0.00054198 | 0.00054198 | 0.00054198 | 0.00033671 | 0.00016756 | -0.00050411 | -0.00033666 | -0.00016751 | 0.00050417 | 0.00041658 | -0.00045847 | 0.00012467 | -0.00041653 | 0.00045853 | -0.00012462 | -49.1598 | -49.1598 | -49.1598 | 130.8402 | 130.8402 | 130.8402 |  | 0.98832 | 0.90066 | 0.95816 | 0.98818 | 0.90072 | 0.95824 | 1.8927 | -119.0836 | 116.9491 | 1.8934 | -119.0917 | 116.9564
Line1_1_3 | 0.0023327 | 0.0023326 | 0.0023327 | 0.0023327 | 0.0023327 | 0.0023327 | 0.0005387 | 0.0005387 | 0.0005387 | 0.00053871 | 0.00053871 | 0.00053871 | 0.00033708 | 0.00016401 | -0.0005003 | -0.00033703 | -0.00016396 | 0.00050036 | 0.00041221 | -0.00045659 | 0.00012682 | -0.00041216 | 0.00045665 | -0.00012677 | -48.8343 | -48.8342 | -48.8342 | 131.1657 | 131.1657 | 131.1657 |  | 0.98846 | 0.9006 | 0.95809 | 0.98832 | 0.90066 | 0.95816 | 1.892 | -119.0756 | 116.9418 | 1.8927 | -119.0835 | 116.9491
Line2_1_4 | 0.0023515 | 0.0023515 | 0.0023515 | 0.0023515 | 0.0023515 | 0.0023515 | 0.00054305 | 0.00054305 | 0.00054305 | 0.00054306 | 0.00054306 | 0.00054306 | 0.00033664 | 0.00016882 | -0.0005053 | -0.00033658 | -0.00016877 | 0.00050536 | 0.00041811 | -0.00045901 | 0.00012401 | -0.00041806 | 0.00045907 | -0.00012396 | -49.2692 | -49.2691 | -49.2691 | 130.7308 | 130.7309 | 130.7309 |  | 0.98846 | 0.9006 | 0.95809 | 0.98832 | 0.90066 | 0.95817 | 1.892 | -119.0756 | 116.9418 | 1.8927 | -119.0836 | 116.9491
Line3_1_5 | 0.0023468 | 0.0023468 | 0.0023468 | 0.0023468 | 0.0023468 | 0.0023468 | 0.00054197 | 0.00054197 | 0.00054197 | 0.00054197 | 0.00054197 | 0.00054197 | 0.00033676 | 0.00016761 | -0.00050405 | -0.00033671 | -0.00016756 | 0.00050411 | 0.00041663 | -0.00045841 | 0.00012473 | -0.00041658 | 0.00045847 | -0.00012467 | -49.1598 | -49.1598 | -49.1598 | 130.8402 | 130.8402 | 130.8402 |  | 0.98846 | 0.9006 | 0.95809 | 0.98832 | 0.90066 | 0.95816 | 1.892 | -119.0756 | 116.9418 | 1.8927 | -119.0836 | 116.9491
Line4_2_6 | 0.0023989 | 0.028111 | 0.029636 | 0.0023989 | 0.028111 | 0.029636 | 0.00055399 | 0.0064919 | 0.0068441 | 0.000554 | 0.0064919 | 0.0068441 | 0.00033511 | 0.00442 | 0.0043016 | -0.00033484 | -0.0044073 | -0.0042838 | 0.0004326 | 0.0037955 | 0.0049188 | -0.00043231 | -0.0037786 | -0.004904 | -50.341 | -159.7735 | 68.144 | 129.659 | 20.2266 | -111.8561 |  | 0.98775 | 0.89743 | 0.95475 | 0.98704 | 0.89425 | 0.95141 | 1.8958 | -119.1203 | 116.9735 | 1.8996 | -119.1653 | 117.0055
Line5_6_7 | 0.0023989 | 0.028111 | 0.029636 | 0.0023989 | 0.028111 | 0.029636 | 0.000554 | 0.0064919 | 0.0068441 | 0.000554 | 0.0064919 | 0.0068441 | 0.00033484 | 0.0044073 | 0.0042838 | -0.00033458 | -0.0043947 | -0.004266 | 0.00043231 | 0.0037786 | 0.004904 | -0.00043203 | -0.0037617 | -0.0048891 | -50.3411 | -159.7734 | 68.1439 | 129.659 | 20.2266 | -111.8561 |  | 0.98704 | 0.89425 | 0.95141 | 0.98634 | 0.89108 | 0.94806 | 1.8996 | -119.1653 | 117.0055 | 1.9035 | -119.2107 | 117.0377
Line6_7_8 | 0 | 0.028997 | 0.030852 | 0 | 0.028997 | 0.030852 | 0 | 0.0066966 | 0.007125 | 0 | 0.0066966 | 0.007125 | -7.4792e-09 | 0.0042167 | 0.0047785 | 4.8503e-09 | -0.0042042 | -0.0047592 | -1.0639e-08 | 0.0042222 | 0.0047744 | 7.2186e-09 | -0.0042042 | -0.0047592 | 0 | -164.2481 | 72.0628 | 0 | 15.752 | -107.9373 |  | 0.98634 | 0.89108 | 0.94806 | 0.98577 | 0.88785 | 0.94465 | 1.9035 | -119.2107 | 117.0377 | 1.9064 | -119.248 | 117.0627
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.4907e-09 | -1.6302e-09 | 4.0359e-09 | -1.3121e-10 | 2.0206e-10 | 1.422e-11 | -3.5522e-09 | 3.5823e-09 | -7.0517e-10 | 1.1423e-10 | 4.0592e-11 | -1.6862e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.98577 | 0.88785 | 0.94465 | 0.98577 | 0.88785 | 0.94465 | 1.9064 | -119.248 | 117.0627 | 1.9064 | -119.248 | 117.0627
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.4907e-09 | -1.6302e-09 | 4.0359e-09 | -1.3121e-10 | 2.0206e-10 | 1.422e-11 | -3.5522e-09 | 3.5823e-09 | -7.0517e-10 | 1.1423e-10 | 4.0592e-11 | -1.6862e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.98577 | 0.88785 | 0.94465 | 0.98577 | 0.88785 | 0.94465 | 1.9064 | -119.248 | 117.0627 | 1.9064 | -119.248 | 117.0627
Line9_3_11 | 0.0023327 | 0.0023327 | 0.0023327 | 0.0023327 | 0.0023327 | 0.0023327 | 0.00053871 | 0.00053871 | 0.00053871 | 0.00053871 | 0.00053871 | 0.00053871 | 0.00033703 | 0.00016396 | -0.00050036 | -0.00033698 | -0.00016391 | 0.00050042 | 0.00041216 | -0.00045665 | 0.00012677 | -0.00041211 | 0.00045671 | -0.00012671 | -48.8343 | -48.8343 | -48.8343 | 131.1657 | 131.1657 | 131.1657 |  | 0.98832 | 0.90066 | 0.95816 | 0.98818 | 0.90072 | 0.95823 | 1.8927 | -119.0835 | 116.9491 | 1.8933 | -119.0915 | 116.9563

## LLG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.0022726 | 0.026631 | 0.028076 | 0.0022726 | 0.026631 | 0.028076 | 0.00052483 | 0.0061502 | 0.0064839 | 0.00052484 | 0.0061502 | 0.0064839 | 0.000301 | 0.0039783 | 0.0038767 | -0.00030076 | -0.003967 | -0.0038607 | 0.00038851 | 0.0034216 | 0.004428 | -0.00038826 | -0.0034065 | -0.0044147 | -50.341 | -159.7735 | 68.144 | 129.659 | 20.2265 | -111.856 |  | 0.93643 | 0.8532 | 0.90767 | 0.93576 | 0.85019 | 0.9045 | 1.892 | -119.0756 | 116.9418 | 1.8958 | -119.1203 | 116.9735
Line10_11_12 | 0.0022099 | 0.0022099 | 0.0022099 | 0.0022099 | 0.0022099 | 0.0022099 | 0.00051036 | 0.00051036 | 0.00051036 | 0.00051036 | 0.00051036 | 0.00051036 | 0.00030244 | 0.00014711 | -0.00044913 | -0.0003024 | -0.00014706 | 0.00044918 | 0.00036987 | -0.0004099 | 0.00011372 | -0.00036983 | 0.00040995 | -0.00011368 | -48.8343 | -48.8343 | -48.8343 | 131.1657 | 131.1657 | 131.1657 |  | 0.93617 | 0.85332 | 0.9078 | 0.93604 | 0.85338 | 0.90787 | 1.8933 | -119.0915 | 116.9563 | 1.8939 | -119.0995 | 116.9636
Line11_12_13 | 0.0022099 | 0.0022099 | 0.0022099 | 0.0022099 | 0.0022099 | 0.0022099 | 0.00051036 | 0.00051036 | 0.00051036 | 0.00051037 | 0.00051037 | 0.00051037 | 0.0003024 | 0.00014706 | -0.00044918 | -0.00030235 | -0.00014702 | 0.00044923 | 0.00036983 | -0.00040995 | 0.00011368 | -0.00036978 | 0.00041 | -0.00011363 | -48.8343 | -48.8343 | -48.8343 | 131.1657 | 131.1657 | 131.1657 |  | 0.93604 | 0.85338 | 0.90787 | 0.93591 | 0.85344 | 0.90793 | 1.8939 | -119.0995 | 116.9636 | 1.8946 | -119.1075 | 116.9709
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.747e-09 | -3.9258e-09 | 1.0703e-08 | 4.3731e-09 | 2.7625e-09 | -7.166e-09 | -9.0505e-09 | 9.5418e-09 | -2.1874e-09 | 6.1358e-09 | -6.3173e-09 | 1.3e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.93591 | 0.85344 | 0.90793 | 0.93591 | 0.85344 | 0.90793 | 1.8946 | -119.1075 | 116.9709 | 1.8946 | -119.1075 | 116.9709
Line13_13_14 | 0.00221 | 0.00221 | 0.00221 | 0.00221 | 0.00221 | 0.00221 | 0.00051038 | 0.00051038 | 0.00051038 | 0.00051038 | 0.00051038 | 0.00051038 | 0.00030236 | 0.00014702 | -0.00044924 | -0.00030231 | -0.00014698 | 0.00044929 | 0.00036979 | -0.00041001 | 0.00011363 | -0.00036974 | 0.00041006 | -0.00011358 | -48.8344 | -48.8344 | -48.8344 | 131.1656 | 131.1656 | 131.1656 |  | 0.93591 | 0.85344 | 0.90793 | 0.93577 | 0.8535 | 0.908 | 1.8946 | -119.1075 | 116.9709 | 1.8952 | -119.1154 | 116.9782
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.498e-09 | -2.6172e-09 | 7.1354e-09 | 2.1241e-09 | 1.454e-09 | -3.5983e-09 | -6.0336e-09 | 6.3612e-09 | -1.4583e-09 | 3.1189e-09 | -3.1367e-09 | 5.7082e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.93591 | 0.85344 | 0.90793 | 0.93591 | 0.85344 | 0.90793 | 1.8946 | -119.1075 | 116.9709 | 1.8946 | -119.1075 | 116.9709
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.249e-09 | -1.3086e-09 | 3.5677e-09 | -1.249e-10 | 1.4537e-10 | -3.0588e-11 | -3.0168e-09 | 3.1806e-09 | -7.2914e-10 | 1.0211e-10 | 4.387e-11 | -1.5833e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.93591 | 0.85344 | 0.90793 | 0.93591 | 0.85344 | 0.90793 | 1.8946 | -119.1075 | 116.9709 | 1.8946 | -119.1075 | 116.9709
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.2463e-09 | -1.3356e-09 | 3.5923e-09 | -1.2631e-10 | 1.4587e-10 | -2.9992e-11 | -3.049e-09 | 3.191e-09 | -7.1435e-10 | 1.0205e-10 | 4.5032e-11 | -1.5943e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.9363 | 0.85326 | 0.90774 | 0.9363 | 0.85326 | 0.90774 | 1.8927 | -119.0836 | 116.9491 | 1.8927 | -119.0836 | 116.9491
Line17_5_19 | 0.0022233 | 0.0022233 | 0.0022233 | 0.0022233 | 0.0022233 | 0.0022233 | 0.00051345 | 0.00051345 | 0.00051345 | 0.00051345 | 0.00051345 | 0.00051345 | 0.0003022 | 0.00015039 | -0.00045244 | -0.00030215 | -0.00015034 | 0.00045249 | 0.00037388 | -0.00041148 | 0.00011189 | -0.00037384 | 0.00041154 | -0.00011185 | -49.1598 | -49.1598 | -49.1598 | 130.8402 | 130.8402 | 130.8402 |  | 0.9363 | 0.85326 | 0.90773 | 0.93617 | 0.85332 | 0.9078 | 1.8927 | -119.0836 | 116.9491 | 1.8934 | -119.0917 | 116.9564
Line1_1_3 | 0.0022099 | 0.0022099 | 0.0022099 | 0.0022099 | 0.0022099 | 0.0022099 | 0.00051035 | 0.00051035 | 0.00051035 | 0.00051035 | 0.00051035 | 0.00051035 | 0.00030253 | 0.0001472 | -0.00044903 | -0.00030248 | -0.00014716 | 0.00044908 | 0.00036996 | -0.00040979 | 0.00011382 | -0.00036992 | 0.00040985 | -0.00011377 | -48.8343 | -48.8342 | -48.8342 | 131.1657 | 131.1657 | 131.1657 |  | 0.93643 | 0.8532 | 0.90767 | 0.9363 | 0.85326 | 0.90773 | 1.892 | -119.0756 | 116.9418 | 1.8927 | -119.0835 | 116.9491
Line2_1_4 | 0.0022277 | 0.0022277 | 0.0022277 | 0.0022277 | 0.0022277 | 0.0022277 | 0.00051447 | 0.00051447 | 0.00051447 | 0.00051447 | 0.00051447 | 0.00051447 | 0.00030213 | 0.00015152 | -0.00045351 | -0.00030209 | -0.00015147 | 0.00045356 | 0.00037526 | -0.00041197 | 0.0001113 | -0.00037521 | 0.00041202 | -0.00011125 | -49.2692 | -49.2691 | -49.2691 | 130.7308 | 130.7309 | 130.7309 |  | 0.93643 | 0.8532 | 0.90767 | 0.9363 | 0.85326 | 0.90774 | 1.892 | -119.0756 | 116.9418 | 1.8927 | -119.0836 | 116.9491
Line3_1_5 | 0.0022233 | 0.0022233 | 0.0022233 | 0.0022233 | 0.0022233 | 0.0022233 | 0.00051344 | 0.00051344 | 0.00051344 | 0.00051345 | 0.00051345 | 0.00051345 | 0.00030224 | 0.00015043 | -0.00045239 | -0.0003022 | -0.00015039 | 0.00045244 | 0.00037393 | -0.00041143 | 0.00011194 | -0.00037388 | 0.00041148 | -0.00011189 | -49.1598 | -49.1598 | -49.1598 | 130.8402 | 130.8402 | 130.8402 |  | 0.93643 | 0.8532 | 0.90767 | 0.9363 | 0.85326 | 0.90773 | 1.892 | -119.0756 | 116.9418 | 1.8927 | -119.0836 | 116.9491
Line4_2_6 | 0.0022726 | 0.026631 | 0.028076 | 0.0022726 | 0.026631 | 0.028076 | 0.00052484 | 0.0061502 | 0.0064839 | 0.00052484 | 0.0061502 | 0.0064839 | 0.00030076 | 0.003967 | 0.0038607 | -0.00030052 | -0.0039556 | -0.0038447 | 0.00038826 | 0.0034065 | 0.0044147 | -0.000388 | -0.0033913 | -0.0044013 | -50.341 | -159.7735 | 68.144 | 129.659 | 20.2266 | -111.8561 |  | 0.93576 | 0.85019 | 0.9045 | 0.9351 | 0.84719 | 0.90133 | 1.8958 | -119.1203 | 116.9735 | 1.8996 | -119.1653 | 117.0055
Line5_6_7 | 0.0022726 | 0.026631 | 0.028076 | 0.0022726 | 0.026631 | 0.028076 | 0.00052484 | 0.0061502 | 0.0064839 | 0.00052484 | 0.0061502 | 0.0064839 | 0.00030052 | 0.0039556 | 0.0038447 | -0.00030029 | -0.0039443 | -0.0038288 | 0.000388 | 0.0033913 | 0.0044013 | -0.00038775 | -0.0033762 | -0.004388 | -50.3411 | -159.7734 | 68.1439 | 129.659 | 20.2266 | -111.8561 |  | 0.9351 | 0.84719 | 0.90133 | 0.93443 | 0.84418 | 0.89817 | 1.8996 | -119.1653 | 117.0055 | 1.9035 | -119.2107 | 117.0377
Line6_7_8 | 0 | 0.027471 | 0.029228 | 0 | 0.027471 | 0.029228 | 0 | 0.0063441 | 0.00675 | 0 | 0.0063441 | 0.00675 | -6.7126e-09 | 0.0037845 | 0.0042888 | 4.3532e-09 | -0.0037733 | -0.0042715 | -9.5486e-09 | 0.0037895 | 0.004285 | 6.4788e-09 | -0.0037733 | -0.0042714 | 0 | -164.2481 | 72.0628 | 0 | 15.752 | -107.9373 |  | 0.93443 | 0.84418 | 0.89817 | 0.93389 | 0.84112 | 0.89493 | 1.9035 | -119.2107 | 117.0377 | 1.9064 | -119.248 | 117.0627
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.2355e-09 | -1.4631e-09 | 3.6222e-09 | -1.1776e-10 | 1.8135e-10 | 1.2762e-11 | -3.1881e-09 | 3.2151e-09 | -6.3289e-10 | 1.0252e-10 | 3.6431e-11 | -1.5133e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.93389 | 0.84112 | 0.89493 | 0.93389 | 0.84112 | 0.89493 | 1.9064 | -119.248 | 117.0627 | 1.9064 | -119.248 | 117.0627
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.2355e-09 | -1.4631e-09 | 3.6222e-09 | -1.1776e-10 | 1.8135e-10 | 1.2762e-11 | -3.1881e-09 | 3.2151e-09 | -6.3289e-10 | 1.0252e-10 | 3.6431e-11 | -1.5133e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.93389 | 0.84112 | 0.89493 | 0.93389 | 0.84112 | 0.89493 | 1.9064 | -119.248 | 117.0627 | 1.9064 | -119.248 | 117.0627
Line9_3_11 | 0.0022099 | 0.0022099 | 0.0022099 | 0.0022099 | 0.0022099 | 0.0022099 | 0.00051035 | 0.00051035 | 0.00051035 | 0.00051036 | 0.00051036 | 0.00051036 | 0.00030248 | 0.00014716 | -0.00044908 | -0.00030244 | -0.00014711 | 0.00044913 | 0.00036992 | -0.00040985 | 0.00011377 | -0.00036987 | 0.0004099 | -0.00011373 | -48.8343 | -48.8343 | -48.8343 | 131.1657 | 131.1657 | 131.1657 |  | 0.9363 | 0.85326 | 0.90773 | 0.93617 | 0.85332 | 0.9078 | 1.8927 | -119.0835 | 116.9491 | 1.8933 | -119.0915 | 116.9563