## LLL_max_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.70184 | 0.70184 | -7.4193 | -7.4193
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.70184 | 0.70184 | -7.4193 | -7.4193
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.70184 | 0.70184 | -7.4193 | -7.4193
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.70184 | 0.70184 | -7.4193 | -7.4193
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.70184 | 0.70184 | -7.4193 | -7.4193
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.70184 | 0.70184 | -7.4193 | -7.4193
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.70184 | 0.70184 | -7.4193 | -7.4193
Line16_4_18 | 3.6243 | 3.6243 | 0 | 7.0007 | 2.511 | 2.511 | 0.39406 | -1e-07 | 0.78812 | -1e-07 | -70.8543 | 109.1457 | 0.35092 | 0 | -7.4193 | 0
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.70184 | 0.70184 | -7.4193 | -7.4193
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.70184 | 0.70184 | -7.4193 | -7.4193
Line2_1_4 | 3.6243 | 3.6243 | 0 | 0 | 2.511 | 2.511 | 0.78812 | -0.39406 | 1.5762 | -0.78812 | -70.8543 | 109.1457 | 0.70184 | 0.35092 | -7.4193 | -7.4193
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.70184 | 0.70184 | -7.4193 | -7.4193
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.70184 | 0.70184 | -7.4193 | -7.4193
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.70184 | 0.70184 | -7.4193 | -7.4193
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.70184 | 0.70184 | -7.4193 | -7.4193
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.70184 | 0.70184 | -7.4193 | -7.4193
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.70184 | 0.70184 | -7.4193 | -7.4193
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.70184 | 0.70184 | -7.4193 | -7.4193

## LLL_max_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72372 | 0.72372 | -7.6495 | -7.6495
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72372 | 0.72372 | -7.6495 | -7.6495
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72372 | 0.72372 | -7.6495 | -7.6495
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72372 | 0.72372 | -7.6495 | -7.6495
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72372 | 0.72372 | -7.6495 | -7.6495
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72372 | 0.72372 | -7.6495 | -7.6495
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72372 | 0.72372 | -7.6495 | -7.6495
Line16_4_18 | 3.7373 | 3.7373 | 0 | 7.2438 | 2.5893 | 2.5893 | 0.41902 | -1e-07 | 0.83803 | -1e-07 | -71.0844 | 108.9156 | 0.36186 | 0 | -7.6495 | 0
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72372 | 0.72372 | -7.6495 | -7.6495
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72372 | 0.72372 | -7.6495 | -7.6495
Line2_1_4 | 3.7373 | 3.7373 | 0 | 0 | 2.5893 | 2.5893 | 0.83803 | -0.41902 | 1.6761 | -0.83803 | -71.0844 | 108.9156 | 0.72372 | 0.36186 | -7.6495 | -7.6495
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72372 | 0.72372 | -7.6495 | -7.6495
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72372 | 0.72372 | -7.6495 | -7.6495
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72372 | 0.72372 | -7.6495 | -7.6495
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72372 | 0.72372 | -7.6495 | -7.6495
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72372 | 0.72372 | -7.6495 | -7.6495
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72372 | 0.72372 | -7.6495 | -7.6495
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72372 | 0.72372 | -7.6495 | -7.6495

## LLL_max_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.12051 | -0.12051
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.12051 | -0.12051
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.12051 | -0.12051
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.12051 | -0.12051
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.12051 | -0.12051
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.12051 | -0.12051
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.12051 | -0.12051
Line16_4_18 | 0.034003 | 0.034003 | 0 | 0.065681 | 0.023558 | 0.023558 | 0.017378 | -0.017343 | 0.017412 | -0.017343 | -45.2344 | 134.7656 | 1.0442 | 1.0411 | -0.17729 | -0.23442
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.12051 | -0.12051
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.12051 | -0.12051
Line2_1_4 | 0.034003 | 0.034003 | 0 | 0 | 0.023558 | 0.023558 | 0.017412 | -0.017378 | 0.017482 | -0.017412 | -45.2344 | 134.7656 | 1.0474 | 1.0442 | -0.12051 | -0.17729
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.12051 | -0.12051
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.12051 | -0.12051
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.12051 | -0.12051
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.12051 | -0.12051
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.12051 | -0.12051
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.12051 | -0.12051
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.12051 | -0.12051

## LLL_max_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12619 | -0.12619
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12619 | -0.12619
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12619 | -0.12619
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12619 | -0.12619
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12619 | -0.12619
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12619 | -0.12619
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12619 | -0.12619
Line16_4_18 | 0.035618 | 0.035618 | 0 | 0.069037 | 0.024677 | 0.024677 | 0.019068 | -0.01903 | 0.019106 | -0.01903 | -45.2401 | 134.7599 | 1.0938 | 1.0906 | -0.18297 | -0.2401
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12619 | -0.12619
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12619 | -0.12619
Line2_1_4 | 0.035618 | 0.035618 | 0 | 0 | 0.024677 | 0.024677 | 0.019106 | -0.019068 | 0.019182 | -0.019106 | -45.2401 | 134.7599 | 1.0971 | 1.0938 | -0.12619 | -0.18297
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12619 | -0.12619
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12619 | -0.12619
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12619 | -0.12619
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12619 | -0.12619
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12619 | -0.12619
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12619 | -0.12619
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12619 | -0.12619

## LLL_min_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.695 | 0.695 | -11.6026 | -11.6026
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.695 | 0.695 | -11.6026 | -11.6026
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.695 | 0.695 | -11.6026 | -11.6026
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.695 | 0.695 | -11.6026 | -11.6026
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.695 | 0.695 | -11.6026 | -11.6026
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.695 | 0.695 | -11.6026 | -11.6026
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.695 | 0.695 | -11.6026 | -11.6026
Line16_4_18 | 2.8946 | 2.8946 | 0 | 4.7808 | 2.0055 | 2.0055 | 0.48263 | -1e-07 | 0.50274 | -1e-07 | -57.7717 | 122.2283 | 0.3475 | 0 | -11.6026 | 0
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.695 | 0.695 | -11.6026 | -11.6026
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.695 | 0.695 | -11.6026 | -11.6026
Line2_1_4 | 2.8946 | 2.8946 | 0 | 0 | 2.0055 | 2.0055 | 0.96525 | -0.48263 | 1.0055 | -0.50274 | -57.7717 | 122.2283 | 0.695 | 0.3475 | -11.6026 | -11.6026
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.695 | 0.695 | -11.6026 | -11.6026
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.695 | 0.695 | -11.6026 | -11.6026
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.695 | 0.695 | -11.6026 | -11.6026
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.695 | 0.695 | -11.6026 | -11.6026
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.695 | 0.695 | -11.6026 | -11.6026
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.695 | 0.695 | -11.6026 | -11.6026
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.695 | 0.695 | -11.6026 | -11.6026

## LLL_min_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65842 | 0.65842 | -11.6026 | -11.6026
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65842 | 0.65842 | -11.6026 | -11.6026
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65842 | 0.65842 | -11.6026 | -11.6026
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65842 | 0.65842 | -11.6026 | -11.6026
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65842 | 0.65842 | -11.6026 | -11.6026
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65842 | 0.65842 | -11.6026 | -11.6026
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65842 | 0.65842 | -11.6026 | -11.6026
Line16_4_18 | 2.7423 | 2.7423 | 0 | 4.5292 | 1.8999 | 1.8999 | 0.43316 | -1e-07 | 0.45121 | -1e-07 | -57.7717 | 122.2283 | 0.32921 | 0 | -11.6026 | 0
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65842 | 0.65842 | -11.6026 | -11.6026
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65842 | 0.65842 | -11.6026 | -11.6026
Line2_1_4 | 2.7423 | 2.7423 | 0 | 0 | 1.8999 | 1.8999 | 0.86632 | -0.43316 | 0.90242 | -0.45121 | -57.7717 | 122.2283 | 0.65842 | 0.32921 | -11.6026 | -11.6026
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65842 | 0.65842 | -11.6026 | -11.6026
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65842 | 0.65842 | -11.6026 | -11.6026
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65842 | 0.65842 | -11.6026 | -11.6026
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65842 | 0.65842 | -11.6026 | -11.6026
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65842 | 0.65842 | -11.6026 | -11.6026
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65842 | 0.65842 | -11.6026 | -11.6026
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65842 | 0.65842 | -11.6026 | -11.6026

## LLL_min_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94754 | 0.94754 | -0.12527 | -0.12527
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94754 | 0.94754 | -0.12527 | -0.12527
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94754 | 0.94754 | -0.12527 | -0.12527
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94754 | 0.94754 | -0.12527 | -0.12527
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94754 | 0.94754 | -0.12527 | -0.12527
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94754 | 0.94754 | -0.12527 | -0.12527
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94754 | 0.94754 | -0.12527 | -0.12527
Line16_4_18 | 0.030706 | 0.030706 | 0 | 0.050714 | 0.021274 | 0.021274 | 0.014197 | -0.014143 | 0.014199 | -0.014143 | -45.1344 | 134.8656 | 0.94385 | 0.94017 | -0.1298 | -0.13436
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94754 | 0.94754 | -0.12527 | -0.12527
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94754 | 0.94754 | -0.12527 | -0.12527
Line2_1_4 | 0.030706 | 0.030706 | 0 | 0 | 0.021274 | 0.021274 | 0.014251 | -0.014197 | 0.014256 | -0.014199 | -45.1344 | 134.8656 | 0.94754 | 0.94385 | -0.12527 | -0.1298
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94754 | 0.94754 | -0.12527 | -0.12527
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94754 | 0.94754 | -0.12527 | -0.12527
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94754 | 0.94754 | -0.12527 | -0.12527
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94754 | 0.94754 | -0.12527 | -0.12527
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94754 | 0.94754 | -0.12527 | -0.12527
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94754 | 0.94754 | -0.12527 | -0.12527
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94754 | 0.94754 | -0.12527 | -0.12527

## LLL_min_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89767 | 0.89767 | -0.12527 | -0.12527
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89767 | 0.89767 | -0.12527 | -0.12527
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89767 | 0.89767 | -0.12527 | -0.12527
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89767 | 0.89767 | -0.12527 | -0.12527
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89767 | 0.89767 | -0.12527 | -0.12527
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89767 | 0.89767 | -0.12527 | -0.12527
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89767 | 0.89767 | -0.12527 | -0.12527
Line16_4_18 | 0.02909 | 0.02909 | 0 | 0.048045 | 0.020154 | 0.020154 | 0.012742 | -0.012693 | 0.012744 | -0.012693 | -45.1344 | 134.8656 | 0.89418 | 0.89069 | -0.1298 | -0.13436
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89767 | 0.89767 | -0.12527 | -0.12527
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89767 | 0.89767 | -0.12527 | -0.12527
Line2_1_4 | 0.02909 | 0.02909 | 0 | 0 | 0.020154 | 0.020154 | 0.012791 | -0.012742 | 0.012795 | -0.012744 | -45.1344 | 134.8656 | 0.89767 | 0.89418 | -0.12527 | -0.1298
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89767 | 0.89767 | -0.12527 | -0.12527
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89767 | 0.89767 | -0.12527 | -0.12527
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89767 | 0.89767 | -0.12527 | -0.12527
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89767 | 0.89767 | -0.12527 | -0.12527
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89767 | 0.89767 | -0.12527 | -0.12527
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89767 | 0.89767 | -0.12527 | -0.12527
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89767 | 0.89767 | -0.12527 | -0.12527

## LL_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7716e-16 | -3.0235e-09 | -4.8365e-09 | -7.7716e-16 | 3.0235e-09 | 4.8365e-09 | 1.5543e-16 | 5.1114e-09 | -1.9712e-09 | -1.5543e-16 | -5.1114e-09 | 1.9712e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.85292 | 0.7501 | 1.05 | 0.85292 | 0.7501 | 2.964e-13 | -135.0364 | 126.5322 | 2.8306e-13 | -135.0364 | 126.5322
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.8287e-16 | -3.0235e-09 | -4.8365e-09 | -6.2172e-16 | 3.0235e-09 | 4.8365e-09 | 2.5258e-16 | 5.1114e-09 | -1.9712e-09 | -2.3315e-16 | -5.1114e-09 | 1.9712e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.85292 | 0.7501 | 1.05 | 0.85292 | 0.7501 | 2.7398e-13 | -135.0364 | 126.5322 | 2.6455e-13 | -135.0364 | 126.5322
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.2172e-16 | -2.5196e-09 | -4.0305e-09 | -6.2172e-16 | 2.5196e-09 | 4.0305e-09 | 1.36e-16 | 4.2595e-09 | -1.6426e-09 | -1.1657e-16 | -4.2595e-09 | 1.6426e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.85292 | 0.7501 | 1.05 | 0.85292 | 0.7501 | 2.6455e-13 | -135.0364 | 126.5322 | 2.5489e-13 | -135.0364 | 126.5322
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3315e-16 | -1.5118e-09 | -2.4183e-09 | -1.9429e-16 | 1.5118e-09 | 2.4183e-09 | 7.7716e-17 | 2.5557e-09 | -9.8558e-10 | -7.7716e-17 | -2.5557e-09 | 9.8558e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.85292 | 0.7501 | 1.05 | 0.85292 | 0.7501 | 2.5489e-13 | -135.0364 | 126.5322 | 2.5136e-13 | -135.0364 | 126.5322
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5543e-16 | -5.0392e-10 | -8.0609e-10 | -7.7716e-17 | 5.0392e-10 | 8.0609e-10 | 1.7486e-16 | 8.5191e-10 | -3.2853e-10 | -1.7486e-16 | -8.5191e-10 | 3.2853e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.85292 | 0.7501 | 1.05 | 0.85292 | 0.7501 | 2.5489e-13 | -135.0364 | 126.5322 | 2.5336e-13 | -135.0364 | 126.5322
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1657e-16 | -1.0078e-09 | -1.6122e-09 | -1.5543e-16 | 1.0078e-09 | 1.6122e-09 | 1.9429e-17 | 1.7038e-09 | -6.5706e-10 | -1.9429e-17 | -1.7038e-09 | 6.5706e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.85292 | 0.7501 | 1.05 | 0.85292 | 0.7501 | 2.5136e-13 | -135.0364 | 126.5322 | 2.4958e-13 | -135.0364 | 126.5322
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1657e-16 | -5.0392e-10 | -8.0609e-10 | -7.7716e-17 | 5.0392e-10 | 8.0609e-10 | -5.8287e-17 | 8.5191e-10 | -3.2853e-10 | 5.8287e-17 | -8.5191e-10 | 3.2853e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.85292 | 0.7501 | 1.05 | 0.85292 | 0.7501 | 2.4958e-13 | -135.0364 | 126.5322 | 2.4906e-13 | -135.0364 | 126.5322
Line16_4_18 | 0 | 3.1387 | 3.1387 | 0 | 3.1387 | 3.1387 | 0 | 0.72485 | 0.72485 | 0 | 0.72485 | 0.72485 | 7.7716e-17 | 0.45801 | -0.26098 | -7.7716e-17 | -0.3595 | 0.3595 | -1.1657e-16 | 0.072221 | 0.32184 | 1.1657e-16 | 0.12481 | -0.12481 | 0 | -160.8543 | 19.1457 | 0 | 19.1457 | -160.8543 | 1.05 | 0.63968 | 0.57164 | 1.05 | 0.525 | 0.525 | 2.8689e-13 | -151.8935 | 148.1848 | 2.8475e-13 | 180 | -180
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.8858e-17 | -5.0392e-10 | -8.0609e-10 | 3.8858e-17 | 5.0392e-10 | 8.0609e-10 | 1.9429e-17 | 8.5191e-10 | -3.2853e-10 | 1.9429e-17 | -8.5191e-10 | 3.2853e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.85292 | 0.7501 | 1.05 | 0.85292 | 0.7501 | 2.9344e-13 | -135.0364 | 126.5322 | 2.9292e-13 | -135.0364 | 126.5322
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.7145e-16 | -4.0313e-09 | -6.4487e-09 | -9.3259e-16 | 4.0313e-09 | 6.4487e-09 | 2.5258e-16 | 6.8153e-09 | -2.6282e-09 | -2.5258e-16 | -6.8153e-09 | 2.6282e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.85292 | 0.7501 | 1.05 | 0.85292 | 0.7501 | 2.964e-13 | -135.0364 | 126.5322 | 2.8404e-13 | -135.0364 | 126.5322
Line2_1_4 | 0 | 3.1387 | 3.1387 | 0 | 3.1387 | 3.1387 | 0 | 0.72485 | 0.72485 | 0 | 0.72485 | 0.72485 | 4.6629e-16 | 0.55653 | -0.16247 | -4.6629e-16 | -0.45801 | 0.26098 | 1.5543e-16 | 0.26925 | 0.51887 | -1.9429e-16 | -0.072221 | -0.32184 | 0 | -160.8543 | 19.1457 | 0 | 19.1457 | -160.8543 | 1.05 | 0.85292 | 0.7501 | 1.05 | 0.63968 | 0.57164 | 2.964e-13 | -135.0364 | 126.5322 | 2.8689e-13 | -151.8935 | 148.1848
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9429e-16 | -1.0078e-09 | -1.6122e-09 | -1.9429e-16 | 1.0078e-09 | 1.6122e-09 | -1.9429e-17 | 1.7038e-09 | -6.5705e-10 | 1.9429e-17 | -1.7038e-09 | 6.5706e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.85292 | 0.7501 | 1.05 | 0.85292 | 0.7501 | 2.964e-13 | -135.0364 | 126.5322 | 2.9344e-13 | -135.0364 | 126.5322
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.2172e-16 | -2.5196e-09 | -4.0305e-09 | -5.8287e-16 | 2.5196e-09 | 4.0305e-09 | 2.1372e-16 | 4.2595e-09 | -1.6426e-09 | -1.9429e-16 | -4.2595e-09 | 1.6426e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.85292 | 0.7501 | 1.05 | 0.85292 | 0.7501 | 2.8306e-13 | -135.0364 | 126.5322 | 2.7228e-13 | -135.0364 | 126.5322
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.0515e-16 | -2.0157e-09 | -3.2244e-09 | -5.0515e-16 | 2.0157e-09 | 3.2244e-09 | 1.1657e-16 | 3.4076e-09 | -1.3141e-09 | -1.5543e-16 | -3.4076e-09 | 1.3141e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.85292 | 0.7501 | 1.05 | 0.85292 | 0.7501 | 2.7228e-13 | -135.0364 | 126.5322 | 2.6442e-13 | -135.0364 | 126.5322
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5543e-16 | -1.5118e-09 | -2.4183e-09 | -1.1657e-16 | 1.5118e-09 | 2.4183e-09 | -1.1657e-16 | 2.5557e-09 | -9.8558e-10 | 1.1657e-16 | -2.5557e-09 | 9.8558e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.85292 | 0.7501 | 1.05 | 0.85292 | 0.7501 | 2.6442e-13 | -135.0364 | 126.5322 | 2.611e-13 | -135.0364 | 126.5322
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7716e-17 | -5.0392e-10 | -8.0609e-10 | -7.7716e-17 | 5.0392e-10 | 8.0609e-10 | -3.8858e-17 | 8.5191e-10 | -3.2853e-10 | 1.9429e-17 | -8.5191e-10 | 3.2853e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.85292 | 0.7501 | 1.05 | 0.85292 | 0.7501 | 2.611e-13 | -135.0364 | 126.5322 | 2.6005e-13 | -135.0364 | 126.5322
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8858e-17 | -5.0392e-10 | -8.0609e-10 | -3.8858e-17 | 5.0392e-10 | 8.0609e-10 | -1.9429e-17 | 8.5191e-10 | -3.2853e-10 | 1.9429e-17 | -8.5191e-10 | 3.2853e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.85292 | 0.7501 | 1.05 | 0.85292 | 0.7501 | 2.611e-13 | -135.0364 | 126.5322 | 2.5947e-13 | -135.0364 | 126.5322
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7716e-16 | -3.5274e-09 | -5.6426e-09 | -7.7716e-16 | 3.5274e-09 | 5.6426e-09 | 2.5258e-16 | 5.9633e-09 | -2.2997e-09 | -2.72e-16 | -5.9633e-09 | 2.2997e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.85292 | 0.7501 | 1.05 | 0.85292 | 0.7501 | 2.8404e-13 | -135.0364 | 126.5322 | 2.7398e-13 | -135.0364 | 126.5322

## LL_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.6991e-16 | -3.3669e-09 | -5.3859e-09 | -5.2921e-16 | 3.3669e-09 | 5.3859e-09 | 6.1062e-16 | 5.759e-09 | -2.262e-09 | -6.1062e-16 | -5.759e-09 | 2.262e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.88719 | 0.77689 | 1.1 | 0.88719 | 0.77689 | -1.8213e-12 | -135.5593 | 126.9102 | -1.8264e-12 | -135.5593 | 126.9102
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2921e-16 | -3.3669e-09 | -5.3859e-09 | -6.1062e-16 | 3.3669e-09 | 5.3859e-09 | 4.4779e-16 | 5.759e-09 | -2.262e-09 | -4.4779e-16 | -5.759e-09 | 2.262e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.88719 | 0.77689 | 1.1 | 0.88719 | 0.77689 | -1.837e-12 | -135.5593 | 126.9102 | -1.8435e-12 | -135.5593 | 126.9102
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0708e-16 | -2.8058e-09 | -4.4883e-09 | -3.6637e-16 | 2.8058e-09 | 4.4883e-09 | 4.4779e-16 | 4.7992e-09 | -1.885e-09 | -3.6637e-16 | -4.7992e-09 | 1.885e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.88719 | 0.77689 | 1.1 | 0.88719 | 0.77689 | -1.8435e-12 | -135.5593 | 126.9102 | -1.8504e-12 | -135.5593 | 126.9102
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0354e-16 | -1.6835e-09 | -2.693e-09 | -2.0354e-16 | 1.6835e-09 | 2.693e-09 | 4.0708e-17 | 2.8795e-09 | -1.131e-09 | -1.2212e-16 | -2.8795e-09 | 1.131e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.88719 | 0.77689 | 1.1 | 0.88719 | 0.77689 | -1.8504e-12 | -135.5593 | 126.9102 | -1.854e-12 | -135.5593 | 126.9102
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.0708e-17 | -5.6115e-10 | -8.9765e-10 | -4.0708e-17 | 5.6115e-10 | 8.9765e-10 | 4.0708e-16 | 9.5983e-10 | -3.77e-10 | -4.4779e-16 | -9.5983e-10 | 3.77e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.88719 | 0.77689 | 1.1 | 0.88719 | 0.77689 | -1.8504e-12 | -135.5593 | 126.9102 | -1.8504e-12 | -135.5593 | 126.9102
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2212e-16 | -1.1223e-09 | -1.7953e-09 | -1.6283e-16 | 1.1223e-09 | 1.7953e-09 | 8.1416e-17 | 1.9197e-09 | -7.5399e-10 | -4.0708e-17 | -1.9197e-09 | 7.5399e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.88719 | 0.77689 | 1.1 | 0.88719 | 0.77689 | -1.854e-12 | -135.5593 | 126.9102 | -1.8558e-12 | -135.5593 | 126.9102
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.1416e-17 | -5.6115e-10 | -8.9765e-10 | 8.1416e-17 | 5.6115e-10 | 8.9765e-10 | 2.6371e-30 | 9.5983e-10 | -3.77e-10 | -4.0708e-17 | -9.5983e-10 | 3.77e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.88719 | 0.77689 | 1.1 | 0.88719 | 0.77689 | -1.8558e-12 | -135.5593 | 126.9102 | -1.8564e-12 | -135.5593 | 126.9102
Line16_4_18 | 0 | 3.2366 | 3.2366 | 0 | 3.2366 | 3.2366 | 0 | 0.74746 | 0.74746 | 0 | 0.74746 | 0.74746 | 0 | 0.49365 | -0.28415 | 0 | -0.3889 | 0.3889 | 0 | 0.07624 | 0.34278 | 0 | 0.13327 | -0.13327 | 0 | -161.0844 | 18.9156 | 0 | 18.9156 | -161.0844 | 1.1 | 0.66828 | 0.59567 | 1.1 | 0.55 | 0.55 | -1.8289e-12 | -152.305 | 148.5727 | -1.8311e-12 | -180 | -180
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0708e-17 | -5.6115e-10 | -8.9765e-10 | -4.0708e-17 | 5.6115e-10 | 8.9765e-10 | -8.1416e-17 | 9.5983e-10 | -3.77e-10 | 8.1416e-17 | -9.5983e-10 | 3.77e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.88719 | 0.77689 | 1.1 | 0.88719 | 0.77689 | -1.8227e-12 | -135.5593 | 126.9102 | -1.8232e-12 | -135.5593 | 126.9102
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.9204e-16 | -4.4892e-09 | -7.1812e-09 | -6.1062e-16 | 4.4892e-09 | 7.1812e-09 | 6.1062e-16 | 7.6787e-09 | -3.016e-09 | -6.1062e-16 | -7.6787e-09 | 3.016e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.88719 | 0.77689 | 1.1 | 0.88719 | 0.77689 | -1.8213e-12 | -135.5593 | 126.9102 | -1.8297e-12 | -135.5593 | 126.9102
Line2_1_4 | 0 | 3.2366 | 3.2366 | 0 | 3.2366 | 3.2366 | 0 | 0.74746 | 0.74746 | 0 | 0.74746 | 0.74746 | 3.2567e-16 | 0.59841 | -0.17939 | -3.2567e-16 | -0.49365 | 0.28415 | 5.6991e-16 | 0.28575 | 0.55229 | -5.6991e-16 | -0.07624 | -0.34278 | 0 | -161.0844 | 18.9156 | 0 | 18.9156 | -161.0844 | 1.1 | 0.88719 | 0.77689 | 1.1 | 0.66828 | 0.59567 | -1.8213e-12 | -135.5593 | 126.9102 | -1.8289e-12 | -152.305 | 148.5727
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0708e-17 | -1.1223e-09 | -1.7953e-09 | 4.0708e-17 | 1.1223e-09 | 1.7953e-09 | 4.0708e-17 | 1.9197e-09 | -7.5399e-10 | -8.1416e-17 | -1.9197e-09 | 7.5399e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.88719 | 0.77689 | 1.1 | 0.88719 | 0.77689 | -1.8213e-12 | -135.5593 | 126.9102 | -1.8227e-12 | -135.5593 | 126.9102
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0708e-16 | -2.8058e-09 | -4.4883e-09 | -4.0708e-16 | 2.8058e-09 | 4.4883e-09 | 5.2921e-16 | 4.7992e-09 | -1.885e-09 | -5.6991e-16 | -4.7992e-09 | 1.885e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.88719 | 0.77689 | 1.1 | 0.88719 | 0.77689 | -1.8264e-12 | -135.5593 | 126.9102 | -1.8316e-12 | -135.5593 | 126.9102
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4425e-16 | -2.2446e-09 | -3.5906e-09 | -2.8496e-16 | 2.2446e-09 | 3.5906e-09 | 3.6637e-16 | 3.8393e-09 | -1.508e-09 | -3.6637e-16 | -3.8393e-09 | 1.508e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.88719 | 0.77689 | 1.1 | 0.88719 | 0.77689 | -1.8316e-12 | -135.5593 | 126.9102 | -1.8342e-12 | -135.5593 | 126.9102
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0354e-16 | -1.6835e-09 | -2.693e-09 | -1.6283e-16 | 1.6835e-09 | 2.693e-09 | -8.1416e-17 | 2.8795e-09 | -1.131e-09 | 1.2212e-16 | -2.8795e-09 | 1.131e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.88719 | 0.77689 | 1.1 | 0.88719 | 0.77689 | -1.8342e-12 | -135.5593 | 126.9102 | -1.835e-12 | -135.5593 | 126.9102
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.0708e-17 | -5.6115e-10 | -8.9765e-10 | 0 | 5.6115e-10 | 8.9765e-10 | 1.3038e-30 | 9.5983e-10 | -3.77e-10 | 0 | -9.5983e-10 | 3.77e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.88719 | 0.77689 | 1.1 | 0.88719 | 0.77689 | -1.835e-12 | -135.5593 | 126.9102 | -1.8361e-12 | -135.5593 | 126.9102
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.1416e-17 | -5.6115e-10 | -8.9765e-10 | 4.0708e-17 | 5.6115e-10 | 8.9765e-10 | 2.6076e-30 | 9.5983e-10 | -3.77e-10 | -4.0708e-17 | -9.5983e-10 | 3.77e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.88719 | 0.77689 | 1.1 | 0.88719 | 0.77689 | -1.835e-12 | -135.5593 | 126.9102 | -1.8353e-12 | -135.5593 | 126.9102
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.9204e-16 | -3.9281e-09 | -6.2836e-09 | -7.3275e-16 | 3.9281e-09 | 6.2836e-09 | 6.1062e-16 | 6.7188e-09 | -2.639e-09 | -5.6991e-16 | -6.7188e-09 | 2.639e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.88719 | 0.77689 | 1.1 | 0.88719 | 0.77689 | -1.8297e-12 | -135.5593 | 126.9102 | -1.837e-12 | -135.5593 | 126.9102

## LL_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2447e-17 | -4.6325e-11 | -1.333e-10 | -1.1839e-17 | 4.6325e-11 | 1.333e-10 | 2.4286e-18 | 1.2762e-10 | 2.3032e-11 | -1.8215e-18 | -1.2762e-10 | -2.3032e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0442 | 1.05 | 1.048 | 1.0442 | 3.9665e-14 | -120.3021 | 119.9453 | 3.9424e-14 | -120.3021 | 119.9453
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1839e-17 | -4.6325e-11 | -1.333e-10 | -1.1839e-17 | 4.6325e-11 | 1.333e-10 | -1.8215e-18 | 1.2762e-10 | 2.3032e-11 | 1.8215e-18 | -1.2762e-10 | -2.3032e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0442 | 1.05 | 1.048 | 1.0442 | 3.9207e-14 | -120.3021 | 119.9453 | 3.8999e-14 | -120.3021 | 119.9453
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0322e-17 | -3.8604e-11 | -1.1109e-10 | -1.0322e-17 | 3.8604e-11 | 1.1109e-10 | -3.6429e-18 | 1.0635e-10 | 1.9193e-11 | 3.6429e-18 | -1.0635e-10 | -1.9193e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0442 | 1.05 | 1.048 | 1.0442 | 3.8999e-14 | -120.3021 | 119.9453 | 3.8773e-14 | -120.3021 | 119.9453
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3393e-18 | -2.3162e-11 | -6.6652e-11 | -3.3393e-18 | 2.3162e-11 | 6.6652e-11 | 1.8215e-18 | 6.3811e-11 | 1.1516e-11 | -1.8215e-18 | -6.3811e-11 | -1.1516e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0442 | 1.05 | 1.048 | 1.0442 | 3.8773e-14 | -120.3021 | 119.9453 | 3.8713e-14 | -120.3021 | 119.9453
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5536e-18 | -7.7208e-12 | -2.2217e-11 | -4.5536e-18 | 7.7208e-12 | 2.2217e-11 | -4.8572e-18 | 2.127e-11 | 3.8387e-12 | 4.8572e-18 | -2.127e-11 | -3.8387e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0442 | 1.05 | 1.048 | 1.0442 | 3.8773e-14 | -120.3021 | 119.9453 | 3.8683e-14 | -120.3021 | 119.9453
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8215e-18 | -1.5442e-11 | -4.4435e-11 | -2.4286e-18 | 1.5442e-11 | 4.4435e-11 | 1.2143e-18 | 4.2541e-11 | 7.6773e-12 | -1.2143e-18 | -4.2541e-11 | -7.6773e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0442 | 1.05 | 1.048 | 1.0442 | 3.8713e-14 | -120.3021 | 119.9453 | 3.8684e-14 | -120.3021 | 119.9453
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0715e-19 | -7.7208e-12 | -2.2217e-11 | -6.0715e-19 | 7.7208e-12 | 2.2217e-11 | 4.0992e-34 | 2.127e-11 | 3.8387e-12 | 6.0715e-19 | -2.127e-11 | -3.8387e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0442 | 1.05 | 1.048 | 1.0442 | 3.8684e-14 | -120.3021 | 119.9453 | 3.8665e-14 | -120.3021 | 119.9453
Line16_4_18 | 0 | 0.0584 | 0.0584 | 0 | 0.0584 | 0.0584 | 0 | 0.013487 | 0.013487 | 0 | 0.013487 | 0.013487 | 0 | 0.013608 | 0.0035134 | 2.4286e-18 | -0.013574 | -0.0034793 | 0 | 0.0036287 | 0.013561 | 1.6704e-33 | -0.0035605 | -0.013493 | 0 | -135.4649 | 44.5351 | 0 | 44.5351 | -135.4649 | 1.05 | 1.0442 | 1.0387 | 1.05 | 1.0405 | 1.0331 | 3.9458e-14 | -120.5336 | 120.01 | 3.9409e-14 | -120.7668 | 120.0754
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.0715e-19 | -7.7208e-12 | -2.2217e-11 | 6.0715e-19 | 7.7208e-12 | 2.2217e-11 | -6.0715e-19 | 2.127e-11 | 3.8387e-12 | 4.1956e-34 | -2.127e-11 | -3.8387e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0442 | 1.05 | 1.048 | 1.0442 | 3.9612e-14 | -120.3021 | 119.9453 | 3.9593e-14 | -120.3021 | 119.9453
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.609e-17 | -6.1766e-11 | -1.7774e-10 | -1.4875e-17 | 6.1766e-11 | 1.7774e-10 | 4.2501e-18 | 1.7016e-10 | 3.0709e-11 | -3.0358e-18 | -1.7016e-10 | -3.0709e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0442 | 1.05 | 1.048 | 1.0442 | 3.9665e-14 | -120.3021 | 119.9453 | 3.9418e-14 | -120.3021 | 119.9453
Line2_1_4 | 0 | 0.0584 | 0.0584 | 0 | 0.0584 | 0.0584 | 0 | 0.013487 | 0.013487 | 0 | 0.013487 | 0.013487 | 9.1073e-18 | 0.013642 | 0.0035475 | -7.2858e-18 | -0.013608 | -0.0035134 | 6.3049e-33 | 0.003697 | 0.013629 | 2.4286e-18 | -0.0036287 | -0.013561 | 0 | -135.4649 | 44.5351 | 0 | 44.5351 | -135.4649 | 1.05 | 1.048 | 1.0442 | 1.05 | 1.0442 | 1.0387 | 3.9665e-14 | -120.3021 | 119.9453 | 3.9458e-14 | -120.5336 | 120.01
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4286e-18 | -1.5442e-11 | -4.4435e-11 | -1.8215e-18 | 1.5442e-11 | 4.4435e-11 | 3.0358e-18 | 4.2541e-11 | 7.6773e-12 | -1.2143e-18 | -4.2541e-11 | -7.6773e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0442 | 1.05 | 1.048 | 1.0442 | 3.9665e-14 | -120.3021 | 119.9453 | 3.9612e-14 | -120.3021 | 119.9453
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0018e-17 | -3.8604e-11 | -1.1109e-10 | -1.0018e-17 | 3.8604e-11 | 1.1109e-10 | 6.8931e-33 | 1.0635e-10 | 1.9193e-11 | -6.8572e-33 | -1.0635e-10 | -1.9193e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0442 | 1.05 | 1.048 | 1.0442 | 3.9424e-14 | -120.3021 | 119.9453 | 3.9218e-14 | -120.3021 | 119.9453
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.8037e-18 | -3.0883e-11 | -8.887e-11 | -8.1966e-18 | 3.0883e-11 | 8.887e-11 | -3.6429e-18 | 8.5081e-11 | 1.5355e-11 | 3.0358e-18 | -8.5081e-11 | -1.5355e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0442 | 1.05 | 1.048 | 1.0442 | 3.9218e-14 | -120.3021 | 119.9453 | 3.905e-14 | -120.3021 | 119.9453
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7322e-18 | -2.3162e-11 | -6.6652e-11 | -2.7322e-18 | 2.3162e-11 | 6.6652e-11 | -1.2143e-18 | 6.3811e-11 | 1.1516e-11 | 2.4286e-18 | -6.3811e-11 | -1.1516e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0442 | 1.05 | 1.048 | 1.0442 | 3.905e-14 | -120.3021 | 119.9453 | 3.8978e-14 | -120.3021 | 119.9453
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.2608e-34 | -7.7208e-12 | -2.2217e-11 | 6.0715e-19 | 7.7208e-12 | 2.2217e-11 | 1.2143e-18 | 2.127e-11 | 3.8387e-12 | -6.0715e-19 | -2.127e-11 | -3.8387e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0442 | 1.05 | 1.048 | 1.0442 | 3.8978e-14 | -120.3021 | 119.9453 | 3.8963e-14 | -120.3021 | 119.9453
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0358e-19 | -7.7208e-12 | -2.2217e-11 | 3.0358e-19 | 7.7208e-12 | 2.2217e-11 | 1.2143e-18 | 2.127e-11 | 3.8387e-12 | 2.0639e-34 | -2.127e-11 | -3.8387e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0442 | 1.05 | 1.048 | 1.0442 | 3.8978e-14 | -120.3021 | 119.9453 | 3.8953e-14 | -120.3021 | 119.9453
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1839e-17 | -5.4045e-11 | -1.5552e-10 | -1.2447e-17 | 5.4045e-11 | 1.5552e-10 | 2.4286e-18 | 1.4889e-10 | 2.6871e-11 | -1.2143e-18 | -1.4889e-10 | -2.6871e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0442 | 1.05 | 1.048 | 1.0442 | 3.9418e-14 | -120.3021 | 119.9453 | 3.9207e-14 | -120.3021 | 119.9453

## LL_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0177e-17 | -5.3219e-11 | -1.5314e-10 | -1.0177e-17 | 5.3219e-11 | 1.5314e-10 | 1.2085e-17 | 1.4664e-10 | 2.6437e-11 | -1.2085e-17 | -1.4664e-10 | -2.6437e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0936 | 1.1 | 1.0978 | 1.0936 | 8.8414e-16 | -120.3163 | 119.9428 | 7.9516e-16 | -120.3163 | 119.9428
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2085e-17 | -5.3219e-11 | -1.5314e-10 | -1.2085e-17 | 5.3219e-11 | 1.5314e-10 | 4.4525e-18 | 1.4664e-10 | 2.6437e-11 | -5.0885e-18 | -1.4664e-10 | -2.6437e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0936 | 1.1 | 1.0978 | 1.0936 | 5.3477e-16 | -120.3163 | 119.9428 | 3.708e-16 | -120.3163 | 119.9428
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6328e-18 | -4.4349e-11 | -1.2762e-10 | -6.9967e-18 | 4.4349e-11 | 1.2762e-10 | 6.3607e-19 | 1.222e-10 | 2.2031e-11 | -1.2721e-18 | -1.222e-10 | -2.2031e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0936 | 1.1 | 1.0978 | 1.0936 | 3.708e-16 | -120.3163 | 119.9428 | 1.8845e-16 | -120.3163 | 119.9428
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7705e-18 | -2.6609e-11 | -7.6572e-11 | -4.7705e-18 | 2.6609e-11 | 7.6572e-11 | 2.5443e-18 | 7.332e-11 | 1.3218e-11 | -3.1803e-18 | -7.332e-11 | -1.3218e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0936 | 1.1 | 1.0978 | 1.0936 | 1.8845e-16 | -120.3163 | 119.9428 | 1.2535e-16 | -120.3163 | 119.9428
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2721e-18 | -8.8697e-12 | -2.5524e-11 | -1.2721e-18 | 8.8697e-12 | 2.5524e-11 | 2.5443e-18 | 2.444e-11 | 4.4061e-12 | -2.5443e-18 | -2.444e-11 | -4.4061e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0936 | 1.1 | 1.0978 | 1.0936 | 1.8845e-16 | -120.3163 | 119.9428 | 1.5682e-16 | -120.3163 | 119.9428
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9082e-18 | -1.7739e-11 | -5.1048e-11 | -1.9082e-18 | 1.7739e-11 | 5.1048e-11 | 1.9082e-18 | 4.888e-11 | 8.8123e-12 | -3.8164e-18 | -4.888e-11 | -8.8122e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0936 | 1.1 | 1.0978 | 1.0936 | 1.2535e-16 | -120.3163 | 119.9428 | 9.4723e-17 | -120.3163 | 119.9428
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.5902e-18 | -8.8697e-12 | -2.5524e-11 | 1.5902e-18 | 8.8698e-12 | 2.5524e-11 | -2.6289e-36 | 2.444e-11 | 4.4061e-12 | 1.9082e-18 | -2.444e-11 | -4.4061e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0936 | 1.1 | 1.0978 | 1.0936 | 9.4723e-17 | -120.3163 | 119.9428 | 7.5001e-17 | -120.3163 | 119.9428
Line16_4_18 | 0 | 0.061167 | 0.061167 | 0 | 0.061167 | 0.061167 | 0 | 0.014126 | 0.014126 | 0 | 0.014126 | 0.014126 | 1.2721e-18 | 0.01493 | 0.0038518 | -6.3266e-35 | -0.014893 | -0.0038144 | -2.5443e-18 | 0.0039805 | 0.014876 | 5.0885e-18 | -0.0039057 | -0.014801 | 0 | -135.4761 | 44.5239 | 0 | 44.5239 | -135.4761 | 1.1 | 1.0938 | 1.0878 | 1.1 | 1.0899 | 1.0821 | 7.5307e-16 | -120.5478 | 120.0075 | 7.1236e-16 | -120.781 | 120.073
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9023e-35 | -8.8697e-12 | -2.5524e-11 | -1.8585e-35 | 8.8697e-12 | 2.5524e-11 | -1.2721e-18 | 2.444e-11 | 4.4061e-12 | 1.2721e-18 | -2.444e-11 | -4.4061e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0936 | 1.1 | 1.0978 | 1.0936 | 8.568e-16 | -120.3163 | 119.9428 | 8.3707e-16 | -120.3163 | 119.9428
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5266e-17 | -7.0958e-11 | -2.0419e-10 | -1.5266e-17 | 7.0958e-11 | 2.0419e-10 | 1.0813e-17 | 1.9552e-10 | 3.5249e-11 | -8.9049e-18 | -1.9552e-10 | -3.5249e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0936 | 1.1 | 1.0978 | 1.0936 | 8.8414e-16 | -120.3163 | 119.9428 | 7.0073e-16 | -120.3163 | 119.9428
Line2_1_4 | 0 | 0.061167 | 0.061167 | 0 | 0.061167 | 0.061167 | 0 | 0.014126 | 0.014126 | 0 | 0.014126 | 0.014126 | 7.6328e-18 | 0.014968 | 0.0038892 | -7.6328e-18 | -0.01493 | -0.0038518 | 6.3607e-18 | 0.0040553 | 0.014951 | -6.3607e-18 | -0.0039805 | -0.014876 | 0 | -135.4761 | 44.5239 | 0 | 44.5239 | -135.4761 | 1.1 | 1.0978 | 1.0936 | 1.1 | 1.0938 | 1.0878 | 8.8414e-16 | -120.3163 | 119.9428 | 7.5307e-16 | -120.5478 | 120.0075
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8623e-18 | -1.7739e-11 | -5.1048e-11 | -2.2262e-18 | 1.7739e-11 | 5.1048e-11 | 1.2721e-18 | 4.888e-11 | 8.8123e-12 | -6.3607e-19 | -4.888e-11 | -8.8123e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0936 | 1.1 | 1.0978 | 1.0936 | 8.8414e-16 | -120.3163 | 119.9428 | 8.568e-16 | -120.3163 | 119.9428
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4066e-18 | -4.4349e-11 | -1.2762e-10 | -4.1344e-18 | 4.4349e-11 | 1.2762e-10 | 8.9049e-18 | 1.222e-10 | 2.2031e-11 | -9.541e-18 | -1.222e-10 | -2.2031e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0936 | 1.1 | 1.0978 | 1.0936 | 7.9516e-16 | -120.3163 | 119.9428 | 6.8818e-16 | -120.3163 | 119.9428
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.0885e-18 | -3.5479e-11 | -1.021e-10 | -5.0885e-18 | 3.5479e-11 | 1.021e-10 | 5.0885e-18 | 9.776e-11 | 1.7624e-11 | -5.0885e-18 | -9.776e-11 | -1.7624e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0936 | 1.1 | 1.0978 | 1.0936 | 6.8818e-16 | -120.3163 | 119.9428 | 5.9408e-16 | -120.3163 | 119.9428
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.3607e-19 | -2.6609e-11 | -7.6572e-11 | 6.3607e-19 | 2.6609e-11 | 7.6572e-11 | -1.9082e-18 | 7.332e-11 | 1.3218e-11 | 2.5443e-18 | -7.332e-11 | -1.3218e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0936 | 1.1 | 1.0978 | 1.0936 | 5.9408e-16 | -120.3163 | 119.9428 | 5.6375e-16 | -120.3163 | 119.9428
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1803e-19 | -8.8698e-12 | -2.5524e-11 | -3.1803e-19 | 8.8698e-12 | 2.5524e-11 | 6.3607e-19 | 2.444e-11 | 4.4061e-12 | -1.2721e-18 | -2.444e-11 | -4.4061e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0936 | 1.1 | 1.0978 | 1.0936 | 5.6375e-16 | -120.3163 | 119.9428 | 5.4869e-16 | -120.3163 | 119.9428
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.2584e-36 | -8.8698e-12 | -2.5524e-11 | -6.3607e-19 | 8.8698e-12 | 2.5524e-11 | -6.3607e-19 | 2.444e-11 | 4.4061e-12 | -6.2361e-36 | -2.444e-11 | -4.4061e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0936 | 1.1 | 1.0978 | 1.0936 | 5.6375e-16 | -120.3163 | 119.9428 | 5.6173e-16 | -120.3163 | 119.9428
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1767e-17 | -6.2088e-11 | -1.7867e-10 | -1.2403e-17 | 6.2088e-11 | 1.7867e-10 | 7.6328e-18 | 1.7108e-10 | 3.0843e-11 | -8.9049e-18 | -1.7108e-10 | -3.0843e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0936 | 1.1 | 1.0978 | 1.0936 | 7.0073e-16 | -120.3163 | 119.9428 | 5.3477e-16 | -120.3163 | 119.9428

## LL_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9336e-16 | -1.4366e-09 | -3.9666e-09 | -1.7579e-16 | 1.4366e-09 | 3.9666e-09 | 3.5157e-16 | 4.6273e-09 | -2.4518e-10 | -3.5157e-16 | -4.6273e-09 | 2.4518e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.83839 | 0.68767 | 0.95 | 0.83839 | 0.68767 | -1.7242e-12 | -135.3123 | 120.9775 | -1.723e-12 | -135.3123 | 120.9775
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4942e-16 | -1.4366e-09 | -3.9666e-09 | -1.4942e-16 | 1.4366e-09 | 3.9666e-09 | 4.5704e-16 | 4.6273e-09 | -2.4518e-10 | -4.5704e-16 | -4.6273e-09 | 2.4518e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.83839 | 0.68767 | 0.95 | 0.83839 | 0.68767 | -1.7127e-12 | -135.3123 | 120.9775 | -1.7083e-12 | -135.3123 | 120.9775
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.6682e-17 | -1.1971e-09 | -3.3055e-09 | -9.6682e-17 | 1.1971e-09 | 3.3055e-09 | 4.5704e-16 | 3.8561e-09 | -2.0432e-10 | -4.922e-16 | -3.8561e-09 | 2.0432e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.83839 | 0.68767 | 0.95 | 0.83839 | 0.68767 | -1.7083e-12 | -135.3123 | 120.9775 | -1.7017e-12 | -135.3123 | 120.9775
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5157e-17 | -7.1829e-10 | -1.9833e-09 | -3.5157e-17 | 7.1829e-10 | 1.9833e-09 | -1.7579e-17 | 2.3137e-09 | -1.2259e-10 | 1.7579e-17 | -2.3137e-09 | 1.2259e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.83839 | 0.68767 | 0.95 | 0.83839 | 0.68767 | -1.7017e-12 | -135.3123 | 120.9775 | -1.7007e-12 | -135.3123 | 120.9775
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7579e-17 | -2.3943e-10 | -6.611e-10 | -1.7579e-17 | 2.3943e-10 | 6.611e-10 | 3.6915e-16 | 7.7122e-10 | -4.0864e-11 | -3.5157e-16 | -7.7122e-10 | 4.0864e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.83839 | 0.68767 | 0.95 | 0.83839 | 0.68767 | -1.7017e-12 | -135.3123 | 120.9775 | -1.6974e-12 | -135.3123 | 120.9775
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6368e-17 | -4.7886e-10 | -1.3222e-09 | -8.7893e-18 | 4.7886e-10 | 1.3222e-09 | 3.5157e-17 | 1.5424e-09 | -8.1728e-11 | -1.7579e-17 | -1.5424e-09 | 8.1728e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.83839 | 0.68767 | 0.95 | 0.83839 | 0.68767 | -1.7007e-12 | -135.3123 | 120.9775 | -1.7e-12 | -135.3123 | 120.9775
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2736e-17 | -2.3943e-10 | -6.611e-10 | -5.2736e-17 | 2.3943e-10 | 6.611e-10 | 3.5157e-17 | 7.7122e-10 | -4.0864e-11 | -1.7579e-17 | -7.7122e-10 | 4.0864e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.83839 | 0.68767 | 0.95 | 0.83839 | 0.68767 | -1.7e-12 | -135.3123 | 120.9775 | -1.7004e-12 | -135.3123 | 120.9775
Line16_4_18 | 0 | 2.5068 | 2.5068 | 0 | 2.5068 | 2.5068 | 0 | 0.57893 | 0.57893 | 0 | 0.57893 | 0.57893 | 7.0314e-17 | 0.35328 | -0.11197 | -7.0314e-17 | -0.23262 | 0.23262 | -7.0314e-17 | -0.020967 | 0.27233 | 7.0314e-17 | 0.14665 | -0.14665 | 0 | -147.7717 | 32.2283 | 0 | 32.2283 | -147.7717 | 0.95 | 0.6113 | 0.50862 | 0.95 | 0.475 | 0.475 | -1.722e-12 | -151.1682 | 144.5775 | -1.7232e-12 | -180 | -180
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5867e-30 | -2.3943e-10 | -6.611e-10 | -2.116e-30 | 2.3943e-10 | 6.611e-10 | 5.2736e-17 | 7.7122e-10 | -4.0864e-11 | -7.0314e-17 | -7.7122e-10 | 4.0864e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.83839 | 0.68767 | 0.95 | 0.83839 | 0.68767 | -1.7239e-12 | -135.3123 | 120.9775 | -1.7243e-12 | -135.3123 | 120.9775
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4063e-16 | -1.9154e-09 | -5.2888e-09 | -1.2305e-16 | 1.9154e-09 | 5.2888e-09 | 4.2188e-16 | 6.1697e-09 | -3.2691e-10 | -4.3946e-16 | -6.1697e-09 | 3.2691e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.83839 | 0.68767 | 0.95 | 0.83839 | 0.68767 | -1.7242e-12 | -135.3123 | 120.9775 | -1.718e-12 | -135.3123 | 120.9775
Line2_1_4 | 0 | 2.5068 | 2.5068 | 0 | 2.5068 | 2.5068 | 0 | 0.57893 | 0.57893 | 0 | 0.57893 | 0.57893 | 3.5157e-17 | 0.47394 | 0.0086903 | -3.5157e-17 | -0.35328 | 0.11197 | 3.1641e-16 | 0.10472 | 0.39802 | -3.1641e-16 | 0.020967 | -0.27233 | 0 | -147.7717 | 32.2283 | 0 | 32.2283 | -147.7717 | 0.95 | 0.83839 | 0.68767 | 0.95 | 0.6113 | 0.50862 | -1.7242e-12 | -135.3123 | 120.9775 | -1.722e-12 | -151.1682 | 144.5775
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7579e-17 | -4.7886e-10 | -1.3222e-09 | -1.7579e-17 | 4.7886e-10 | 1.3222e-09 | -5.2898e-31 | 1.5424e-09 | -8.1728e-11 | -1.7579e-17 | -1.5424e-09 | 8.1728e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.83839 | 0.68767 | 0.95 | 0.83839 | 0.68767 | -1.7242e-12 | -135.3123 | 120.9775 | -1.7239e-12 | -135.3123 | 120.9775
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9336e-16 | -1.1971e-09 | -3.3055e-09 | -2.1094e-16 | 1.1971e-09 | 3.3055e-09 | 3.6915e-16 | 3.8561e-09 | -2.0432e-10 | -3.5157e-16 | -3.8561e-09 | 2.0432e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.83839 | 0.68767 | 0.95 | 0.83839 | 0.68767 | -1.723e-12 | -135.3123 | 120.9775 | -1.721e-12 | -135.3123 | 120.9775
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4942e-16 | -9.5772e-10 | -2.6444e-09 | -1.1426e-16 | 9.5772e-10 | 2.6444e-09 | 4.2188e-16 | 3.0849e-09 | -1.6346e-10 | -4.2188e-16 | -3.0849e-09 | 1.6346e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.83839 | 0.68767 | 0.95 | 0.83839 | 0.68767 | -1.721e-12 | -135.3123 | 120.9775 | -1.7167e-12 | -135.3123 | 120.9775
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2736e-17 | -7.1829e-10 | -1.9833e-09 | -3.5157e-17 | 7.1829e-10 | 1.9833e-09 | 8.7893e-17 | 2.3136e-09 | -1.2259e-10 | -1.0547e-16 | -2.3136e-09 | 1.2259e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.83839 | 0.68767 | 0.95 | 0.83839 | 0.68767 | -1.7167e-12 | -135.3123 | 120.9775 | -1.7159e-12 | -135.3123 | 120.9775
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.7893e-18 | -2.3943e-10 | -6.611e-10 | -8.7893e-18 | 2.3943e-10 | 6.611e-10 | 1.7579e-17 | 7.7122e-10 | -4.0864e-11 | -3.5157e-17 | -7.7122e-10 | 4.0864e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.83839 | 0.68767 | 0.95 | 0.83839 | 0.68767 | -1.7159e-12 | -135.3123 | 120.9775 | -1.716e-12 | -135.3123 | 120.9775
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6368e-17 | -2.3943e-10 | -6.611e-10 | -2.6368e-17 | 2.3943e-10 | 6.611e-10 | 3.5157e-17 | 7.7122e-10 | -4.0864e-11 | -5.2736e-17 | -7.7122e-10 | 4.0864e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.83839 | 0.68767 | 0.95 | 0.83839 | 0.68767 | -1.7159e-12 | -135.3123 | 120.9775 | -1.7151e-12 | -135.3123 | 120.9775
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2305e-16 | -1.676e-09 | -4.6277e-09 | -1.4063e-16 | 1.676e-09 | 4.6277e-09 | 4.0431e-16 | 5.3985e-09 | -2.8605e-10 | -4.2188e-16 | -5.3985e-09 | 2.8605e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.83839 | 0.68767 | 0.95 | 0.83839 | 0.68767 | -1.718e-12 | -135.3123 | 120.9775 | -1.7127e-12 | -135.3123 | 120.9775

## LL_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6653e-16 | -1.2893e-09 | -3.56e-09 | -1.4988e-16 | 1.2893e-09 | 3.56e-09 | 2.9976e-16 | 4.153e-09 | -2.2006e-10 | -2.9976e-16 | -4.153e-09 | 2.2006e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.79426 | 0.65148 | 0.9 | 0.79426 | 0.65148 | -1.6808e-12 | -135.3123 | 120.9775 | -1.6791e-12 | -135.3123 | 120.9775
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821e-16 | -1.2893e-09 | -3.56e-09 | -1.5821e-16 | 1.2893e-09 | 3.56e-09 | 3.6637e-16 | 4.153e-09 | -2.2006e-10 | -3.8303e-16 | -4.153e-09 | 2.2006e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.79426 | 0.65148 | 0.9 | 0.79426 | 0.65148 | -1.6695e-12 | -135.3123 | 120.9775 | -1.6651e-12 | -135.3123 | 120.9775
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3267e-17 | -1.0744e-09 | -2.9667e-09 | -9.992e-17 | 1.0744e-09 | 2.9667e-09 | 4.1633e-16 | 3.4609e-09 | -1.8338e-10 | -3.9968e-16 | -3.4609e-09 | 1.8338e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.79426 | 0.65148 | 0.9 | 0.79426 | 0.65148 | -1.6651e-12 | -135.3123 | 120.9775 | -1.6587e-12 | -135.3123 | 120.9775
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3267e-18 | -6.4467e-10 | -1.78e-09 | -2.498e-17 | 6.4467e-10 | 1.78e-09 | 1.6653e-17 | 2.0765e-09 | -1.1003e-10 | 1.6653e-17 | -2.0765e-09 | 1.1003e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.79426 | 0.65148 | 0.9 | 0.79426 | 0.65148 | -1.6587e-12 | -135.3123 | 120.9775 | -1.6577e-12 | -135.3123 | 120.9775
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1633e-17 | -2.1489e-10 | -5.9334e-10 | -4.1633e-17 | 2.1489e-10 | 5.9334e-10 | 3.3307e-16 | 6.9217e-10 | -3.6676e-11 | -2.9976e-16 | -6.9217e-10 | 3.6676e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.79426 | 0.65148 | 0.9 | 0.79426 | 0.65148 | -1.6587e-12 | -135.3123 | 120.9775 | -1.655e-12 | -135.3123 | 120.9775
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.3307e-17 | -4.2978e-10 | -1.1867e-09 | -9.6323e-31 | 4.2978e-10 | 1.1867e-09 | 3.3307e-17 | 1.3843e-09 | -7.3352e-11 | -3.3307e-17 | -1.3843e-09 | 7.3352e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.79426 | 0.65148 | 0.9 | 0.79426 | 0.65148 | -1.6577e-12 | -135.3123 | 120.9775 | -1.657e-12 | -135.3123 | 120.9775
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.1633e-17 | -2.1489e-10 | -5.9334e-10 | 2.498e-17 | 2.1489e-10 | 5.9334e-10 | 4.996e-17 | 6.9217e-10 | -3.6676e-11 | -3.3307e-17 | -6.9217e-10 | 3.6676e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.79426 | 0.65148 | 0.9 | 0.79426 | 0.65148 | -1.657e-12 | -135.3123 | 120.9775 | -1.6574e-12 | -135.3123 | 120.9775
Line16_4_18 | 0 | 2.3749 | 2.3749 | 0 | 2.3749 | 2.3749 | 0 | 0.54846 | 0.54846 | 0 | 0.54846 | 0.54846 | 6.6613e-17 | 0.31707 | -0.10049 | 1.9541e-30 | -0.20878 | 0.20878 | -1.3323e-16 | -0.018818 | 0.24442 | 6.6613e-17 | 0.13162 | -0.13162 | 0 | -147.7717 | 32.2283 | 0 | 32.2283 | -147.7717 | 0.9 | 0.57913 | 0.48185 | 0.9 | 0.45 | 0.45 | -1.6793e-12 | -151.1682 | 144.5775 | -1.6807e-12 | -180 | -180
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.3267e-18 | -2.1489e-10 | -5.9334e-10 | 8.3267e-18 | 2.1489e-10 | 5.9334e-10 | 2.4422e-31 | 6.9217e-10 | -3.6676e-11 | -1.6653e-17 | -6.9217e-10 | 3.6676e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.79426 | 0.65148 | 0.9 | 0.79426 | 0.65148 | -1.6805e-12 | -135.3123 | 120.9775 | -1.6809e-12 | -135.3123 | 120.9775
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4155e-16 | -1.7191e-09 | -4.7467e-09 | -1.249e-16 | 1.7191e-09 | 4.7467e-09 | 3.4972e-16 | 5.5374e-09 | -2.9341e-10 | -3.4972e-16 | -5.5374e-09 | 2.9341e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.79426 | 0.65148 | 0.9 | 0.79426 | 0.65148 | -1.6808e-12 | -135.3123 | 120.9775 | -1.6748e-12 | -135.3123 | 120.9775
Line2_1_4 | 0 | 2.3749 | 2.3749 | 0 | 2.3749 | 2.3749 | 0 | 0.54846 | 0.54846 | 0 | 0.54846 | 0.54846 | 9.992e-17 | 0.42536 | 0.0077996 | -3.3307e-17 | -0.31707 | 0.10049 | 2.9976e-16 | 0.093984 | 0.35722 | -2.9976e-16 | 0.018818 | -0.24442 | 0 | -147.7717 | 32.2283 | 0 | 32.2283 | -147.7717 | 0.9 | 0.79426 | 0.65148 | 0.9 | 0.57913 | 0.48185 | -1.6808e-12 | -135.3123 | 120.9775 | -1.6793e-12 | -151.1682 | 144.5775
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.498e-17 | -4.2978e-10 | -1.1867e-09 | 8.3267e-18 | 4.2978e-10 | 1.1867e-09 | -7.328e-31 | 1.3843e-09 | -7.3352e-11 | -1.6653e-17 | -1.3843e-09 | 7.3352e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.79426 | 0.65148 | 0.9 | 0.79426 | 0.65148 | -1.6808e-12 | -135.3123 | 120.9775 | -1.6805e-12 | -135.3123 | 120.9775
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821e-16 | -1.0744e-09 | -2.9667e-09 | -1.7486e-16 | 1.0744e-09 | 2.9667e-09 | 2.9976e-16 | 3.4609e-09 | -1.8338e-10 | -2.9976e-16 | -3.4609e-09 | 1.8338e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.79426 | 0.65148 | 0.9 | 0.79426 | 0.65148 | -1.6791e-12 | -135.3123 | 120.9775 | -1.6768e-12 | -135.3123 | 120.9775
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.249e-16 | -8.5956e-10 | -2.3734e-09 | -1.4155e-16 | 8.5956e-10 | 2.3734e-09 | 3.8303e-16 | 2.7687e-09 | -1.467e-10 | -3.8303e-16 | -2.7687e-09 | 1.467e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.79426 | 0.65148 | 0.9 | 0.79426 | 0.65148 | -1.6768e-12 | -135.3123 | 120.9775 | -1.6725e-12 | -135.3123 | 120.9775
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.498e-17 | -6.4467e-10 | -1.78e-09 | -2.498e-17 | 6.4467e-10 | 1.78e-09 | 6.6613e-17 | 2.0765e-09 | -1.1003e-10 | -8.3267e-17 | -2.0765e-09 | 1.1003e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.79426 | 0.65148 | 0.9 | 0.79426 | 0.65148 | -1.6725e-12 | -135.3123 | 120.9775 | -1.6715e-12 | -135.3123 | 120.9775
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3307e-17 | -2.1489e-10 | -5.9334e-10 | -3.3307e-17 | 2.1489e-10 | 5.9334e-10 | 1.6653e-17 | 6.9217e-10 | -3.6676e-11 | 9.7177e-31 | -6.9217e-10 | 3.6676e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.79426 | 0.65148 | 0.9 | 0.79426 | 0.65148 | -1.6715e-12 | -135.3123 | 120.9775 | -1.6717e-12 | -135.3123 | 120.9775
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6653e-17 | -2.1489e-10 | -5.9334e-10 | -1.6653e-17 | 2.1489e-10 | 5.9334e-10 | 4.996e-17 | 6.9217e-10 | -3.6676e-11 | -3.3307e-17 | -6.9217e-10 | 3.6676e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.79426 | 0.65148 | 0.9 | 0.79426 | 0.65148 | -1.6715e-12 | -135.3123 | 120.9775 | -1.6709e-12 | -135.3123 | 120.9775
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4155e-16 | -1.5042e-09 | -4.1534e-09 | -1.4155e-16 | 1.5042e-09 | 4.1534e-09 | 3.8303e-16 | 4.8452e-09 | -2.5673e-10 | -3.4972e-16 | -4.8452e-09 | 2.5673e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.79426 | 0.65148 | 0.9 | 0.79426 | 0.65148 | -1.6748e-12 | -135.3123 | 120.9775 | -1.6695e-12 | -135.3123 | 120.9775

## LL_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7593e-18 | -3.8862e-11 | -1.1288e-10 | -7.2099e-18 | 3.8862e-11 | 1.1288e-10 | 6.5919e-18 | 1.0829e-10 | 1.9912e-11 | -6.0426e-18 | -1.0829e-10 | -1.9912e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94812 | 0.94457 | 0.95 | 0.94812 | 0.94457 | -2.9248e-14 | -120.3131 | 119.9422 | -2.9268e-14 | -120.3131 | 119.9422
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.532e-18 | -3.8862e-11 | -1.1288e-10 | -4.8066e-18 | 3.8862e-11 | 1.1288e-10 | 1.0437e-17 | 1.0829e-10 | 1.9912e-11 | -1.0987e-17 | -1.0829e-10 | -1.9912e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94812 | 0.94457 | 0.95 | 0.94812 | 0.94457 | -2.9058e-14 | -120.3131 | 119.9422 | -2.8981e-14 | -120.3131 | 119.9422
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7766e-18 | -3.2385e-11 | -9.4068e-11 | -4.0513e-18 | 3.2385e-11 | 9.4068e-11 | 9.8879e-18 | 9.0245e-11 | 1.6593e-11 | -1.0987e-17 | -9.0245e-11 | -1.6593e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94812 | 0.94457 | 0.95 | 0.94812 | 0.94457 | -2.8981e-14 | -120.3131 | 119.9422 | -2.8859e-14 | -120.3131 | 119.9422
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4333e-19 | -1.9431e-11 | -5.6441e-11 | -3.4333e-19 | 1.9431e-11 | 5.6441e-11 | 1.648e-18 | 5.4147e-11 | 9.9561e-12 | -1.0987e-18 | -5.4147e-11 | -9.9561e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94812 | 0.94457 | 0.95 | 0.94812 | 0.94457 | -2.8859e-14 | -120.3131 | 119.9422 | -2.8839e-14 | -120.3131 | 119.9422
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.236e-18 | -6.477e-12 | -1.8814e-11 | -1.236e-18 | 6.477e-12 | 1.8814e-11 | 8.7893e-18 | 1.8049e-11 | 3.3187e-12 | -7.6906e-18 | -1.8049e-11 | -3.3187e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94812 | 0.94457 | 0.95 | 0.94812 | 0.94457 | -2.8859e-14 | -120.3131 | 119.9422 | -2.8768e-14 | -120.3131 | 119.9422
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.06e-19 | -1.2954e-11 | -3.7627e-11 | -2.06e-19 | 1.2954e-11 | 3.7627e-11 | 5.4933e-19 | 3.6098e-11 | 6.6374e-12 | -5.4933e-19 | -3.6098e-11 | -6.6374e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94812 | 0.94457 | 0.95 | 0.94812 | 0.94457 | -2.8839e-14 | -120.3131 | 119.9422 | -2.8823e-14 | -120.3131 | 119.9422
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0987e-18 | -6.477e-12 | -1.8814e-11 | -1.0987e-18 | 6.477e-12 | 1.8814e-11 | 1.0987e-18 | 1.8049e-11 | 3.3187e-12 | -1.648e-18 | -1.8049e-11 | -3.3187e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94812 | 0.94457 | 0.95 | 0.94812 | 0.94457 | -2.8823e-14 | -120.3131 | 119.9422 | -2.883e-14 | -120.3131 | 119.9422
Line16_4_18 | 0 | 0.052639 | 0.052639 | 0 | 0.052639 | 0.052639 | 0 | 0.012156 | 0.012156 | 0 | 0.012156 | 0.012156 | 3.296e-18 | 0.011082 | 0.0028784 | -3.296e-18 | -0.011029 | -0.0028252 | -2.1973e-18 | 0.0029185 | 0.011047 | 1.6831e-33 | -0.0028631 | -0.010991 | 0 | -135.266 | 44.734 | 0 | 44.734 | -135.266 | 0.95 | 0.94272 | 0.93905 | 0.95 | 0.93734 | 0.93354 | -2.9217e-14 | -120.5122 | 120.1294 | -2.9258e-14 | -120.7135 | 120.3187
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.7466e-19 | -6.477e-12 | -1.8814e-11 | 2.7466e-19 | 6.477e-12 | 1.8814e-11 | 5.4933e-19 | 1.8049e-11 | 3.3187e-12 | -5.4933e-19 | -1.8049e-11 | -3.3187e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94812 | 0.94457 | 0.95 | 0.94812 | 0.94457 | -2.9245e-14 | -120.3131 | 119.9422 | -2.9252e-14 | -120.3131 | 119.9422
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.4546e-18 | -5.1816e-11 | -1.5051e-10 | -6.18e-18 | 5.1816e-11 | 1.5051e-10 | 8.2399e-18 | 1.4439e-10 | 2.655e-11 | -8.2399e-18 | -1.4439e-10 | -2.655e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94812 | 0.94457 | 0.95 | 0.94812 | 0.94457 | -2.9248e-14 | -120.3131 | 119.9422 | -2.9147e-14 | -120.3131 | 119.9422
Line2_1_4 | 0 | 0.052639 | 0.052639 | 0 | 0.052639 | 0.052639 | 0 | 0.012156 | 0.012156 | 0 | 0.012156 | 0.012156 | 3.8453e-18 | 0.011136 | 0.0029316 | -3.296e-18 | -0.011082 | -0.0028784 | 6.5919e-18 | 0.0029739 | 0.011102 | -7.6906e-18 | -0.0029185 | -0.011047 | 0 | -135.266 | 44.734 | 0 | 44.734 | -135.266 | 0.95 | 0.94812 | 0.94457 | 0.95 | 0.94272 | 0.93905 | -2.9248e-14 | -120.3131 | 119.9422 | -2.9217e-14 | -120.5122 | 120.1294
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.8666e-20 | -1.2954e-11 | -3.7627e-11 | 3.4333e-19 | 1.2954e-11 | 3.7627e-11 | 2.1973e-18 | 3.6098e-11 | 6.6374e-12 | -1.648e-18 | -3.6098e-11 | -6.6374e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94812 | 0.94457 | 0.95 | 0.94812 | 0.94457 | -2.9248e-14 | -120.3131 | 119.9422 | -2.9245e-14 | -120.3131 | 119.9422
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.8366e-18 | -3.2385e-11 | -9.4068e-11 | -5.8366e-18 | 3.2385e-11 | 9.4068e-11 | 7.1413e-18 | 9.0245e-11 | 1.6593e-11 | -6.5919e-18 | -9.0245e-11 | -1.6593e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94812 | 0.94457 | 0.95 | 0.94812 | 0.94457 | -2.9268e-14 | -120.3131 | 119.9422 | -2.9256e-14 | -120.3131 | 119.9422
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2573e-18 | -2.5908e-11 | -7.5255e-11 | -4.532e-18 | 2.5908e-11 | 7.5255e-11 | 8.2399e-18 | 7.2196e-11 | 1.3275e-11 | -8.7893e-18 | -7.2196e-11 | -1.3275e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94812 | 0.94457 | 0.95 | 0.94812 | 0.94457 | -2.9256e-14 | -120.3131 | 119.9422 | -2.9189e-14 | -120.3131 | 119.9422
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3733e-19 | -1.9431e-11 | -5.6441e-11 | -4.12e-19 | 1.9431e-11 | 5.6441e-11 | 2.1973e-18 | 5.4147e-11 | 9.9561e-12 | -1.648e-18 | -5.4147e-11 | -9.9561e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94812 | 0.94457 | 0.95 | 0.94812 | 0.94457 | -2.9189e-14 | -120.3131 | 119.9422 | -2.9178e-14 | -120.3131 | 119.9422
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.06e-19 | -6.477e-12 | -1.8814e-11 | 6.8666e-20 | 6.477e-12 | 1.8814e-11 | 1.0987e-18 | 1.8049e-11 | 3.3187e-12 | -1.648e-18 | -1.8049e-11 | -3.3187e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94812 | 0.94457 | 0.95 | 0.94812 | 0.94457 | -2.9178e-14 | -120.3131 | 119.9422 | -2.918e-14 | -120.3131 | 119.9422
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7466e-19 | -6.477e-12 | -1.8814e-11 | -2.7466e-19 | 6.477e-12 | 1.8814e-11 | 1.0987e-18 | 1.8049e-11 | 3.3187e-12 | -1.0987e-18 | -1.8049e-11 | -3.3187e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94812 | 0.94457 | 0.95 | 0.94812 | 0.94457 | -2.9178e-14 | -120.3131 | 119.9422 | -2.9171e-14 | -120.3131 | 119.9422
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8753e-18 | -4.5339e-11 | -1.317e-10 | -5.15e-18 | 4.5339e-11 | 1.317e-10 | 1.0987e-17 | 1.2634e-10 | 2.3231e-11 | -1.0437e-17 | -1.2634e-10 | -2.3231e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94812 | 0.94457 | 0.95 | 0.94812 | 0.94457 | -2.9147e-14 | -120.3131 | 119.9422 | -2.9058e-14 | -120.3131 | 119.9422

## LL_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.5052e-18 | -3.4879e-11 | -1.0131e-10 | -6.7654e-18 | 3.4879e-11 | 1.0131e-10 | 4.6838e-18 | 9.7195e-11 | 1.7871e-11 | -4.1633e-18 | -9.7195e-11 | -1.7871e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89822 | 0.89485 | 0.9 | 0.89822 | 0.89485 | -2.785e-14 | -120.3131 | 119.9422 | -2.7873e-14 | -120.3131 | 119.9422
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1633e-18 | -3.4879e-11 | -1.0131e-10 | -4.4235e-18 | 3.4879e-11 | 1.0131e-10 | 8.3267e-18 | 9.7195e-11 | 1.7871e-11 | -8.8471e-18 | -9.7195e-11 | -1.7871e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89822 | 0.89485 | 0.9 | 0.89822 | 0.89485 | -2.7665e-14 | -120.3131 | 119.9422 | -2.7591e-14 | -120.3131 | 119.9422
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6021e-18 | -2.9066e-11 | -8.4427e-11 | -2.8623e-18 | 2.9066e-11 | 8.4427e-11 | 8.8471e-18 | 8.0996e-11 | 1.4893e-11 | -8.8471e-18 | -8.0996e-11 | -1.4893e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89822 | 0.89485 | 0.9 | 0.89822 | 0.89485 | -2.7591e-14 | -120.3131 | 119.9422 | -2.7471e-14 | -120.3131 | 119.9422
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.1557e-19 | -1.7439e-11 | -5.0656e-11 | -9.7578e-19 | 1.7439e-11 | 5.0656e-11 | 1.5613e-18 | 4.8598e-11 | 8.9356e-12 | -1.0408e-18 | -4.8598e-11 | -8.9356e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89822 | 0.89485 | 0.9 | 0.89822 | 0.89485 | -2.7471e-14 | -120.3131 | 119.9422 | -2.7451e-14 | -120.3131 | 119.9422
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.301e-18 | -5.8131e-12 | -1.6885e-11 | -1.301e-18 | 5.8131e-12 | 1.6885e-11 | 7.2858e-18 | 1.6199e-11 | 2.9785e-12 | -6.7654e-18 | -1.6199e-11 | -2.9785e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89822 | 0.89485 | 0.9 | 0.89822 | 0.89485 | -2.7471e-14 | -120.3131 | 119.9422 | -2.7389e-14 | -120.3131 | 119.9422
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.5052e-20 | -1.1626e-11 | -3.3771e-11 | 6.5052e-20 | 1.1626e-11 | 3.3771e-11 | 1.5613e-18 | 3.2398e-11 | 5.9571e-12 | -1.0408e-18 | -3.2398e-11 | -5.9571e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89822 | 0.89485 | 0.9 | 0.89822 | 0.89485 | -2.7451e-14 | -120.3131 | 119.9422 | -2.7435e-14 | -120.3131 | 119.9422
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.5052e-20 | -5.8131e-12 | -1.6885e-11 | 6.5052e-20 | 5.8131e-12 | 1.6885e-11 | 1.0408e-18 | 1.6199e-11 | 2.9785e-12 | -5.2042e-19 | -1.6199e-11 | -2.9785e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89822 | 0.89485 | 0.9 | 0.89822 | 0.89485 | -2.7435e-14 | -120.3131 | 119.9422 | -2.7442e-14 | -120.3131 | 119.9422
Line16_4_18 | 0 | 0.049869 | 0.049869 | 0 | 0.049869 | 0.049869 | 0 | 0.011517 | 0.011517 | 0 | 0.011517 | 0.011517 | 1.0408e-18 | 0.0099465 | 0.0025834 | -1.0408e-18 | -0.0098987 | -0.0025356 | 1.0408e-18 | 0.0026194 | 0.0099144 | 5.0661e-34 | -0.0025697 | -0.0098647 | 0 | -135.266 | 44.734 | 0 | 44.734 | -135.266 | 0.9 | 0.89311 | 0.88962 | 0.9 | 0.888 | 0.8844 | -2.7845e-14 | -120.5122 | 120.1294 | -2.7888e-14 | -120.7135 | 120.3187
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.5052e-20 | -5.8131e-12 | -1.6885e-11 | 6.5052e-20 | 5.8131e-12 | 1.6885e-11 | 3.1617e-35 | 1.6199e-11 | 2.9785e-12 | -5.2042e-19 | -1.6199e-11 | -2.9786e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89822 | 0.89485 | 0.9 | 0.89822 | 0.89485 | -2.7847e-14 | -120.3131 | 119.9422 | -2.7854e-14 | -120.3131 | 119.9422
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9031e-18 | -4.6505e-11 | -1.3508e-10 | -4.1633e-18 | 4.6505e-11 | 1.3508e-10 | 7.8063e-18 | 1.2959e-10 | 2.3828e-11 | -7.8063e-18 | -1.2959e-10 | -2.3828e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89822 | 0.89485 | 0.9 | 0.89822 | 0.89485 | -2.785e-14 | -120.3131 | 119.9422 | -2.7752e-14 | -120.3131 | 119.9422
Line2_1_4 | 0 | 0.049869 | 0.049869 | 0 | 0.049869 | 0.049869 | 0 | 0.011517 | 0.011517 | 0 | 0.011517 | 0.011517 | 1.5613e-18 | 0.0099942 | 0.0026311 | -3.1225e-18 | -0.0099465 | -0.0025834 | 7.2858e-18 | 0.0026691 | 0.0099642 | -6.245e-18 | -0.0026194 | -0.0099144 | 0 | -135.266 | 44.734 | 0 | 44.734 | -135.266 | 0.9 | 0.89822 | 0.89485 | 0.9 | 0.89311 | 0.88962 | -2.785e-14 | -120.3131 | 119.9422 | -2.7845e-14 | -120.5122 | 120.1294
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.5052e-20 | -1.1626e-11 | -3.3771e-11 | -1.9516e-19 | 1.1626e-11 | 3.3771e-11 | 1.5613e-18 | 3.2398e-11 | 5.9571e-12 | -1.0408e-18 | -3.2398e-11 | -5.9571e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89822 | 0.89485 | 0.9 | 0.89822 | 0.89485 | -2.785e-14 | -120.3131 | 119.9422 | -2.7847e-14 | -120.3131 | 119.9422
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.7896e-18 | -2.9066e-11 | -8.4427e-11 | -5.7896e-18 | 2.9066e-11 | 8.4427e-11 | 6.7654e-18 | 8.0996e-11 | 1.4893e-11 | -6.245e-18 | -8.0996e-11 | -1.4893e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89822 | 0.89485 | 0.9 | 0.89822 | 0.89485 | -2.7873e-14 | -120.3131 | 119.9422 | -2.7864e-14 | -120.3131 | 119.9422
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.6838e-18 | -2.3253e-11 | -6.7542e-11 | -4.6838e-18 | 2.3253e-11 | 6.7542e-11 | 6.7654e-18 | 6.4797e-11 | 1.1914e-11 | -6.245e-18 | -6.4797e-11 | -1.1914e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89822 | 0.89485 | 0.9 | 0.89822 | 0.89485 | -2.7864e-14 | -120.3131 | 119.9422 | -2.7799e-14 | -120.3131 | 119.9422
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.7578e-19 | -1.7439e-11 | -5.0656e-11 | -9.7578e-19 | 1.7439e-11 | 5.0656e-11 | 2.0817e-18 | 4.8598e-11 | 8.9357e-12 | -1.5613e-18 | -4.8598e-11 | -8.9357e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89822 | 0.89485 | 0.9 | 0.89822 | 0.89485 | -2.7799e-14 | -120.3131 | 119.9422 | -2.7773e-14 | -120.3131 | 119.9422
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.236e-18 | -5.8131e-12 | -1.6885e-11 | -1.236e-18 | 5.8131e-12 | 1.6885e-11 | -5.9912e-34 | 1.6199e-11 | 2.9786e-12 | -1.0408e-18 | -1.6199e-11 | -2.9786e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89822 | 0.89485 | 0.9 | 0.89822 | 0.89485 | -2.7773e-14 | -120.3131 | 119.9422 | -2.7774e-14 | -120.3131 | 119.9422
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.5052e-20 | -5.8131e-12 | -1.6885e-11 | 1.9516e-19 | 5.8131e-12 | 1.6885e-11 | 1.0408e-18 | 1.6199e-11 | 2.9785e-12 | -1.5613e-18 | -1.6199e-11 | -2.9785e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89822 | 0.89485 | 0.9 | 0.89822 | 0.89485 | -2.7773e-14 | -120.3131 | 119.9422 | -2.7754e-14 | -120.3131 | 119.9422
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8139e-18 | -4.0692e-11 | -1.182e-10 | -4.5536e-18 | 4.0692e-11 | 1.182e-10 | 7.2858e-18 | 1.1339e-10 | 2.085e-11 | -7.8063e-18 | -1.1339e-10 | -2.085e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89822 | 0.89485 | 0.9 | 0.89822 | 0.89485 | -2.7752e-14 | -120.3131 | 119.9422 | -2.7665e-14 | -120.3131 | 119.9422

## LG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.032243 | 0.032243 | 0.032243 | 0.032243 | 0.032243 | 0.032243 | 0.0074461 | 0.0074461 | 0.0074461 | 0.0074462 | 0.0074462 | 0.0074462 | -0.0001508 | 0.0029808 | 0.012812 | 0.000156 | -0.0029756 | -0.012807 | -0.00030194 | 0.012651 | 0.0033381 | 0.00031234 | -0.012641 | -0.0033278 | 133.4498 | 133.4498 | 133.4498 | -46.5506 | -46.5506 | -46.5506 |  | 0.045326 | 1.7455 | 1.7781 | 0.046887 | 1.744 | 1.777 | 16.9097 | -149.8084 | 148.0533 | 16.9089 | -149.7966 | 148.0154
Line10_11_12 | 0.032146 | 0.032146 | 0.032146 | 0.032147 | 0.032147 | 0.032147 | 0.0074239 | 0.0074239 | 0.0074239 | 0.007424 | 0.007424 | 0.007424 | -0.00016039 | 0.0029492 | 0.01276 | 0.00016556 | -0.0029439 | -0.012755 | -0.00032185 | 0.012596 | 0.0033201 | 0.00033219 | -0.012585 | -0.0033099 | 133.3932 | 133.3932 | 133.3932 | -46.6072 | -46.6072 | -46.6072 |  | 0.048438 | 1.7425 | 1.776 | 0.049995 | 1.741 | 1.775 | 16.9045 | -149.7847 | 147.9777 | 16.9022 | -149.7729 | 147.9399
Line11_12_13 | 0.032147 | 0.032147 | 0.032147 | 0.032147 | 0.032147 | 0.032147 | 0.007424 | 0.007424 | 0.007424 | 0.007424 | 0.007424 | 0.007424 | -0.00016556 | 0.0029439 | 0.012755 | 0.00017072 | -0.0029387 | -0.01275 | -0.00033219 | 0.012585 | 0.0033099 | 0.00034253 | -0.012575 | -0.0032997 | 133.3927 | 133.3927 | 133.3927 | -46.6077 | -46.6077 | -46.6077 |  | 0.049995 | 1.741 | 1.775 | 0.051551 | 1.7395 | 1.774 | 16.9022 | -149.7729 | 147.9399 | 16.8999 | -149.761 | 147.902
Line12_13_15 | 1.0745e-06 | 1.0735e-06 | 1.0735e-06 | 0 | 0 | 0 | 2.4814e-07 | 2.4792e-07 | 2.4792e-07 | 0 | 0 | 0 | -4.5891e-09 | 2.4308e-07 | -2.0667e-07 | 3.2396e-09 | -1.6733e-07 | 1.3228e-07 | 1.194e-08 | -3.5623e-07 | -3.8822e-07 | -7.9026e-09 | 2.3416e-07 | 2.6201e-07 | -94.1235 | -94.0689 | -94.0689 | 0 | 0 | 0 |  | 0.051551 | 1.7395 | 1.774 | 0.051551 | 1.7395 | 1.774 | 16.8999 | -149.761 | 147.902 | 16.8999 | -149.761 | 147.902
Line13_13_14 | 0.032148 | 0.032148 | 0.032148 | 0.032148 | 0.032148 | 0.032148 | 0.0074242 | 0.0074242 | 0.0074242 | 0.0074242 | 0.0074242 | 0.0074242 | -0.00017072 | 0.0029384 | 0.01275 | 0.00017588 | -0.0029332 | -0.012745 | -0.00034254 | 0.012576 | 0.0033001 | 0.00035288 | -0.012565 | -0.0032899 | 133.3909 | 133.3909 | 133.3909 | -46.6096 | -46.6096 | -46.6096 |  | 0.051551 | 1.7395 | 1.774 | 0.053107 | 1.738 | 1.7729 | 16.8999 | -149.761 | 147.902 | 16.8977 | -149.7491 | 147.8641
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.0594e-09 | 1.6205e-07 | -1.3778e-07 | 1.7099e-09 | -8.6306e-08 | 6.3388e-08 | 7.9603e-09 | -2.3749e-07 | -2.5882e-07 | -3.9225e-09 | 1.1542e-07 | 1.326e-07 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.051551 | 1.7395 | 1.774 | 0.051551 | 1.7395 | 1.774 | 16.8999 | -149.761 | 147.902 | 16.9 | -149.761 | 147.902
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.5297e-09 | 8.1025e-08 | -6.8892e-08 | 1.8016e-10 | -5.281e-09 | -5.5031e-09 | 3.9802e-09 | -1.1874e-07 | -1.2941e-07 | 5.7696e-11 | -3.3243e-09 | 3.1961e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.051551 | 1.7395 | 1.774 | 0.051551 | 1.7395 | 1.774 | 16.9 | -149.761 | 147.902 | 16.9 | -149.761 | 147.902
Line16_4_18 | 0.29062 | 0 | 0 | 0.29062 | 0 | 0 | 0.067116 | 0 | 0 | 0.067116 | 0 | 0 | 0.00070383 | 8.1388e-08 | -7.0224e-08 | -1.0174e-14 | -5.2357e-09 | -5.467e-09 | 0.0014077 | -1.204e-07 | -1.3052e-07 | 1.1127e-14 | -3.3119e-09 | 3.1783e-09 | -46.5214 | 0 | 0 | 133.4787 | 0 | 0 |  | 0.023449 | 1.7395 | 1.774 | 0 | 1.7349 | 1.7709 | 16.9136 | -149.7611 | 147.9009 | 0 | -149.7254 | 147.7863
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.3467e-09 | 8.1458e-08 | -6.9379e-08 | 1.5943e-10 | -5.3409e-09 | -5.551e-09 | 3.5229e-09 | -1.201e-07 | -1.3053e-07 | 5.0757e-11 | -3.3407e-09 | 3.2194e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.045326 | 1.7455 | 1.7781 | 0.045326 | 1.7455 | 1.7781 | 16.9098 | -149.8084 | 148.0533 | 16.9098 | -149.8084 | 148.0533
Line1_1_3 | 0.032146 | 0.032146 | 0.032146 | 0.032146 | 0.032146 | 0.032146 | 0.0074238 | 0.0074238 | 0.0074238 | 0.0074239 | 0.0074239 | 0.0074239 | -0.00015006 | 0.0029597 | 0.01277 | 0.00015522 | -0.0029544 | -0.012765 | -0.00030118 | 0.012616 | 0.0033405 | 0.00031151 | -0.012606 | -0.0033303 | 133.3942 | 133.3941 | 133.3941 | -46.6063 | -46.6063 | -46.6063 |  | 0.045326 | 1.7455 | 1.7781 | 0.046882 | 1.744 | 1.777 | 16.9097 | -149.8084 | 148.0533 | 16.9071 | -149.7966 | 148.0155
Line2_1_4 | 0.25813 | 0.032485 | 0.032485 | 0.25813 | 0.032486 | 0.032486 | 0.059614 | 0.0075022 | 0.0075022 | 0.059614 | 0.0075022 | 0.0075022 | 0.001208 | 0.0030345 | 0.012917 | -0.00062485 | -0.0030133 | -0.012896 | 0.002417 | 0.012739 | 0.0033316 | -0.0012505 | -0.012697 | -0.0032898 | -46.5353 | 133.59 | 133.59 | 133.4647 | -46.4105 | -46.4105 |  | 0.045326 | 1.7455 | 1.7781 | 0.023449 | 1.7395 | 1.774 | 16.9097 | -149.8084 | 148.0533 | 16.9136 | -149.7611 | 147.9009
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.6933e-09 | 1.6292e-07 | -1.3876e-07 | 1.5061e-09 | -8.6799e-08 | 6.3828e-08 | 7.0459e-09 | -2.402e-07 | -2.6106e-07 | -3.4722e-09 | 1.1676e-07 | 1.3375e-07 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.045326 | 1.7455 | 1.7781 | 0.045326 | 1.7455 | 1.7781 | 16.9097 | -149.8084 | 148.0533 | 16.9098 | -149.8084 | 148.0533
Line4_2_6 | 0.032243 | 0.032243 | 0.032243 | 0.032243 | 0.032243 | 0.032243 | 0.0074462 | 0.0074462 | 0.0074462 | 0.0074462 | 0.0074462 | 0.0074462 | -0.000156 | 0.0029756 | 0.012807 | 0.0001612 | -0.0029703 | -0.012802 | -0.00031234 | 0.012641 | 0.0033278 | 0.00032273 | -0.012631 | -0.0033175 | 133.4494 | 133.4493 | 133.4493 | -46.5511 | -46.5511 | -46.5511 |  | 0.046887 | 1.744 | 1.777 | 0.048448 | 1.7425 | 1.776 | 16.9089 | -149.7966 | 148.0154 | 16.9081 | -149.7848 | 147.9774
Line5_6_7 | 0.032243 | 0.032243 | 0.032243 | 0.032243 | 0.032243 | 0.032243 | 0.0074462 | 0.0074462 | 0.0074462 | 0.0074463 | 0.0074463 | 0.0074463 | -0.0001612 | 0.0029703 | 0.012802 | 0.00016639 | -0.002965 | -0.012797 | -0.00032273 | 0.012631 | 0.0033175 | 0.00033314 | -0.01262 | -0.0033073 | 133.4489 | 133.4489 | 133.4489 | -46.5516 | -46.5516 | -46.5516 |  | 0.048448 | 1.7425 | 1.776 | 0.050009 | 1.741 | 1.775 | 16.9081 | -149.7848 | 147.9774 | 16.9073 | -149.7729 | 147.9395
Line6_7_8 | 1.0761e-06 | 1.0751e-06 | 1.0751e-06 | 0 | 0 | 0 | 2.4851e-07 | 2.4829e-07 | 2.4829e-07 | 0 | 0 | 0 | -4.4543e-09 | 2.434e-07 | -2.0704e-07 | 3.1446e-09 | -1.6756e-07 | 1.3251e-07 | 1.1602e-08 | -3.5724e-07 | -3.8906e-07 | -7.6787e-09 | 2.3483e-07 | 2.6257e-07 | -94.0955 | -94.0409 | -94.0409 | 0 | 0 | 0 |  | 0.050009 | 1.741 | 1.775 | 0.050009 | 1.741 | 1.775 | 16.9073 | -149.7729 | 147.9395 | 16.9074 | -149.7729 | 147.9395
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.4848e-09 | 8.1133e-08 | -6.9012e-08 | 1.7504e-10 | -5.2958e-09 | -5.5149e-09 | 3.8673e-09 | -1.1908e-07 | -1.2969e-07 | 5.5994e-11 | -3.3284e-09 | 3.2019e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.050009 | 1.741 | 1.775 | 0.050009 | 1.741 | 1.775 | 16.9074 | -149.7729 | 147.9395 | 16.9074 | -149.7729 | 147.9395
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.4848e-09 | 8.1133e-08 | -6.9012e-08 | 1.7504e-10 | -5.2958e-09 | -5.5149e-09 | 3.8673e-09 | -1.1908e-07 | -1.2969e-07 | 5.5994e-11 | -3.3284e-09 | 3.2019e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.050009 | 1.741 | 1.775 | 0.050009 | 1.741 | 1.775 | 16.9074 | -149.7729 | 147.9395 | 16.9074 | -149.7729 | 147.9395
Line9_3_11 | 0.032146 | 0.032146 | 0.032146 | 0.032146 | 0.032146 | 0.032146 | 0.0074239 | 0.0074239 | 0.0074239 | 0.0074239 | 0.0074239 | 0.0074239 | -0.00015522 | 0.0029544 | 0.012765 | 0.00016039 | -0.0029492 | -0.01276 | -0.00031151 | 0.012606 | 0.0033303 | 0.00032185 | -0.012596 | -0.0033201 | 133.3937 | 133.3937 | 133.3937 | -46.6068 | -46.6068 | -46.6068 |  | 0.046882 | 1.744 | 1.777 | 0.048438 | 1.7425 | 1.776 | 16.9071 | -149.7966 | 148.0155 | 16.9045 | -149.7847 | 147.9777

## LG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.033755 | 0.033755 | 0.033755 | 0.033755 | 0.033755 | 0.033755 | 0.0077953 | 0.0077953 | 0.0077953 | 0.0077954 | 0.0077954 | 0.0077954 | -0.00016528 | 0.0032605 | 0.014048 | 0.00017098 | -0.0032547 | -0.014043 | -0.00033092 | 0.013866 | 0.003658 | 0.00034232 | -0.013855 | -0.0036467 | 133.4183 | 133.4183 | 133.4183 | -46.5821 | -46.5821 | -46.5821 |  | 0.047452 | 1.8273 | 1.8622 | 0.049086 | 1.8257 | 1.8612 | 16.8783 | -149.8139 | 148.0132 | 16.8774 | -149.8021 | 147.9754
Line10_11_12 | 0.033654 | 0.033654 | 0.033654 | 0.033654 | 0.033654 | 0.033654 | 0.0077721 | 0.0077721 | 0.0077721 | 0.0077722 | 0.0077722 | 0.0077722 | -0.00017579 | 0.0032258 | 0.013992 | 0.00018145 | -0.0032201 | -0.013986 | -0.00035275 | 0.013805 | 0.0036383 | 0.00036408 | -0.013794 | -0.0036271 | 133.3617 | 133.3617 | 133.3617 | -46.6387 | -46.6387 | -46.6387 |  | 0.05071 | 1.8241 | 1.8601 | 0.052339 | 1.8225 | 1.859 | 16.8731 | -149.7902 | 147.9377 | 16.8707 | -149.7783 | 147.8999
Line11_12_13 | 0.033654 | 0.033654 | 0.033654 | 0.033655 | 0.033655 | 0.033655 | 0.0077722 | 0.0077722 | 0.0077722 | 0.0077722 | 0.0077722 | 0.0077722 | -0.00018145 | 0.0032201 | 0.013986 | 0.00018711 | -0.0032143 | -0.01398 | -0.00036408 | 0.013794 | 0.0036271 | 0.00037541 | -0.013783 | -0.0036159 | 133.3613 | 133.3613 | 133.3613 | -46.6392 | -46.6392 | -46.6392 |  | 0.052339 | 1.8225 | 1.859 | 0.053969 | 1.821 | 1.858 | 16.8707 | -149.7783 | 147.8999 | 16.8684 | -149.7664 | 147.8621
Line12_13_15 | 1.1249e-06 | 1.1239e-06 | 1.1239e-06 | 0 | 0 | 0 | 2.5979e-07 | 2.5955e-07 | 2.5955e-07 | 0 | 0 | 0 | -5.0302e-09 | 2.6656e-07 | -2.2668e-07 | 3.5511e-09 | -1.8349e-07 | 1.4509e-07 | 1.3087e-08 | -3.9028e-07 | -4.2563e-07 | -8.6615e-09 | 2.5654e-07 | 2.8726e-07 | -94.1567 | -94.0995 | -94.0995 | 0 | 0 | 0 |  | 0.053969 | 1.821 | 1.858 | 0.053969 | 1.821 | 1.858 | 16.8684 | -149.7664 | 147.8621 | 16.8685 | -149.7664 | 147.8621
Line13_13_14 | 0.033655 | 0.033655 | 0.033655 | 0.033656 | 0.033656 | 0.033656 | 0.0077724 | 0.0077724 | 0.0077724 | 0.0077724 | 0.0077724 | 0.0077724 | -0.00018711 | 0.003214 | 0.013981 | 0.00019277 | -0.0032083 | -0.013975 | -0.00037542 | 0.013783 | 0.0036163 | 0.00038676 | -0.013772 | -0.0036052 | 133.3594 | 133.3594 | 133.3594 | -46.6411 | -46.6411 | -46.6411 |  | 0.053969 | 1.821 | 1.858 | 0.055598 | 1.8194 | 1.8569 | 16.8684 | -149.7664 | 147.8621 | 16.8662 | -149.7545 | 147.8242
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.3535e-09 | 1.7771e-07 | -1.5112e-07 | 1.8744e-09 | -9.4636e-08 | 6.9527e-08 | 8.7246e-09 | -2.6019e-07 | -2.8375e-07 | -4.2992e-09 | 1.2645e-07 | 1.4538e-07 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.053969 | 1.821 | 1.858 | 0.053969 | 1.821 | 1.858 | 16.8685 | -149.7664 | 147.8621 | 16.8685 | -149.7664 | 147.8621
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.6767e-09 | 8.8854e-08 | -7.5559e-08 | 1.9763e-10 | -5.7827e-09 | -6.0323e-09 | 4.3623e-09 | -1.3009e-07 | -1.4188e-07 | 6.3164e-11 | -3.6463e-09 | 3.5022e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.053969 | 1.821 | 1.858 | 0.053969 | 1.821 | 1.858 | 16.8685 | -149.7664 | 147.8621 | 16.8685 | -149.7664 | 147.8621
Line16_4_18 | 0.30425 | 0 | 0 | 0.30425 | 0 | 0 | 0.070264 | 0 | 0 | 0.070264 | 0 | 0 | 0.0007714 | 8.9252e-08 | -7.702e-08 | -7.0229e-15 | -5.7331e-09 | -5.9928e-09 | 0.0015428 | -1.3191e-07 | -1.431e-07 | 9.059e-15 | -3.6327e-09 | 3.4827e-09 | -46.5529 | 0 | 0 | 133.4472 | 0 | 0 |  | 0.024549 | 1.8209 | 1.8579 | 0 | 1.8161 | 1.8547 | 16.8821 | -149.7665 | 147.8609 | 0 | -149.7308 | 147.7464
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.4761e-09 | 8.9328e-08 | -7.6094e-08 | 1.7489e-10 | -5.8484e-09 | -6.0848e-09 | 3.8612e-09 | -1.3158e-07 | -1.4311e-07 | 5.5568e-11 | -3.6643e-09 | 3.5278e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.047452 | 1.8273 | 1.8622 | 0.047452 | 1.8273 | 1.8622 | 16.8783 | -149.8139 | 148.0132 | 16.8783 | -149.8139 | 148.0132
Line1_1_3 | 0.033654 | 0.033654 | 0.033654 | 0.033654 | 0.033654 | 0.033654 | 0.007772 | 0.007772 | 0.007772 | 0.007772 | 0.007772 | 0.007772 | -0.00016446 | 0.0032373 | 0.014003 | 0.00017013 | -0.0032316 | -0.013997 | -0.00033009 | 0.013828 | 0.0036607 | 0.00034142 | -0.013817 | -0.0036495 | 133.3627 | 133.3627 | 133.3627 | -46.6378 | -46.6378 | -46.6378 |  | 0.047452 | 1.8273 | 1.8622 | 0.049081 | 1.8257 | 1.8612 | 16.8783 | -149.8139 | 148.0132 | 16.8756 | -149.8021 | 147.9755
Line2_1_4 | 0.27024 | 0.034009 | 0.034009 | 0.27024 | 0.034009 | 0.034009 | 0.06241 | 0.007854 | 0.007854 | 0.062409 | 0.0078541 | 0.0078541 | 0.0013239 | 0.0033192 | 0.014163 | -0.00068484 | -0.003296 | -0.01414 | 0.002649 | 0.013962 | 0.0036509 | -0.0013705 | -0.013917 | -0.003605 | -46.5668 | 133.5585 | 133.5585 | 133.4332 | -46.442 | -46.442 |  | 0.047452 | 1.8273 | 1.8622 | 0.024549 | 1.8209 | 1.8579 | 16.8783 | -149.8139 | 148.0132 | 16.8821 | -149.7665 | 147.8609
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.9522e-09 | 1.7866e-07 | -1.5219e-07 | 1.651e-09 | -9.5177e-08 | 7.0009e-08 | 7.7224e-09 | -2.6316e-07 | -2.8621e-07 | -3.8056e-09 | 1.2792e-07 | 1.4663e-07 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.047452 | 1.8273 | 1.8622 | 0.047452 | 1.8273 | 1.8622 | 16.8783 | -149.8139 | 148.0132 | 16.8783 | -149.8139 | 148.0132
Line4_2_6 | 0.033755 | 0.033755 | 0.033755 | 0.033755 | 0.033755 | 0.033755 | 0.0077954 | 0.0077954 | 0.0077954 | 0.0077954 | 0.0077954 | 0.0077954 | -0.00017098 | 0.0032547 | 0.014043 | 0.00017667 | -0.0032489 | -0.014037 | -0.00034232 | 0.013855 | 0.0036467 | 0.00035372 | -0.013844 | -0.0036355 | 133.4179 | 133.4179 | 133.4179 | -46.5826 | -46.5826 | -46.5826 |  | 0.049086 | 1.8257 | 1.8612 | 0.05072 | 1.8241 | 1.8601 | 16.8774 | -149.8021 | 147.9754 | 16.8766 | -149.7902 | 147.9375
Line5_6_7 | 0.033755 | 0.033755 | 0.033755 | 0.033756 | 0.033756 | 0.033756 | 0.0077954 | 0.0077954 | 0.0077954 | 0.0077955 | 0.0077955 | 0.0077955 | -0.00017667 | 0.0032489 | 0.014037 | 0.00018237 | -0.0032432 | -0.014032 | -0.00035372 | 0.013844 | 0.0036355 | 0.00036512 | -0.013832 | -0.0036242 | 133.4174 | 133.4174 | 133.4174 | -46.583 | -46.583 | -46.583 |  | 0.05072 | 1.8241 | 1.8601 | 0.052354 | 1.8225 | 1.859 | 16.8766 | -149.7902 | 147.9375 | 16.8759 | -149.7784 | 147.8995
Line6_7_8 | 1.1266e-06 | 1.1255e-06 | 1.1255e-06 | 0 | 0 | 0 | 2.6017e-07 | 2.5993e-07 | 2.5993e-07 | 0 | 0 | 0 | -4.8824e-09 | 2.6691e-07 | -2.2708e-07 | 3.447e-09 | -1.8374e-07 | 1.4534e-07 | 1.2716e-08 | -3.9138e-07 | -4.2655e-07 | -8.4161e-09 | 2.5727e-07 | 2.8787e-07 | -94.1287 | -94.0715 | -94.0715 | 0 | 0 | 0 |  | 0.052354 | 1.8225 | 1.859 | 0.052354 | 1.8225 | 1.859 | 16.8759 | -149.7784 | 147.8995 | 16.8759 | -149.7784 | 147.8995
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.6275e-09 | 8.8971e-08 | -7.5692e-08 | 1.9202e-10 | -5.7989e-09 | -6.0453e-09 | 4.2387e-09 | -1.3046e-07 | -1.4218e-07 | 6.13e-11 | -3.6508e-09 | 3.5085e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.052354 | 1.8225 | 1.859 | 0.052354 | 1.8225 | 1.859 | 16.8759 | -149.7784 | 147.8995 | 16.8759 | -149.7784 | 147.8995
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.6275e-09 | 8.8971e-08 | -7.5692e-08 | 1.9202e-10 | -5.799e-09 | -6.0453e-09 | 4.2387e-09 | -1.3046e-07 | -1.4218e-07 | 6.13e-11 | -3.6508e-09 | 3.5085e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.052354 | 1.8225 | 1.859 | 0.052354 | 1.8225 | 1.859 | 16.8759 | -149.7784 | 147.8995 | 16.8759 | -149.7784 | 147.8995
Line9_3_11 | 0.033654 | 0.033654 | 0.033654 | 0.033654 | 0.033654 | 0.033654 | 0.007772 | 0.007772 | 0.007772 | 0.0077721 | 0.0077721 | 0.0077721 | -0.00017013 | 0.0032316 | 0.013997 | 0.00017579 | -0.0032258 | -0.013992 | -0.00034142 | 0.013817 | 0.0036495 | 0.00035275 | -0.013805 | -0.0036383 | 133.3622 | 133.3622 | 133.3622 | -46.6383 | -46.6383 | -46.6383 |  | 0.049081 | 1.8257 | 1.8612 | 0.05071 | 1.8241 | 1.8601 | 16.8756 | -149.8021 | 147.9755 | 16.8731 | -149.7902 | 147.9377

## LG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.0034031 | 0.0034031 | 0.0034031 | 0.0034032 | 0.0034032 | 0.0034032 | 0.00078592 | 0.00078592 | 0.00078592 | 0.00078593 | 0.00078593 | 0.00078593 | -0.00052337 | -0.0001582 | 0.00085582 | 0.00052342 | 0.00015826 | -0.00085577 | -0.00052557 | 0.00085384 | -0.0001535 | 0.0005257 | -0.00085373 | 0.00015361 | 134.8106 | 134.8106 | 134.8106 | -45.1898 | -45.1899 | -45.1899 |  | 0.94375 | 1.1049 | 1.1063 | 0.94391 | 1.1048 | 1.1063 | -0.068728 | -124.6928 | 124.6422 | -0.065585 | -124.6876 | 124.634
Line10_11_12 | 0.003393 | 0.003393 | 0.003393 | 0.003393 | 0.003393 | 0.003393 | 0.00078358 | 0.00078358 | 0.00078358 | 0.00078359 | 0.00078359 | 0.00078359 | -0.0005214 | -0.00015868 | 0.00085331 | 0.00052146 | 0.00015875 | -0.00085326 | -0.00052475 | 0.00085091 | -0.00015243 | 0.00052488 | -0.0008508 | 0.00015254 | 134.754 | 134.754 | 134.754 | -45.2465 | -45.2465 | -45.2465 |  | 0.94406 | 1.1046 | 1.1062 | 0.94422 | 1.1045 | 1.1062 | -0.062481 | -124.6825 | 124.6259 | -0.059359 | -124.6774 | 124.6177
Line11_12_13 | 0.003393 | 0.003393 | 0.003393 | 0.0033931 | 0.0033931 | 0.0033931 | 0.00078359 | 0.00078359 | 0.00078359 | 0.00078359 | 0.00078359 | 0.00078359 | -0.00052146 | -0.00015875 | 0.00085326 | 0.00052152 | 0.00015881 | -0.00085321 | -0.00052488 | 0.0008508 | -0.00015254 | 0.000525 | -0.00085069 | 0.00015265 | 134.7535 | 134.7535 | 134.7535 | -45.2469 | -45.2469 | -45.2469 |  | 0.94422 | 1.1045 | 1.1062 | 0.94437 | 1.1044 | 1.1061 | -0.059359 | -124.6774 | 124.6177 | -0.056239 | -124.6722 | 124.6095
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.1679e-09 | 2.4518e-08 | -2.302e-08 | 1.1444e-09 | -1.6579e-08 | 1.5105e-08 | 2.4706e-08 | -1.5299e-08 | -1.7547e-08 | -1.6475e-08 | 9.8529e-09 | 1.2041e-08 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.94437 | 1.1044 | 1.1061 | 0.94437 | 1.1044 | 1.1061 | -0.056239 | -124.6722 | 124.6095 | -0.056239 | -124.6722 | 124.6095
Line13_13_14 | 0.0033931 | 0.0033931 | 0.0033931 | 0.0033932 | 0.0033932 | 0.0033932 | 0.00078361 | 0.00078361 | 0.00078361 | 0.00078362 | 0.00078362 | 0.00078362 | -0.00052152 | -0.00015884 | 0.00085323 | 0.00052157 | 0.0001589 | -0.00085318 | -0.00052503 | 0.0008507 | -0.00015263 | 0.00052515 | -0.00085059 | 0.00015274 | 134.7516 | 134.7516 | 134.7516 | -45.2488 | -45.2488 | -45.2488 |  | 0.94437 | 1.1044 | 1.1061 | 0.94453 | 1.1042 | 1.1061 | -0.056239 | -124.6722 | 124.6095 | -0.053119 | -124.6671 | 124.6014
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.7863e-10 | 1.6345e-08 | -1.5346e-08 | 7.5507e-10 | -8.4069e-09 | 7.4318e-09 | 1.6471e-08 | -1.0199e-08 | -1.1698e-08 | -8.2391e-09 | 4.7533e-09 | 6.1914e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.94437 | 1.1044 | 1.1061 | 0.94437 | 1.1044 | 1.1061 | -0.056239 | -124.6722 | 124.6095 | -0.056238 | -124.6722 | 124.6095
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.8931e-10 | 8.1725e-09 | -7.6732e-09 | 3.6575e-10 | -2.3433e-10 | -2.4142e-10 | 8.2355e-09 | -5.0996e-09 | -5.8492e-09 | -3.5689e-12 | -3.4634e-10 | 3.4224e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.94437 | 1.1044 | 1.1061 | 0.94437 | 1.1044 | 1.1061 | -0.056238 | -124.6722 | 124.6095 | -0.056238 | -124.6722 | 124.6095
Line16_4_18 | 0.030674 | 0 | 0 | 0.030674 | 0 | 0 | 0.007084 | 0 | 0 | 0.007084 | 0 | 0 | 0.0047124 | 8.2397e-09 | -7.7835e-09 | -0.0047046 | -2.3254e-10 | -2.4068e-10 | 0.0047203 | -5.1918e-09 | -5.8794e-09 | -0.0047046 | -3.4506e-10 | 3.4036e-10 | -45.1606 | 0 | 0 | 134.8394 | 0 | 0 |  | 0.94156 | 1.1044 | 1.1061 | 0.93921 | 1.104 | 1.106 | -0.11293 | -124.6721 | 124.6093 | -0.16056 | -124.6567 | 124.5847
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.7315e-10 | 8.2134e-09 | -7.7288e-09 | 3.6767e-10 | -2.3669e-10 | -2.4241e-10 | 8.2802e-09 | -5.1519e-09 | -5.8743e-09 | -4.3584e-12 | -3.4802e-10 | 3.4472e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.94375 | 1.1049 | 1.1063 | 0.94375 | 1.1049 | 1.1063 | -0.068728 | -124.6928 | 124.6422 | -0.068728 | -124.6928 | 124.6422
Line1_1_3 | 0.003393 | 0.003393 | 0.003393 | 0.003393 | 0.003393 | 0.003393 | 0.00078357 | 0.00078357 | 0.00078357 | 0.00078358 | 0.00078358 | 0.00078358 | -0.00052129 | -0.00015855 | 0.00085341 | 0.00052135 | 0.00015862 | -0.00085336 | -0.00052451 | 0.00085113 | -0.00015221 | 0.00052463 | -0.00085102 | 0.00015232 | 134.7549 | 134.7549 | 134.7549 | -45.2455 | -45.2455 | -45.2455 |  | 0.94375 | 1.1049 | 1.1063 | 0.9439 | 1.1048 | 1.1063 | -0.068728 | -124.6928 | 124.6422 | -0.065604 | -124.6876 | 124.634
Line2_1_4 | 0.027246 | 0.0034288 | 0.0034288 | 0.027246 | 0.0034288 | 0.0034288 | 0.0062921 | 0.00079184 | 0.00079184 | 0.0062921 | 0.00079185 | 0.00079185 | 0.0041912 | -0.00015728 | 0.00086188 | -0.0041847 | 0.00015753 | -0.00086166 | 0.0042067 | 0.00086065 | -0.00015676 | -0.0041937 | -0.00086019 | 0.00015723 | -45.1746 | 134.9507 | 134.9507 | 134.8255 | -45.0497 | -45.0497 |  | 0.94375 | 1.1049 | 1.1063 | 0.94156 | 1.1044 | 1.1061 | -0.068728 | -124.6928 | 124.6422 | -0.11293 | -124.6721 | 124.6093
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.463e-10 | 1.6427e-08 | -1.5458e-08 | 7.4082e-10 | -8.4501e-09 | 7.4864e-09 | 1.656e-08 | -1.0304e-08 | -1.1749e-08 | -8.2845e-09 | 4.8039e-09 | 6.219e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.94375 | 1.1049 | 1.1063 | 0.94375 | 1.1049 | 1.1063 | -0.068728 | -124.6928 | 124.6422 | -0.068728 | -124.6928 | 124.6422
Line4_2_6 | 0.0034032 | 0.0034032 | 0.0034032 | 0.0034032 | 0.0034032 | 0.0034032 | 0.00078593 | 0.00078593 | 0.00078593 | 0.00078594 | 0.00078594 | 0.00078594 | -0.00052342 | -0.00015826 | 0.00085577 | 0.00052348 | 0.00015833 | -0.00085572 | -0.0005257 | 0.00085373 | -0.00015361 | 0.00052582 | -0.00085362 | 0.00015372 | 134.8101 | 134.8101 | 134.8101 | -45.1903 | -45.1903 | -45.1903 |  | 0.94391 | 1.1048 | 1.1063 | 0.94406 | 1.1046 | 1.1062 | -0.065585 | -124.6876 | 124.634 | -0.062444 | -124.6825 | 124.6258
Line5_6_7 | 0.0034032 | 0.0034032 | 0.0034032 | 0.0034032 | 0.0034032 | 0.0034032 | 0.00078594 | 0.00078594 | 0.00078594 | 0.00078594 | 0.00078594 | 0.00078594 | -0.00052348 | -0.00015833 | 0.00085572 | 0.00052354 | 0.0001584 | -0.00085567 | -0.00052582 | 0.00085362 | -0.00015372 | 0.00052595 | -0.00085351 | 0.00015383 | 134.8097 | 134.8097 | 134.8097 | -45.1908 | -45.1908 | -45.1908 |  | 0.94406 | 1.1046 | 1.1062 | 0.94422 | 1.1045 | 1.1062 | -0.062444 | -124.6825 | 124.6258 | -0.059304 | -124.6773 | 124.6176
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.1561e-09 | 2.4548e-08 | -2.3061e-08 | 1.1369e-09 | -1.66e-08 | 1.5132e-08 | 2.474e-08 | -1.5338e-08 | -1.7566e-08 | -1.6497e-08 | 9.8783e-09 | 1.2054e-08 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.94422 | 1.1045 | 1.1062 | 0.94422 | 1.1045 | 1.1062 | -0.059304 | -124.6773 | 124.6176 | -0.059303 | -124.6773 | 124.6176
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.8535e-10 | 8.1827e-09 | -7.687e-09 | 3.6623e-10 | -2.3491e-10 | -2.4167e-10 | 8.2466e-09 | -5.1126e-09 | -5.8554e-09 | -3.7627e-12 | -3.4675e-10 | 3.4285e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.94422 | 1.1045 | 1.1062 | 0.94422 | 1.1045 | 1.1062 | -0.059303 | -124.6773 | 124.6176 | -0.059303 | -124.6773 | 124.6176
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.8535e-10 | 8.1827e-09 | -7.687e-09 | 3.6623e-10 | -2.3491e-10 | -2.4167e-10 | 8.2466e-09 | -5.1126e-09 | -5.8554e-09 | -3.7628e-12 | -3.4675e-10 | 3.4285e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.94422 | 1.1045 | 1.1062 | 0.94422 | 1.1045 | 1.1062 | -0.059303 | -124.6773 | 124.6176 | -0.059303 | -124.6773 | 124.6176
Line9_3_11 | 0.003393 | 0.003393 | 0.003393 | 0.003393 | 0.003393 | 0.003393 | 0.00078358 | 0.00078358 | 0.00078358 | 0.00078358 | 0.00078358 | 0.00078358 | -0.00052135 | -0.00015862 | 0.00085336 | 0.0005214 | 0.00015868 | -0.00085331 | -0.00052463 | 0.00085102 | -0.00015232 | 0.00052475 | -0.00085091 | 0.00015243 | 134.7545 | 134.7545 | 134.7545 | -45.246 | -45.246 | -45.246 |  | 0.9439 | 1.1048 | 1.1063 | 0.94406 | 1.1046 | 1.1062 | -0.065604 | -124.6876 | 124.634 | -0.062481 | -124.6825 | 124.6259

## LG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.0035649 | 0.0035649 | 0.0035649 | 0.003565 | 0.003565 | 0.003565 | 0.00082329 | 0.00082329 | 0.00082329 | 0.0008233 | 0.0008233 | 0.0008233 | -0.00057432 | -0.00017367 | 0.00093921 | 0.00057438 | 0.00017374 | -0.00093915 | -0.00057674 | 0.00093696 | -0.00016845 | 0.00057688 | -0.00093684 | 0.00016857 | 134.8072 | 134.8072 | 134.8072 | -45.1933 | -45.1933 | -45.1933 |  | 0.98862 | 1.1575 | 1.159 | 0.98878 | 1.1573 | 1.159 | -0.07215 | -124.692 | 124.6392 | -0.069007 | -124.6868 | 124.631
Line10_11_12 | 0.0035543 | 0.0035543 | 0.0035543 | 0.0035544 | 0.0035544 | 0.0035544 | 0.00082084 | 0.00082084 | 0.00082084 | 0.00082084 | 0.00082084 | 0.00082084 | -0.00057216 | -0.0001742 | 0.00093645 | 0.00057222 | 0.00017427 | -0.00093639 | -0.00057584 | 0.00093375 | -0.00016727 | 0.00057597 | -0.00093363 | 0.00016739 | 134.7506 | 134.7506 | 134.7506 | -45.2499 | -45.2499 | -45.2499 |  | 0.98895 | 1.1572 | 1.1589 | 0.98911 | 1.157 | 1.1589 | -0.065903 | -124.6817 | 124.6229 | -0.062781 | -124.6766 | 124.6147
Line11_12_13 | 0.0035544 | 0.0035544 | 0.0035544 | 0.0035544 | 0.0035544 | 0.0035544 | 0.00082084 | 0.00082084 | 0.00082084 | 0.00082085 | 0.00082085 | 0.00082085 | -0.00057222 | -0.00017427 | 0.00093639 | 0.00057229 | 0.00017435 | -0.00093634 | -0.00057597 | 0.00093363 | -0.00016739 | 0.00057611 | -0.00093351 | 0.00016751 | 134.7501 | 134.7501 | 134.7501 | -45.2504 | -45.2504 | -45.2504 |  | 0.98911 | 1.157 | 1.1589 | 0.98927 | 1.1569 | 1.1588 | -0.062781 | -124.6766 | 124.6147 | -0.059661 | -124.6714 | 124.6065
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.2825e-09 | 2.6905e-08 | -2.5262e-08 | 1.2566e-09 | -1.8194e-08 | 1.6577e-08 | 2.7112e-08 | -1.6787e-08 | -1.9257e-08 | -1.8079e-08 | 1.0811e-08 | 1.3213e-08 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.98927 | 1.1569 | 1.1588 | 0.98927 | 1.1569 | 1.1588 | -0.059661 | -124.6714 | 124.6065 | -0.059661 | -124.6714 | 124.6065
Line13_13_14 | 0.0035545 | 0.0035545 | 0.0035545 | 0.0035545 | 0.0035545 | 0.0035545 | 0.00082087 | 0.00082087 | 0.00082087 | 0.00082087 | 0.00082087 | 0.00082087 | -0.00057229 | -0.00017437 | 0.00093636 | 0.00057235 | 0.00017445 | -0.00093631 | -0.00057614 | 0.00093352 | -0.00016749 | 0.00057627 | -0.0009334 | 0.00016762 | 134.7482 | 134.7482 | 134.7482 | -45.2522 | -45.2522 | -45.2522 |  | 0.98927 | 1.1569 | 1.1588 | 0.98944 | 1.1568 | 1.1588 | -0.059661 | -124.6714 | 124.6065 | -0.056541 | -124.6663 | 124.5984
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.55e-10 | 1.7937e-08 | -1.6842e-08 | 8.2914e-10 | -9.2254e-09 | 8.1558e-09 | 1.8075e-08 | -1.1191e-08 | -1.2838e-08 | -9.0416e-09 | 5.2156e-09 | 6.7943e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.98927 | 1.1569 | 1.1588 | 0.98927 | 1.1569 | 1.1588 | -0.059661 | -124.6714 | 124.6065 | -0.059661 | -124.6714 | 124.6065
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.275e-10 | 8.9685e-09 | -8.4208e-09 | 4.0164e-10 | -2.5691e-10 | -2.6497e-10 | 9.0375e-09 | -5.5956e-09 | -6.4189e-09 | -4.1549e-12 | -3.8002e-10 | 3.7537e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.98927 | 1.1569 | 1.1588 | 0.98927 | 1.1569 | 1.1588 | -0.059661 | -124.6714 | 124.6065 | -0.059661 | -124.6714 | 124.6065
Line16_4_18 | 0.032133 | 0 | 0 | 0.032133 | 0 | 0 | 0.0074208 | 0 | 0 | 0.0074208 | 0 | 0 | 0.0051712 | 9.0423e-09 | -8.5418e-09 | -0.0051626 | -2.5494e-10 | -2.6415e-10 | 0.0051798 | -5.6968e-09 | -6.4521e-09 | -0.0051626 | -3.7862e-10 | 3.733e-10 | -45.164 | 0 | 0 | 134.836 | 0 | 0 |  | 0.98632 | 1.1569 | 1.1588 | 0.98386 | 1.1565 | 1.1587 | -0.11635 | -124.6713 | 124.6063 | -0.16398 | -124.6559 | 124.5817
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.0976e-10 | 9.0134e-09 | -8.4818e-09 | 4.0375e-10 | -2.595e-10 | -2.6605e-10 | 9.0865e-09 | -5.6529e-09 | -6.4465e-09 | -5.0213e-12 | -3.8187e-10 | 3.7809e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.98862 | 1.1575 | 1.159 | 0.98862 | 1.1575 | 1.159 | -0.07215 | -124.692 | 124.6392 | -0.07215 | -124.692 | 124.6392
Line1_1_3 | 0.0035543 | 0.0035543 | 0.0035543 | 0.0035543 | 0.0035543 | 0.0035543 | 0.00082082 | 0.00082082 | 0.00082082 | 0.00082083 | 0.00082083 | 0.00082083 | -0.00057204 | -0.00017406 | 0.00093656 | 0.0005721 | 0.00017413 | -0.0009365 | -0.00057557 | 0.00093399 | -0.00016703 | 0.0005757 | -0.00093387 | 0.00016715 | 134.7515 | 134.7515 | 134.7515 | -45.2489 | -45.2489 | -45.2489 |  | 0.98862 | 1.1575 | 1.159 | 0.98878 | 1.1573 | 1.159 | -0.07215 | -124.692 | 124.6392 | -0.069026 | -124.6868 | 124.631
Line2_1_4 | 0.028541 | 0.0035918 | 0.0035918 | 0.028541 | 0.0035918 | 0.0035918 | 0.0065913 | 0.00082949 | 0.00082949 | 0.0065913 | 0.00082949 | 0.00082949 | 0.0045992 | -0.00017267 | 0.00094586 | -0.004592 | 0.00017293 | -0.00094561 | 0.0046162 | 0.00094444 | -0.00017203 | -0.0046019 | -0.00094394 | 0.00017254 | -45.178 | 134.9473 | 134.9473 | 134.8221 | -45.0531 | -45.0531 |  | 0.98862 | 1.1575 | 1.159 | 0.98632 | 1.1569 | 1.1588 | -0.07215 | -124.692 | 124.6392 | -0.11635 | -124.6713 | 124.6063
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.1951e-10 | 1.8027e-08 | -1.6964e-08 | 8.135e-10 | -9.2728e-09 | 8.2157e-09 | 1.8173e-08 | -1.1306e-08 | -1.2893e-08 | -9.0915e-09 | 5.2711e-09 | 6.8246e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.98862 | 1.1575 | 1.159 | 0.98862 | 1.1575 | 1.159 | -0.07215 | -124.692 | 124.6392 | -0.07215 | -124.692 | 124.6392
Line4_2_6 | 0.003565 | 0.003565 | 0.003565 | 0.003565 | 0.003565 | 0.003565 | 0.0008233 | 0.0008233 | 0.0008233 | 0.0008233 | 0.0008233 | 0.0008233 | -0.00057438 | -0.00017374 | 0.00093915 | 0.00057444 | 0.00017382 | -0.0009391 | -0.00057688 | 0.00093684 | -0.00016857 | 0.00057701 | -0.00093672 | 0.00016869 | 134.8067 | 134.8067 | 134.8067 | -45.1937 | -45.1937 | -45.1937 |  | 0.98878 | 1.1573 | 1.159 | 0.98895 | 1.1572 | 1.1589 | -0.069007 | -124.6868 | 124.631 | -0.065866 | -124.6817 | 124.6228
Line5_6_7 | 0.003565 | 0.003565 | 0.003565 | 0.003565 | 0.003565 | 0.003565 | 0.0008233 | 0.0008233 | 0.0008233 | 0.00082331 | 0.00082331 | 0.00082331 | -0.00057444 | -0.00017382 | 0.0009391 | 0.0005745 | 0.00017389 | -0.00093904 | -0.00057701 | 0.00093672 | -0.00016869 | 0.00057715 | -0.0009366 | 0.00016881 | 134.8062 | 134.8062 | 134.8062 | -45.1942 | -45.1942 | -45.1942 |  | 0.98895 | 1.1572 | 1.1589 | 0.98911 | 1.157 | 1.1589 | -0.065866 | -124.6817 | 124.6228 | -0.062726 | -124.6765 | 124.6146
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.2694e-09 | 2.6939e-08 | -2.5308e-08 | 1.2485e-09 | -1.8217e-08 | 1.6607e-08 | 2.7149e-08 | -1.6829e-08 | -1.9277e-08 | -1.8104e-08 | 1.0839e-08 | 1.3228e-08 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.98911 | 1.157 | 1.1589 | 0.98911 | 1.157 | 1.1589 | -0.062726 | -124.6765 | 124.6146 | -0.062725 | -124.6765 | 124.6146
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.2315e-10 | 8.9796e-09 | -8.4359e-09 | 4.0216e-10 | -2.5755e-10 | -2.6524e-10 | 9.0496e-09 | -5.6098e-09 | -6.4258e-09 | -4.3676e-12 | -3.8048e-10 | 3.7604e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.98911 | 1.157 | 1.1589 | 0.98911 | 1.157 | 1.1589 | -0.062725 | -124.6765 | 124.6146 | -0.062725 | -124.6765 | 124.6146
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.2315e-10 | 8.9796e-09 | -8.4359e-09 | 4.0216e-10 | -2.5755e-10 | -2.6524e-10 | 9.0496e-09 | -5.6098e-09 | -6.4258e-09 | -4.3675e-12 | -3.8048e-10 | 3.7604e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.98911 | 1.157 | 1.1589 | 0.98911 | 1.157 | 1.1589 | -0.062725 | -124.6765 | 124.6146 | -0.062725 | -124.6765 | 124.6146
Line9_3_11 | 0.0035543 | 0.0035543 | 0.0035543 | 0.0035543 | 0.0035543 | 0.0035543 | 0.00082083 | 0.00082083 | 0.00082083 | 0.00082084 | 0.00082084 | 0.00082084 | -0.0005721 | -0.00017413 | 0.0009365 | 0.00057216 | 0.0001742 | -0.00093645 | -0.0005757 | 0.00093387 | -0.00016715 | 0.00057584 | -0.00093375 | 0.00016727 | 134.751 | 134.751 | 134.751 | -45.2494 | -45.2494 | -45.2494 |  | 0.98878 | 1.1573 | 1.159 | 0.98895 | 1.1572 | 1.1589 | -0.069026 | -124.6868 | 124.631 | -0.065903 | -124.6817 | 124.6229

## LG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.028764 | 0.028764 | 0.028764 | 0.028764 | 0.028764 | 0.028764 | 0.0066428 | 0.0066428 | 0.0066428 | 0.0066428 | 0.0066428 | 0.0066428 | -0.00023072 | 0.0024408 | 0.010273 | 0.00023866 | -0.0024328 | -0.010265 | -0.00024035 | 0.010175 | 0.0025505 | 0.00024863 | -0.010167 | -0.0025424 | 134.2288 | 134.2288 | 134.2288 | -45.7717 | -45.7717 | -45.7717 |  | 0.050155 | 1.5752 | 1.5935 | 0.051882 | 1.5737 | 1.592 | 0.39999 | -149.2611 | 148.172 | 0.39992 | -149.2293 | 148.1389
Line10_11_12 | 0.028652 | 0.028652 | 0.028652 | 0.028653 | 0.028653 | 0.028653 | 0.006617 | 0.006617 | 0.006617 | 0.006617 | 0.006617 | 0.006617 | -0.00024557 | 0.0024148 | 0.010217 | 0.00025345 | -0.0024068 | -0.010209 | -0.00025586 | 0.010119 | 0.002525 | 0.00026407 | -0.010111 | -0.0025169 | 134.2243 | 134.2243 | 134.2243 | -45.7762 | -45.7762 | -45.7762 |  | 0.053595 | 1.5722 | 1.5905 | 0.055315 | 1.5707 | 1.5891 | 0.3996 | -149.1977 | 148.1059 | 0.3994 | -149.166 | 148.0728
Line11_12_13 | 0.028653 | 0.028653 | 0.028653 | 0.028653 | 0.028653 | 0.028653 | 0.006617 | 0.006617 | 0.006617 | 0.0066171 | 0.0066171 | 0.0066171 | -0.00025345 | 0.0024068 | 0.010209 | 0.00026133 | -0.0023989 | -0.010202 | -0.00026407 | 0.010111 | 0.0025169 | 0.00027228 | -0.010103 | -0.0025088 | 134.2238 | 134.2238 | 134.2238 | -45.7767 | -45.7767 | -45.7767 |  | 0.055315 | 1.5707 | 1.5891 | 0.057035 | 1.5692 | 1.5876 | 0.3994 | -149.166 | 148.0728 | 0.3992 | -149.1342 | 148.0396
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.1871e-10 | 1.9464e-07 | -1.6854e-07 | 7.3255e-10 | -1.3401e-07 | 1.08e-07 | 1.2594e-08 | -2.8717e-07 | -3.0788e-07 | -8.3945e-09 | 1.8878e-07 | 2.0785e-07 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.057035 | 1.5692 | 1.5876 | 0.057035 | 1.5692 | 1.5876 | 0.3992 | -149.1342 | 148.0396 | 0.39923 | -149.1342 | 148.0396
Line13_13_14 | 0.028653 | 0.028653 | 0.028653 | 0.028654 | 0.028654 | 0.028654 | 0.0066172 | 0.0066172 | 0.0066172 | 0.0066173 | 0.0066173 | 0.0066173 | -0.00026133 | 0.0023987 | 0.010202 | 0.00026921 | -0.0023908 | -0.010194 | -0.0002723 | 0.010103 | 0.0025091 | 0.00028051 | -0.010095 | -0.002501 | 134.2219 | 134.2219 | 134.2219 | -45.7785 | -45.7785 | -45.7785 |  | 0.057035 | 1.5692 | 1.5876 | 0.058755 | 1.5677 | 1.5862 | 0.3992 | -149.1342 | 148.0396 | 0.39895 | -149.1023 | 148.0064
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.4581e-10 | 1.2976e-07 | -1.1236e-07 | 4.5965e-10 | -6.9135e-08 | 5.1817e-08 | 8.3959e-09 | -1.9144e-07 | -2.0525e-07 | -4.1966e-09 | 9.3061e-08 | 1.0522e-07 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.057035 | 1.5692 | 1.5876 | 0.057035 | 1.5692 | 1.5876 | 0.39923 | -149.1342 | 148.0396 | 0.39926 | -149.1342 | 148.0396
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.7291e-10 | 6.488e-08 | -5.6179e-08 | 1.8674e-10 | -4.2545e-09 | -4.361e-09 | 4.198e-09 | -9.5722e-08 | -1.0263e-07 | 1.3844e-12 | -2.6612e-09 | 2.5997e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.057035 | 1.5692 | 1.5876 | 0.057035 | 1.5692 | 1.5876 | 0.39926 | -149.1342 | 148.0396 | 0.39926 | -149.1342 | 148.0396
Line16_4_18 | 0.25939 | 0 | 0 | 0.25939 | 0 | 0 | 0.059903 | 0 | 0 | 0.059903 | 0 | 0 | 0.0010765 | 6.5715e-08 | -5.7124e-08 | -8.6553e-17 | -4.2118e-09 | -4.3186e-09 | 0.0011214 | -9.7198e-08 | -1.0406e-07 | -1.8185e-15 | -2.6455e-09 | 2.5838e-09 | -45.769 | 0 | 0 | 134.2311 | 0 | 0 |  | 0.025949 | 1.5692 | 1.5876 | 0 | 1.5647 | 1.5832 | 0.40022 | -149.1332 | 148.0385 | 0 | -149.0368 | 147.938
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.4131e-10 | 6.5405e-08 | -5.6602e-08 | 1.6548e-10 | -4.3107e-09 | -4.417e-09 | 3.7205e-09 | -9.6992e-08 | -1.0393e-07 | 1.2198e-12 | -2.6819e-09 | 2.6205e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.050155 | 1.5752 | 1.5935 | 0.050155 | 1.5752 | 1.5935 | 0.40002 | -149.2611 | 148.172 | 0.40003 | -149.2611 | 148.172
Line1_1_3 | 0.028652 | 0.028652 | 0.028652 | 0.028652 | 0.028652 | 0.028652 | 0.0066169 | 0.0066169 | 0.0066169 | 0.0066169 | 0.0066169 | 0.0066169 | -0.00022981 | 0.0024307 | 0.010233 | 0.00023769 | -0.0024227 | -0.010225 | -0.00023943 | 0.010135 | 0.0025412 | 0.00024764 | -0.010127 | -0.0025331 | 134.2252 | 134.2252 | 134.2252 | -45.7752 | -45.7752 | -45.7752 |  | 0.050155 | 1.5752 | 1.5935 | 0.051875 | 1.5737 | 1.592 | 0.39999 | -149.2611 | 148.172 | 0.3998 | -149.2294 | 148.139
Line2_1_4 | 0.23034 | 0.029047 | 0.029047 | 0.23034 | 0.029047 | 0.029047 | 0.053195 | 0.006708 | 0.006708 | 0.053195 | 0.0067081 | 0.0067081 | 0.0018476 | 0.0024665 | 0.010374 | -0.00095593 | -0.0024342 | -0.010342 | 0.0019247 | 0.010274 | 0.0025739 | -0.00099579 | -0.010241 | -0.0025404 | -45.7698 | 134.2383 | 134.2383 | 134.2303 | -45.7622 | -45.7622 |  | 0.050155 | 1.5752 | 1.5935 | 0.025949 | 1.5692 | 1.5876 | 0.39999 | -149.2611 | 148.172 | 0.40022 | -149.1332 | 148.0385
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.8261e-10 | 1.3081e-07 | -1.132e-07 | 4.0679e-10 | -6.9716e-08 | 5.2185e-08 | 7.441e-09 | -1.9398e-07 | -2.0786e-07 | -3.7193e-09 | 9.431e-08 | 1.0655e-07 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.050155 | 1.5752 | 1.5935 | 0.050155 | 1.5752 | 1.5935 | 0.39999 | -149.2611 | 148.172 | 0.40002 | -149.2611 | 148.172
Line4_2_6 | 0.028764 | 0.028764 | 0.028764 | 0.028764 | 0.028764 | 0.028764 | 0.0066428 | 0.0066428 | 0.0066428 | 0.0066429 | 0.0066429 | 0.0066429 | -0.00023866 | 0.0024328 | 0.010265 | 0.00024661 | -0.0024248 | -0.010257 | -0.00024863 | 0.010167 | 0.0025424 | 0.00025691 | -0.010158 | -0.0025342 | 134.2283 | 134.2283 | 134.2283 | -45.7721 | -45.7721 | -45.7721 |  | 0.051882 | 1.5737 | 1.592 | 0.053608 | 1.5722 | 1.5905 | 0.39992 | -149.2293 | 148.1389 | 0.39983 | -149.1975 | 148.1057
Line5_6_7 | 0.028764 | 0.028764 | 0.028764 | 0.028765 | 0.028765 | 0.028765 | 0.0066429 | 0.0066429 | 0.0066429 | 0.0066429 | 0.0066429 | 0.0066429 | -0.00024661 | 0.0024248 | 0.010257 | 0.00025455 | -0.0024168 | -0.010249 | -0.00025691 | 0.010158 | 0.0025342 | 0.00026519 | -0.01015 | -0.002526 | 134.2278 | 134.2278 | 134.2278 | -45.7726 | -45.7726 | -45.7726 |  | 0.053608 | 1.5722 | 1.5905 | 0.055335 | 1.5707 | 1.5891 | 0.39983 | -149.1975 | 148.1057 | 0.39973 | -149.1656 | 148.0724
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.9547e-10 | 1.9503e-07 | -1.6885e-07 | 7.1184e-10 | -1.3429e-07 | 1.0819e-07 | 1.2242e-08 | -2.8811e-07 | -3.0884e-07 | -8.1601e-09 | 1.894e-07 | 2.085e-07 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.055335 | 1.5707 | 1.5891 | 0.055335 | 1.5707 | 1.5891 | 0.39973 | -149.1656 | 148.0724 | 0.39977 | -149.1656 | 148.0724
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.6516e-10 | 6.501e-08 | -5.6283e-08 | 1.8152e-10 | -4.2683e-09 | -4.3749e-09 | 4.0807e-09 | -9.6035e-08 | -1.0295e-07 | 1.3449e-12 | -2.6663e-09 | 2.6048e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.055335 | 1.5707 | 1.5891 | 0.055335 | 1.5707 | 1.5891 | 0.39977 | -149.1656 | 148.0724 | 0.39978 | -149.1656 | 148.0724
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.6516e-10 | 6.501e-08 | -5.6283e-08 | 1.8152e-10 | -4.2683e-09 | -4.3749e-09 | 4.0807e-09 | -9.6035e-08 | -1.0295e-07 | 1.3449e-12 | -2.6663e-09 | 2.6048e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.055335 | 1.5707 | 1.5891 | 0.055335 | 1.5707 | 1.5891 | 0.39977 | -149.1656 | 148.0724 | 0.39978 | -149.1656 | 148.0724
Line9_3_11 | 0.028652 | 0.028652 | 0.028652 | 0.028652 | 0.028652 | 0.028652 | 0.0066169 | 0.0066169 | 0.0066169 | 0.006617 | 0.006617 | 0.006617 | -0.00023769 | 0.0024227 | 0.010225 | 0.00024557 | -0.0024148 | -0.010217 | -0.00024764 | 0.010127 | 0.0025331 | 0.00025586 | -0.010119 | -0.002525 | 134.2247 | 134.2247 | 134.2247 | -45.7757 | -45.7757 | -45.7757 |  | 0.051875 | 1.5737 | 1.592 | 0.053595 | 1.5722 | 1.5905 | 0.3998 | -149.2294 | 148.139 | 0.3996 | -149.1977 | 148.1059

## LG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.02725 | 0.02725 | 0.02725 | 0.02725 | 0.02725 | 0.02725 | 0.0062931 | 0.0062931 | 0.0062931 | 0.0062932 | 0.0062932 | 0.0062932 | -0.00020707 | 0.0021907 | 0.0092201 | 0.0002142 | -0.0021835 | -0.0092131 | -0.00021572 | 0.0091319 | 0.0022891 | 0.00022315 | -0.0091245 | -0.0022818 | 134.2288 | 134.2288 | 134.2288 | -45.7717 | -45.7717 | -45.7717 |  | 0.047516 | 1.4923 | 1.5096 | 0.049151 | 1.4908 | 1.5082 | 0.39999 | -149.2611 | 148.172 | 0.39992 | -149.2293 | 148.1389
Line10_11_12 | 0.027144 | 0.027144 | 0.027144 | 0.027145 | 0.027145 | 0.027145 | 0.0062687 | 0.0062687 | 0.0062687 | 0.0062688 | 0.0062688 | 0.0062688 | -0.0002204 | 0.0021673 | 0.00917 | 0.00022747 | -0.0021602 | -0.009163 | -0.00022963 | 0.0090819 | 0.0022662 | 0.000237 | -0.0090746 | -0.002259 | 134.2243 | 134.2243 | 134.2243 | -45.7762 | -45.7762 | -45.7762 |  | 0.050774 | 1.4894 | 1.5068 | 0.052404 | 1.488 | 1.5055 | 0.3996 | -149.1977 | 148.1059 | 0.3994 | -149.166 | 148.0728
Line11_12_13 | 0.027145 | 0.027145 | 0.027145 | 0.027145 | 0.027145 | 0.027145 | 0.0062688 | 0.0062688 | 0.0062688 | 0.0062688 | 0.0062688 | 0.0062688 | -0.00022747 | 0.0021602 | 0.009163 | 0.00023455 | -0.002153 | -0.009156 | -0.000237 | 0.0090746 | 0.002259 | 0.00024438 | -0.0090673 | -0.0022517 | 134.2238 | 134.2238 | 134.2238 | -45.7767 | -45.7767 | -45.7767 |  | 0.052404 | 1.488 | 1.5055 | 0.054033 | 1.4866 | 1.5041 | 0.3994 | -149.166 | 148.0728 | 0.3992 | -149.1342 | 148.0396
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.348e-10 | 1.7469e-07 | -1.5126e-07 | 6.5747e-10 | -1.2028e-07 | 9.6927e-08 | 1.1303e-08 | -2.5773e-07 | -2.7632e-07 | -7.5342e-09 | 1.6943e-07 | 1.8655e-07 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.054033 | 1.4866 | 1.5041 | 0.054033 | 1.4866 | 1.5041 | 0.3992 | -149.1342 | 148.0396 | 0.39923 | -149.1342 | 148.0396
Line13_13_14 | 0.027145 | 0.027145 | 0.027145 | 0.027146 | 0.027146 | 0.027146 | 0.0062689 | 0.0062689 | 0.0062689 | 0.006269 | 0.006269 | 0.006269 | -0.00023455 | 0.0021528 | 0.0091561 | 0.00024162 | -0.0021457 | -0.0091491 | -0.00024439 | 0.0090676 | 0.002252 | 0.00025176 | -0.0090603 | -0.0022447 | 134.2219 | 134.2219 | 134.2219 | -45.7785 | -45.7785 | -45.7785 |  | 0.054033 | 1.4866 | 1.5041 | 0.055662 | 1.4852 | 1.5027 | 0.3992 | -149.1342 | 148.0396 | 0.39895 | -149.1023 | 148.0064
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.8987e-10 | 1.1646e-07 | -1.0084e-07 | 4.1254e-10 | -6.2049e-08 | 4.6507e-08 | 7.5354e-09 | -1.7182e-07 | -1.8421e-07 | -3.7665e-09 | 8.3523e-08 | 9.444e-08 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.054033 | 1.4866 | 1.5041 | 0.054033 | 1.4866 | 1.5041 | 0.39923 | -149.1342 | 148.0396 | 0.39926 | -149.1342 | 148.0396
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.4494e-10 | 5.823e-08 | -5.0421e-08 | 1.676e-10 | -3.8184e-09 | -3.9141e-09 | 3.7677e-09 | -8.5912e-08 | -9.2107e-08 | 1.2425e-12 | -2.3885e-09 | 2.3332e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.054033 | 1.4866 | 1.5041 | 0.054033 | 1.4866 | 1.5041 | 0.39926 | -149.1342 | 148.0396 | 0.39926 | -149.1342 | 148.0396
Line16_4_18 | 0.24573 | 0 | 0 | 0.24573 | 0 | 0 | 0.05675 | 0 | 0 | 0.05675 | 0 | 0 | 0.00096616 | 5.898e-08 | -5.127e-08 | -7.8657e-17 | -3.7801e-09 | -3.876e-09 | 0.0010064 | -8.7236e-08 | -9.3391e-08 | -1.6381e-15 | -2.3743e-09 | 2.319e-09 | -45.769 | 0 | 0 | 134.2311 | 0 | 0 |  | 0.024584 | 1.4866 | 1.504 | 0 | 1.4824 | 1.4999 | 0.40022 | -149.1332 | 148.0385 | 0 | -149.0368 | 147.938
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.1658e-10 | 5.8702e-08 | -5.0801e-08 | 1.4852e-10 | -3.8689e-09 | -3.9643e-09 | 3.3392e-09 | -8.7051e-08 | -9.3277e-08 | 1.0948e-12 | -2.407e-09 | 2.3519e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.047515 | 1.4923 | 1.5096 | 0.047515 | 1.4923 | 1.5096 | 0.40002 | -149.2611 | 148.172 | 0.40003 | -149.2611 | 148.172
Line1_1_3 | 0.027144 | 0.027144 | 0.027144 | 0.027144 | 0.027144 | 0.027144 | 0.0062686 | 0.0062686 | 0.0062686 | 0.0062687 | 0.0062687 | 0.0062687 | -0.00020625 | 0.0021816 | 0.0091841 | 0.00021333 | -0.0021744 | -0.009177 | -0.00021489 | 0.0090964 | 0.0022808 | 0.00022226 | -0.0090891 | -0.0022735 | 134.2252 | 134.2252 | 134.2252 | -45.7752 | -45.7752 | -45.7752 |  | 0.047516 | 1.4923 | 1.5096 | 0.049145 | 1.4908 | 1.5082 | 0.39999 | -149.2611 | 148.172 | 0.3998 | -149.2294 | 148.139
Line2_1_4 | 0.21822 | 0.027518 | 0.027518 | 0.21822 | 0.027518 | 0.027518 | 0.050395 | 0.006355 | 0.006355 | 0.050395 | 0.006355 | 0.006355 | 0.0016583 | 0.0022137 | 0.0093111 | -0.00085796 | -0.0021847 | -0.0092822 | 0.0017274 | 0.0092212 | 0.0023101 | -0.00089373 | -0.0091912 | -0.0022801 | -45.7698 | 134.2383 | 134.2383 | 134.2303 | -45.7622 | -45.7622 |  | 0.047516 | 1.4923 | 1.5096 | 0.024584 | 1.4866 | 1.504 | 0.39999 | -149.2611 | 148.172 | 0.40022 | -149.1332 | 148.0385
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.3315e-10 | 1.174e-07 | -1.016e-07 | 3.6509e-10 | -6.2571e-08 | 4.6836e-08 | 6.6784e-09 | -1.741e-07 | -1.8655e-07 | -3.3381e-09 | 8.4644e-08 | 9.5629e-08 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.047516 | 1.4923 | 1.5096 | 0.047515 | 1.4923 | 1.5096 | 0.39999 | -149.2611 | 148.172 | 0.40002 | -149.2611 | 148.172
Line4_2_6 | 0.02725 | 0.02725 | 0.02725 | 0.027251 | 0.027251 | 0.027251 | 0.0062932 | 0.0062932 | 0.0062932 | 0.0062932 | 0.0062932 | 0.0062932 | -0.0002142 | 0.0021835 | 0.0092131 | 0.00022133 | -0.0021763 | -0.009206 | -0.00022315 | 0.0091245 | 0.0022818 | 0.00023058 | -0.0091172 | -0.0022745 | 134.2283 | 134.2283 | 134.2283 | -45.7721 | -45.7721 | -45.7721 |  | 0.049151 | 1.4908 | 1.5082 | 0.050787 | 1.4894 | 1.5068 | 0.39992 | -149.2293 | 148.1389 | 0.39983 | -149.1975 | 148.1057
Line5_6_7 | 0.02725 | 0.02725 | 0.02725 | 0.027251 | 0.027251 | 0.027251 | 0.0062932 | 0.0062932 | 0.0062932 | 0.0062933 | 0.0062933 | 0.0062933 | -0.00022133 | 0.0021763 | 0.009206 | 0.00022846 | -0.0021691 | -0.0091989 | -0.00023058 | 0.0091172 | 0.0022745 | 0.00023801 | -0.0091099 | -0.0022671 | 134.2278 | 134.2278 | 134.2278 | -45.7726 | -45.7726 | -45.7726 |  | 0.050787 | 1.4894 | 1.5068 | 0.052423 | 1.488 | 1.5054 | 0.39983 | -149.1975 | 148.1057 | 0.39973 | -149.1656 | 148.0724
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.1394e-10 | 1.7504e-07 | -1.5154e-07 | 6.3888e-10 | -1.2052e-07 | 9.7103e-08 | 1.0987e-08 | -2.5858e-07 | -2.7719e-07 | -7.3238e-09 | 1.6999e-07 | 1.8713e-07 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.052423 | 1.488 | 1.5054 | 0.052423 | 1.488 | 1.5054 | 0.39973 | -149.1656 | 148.0724 | 0.39977 | -149.1656 | 148.0724
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.3798e-10 | 5.8347e-08 | -5.0515e-08 | 1.6291e-10 | -3.8309e-09 | -3.9265e-09 | 3.6625e-09 | -8.6192e-08 | -9.2395e-08 | 1.207e-12 | -2.393e-09 | 2.3379e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.052423 | 1.488 | 1.5054 | 0.052423 | 1.488 | 1.5054 | 0.39977 | -149.1656 | 148.0724 | 0.39978 | -149.1656 | 148.0724
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.3798e-10 | 5.8347e-08 | -5.0515e-08 | 1.6291e-10 | -3.8309e-09 | -3.9265e-09 | 3.6625e-09 | -8.6192e-08 | -9.2395e-08 | 1.207e-12 | -2.393e-09 | 2.3379e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.052423 | 1.488 | 1.5054 | 0.052423 | 1.488 | 1.5054 | 0.39977 | -149.1656 | 148.0724 | 0.39978 | -149.1656 | 148.0724
Line9_3_11 | 0.027144 | 0.027144 | 0.027144 | 0.027144 | 0.027144 | 0.027144 | 0.0062687 | 0.0062687 | 0.0062687 | 0.0062687 | 0.0062687 | 0.0062687 | -0.00021333 | 0.0021744 | 0.009177 | 0.0002204 | -0.0021673 | -0.00917 | -0.00022226 | 0.0090891 | 0.0022735 | 0.00022963 | -0.0090819 | -0.0022662 | 134.2247 | 134.2247 | 134.2247 | -45.7757 | -45.7757 | -45.7757 |  | 0.049145 | 1.4908 | 1.5082 | 0.050774 | 1.4894 | 1.5068 | 0.3998 | -149.2294 | 148.139 | 0.3996 | -149.1977 | 148.1059

## LG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.0030731 | 0.0030731 | 0.0030731 | 0.0030731 | 0.0030731 | 0.0030731 | 0.0007097 | 0.0007097 | 0.0007097 | 0.0007097 | 0.0007097 | 0.0007097 | -0.00042843 | -0.00012802 | 0.00069894 | 0.00042852 | 0.00012812 | -0.00069885 | -0.00042857 | 0.0006978 | -0.00012672 | 0.00042867 | -0.00069771 | 0.00012681 | 134.9155 | 134.9155 | 134.9155 | -45.0849 | -45.0849 | -45.0849 |  | 0.85387 | 0.99964 | 1.0009 | 0.85405 | 0.99954 | 1.0008 | -0.07481 | -124.6884 | 124.6391 | -0.07456 | -124.6798 | 124.6303
Line10_11_12 | 0.0030612 | 0.0030612 | 0.0030612 | 0.0030612 | 0.0030612 | 0.0030612 | 0.00070694 | 0.00070694 | 0.00070694 | 0.00070695 | 0.00070695 | 0.00070695 | -0.00042691 | -0.00012776 | 0.00069605 | 0.000427 | 0.00012786 | -0.00069597 | -0.00042713 | 0.00069489 | -0.00012636 | 0.00042723 | -0.00069481 | 0.00012645 | 134.911 | 134.911 | 134.911 | -45.0894 | -45.0894 | -45.0894 |  | 0.85424 | 0.99943 | 1.0007 | 0.85442 | 0.99932 | 1.0006 | -0.074313 | -124.6713 | 124.6216 | -0.074065 | -124.6628 | 124.6128
Line11_12_13 | 0.0030612 | 0.0030612 | 0.0030612 | 0.0030612 | 0.0030612 | 0.0030612 | 0.00070695 | 0.00070695 | 0.00070695 | 0.00070696 | 0.00070696 | 0.00070696 | -0.000427 | -0.00012786 | 0.00069597 | 0.00042709 | 0.00012795 | -0.00069589 | -0.00042723 | 0.00069481 | -0.00012645 | 0.00042733 | -0.00069472 | 0.00012654 | 134.9105 | 134.9105 | 134.9105 | -45.0899 | -45.0899 | -45.0899 |  | 0.85442 | 0.99932 | 1.0006 | 0.8546 | 0.99922 | 1.0005 | -0.074065 | -124.6628 | 124.6128 | -0.073817 | -124.6542 | 124.604
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -9.0231e-10 | 1.9998e-08 | -1.8827e-08 | 9.0046e-10 | -1.3523e-08 | 1.2355e-08 | 2.0183e-08 | -1.2534e-08 | -1.4281e-08 | -1.3459e-08 | 8.0732e-09 | 9.8002e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.8546 | 0.99922 | 1.0005 | 0.8546 | 0.99922 | 1.0005 | -0.073817 | -124.6542 | 124.604 | -0.073817 | -124.6542 | 124.604
Line13_13_14 | 0.0030613 | 0.0030613 | 0.0030613 | 0.0030613 | 0.0030613 | 0.0030613 | 0.00070697 | 0.00070697 | 0.00070697 | 0.00070698 | 0.00070698 | 0.00070698 | -0.00042709 | -0.00012797 | 0.0006959 | 0.00042718 | 0.00012807 | -0.00069582 | -0.00042735 | 0.00069473 | -0.00012653 | 0.00042745 | -0.00069464 | 0.00012661 | 134.9087 | 134.9087 | 134.9087 | -45.0918 | -45.0918 | -45.0918 |  | 0.8546 | 0.99922 | 1.0005 | 0.85479 | 0.99911 | 1.0004 | -0.073817 | -124.6542 | 124.604 | -0.073569 | -124.6457 | 124.5952
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.0154e-10 | 1.3332e-08 | -1.2552e-08 | 5.9969e-10 | -6.8576e-09 | 6.0793e-09 | 1.3456e-08 | -8.3557e-09 | -9.5204e-09 | -6.7316e-09 | 3.8954e-09 | 5.04e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.8546 | 0.99922 | 1.0005 | 0.8546 | 0.99922 | 1.0005 | -0.073817 | -124.6542 | 124.604 | -0.073817 | -124.6542 | 124.604
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.0077e-10 | 6.6658e-09 | -6.2758e-09 | 2.9892e-10 | -1.9179e-10 | -1.9644e-10 | 6.7278e-09 | -4.1778e-09 | -4.7602e-09 | -3.8352e-12 | -2.8242e-10 | 2.7974e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.8546 | 0.99922 | 1.0005 | 0.8546 | 0.99922 | 1.0005 | -0.073817 | -124.6542 | 124.604 | -0.073817 | -124.6542 | 124.604
Line16_4_18 | 0.027712 | 0 | 0 | 0.027712 | 0 | 0 | 0.0063999 | 0 | 0 | 0.0063999 | 0 | 0 | 0.0038521 | 6.7584e-09 | -6.3734e-09 | -0.0038399 | -1.904e-10 | -1.9512e-10 | 0.0038527 | -4.2469e-09 | -4.8224e-09 | -0.0038399 | -2.8075e-10 | 2.7803e-10 | -45.0822 | 0 | 0 | 134.9179 | 0 | 0 |  | 0.85128 | 0.99921 | 1.0005 | 0.84851 | 0.99889 | 1.0002 | -0.078338 | -124.6539 | 124.6037 | -0.082145 | -124.6281 | 124.5773
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.0163e-10 | 6.7177e-09 | -6.3253e-09 | 3.0097e-10 | -1.9362e-10 | -1.9818e-10 | 6.7746e-09 | -4.2174e-09 | -4.8023e-09 | -3.8835e-12 | -2.8462e-10 | 2.8198e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.85387 | 0.99964 | 1.0009 | 0.85387 | 0.99964 | 1.0009 | -0.07481 | -124.6884 | 124.6391 | -0.07481 | -124.6884 | 124.6391
Line1_1_3 | 0.0030611 | 0.0030611 | 0.0030611 | 0.0030611 | 0.0030611 | 0.0030611 | 0.00070693 | 0.00070693 | 0.00070693 | 0.00070694 | 0.00070694 | 0.00070694 | -0.00042673 | -0.00012757 | 0.00069622 | 0.00042682 | 0.00012766 | -0.00069614 | -0.00042693 | 0.00069507 | -0.00012618 | 0.00042703 | -0.00069498 | 0.00012627 | 134.912 | 134.912 | 134.912 | -45.0885 | -45.0885 | -45.0885 |  | 0.85387 | 0.99964 | 1.0009 | 0.85405 | 0.99954 | 1.0008 | -0.07481 | -124.6884 | 124.6391 | -0.074562 | -124.6799 | 124.6303
Line2_1_4 | 0.024609 | 0.0031033 | 0.0031033 | 0.024609 | 0.0031033 | 0.0031033 | 0.0056832 | 0.00071667 | 0.00071667 | 0.0056832 | 0.00071668 | 0.00071668 | 0.0034309 | -0.00012916 | 0.00070578 | -0.0034207 | 0.00012954 | -0.00070542 | 0.0034319 | 0.00070468 | -0.00012808 | -0.0034213 | -0.0007043 | 0.00012846 | -45.083 | 134.925 | 134.925 | 134.917 | -45.0754 | -45.0754 |  | 0.85387 | 0.99964 | 1.0009 | 0.85128 | 0.99921 | 1.0005 | -0.07481 | -124.6884 | 124.6391 | -0.078338 | -124.6539 | 124.6037
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.0327e-10 | 1.3435e-08 | -1.2651e-08 | 6.026e-10 | -6.9113e-09 | 6.1271e-09 | 1.3549e-08 | -8.4348e-09 | -9.6046e-09 | -6.7785e-09 | 3.9328e-09 | 5.0843e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.85387 | 0.99964 | 1.0009 | 0.85387 | 0.99964 | 1.0009 | -0.07481 | -124.6884 | 124.6391 | -0.07481 | -124.6884 | 124.6391
Line4_2_6 | 0.0030731 | 0.0030731 | 0.0030731 | 0.0030731 | 0.0030731 | 0.0030731 | 0.0007097 | 0.0007097 | 0.0007097 | 0.00070971 | 0.00070971 | 0.00070971 | -0.00042852 | -0.00012812 | 0.00069885 | 0.00042861 | 0.00012822 | -0.00069877 | -0.00042867 | 0.00069771 | -0.00012681 | 0.00042877 | -0.00069762 | 0.0001269 | 134.9151 | 134.9151 | 134.9151 | -45.0854 | -45.0854 | -45.0854 |  | 0.85405 | 0.99954 | 1.0008 | 0.85424 | 0.99943 | 1.0007 | -0.07456 | -124.6798 | 124.6303 | -0.07431 | -124.6712 | 124.6215
Line5_6_7 | 0.0030731 | 0.0030731 | 0.0030731 | 0.0030732 | 0.0030732 | 0.0030732 | 0.00070971 | 0.00070971 | 0.00070971 | 0.00070972 | 0.00070972 | 0.00070972 | -0.00042861 | -0.00012822 | 0.00069877 | 0.0004287 | 0.00012831 | -0.00069868 | -0.00042877 | 0.00069762 | -0.0001269 | 0.00042888 | -0.00069753 | 0.00012699 | 134.9146 | 134.9146 | 134.9146 | -45.0859 | -45.0859 | -45.0859 |  | 0.85424 | 0.99943 | 1.0007 | 0.85442 | 0.99932 | 1.0006 | -0.07431 | -124.6712 | 124.6215 | -0.07406 | -124.6627 | 124.6127
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -9.0296e-10 | 2.0036e-08 | -1.8864e-08 | 9.014e-10 | -1.355e-08 | 1.2379e-08 | 2.0218e-08 | -1.2563e-08 | -1.4312e-08 | -1.3483e-08 | 8.0922e-09 | 9.8215e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.85442 | 0.99932 | 1.0006 | 0.85442 | 0.99932 | 1.0006 | -0.07406 | -124.6627 | 124.6127 | -0.074059 | -124.6627 | 124.6127
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.0099e-10 | 6.6787e-09 | -6.288e-09 | 2.9943e-10 | -1.9224e-10 | -1.9687e-10 | 6.7394e-09 | -4.1876e-09 | -4.7706e-09 | -3.8471e-12 | -2.8296e-10 | 2.8029e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.85442 | 0.99932 | 1.0006 | 0.85442 | 0.99932 | 1.0006 | -0.074059 | -124.6627 | 124.6127 | -0.074059 | -124.6627 | 124.6127
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.0099e-10 | 6.6787e-09 | -6.288e-09 | 2.9943e-10 | -1.9224e-10 | -1.9687e-10 | 6.7394e-09 | -4.1876e-09 | -4.7706e-09 | -3.8471e-12 | -2.8296e-10 | 2.8029e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.85442 | 0.99932 | 1.0006 | 0.85442 | 0.99932 | 1.0006 | -0.074059 | -124.6627 | 124.6127 | -0.074059 | -124.6627 | 124.6127
Line9_3_11 | 0.0030611 | 0.0030611 | 0.0030611 | 0.0030612 | 0.0030612 | 0.0030612 | 0.00070694 | 0.00070694 | 0.00070694 | 0.00070694 | 0.00070694 | 0.00070694 | -0.00042682 | -0.00012766 | 0.00069614 | 0.00042691 | 0.00012776 | -0.00069605 | -0.00042703 | 0.00069498 | -0.00012627 | 0.00042713 | -0.00069489 | 0.00012636 | 134.9115 | 134.9115 | 134.9115 | -45.089 | -45.089 | -45.089 |  | 0.85405 | 0.99954 | 1.0008 | 0.85424 | 0.99943 | 1.0007 | -0.074562 | -124.6799 | 124.6303 | -0.074313 | -124.6713 | 124.6216

## LG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.0029113 | 0.0029113 | 0.0029113 | 0.0029114 | 0.0029114 | 0.0029114 | 0.00067235 | 0.00067235 | 0.00067235 | 0.00067235 | 0.00067235 | 0.00067235 | -0.00038452 | -0.0001149 | 0.0006273 | 0.0003846 | 0.00011499 | -0.00062722 | -0.00038465 | 0.00062628 | -0.00011373 | 0.00038474 | -0.0006262 | 0.00011381 | 134.9155 | 134.9155 | 134.9155 | -45.0849 | -45.0849 | -45.0849 |  | 0.80893 | 0.94703 | 0.94821 | 0.8091 | 0.94693 | 0.94811 | -0.07481 | -124.6884 | 124.6391 | -0.07456 | -124.6798 | 124.6303
Line10_11_12 | 0.0029 | 0.0029 | 0.0029 | 0.0029001 | 0.0029001 | 0.0029001 | 0.00066974 | 0.00066974 | 0.00066974 | 0.00066974 | 0.00066974 | 0.00066974 | -0.00038316 | -0.00011466 | 0.00062471 | 0.00038324 | 0.00011475 | -0.00062464 | -0.00038335 | 0.00062367 | -0.00011341 | 0.00038344 | -0.00062359 | 0.00011349 | 134.911 | 134.911 | 134.911 | -45.0894 | -45.0894 | -45.0894 |  | 0.80928 | 0.94683 | 0.94802 | 0.80945 | 0.94673 | 0.94792 | -0.074313 | -124.6713 | 124.6216 | -0.074065 | -124.6628 | 124.6128
Line11_12_13 | 0.0029001 | 0.0029001 | 0.0029001 | 0.0029001 | 0.0029001 | 0.0029001 | 0.00066974 | 0.00066974 | 0.00066974 | 0.00066975 | 0.00066975 | 0.00066975 | -0.00038324 | -0.00011475 | 0.00062464 | 0.00038332 | 0.00011484 | -0.00062456 | -0.00038344 | 0.00062359 | -0.00011349 | 0.00038353 | -0.00062351 | 0.00011357 | 134.9105 | 134.9105 | 134.9105 | -45.0899 | -45.0899 | -45.0899 |  | 0.80945 | 0.94673 | 0.94792 | 0.80963 | 0.94663 | 0.94783 | -0.074065 | -124.6628 | 124.6128 | -0.073817 | -124.6542 | 124.604
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.0983e-10 | 1.7948e-08 | -1.6898e-08 | 8.0817e-10 | -1.2137e-08 | 1.1089e-08 | 1.8115e-08 | -1.1249e-08 | -1.2817e-08 | -1.208e-08 | 7.2458e-09 | 8.7957e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.80963 | 0.94663 | 0.94783 | 0.80963 | 0.94663 | 0.94783 | -0.073817 | -124.6542 | 124.604 | -0.073817 | -124.6542 | 124.604
Line13_13_14 | 0.0029002 | 0.0029002 | 0.0029002 | 0.0029002 | 0.0029002 | 0.0029002 | 0.00066976 | 0.00066976 | 0.00066976 | 0.00066977 | 0.00066977 | 0.00066977 | -0.00038332 | -0.00011486 | 0.00062458 | 0.0003834 | 0.00011494 | -0.0006245 | -0.00038355 | 0.00062352 | -0.00011356 | 0.00038364 | -0.00062344 | 0.00011364 | 134.9087 | 134.9087 | 134.9087 | -45.0918 | -45.0918 | -45.0918 |  | 0.80963 | 0.94663 | 0.94783 | 0.8098 | 0.94652 | 0.94773 | -0.073817 | -124.6542 | 124.604 | -0.073569 | -124.6457 | 124.5952
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.3988e-10 | 1.1965e-08 | -1.1265e-08 | 5.3823e-10 | -6.1548e-09 | 5.4562e-09 | 1.2076e-08 | -7.4993e-09 | -8.5447e-09 | -6.0417e-09 | 3.4962e-09 | 4.5234e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.80963 | 0.94663 | 0.94783 | 0.80963 | 0.94663 | 0.94783 | -0.073817 | -124.6542 | 124.604 | -0.073817 | -124.6542 | 124.604
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.6994e-10 | 5.9826e-09 | -5.6325e-09 | 2.6829e-10 | -1.7214e-10 | -1.7631e-10 | 6.0382e-09 | -3.7496e-09 | -4.2723e-09 | -3.4421e-12 | -2.5348e-10 | 2.5107e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.80963 | 0.94663 | 0.94783 | 0.80963 | 0.94663 | 0.94783 | -0.073817 | -124.6542 | 124.604 | -0.073817 | -124.6542 | 124.604
Line16_4_18 | 0.026254 | 0 | 0 | 0.026254 | 0 | 0 | 0.006063 | 0 | 0 | 0.006063 | 0 | 0 | 0.0034573 | 6.0657e-09 | -5.7201e-09 | -0.0034463 | -1.7089e-10 | -1.7512e-10 | 0.0034578 | -3.8117e-09 | -4.3281e-09 | -0.0034463 | -2.5198e-10 | 2.4953e-10 | -45.0822 | 0 | 0 | 134.9179 | 0 | 0 |  | 0.80648 | 0.94662 | 0.94782 | 0.80385 | 0.94632 | 0.94753 | -0.078338 | -124.6539 | 124.6037 | -0.082145 | -124.6281 | 124.5773
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.7072e-10 | 6.0292e-09 | -5.677e-09 | 2.7012e-10 | -1.7377e-10 | -1.7787e-10 | 6.0803e-09 | -3.7851e-09 | -4.3101e-09 | -3.4855e-12 | -2.5544e-10 | 2.5308e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.80893 | 0.94703 | 0.94821 | 0.80893 | 0.94703 | 0.94821 | -0.07481 | -124.6884 | 124.6391 | -0.07481 | -124.6884 | 124.6391
Line1_1_3 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00066973 | 0.00066973 | 0.00066973 | 0.00066973 | 0.00066973 | 0.00066973 | -0.00038299 | -0.00011449 | 0.00062486 | 0.00038308 | 0.00011458 | -0.00062479 | -0.00038317 | 0.00062383 | -0.00011325 | 0.00038326 | -0.00062375 | 0.00011333 | 134.912 | 134.912 | 134.912 | -45.0885 | -45.0885 | -45.0885 |  | 0.80893 | 0.94703 | 0.94821 | 0.8091 | 0.94693 | 0.94812 | -0.07481 | -124.6884 | 124.6391 | -0.074562 | -124.6799 | 124.6303
Line2_1_4 | 0.023314 | 0.0029399 | 0.0029399 | 0.023314 | 0.00294 | 0.00294 | 0.0053841 | 0.00067895 | 0.00067895 | 0.0053841 | 0.00067896 | 0.00067896 | 0.0030793 | -0.00011592 | 0.00063344 | -0.0030701 | 0.00011626 | -0.00063312 | 0.0030801 | 0.00063245 | -0.00011496 | -0.0030706 | -0.00063211 | 0.00011529 | -45.083 | 134.925 | 134.925 | 134.917 | -45.0754 | -45.0754 |  | 0.80893 | 0.94703 | 0.94821 | 0.80648 | 0.94662 | 0.94782 | -0.07481 | -124.6884 | 124.6391 | -0.078338 | -124.6539 | 124.6037
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.4144e-10 | 1.2058e-08 | -1.1354e-08 | 5.4084e-10 | -6.203e-09 | 5.4991e-09 | 1.2161e-08 | -7.5703e-09 | -8.6202e-09 | -6.0838e-09 | 3.5297e-09 | 4.5632e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.80893 | 0.94703 | 0.94821 | 0.80893 | 0.94703 | 0.94821 | -0.07481 | -124.6884 | 124.6391 | -0.07481 | -124.6884 | 124.6391
Line4_2_6 | 0.0029114 | 0.0029114 | 0.0029114 | 0.0029114 | 0.0029114 | 0.0029114 | 0.00067235 | 0.00067235 | 0.00067235 | 0.00067236 | 0.00067236 | 0.00067236 | -0.0003846 | -0.00011499 | 0.00062722 | 0.00038468 | 0.00011507 | -0.00062715 | -0.00038474 | 0.0006262 | -0.00011381 | 0.00038483 | -0.00062612 | 0.00011389 | 134.9151 | 134.9151 | 134.9151 | -45.0854 | -45.0854 | -45.0854 |  | 0.8091 | 0.94693 | 0.94811 | 0.80928 | 0.94683 | 0.94802 | -0.07456 | -124.6798 | 124.6303 | -0.07431 | -124.6712 | 124.6215
Line5_6_7 | 0.0029114 | 0.0029114 | 0.0029114 | 0.0029114 | 0.0029114 | 0.0029114 | 0.00067236 | 0.00067236 | 0.00067236 | 0.00067236 | 0.00067236 | 0.00067236 | -0.00038468 | -0.00011507 | 0.00062715 | 0.00038476 | 0.00011516 | -0.00062707 | -0.00038483 | 0.00062612 | -0.00011389 | 0.00038492 | -0.00062604 | 0.00011397 | 134.9146 | 134.9146 | 134.9146 | -45.0859 | -45.0859 | -45.0859 |  | 0.80928 | 0.94683 | 0.94802 | 0.80945 | 0.94673 | 0.94792 | -0.07431 | -124.6712 | 124.6215 | -0.07406 | -124.6627 | 124.6127
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.1041e-10 | 1.7982e-08 | -1.6931e-08 | 8.0901e-10 | -1.2161e-08 | 1.111e-08 | 1.8146e-08 | -1.1275e-08 | -1.2845e-08 | -1.2101e-08 | 7.2628e-09 | 8.8149e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.80945 | 0.94673 | 0.94792 | 0.80945 | 0.94673 | 0.94792 | -0.07406 | -124.6627 | 124.6127 | -0.074059 | -124.6627 | 124.6127
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.7014e-10 | 5.9941e-09 | -5.6435e-09 | 2.6874e-10 | -1.7254e-10 | -1.7669e-10 | 6.0486e-09 | -3.7584e-09 | -4.2817e-09 | -3.4528e-12 | -2.5396e-10 | 2.5156e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.80945 | 0.94673 | 0.94792 | 0.80945 | 0.94673 | 0.94792 | -0.074059 | -124.6627 | 124.6127 | -0.074059 | -124.6627 | 124.6127
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.7014e-10 | 5.9941e-09 | -5.6435e-09 | 2.6874e-10 | -1.7254e-10 | -1.7669e-10 | 6.0486e-09 | -3.7584e-09 | -4.2817e-09 | -3.4528e-12 | -2.5396e-10 | 2.5156e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.80945 | 0.94673 | 0.94792 | 0.80945 | 0.94673 | 0.94792 | -0.074059 | -124.6627 | 124.6127 | -0.074059 | -124.6627 | 124.6127
Line9_3_11 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00066973 | 0.00066973 | 0.00066973 | 0.00066974 | 0.00066974 | 0.00066974 | -0.00038308 | -0.00011458 | 0.00062479 | 0.00038316 | 0.00011466 | -0.00062471 | -0.00038326 | 0.00062375 | -0.00011333 | 0.00038335 | -0.00062367 | 0.00011341 | 134.9115 | 134.9115 | 134.9115 | -45.089 | -45.089 | -45.089 |  | 0.8091 | 0.94693 | 0.94812 | 0.80928 | 0.94683 | 0.94802 | -0.074562 | -124.6799 | 124.6303 | -0.074313 | -124.6713 | 124.6216

## LLG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.01673 | 0.01673 | 0.01673 | 0.01673 | 0.01673 | 0.01673 | 0.0038636 | 0.0038636 | 0.0038637 | 0.0038637 | 0.0038637 | 0.0038637 | 0.0042422 | 0.0014352 | -0.001466 | -0.0042408 | -0.0014338 | 0.0014674 | 0.0042853 | -0.0018776 | 0.001816 | -0.0042825 | 0.0018804 | -0.0018132 | -45.5679 | -45.5678 | -45.5679 | 134.4317 | 134.4317 | 134.4316 |  | 1.5607 | 0.61167 | 0.60405 | 1.5599 | 0.61203 | 0.60372 | -0.27874 | -98.1745 | 83.3454 | -0.28801 | -98.2427 | 83.4154
Line10_11_12 | 0.01668 | 0.01668 | 0.01668 | 0.01668 | 0.01668 | 0.01668 | 0.0038521 | 0.0038521 | 0.0038521 | 0.0038522 | 0.0038522 | 0.0038522 | 0.0042226 | 0.00143 | -0.0014662 | -0.0042212 | -0.0014286 | 0.0014676 | 0.0042711 | -0.0018762 | 0.0018035 | -0.0042684 | 0.0018789 | -0.0018008 | -45.6245 | -45.6244 | -45.6245 | 134.3751 | 134.3751 | 134.375 |  | 1.5591 | 0.61238 | 0.60338 | 1.5584 | 0.61274 | 0.60305 | -0.29717 | -98.3104 | 83.485 | -0.3064 | -98.3782 | 83.5549
Line11_12_13 | 0.01668 | 0.01668 | 0.01668 | 0.01668 | 0.01668 | 0.016681 | 0.0038522 | 0.0038522 | 0.0038522 | 0.0038522 | 0.0038522 | 0.0038522 | 0.0042212 | 0.0014286 | -0.0014676 | -0.0042198 | -0.0014272 | 0.001469 | 0.0042684 | -0.0018789 | 0.0018008 | -0.0042657 | 0.0018817 | -0.001798 | -45.6249 | -45.6249 | -45.625 | 134.3746 | 134.3746 | 134.3746 |  | 1.5584 | 0.61274 | 0.60305 | 1.5576 | 0.6131 | 0.60272 | -0.3064 | -98.3782 | 83.5549 | -0.31564 | -98.4459 | 83.6249
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.6868e-09 | -8.0532e-08 | 7.5482e-08 | -9.357e-09 | 5.4505e-08 | -4.9785e-08 | -2.0014e-07 | 8.1597e-09 | -3.6699e-09 | 1.3339e-07 | -4.5726e-09 | 1.0704e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.5576 | 0.6131 | 0.60272 | 1.5576 | 0.6131 | 0.60272 | -0.31564 | -98.4459 | 83.6249 | -0.31564 | -98.4459 | 83.6249
Line13_13_14 | 0.016681 | 0.016681 | 0.016681 | 0.016681 | 0.016681 | 0.016681 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0038523 | 0.0042198 | 0.0014273 | -0.0014691 | -0.0042184 | -0.001426 | 0.0014705 | 0.0042659 | -0.0018817 | 0.001798 | -0.0042632 | 0.0018845 | -0.0017952 | -45.6268 | -45.6268 | -45.6268 | 134.3727 | 134.3727 | 134.3727 |  | 1.5576 | 0.6131 | 0.60272 | 1.5568 | 0.61345 | 0.60239 | -0.31564 | -98.4459 | 83.6249 | -0.32488 | -98.5135 | 83.695
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.4578e-09 | -5.3688e-08 | 5.0321e-08 | -6.1281e-09 | 2.7661e-08 | -2.4624e-08 | -1.3343e-07 | 5.4398e-09 | -2.4466e-09 | 6.6681e-08 | -1.8527e-09 | -1.5289e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.5576 | 0.6131 | 0.60272 | 1.5576 | 0.6131 | 0.60272 | -0.31564 | -98.4459 | 83.6249 | -0.31564 | -98.4459 | 83.6249
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2289e-09 | -2.6844e-08 | 2.5161e-08 | -2.8992e-09 | 8.1711e-10 | 5.3634e-10 | -6.6714e-08 | 2.7199e-09 | -1.2233e-09 | -3.3035e-11 | 8.6717e-10 | -1.3762e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.5576 | 0.6131 | 0.60272 | 1.5576 | 0.6131 | 0.60272 | -0.31564 | -98.4459 | 83.6249 | -0.31564 | -98.4459 | 83.6249
Line16_4_18 | 0 | 3.1717 | 3.1072 | 0 | 3.1717 | 3.1072 | 0 | 0.73247 | 0.71758 | 0 | 0.73247 | 0.71758 | 2.9685e-09 | 0.098813 | 0.098293 | -2.8816e-09 | 9.3997e-14 | 1.5365e-14 | -6.7461e-08 | 0.20119 | 0.19302 | -3.596e-11 | 8.1914e-14 | -2.0165e-14 | 0 | -162.0856 | 20.4026 | 0 | 17.9144 | -159.5974 |  | 1.5576 | 0.30602 | 0.30186 | 1.5553 | 0 | 0 | -0.31608 | -98.2431 | 83.4158 | -0.3441 | 0 | 0
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1648e-09 | -2.6946e-08 | 2.5362e-08 | -2.9224e-09 | 8.1428e-10 | 5.2782e-10 | -6.725e-08 | 2.6527e-09 | -1.4102e-09 | -2.9231e-11 | 8.7552e-10 | -1.3884e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.5607 | 0.61167 | 0.60405 | 1.5607 | 0.61167 | 0.60405 | -0.27874 | -98.1745 | 83.3454 | -0.27874 | -98.1745 | 83.3454
Line1_1_3 | 0.01668 | 0.01668 | 0.01668 | 0.01668 | 0.01668 | 0.01668 | 0.0038521 | 0.0038521 | 0.0038521 | 0.0038521 | 0.0038521 | 0.0038521 | 0.0042254 | 0.0014327 | -0.0014634 | -0.004224 | -0.0014313 | 0.0014648 | 0.0042765 | -0.0018706 | 0.0018091 | -0.0042738 | 0.0018734 | -0.0018063 | -45.6235 | -45.6235 | -45.6236 | 134.376 | 134.3761 | 134.376 |  | 1.5607 | 0.61167 | 0.60405 | 1.5599 | 0.61203 | 0.60372 | -0.27874 | -98.1745 | 83.3454 | -0.28795 | -98.2425 | 83.4152
Line2_1_4 | 0.016856 | 3.1642 | 3.1142 | 0.016856 | 3.1642 | 3.1142 | 0.0038927 | 0.73073 | 0.71918 | 0.0038928 | 0.73073 | 0.71918 | 0.0042847 | 0.19847 | 0.1957 | -0.004279 | -0.099533 | -0.097556 | 0.0043071 | 0.40049 | 0.38785 | -0.0042958 | -0.20024 | -0.19394 | -45.4277 | -161.8128 | 20.1197 | 134.5718 | 18.1872 | -159.8803 |  | 1.5607 | 0.61167 | 0.60405 | 1.5576 | 0.30602 | 0.30186 | -0.27874 | -98.1745 | 83.3454 | -0.31608 | -98.2431 | 83.4158
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.3295e-09 | -5.3892e-08 | 5.0723e-08 | -6.0872e-09 | 2.776e-08 | -2.4834e-08 | -1.345e-07 | 5.3055e-09 | -2.8204e-09 | 6.7221e-08 | -1.7772e-09 | 2.183e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.5607 | 0.61167 | 0.60405 | 1.5607 | 0.61167 | 0.60405 | -0.27874 | -98.1745 | 83.3454 | -0.27874 | -98.1745 | 83.3454
Line4_2_6 | 0.01673 | 0.01673 | 0.01673 | 0.01673 | 0.01673 | 0.01673 | 0.0038637 | 0.0038637 | 0.0038637 | 0.0038637 | 0.0038637 | 0.0038637 | 0.0042408 | 0.0014338 | -0.0014674 | -0.0042394 | -0.0014324 | 0.0014688 | 0.0042825 | -0.0018804 | 0.0018132 | -0.0042798 | 0.0018832 | -0.0018104 | -45.5683 | -45.5683 | -45.5684 | 134.4312 | 134.4313 | 134.4312 |  | 1.5599 | 0.61203 | 0.60372 | 1.5591 | 0.61239 | 0.60338 | -0.28801 | -98.2427 | 83.4154 | -0.29728 | -98.3107 | 83.4854
Line5_6_7 | 0.01673 | 0.01673 | 0.01673 | 0.01673 | 0.01673 | 0.01673 | 0.0038637 | 0.0038637 | 0.0038637 | 0.0038637 | 0.0038637 | 0.0038637 | 0.0042394 | 0.0014324 | -0.0014688 | -0.004238 | -0.0014311 | 0.0014703 | 0.0042798 | -0.0018832 | 0.0018104 | -0.0042771 | 0.001886 | -0.0018076 | -45.5688 | -45.5688 | -45.5688 | 134.4308 | 134.4308 | 134.4307 |  | 1.5591 | 0.61239 | 0.60338 | 1.5584 | 0.61274 | 0.60305 | -0.29728 | -98.3107 | 83.4854 | -0.30656 | -98.3787 | 83.5555
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.6397e-09 | -8.0608e-08 | 7.5631e-08 | -9.3314e-09 | 5.4555e-08 | -4.9887e-08 | -2.0054e-07 | 8.1098e-09 | -3.8081e-09 | 1.3366e-07 | -4.5373e-09 | 1.1595e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.5584 | 0.61274 | 0.60305 | 1.5584 | 0.61274 | 0.60305 | -0.30656 | -98.3787 | 83.5555 | -0.30656 | -98.3787 | 83.5555
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2132e-09 | -2.6869e-08 | 2.521e-08 | -2.9049e-09 | 8.1641e-10 | 5.3423e-10 | -6.6847e-08 | 2.7033e-09 | -1.2694e-09 | -3.2101e-11 | 8.6925e-10 | -1.3792e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.5584 | 0.61274 | 0.60305 | 1.5584 | 0.61274 | 0.60305 | -0.30656 | -98.3787 | 83.5555 | -0.30656 | -98.3787 | 83.5555
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2132e-09 | -2.6869e-08 | 2.521e-08 | -2.9049e-09 | 8.1641e-10 | 5.3423e-10 | -6.6847e-08 | 2.7033e-09 | -1.2694e-09 | -3.2101e-11 | 8.6925e-10 | -1.3792e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.5584 | 0.61274 | 0.60305 | 1.5584 | 0.61274 | 0.60305 | -0.30656 | -98.3787 | 83.5555 | -0.30656 | -98.3787 | 83.5555
Line9_3_11 | 0.01668 | 0.01668 | 0.01668 | 0.01668 | 0.01668 | 0.01668 | 0.0038521 | 0.0038521 | 0.0038521 | 0.0038521 | 0.0038521 | 0.0038521 | 0.004224 | 0.0014313 | -0.0014648 | -0.0042226 | -0.00143 | 0.0014662 | 0.0042738 | -0.0018734 | 0.0018063 | -0.0042711 | 0.0018762 | -0.0018035 | -45.624 | -45.6239 | -45.6241 | 134.3755 | 134.3756 | 134.3755 |  | 1.5599 | 0.61203 | 0.60372 | 1.5591 | 0.61238 | 0.60338 | -0.28795 | -98.2425 | 83.4152 | -0.29717 | -98.3104 | 83.485

## LLG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.017524 | 0.017524 | 0.017524 | 0.017524 | 0.017524 | 0.017524 | 0.0040469 | 0.0040469 | 0.0040469 | 0.004047 | 0.0040469 | 0.004047 | 0.0046542 | 0.0015421 | -0.0015759 | -0.0046527 | -0.0015406 | 0.0015775 | 0.0047014 | -0.0020346 | 0.0019669 | -0.0046984 | 0.0020376 | -0.0019639 | -45.5762 | -45.5761 | -45.5763 | 134.4233 | 134.4234 | 134.4233 |  | 1.6347 | 0.63084 | 0.62279 | 1.6339 | 0.63122 | 0.62244 | -0.28709 | -98.4151 | 83.126 | -0.29635 | -98.4841 | 83.1969
Line10_11_12 | 0.017471 | 0.017471 | 0.017471 | 0.017472 | 0.017472 | 0.017472 | 0.0040349 | 0.0040349 | 0.0040349 | 0.0040349 | 0.0040349 | 0.0040349 | 0.0046327 | 0.0015365 | -0.0015762 | -0.0046312 | -0.001535 | 0.0015778 | 0.0046859 | -0.0020331 | 0.0019534 | -0.0046829 | 0.0020361 | -0.0019504 | -45.6328 | -45.6328 | -45.6329 | 134.3667 | 134.3668 | 134.3667 |  | 1.6331 | 0.63159 | 0.62209 | 1.6323 | 0.63197 | 0.62174 | -0.30552 | -98.5527 | 83.2676 | -0.31474 | -98.6215 | 83.3385
Line11_12_13 | 0.017472 | 0.017472 | 0.017472 | 0.017472 | 0.017472 | 0.017472 | 0.0040349 | 0.0040349 | 0.0040349 | 0.0040349 | 0.0040349 | 0.0040349 | 0.0046311 | 0.001535 | -0.0015778 | -0.0046296 | -0.0015335 | 0.0015793 | 0.0046829 | -0.0020361 | 0.0019504 | -0.00468 | 0.0020392 | -0.0019473 | -45.6333 | -45.6332 | -45.6333 | 134.3663 | 134.3663 | 134.3662 |  | 1.6323 | 0.63197 | 0.62174 | 1.6315 | 0.63234 | 0.62139 | -0.31474 | -98.6215 | 83.3385 | -0.32398 | -98.6901 | 83.4095
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0624e-08 | -8.7033e-08 | 8.1428e-08 | -1.0262e-08 | 5.8932e-08 | -5.3689e-08 | -2.1958e-07 | 9.1921e-09 | -4.2404e-09 | 1.4635e-07 | -5.2012e-09 | 1.333e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.6315 | 0.63234 | 0.62139 | 1.6315 | 0.63234 | 0.62139 | -0.32398 | -98.6901 | 83.4095 | -0.32398 | -98.6901 | 83.4095
Line13_13_14 | 0.017472 | 0.017472 | 0.017472 | 0.017472 | 0.017472 | 0.017472 | 0.004035 | 0.004035 | 0.004035 | 0.004035 | 0.004035 | 0.004035 | 0.0046296 | 0.0015336 | -0.0015794 | -0.0046281 | -0.0015321 | 0.001581 | 0.0046802 | -0.0020392 | 0.0019473 | -0.0046772 | 0.0020423 | -0.0019443 | -45.6352 | -45.6352 | -45.6352 | 134.3644 | 134.3644 | 134.3644 |  | 1.6315 | 0.63234 | 0.62139 | 1.6307 | 0.63272 | 0.62104 | -0.32398 | -98.6901 | 83.4095 | -0.33322 | -98.7586 | 83.4806
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.0827e-09 | -5.8022e-08 | 5.4285e-08 | -6.7209e-09 | 2.9921e-08 | -2.6546e-08 | -1.4638e-07 | 6.128e-09 | -2.8269e-09 | 7.3155e-08 | -2.1371e-09 | -8.0501e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.6315 | 0.63234 | 0.62139 | 1.6315 | 0.63234 | 0.62139 | -0.32398 | -98.6901 | 83.4095 | -0.32398 | -98.6901 | 83.4095
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5414e-09 | -2.9011e-08 | 2.7143e-08 | -3.1796e-09 | 9.0993e-10 | 5.9654e-10 | -7.3192e-08 | 3.064e-09 | -1.4135e-09 | -3.7208e-11 | 9.2687e-10 | -1.494e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.6315 | 0.63234 | 0.62139 | 1.6315 | 0.63234 | 0.62139 | -0.32398 | -98.6901 | 83.4095 | -0.32398 | -98.6901 | 83.4095
Line16_4_18 | 0 | 3.2714 | 3.2033 | 0 | 3.2714 | 3.2033 | 0 | 0.7555 | 0.73978 | 0 | 0.7555 | 0.73978 | 3.2557e-09 | 0.10509 | 0.1045 | -3.1603e-09 | 1.0381e-13 | 3.7204e-14 | -7.4011e-08 | 0.21403 | 0.20515 | -4.0416e-11 | 2.9084e-14 | -2.0468e-16 | 0 | -162.3326 | 20.1903 | 0 | 17.6674 | -159.8097 |  | 1.6315 | 0.31561 | 0.31122 | 1.6291 | 0 | 0 | -0.32443 | -98.4846 | 83.1974 | -0.35244 | 0 | 0
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.471e-09 | -2.912e-08 | 2.736e-08 | -3.2051e-09 | 9.0677e-10 | 5.8724e-10 | -7.3781e-08 | 2.9898e-09 | -1.6179e-09 | -3.3036e-11 | 9.3603e-10 | -1.5073e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.6347 | 0.63084 | 0.62279 | 1.6347 | 0.63084 | 0.62279 | -0.28709 | -98.4151 | 83.126 | -0.28709 | -98.4151 | 83.126
Line1_1_3 | 0.017471 | 0.017471 | 0.017471 | 0.017471 | 0.017471 | 0.017471 | 0.0040348 | 0.0040348 | 0.0040348 | 0.0040348 | 0.0040348 | 0.0040348 | 0.0046357 | 0.0015395 | -0.0015731 | -0.0046342 | -0.001538 | 0.0015747 | 0.0046919 | -0.002027 | 0.0019595 | -0.0046889 | 0.00203 | -0.0019565 | -45.6319 | -45.6318 | -45.6319 | 134.3677 | 134.3677 | 134.3676 |  | 1.6347 | 0.63084 | 0.62279 | 1.6339 | 0.63122 | 0.62244 | -0.28709 | -98.4151 | 83.126 | -0.2963 | -98.4839 | 83.1968
Line2_1_4 | 0.017656 | 3.2634 | 3.2106 | 0.017656 | 3.2634 | 3.2106 | 0.0040774 | 0.75366 | 0.74147 | 0.0040774 | 0.75366 | 0.74147 | 0.0047008 | 0.21109 | 0.20804 | -0.0046946 | -0.10587 | -0.1037 | 0.0047254 | 0.42601 | 0.41226 | -0.004713 | -0.21301 | -0.20614 | -45.4361 | -162.0561 | 19.9033 | 134.5635 | 17.9439 | -160.0967 |  | 1.6347 | 0.63084 | 0.62279 | 1.6315 | 0.31561 | 0.31122 | -0.28709 | -98.4151 | 83.126 | -0.32443 | -98.4846 | 83.1974
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.9419e-09 | -5.824e-08 | 5.4721e-08 | -6.6761e-09 | 3.0027e-08 | -2.6773e-08 | -1.4756e-07 | 5.9795e-09 | -3.2358e-09 | 7.3748e-08 | -2.0537e-09 | 1.1061e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.6347 | 0.63084 | 0.62279 | 1.6347 | 0.63084 | 0.62279 | -0.28709 | -98.4151 | 83.126 | -0.28709 | -98.4151 | 83.126
Line4_2_6 | 0.017524 | 0.017524 | 0.017524 | 0.017524 | 0.017524 | 0.017524 | 0.004047 | 0.0040469 | 0.004047 | 0.004047 | 0.004047 | 0.004047 | 0.0046527 | 0.0015406 | -0.0015775 | -0.0046512 | -0.0015391 | 0.0015791 | 0.0046984 | -0.0020376 | 0.0019639 | -0.0046954 | 0.0020407 | -0.0019608 | -45.5767 | -45.5766 | -45.5767 | 134.4229 | 134.4229 | 134.4228 |  | 1.6339 | 0.63122 | 0.62244 | 1.6331 | 0.63159 | 0.62208 | -0.29635 | -98.4841 | 83.1969 | -0.30563 | -98.5531 | 83.2679
Line5_6_7 | 0.017524 | 0.017524 | 0.017524 | 0.017524 | 0.017524 | 0.017524 | 0.004047 | 0.004047 | 0.004047 | 0.004047 | 0.004047 | 0.004047 | 0.0046512 | 0.0015391 | -0.0015791 | -0.0046496 | -0.0015376 | 0.0015806 | 0.0046954 | -0.0020407 | 0.0019608 | -0.0046924 | 0.0020438 | -0.0019577 | -45.5771 | -45.5771 | -45.5772 | 134.4224 | 134.4224 | 134.4224 |  | 1.6331 | 0.63159 | 0.62208 | 1.6323 | 0.63197 | 0.62173 | -0.30563 | -98.5531 | 83.2679 | -0.31491 | -98.622 | 83.339
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0572e-08 | -8.7114e-08 | 8.159e-08 | -1.0234e-08 | 5.8985e-08 | -5.3799e-08 | -2.2001e-07 | 9.1369e-09 | -4.3916e-09 | 1.4664e-07 | -5.1621e-09 | 1.4304e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.6323 | 0.63197 | 0.62173 | 1.6323 | 0.63197 | 0.62173 | -0.31491 | -98.622 | 83.339 | -0.31491 | -98.622 | 83.339
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5241e-09 | -2.9038e-08 | 2.7197e-08 | -3.1859e-09 | 9.0915e-10 | 5.9424e-10 | -7.3338e-08 | 3.0456e-09 | -1.4639e-09 | -3.6184e-11 | 9.2914e-10 | -1.4973e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.6323 | 0.63197 | 0.62173 | 1.6323 | 0.63197 | 0.62173 | -0.31491 | -98.622 | 83.339 | -0.31491 | -98.622 | 83.339
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5241e-09 | -2.9038e-08 | 2.7197e-08 | -3.1859e-09 | 9.0915e-10 | 5.9424e-10 | -7.3338e-08 | 3.0456e-09 | -1.4639e-09 | -3.6184e-11 | 9.2914e-10 | -1.4973e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.6323 | 0.63197 | 0.62173 | 1.6323 | 0.63197 | 0.62173 | -0.31491 | -98.622 | 83.339 | -0.31491 | -98.622 | 83.339
Line9_3_11 | 0.017471 | 0.017471 | 0.017471 | 0.017471 | 0.017471 | 0.017472 | 0.0040348 | 0.0040348 | 0.0040348 | 0.0040349 | 0.0040349 | 0.0040349 | 0.0046342 | 0.001538 | -0.0015747 | -0.0046327 | -0.0015365 | 0.0015762 | 0.0046889 | -0.00203 | 0.0019565 | -0.0046859 | 0.0020331 | -0.0019534 | -45.6323 | -45.6323 | -45.6324 | 134.3672 | 134.3673 | 134.3671 |  | 1.6339 | 0.63122 | 0.62244 | 1.6331 | 0.63159 | 0.62209 | -0.2963 | -98.4839 | 83.1968 | -0.30552 | -98.5527 | 83.2676

## LLG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.0030997 | 0.0030997 | 0.0030997 | 0.0030997 | 0.0030997 | 0.0030997 | 0.00071585 | 0.00071585 | 0.00071585 | 0.00071585 | 0.00071585 | 0.00071585 | 0.00057843 | 0.00024227 | -0.00067613 | -0.00057838 | -0.00024223 | 0.00067618 | 0.00058034 | -0.00067674 | 0.00024139 | -0.00058025 | 0.00067684 | -0.00024129 | -45.1287 | -45.1287 | -45.1287 | 134.8708 | 134.8708 | 134.8708 |  | 1.1446 | 1.0041 | 1.0029 | 1.1445 | 1.0042 | 1.0029 | -0.034115 | -115.4318 | 115.2238 | -0.036479 | -115.4379 | 115.2323
Line10_11_12 | 0.0030905 | 0.0030905 | 0.0030905 | 0.0030905 | 0.0030905 | 0.0030905 | 0.00071371 | 0.00071371 | 0.00071371 | 0.00071372 | 0.00071372 | 0.00071372 | 0.00057604 | 0.00024212 | -0.00067445 | -0.00057599 | -0.00024208 | 0.0006745 | 0.00057899 | -0.00067468 | 0.00023981 | -0.0005789 | 0.00067478 | -0.00023971 | -45.1853 | -45.1853 | -45.1853 | 134.8142 | 134.8142 | 134.8142 |  | 1.1443 | 1.0043 | 1.0029 | 1.1442 | 1.0044 | 1.003 | -0.038816 | -115.4441 | 115.2408 | -0.041167 | -115.4503 | 115.2493
Line11_12_13 | 0.0030905 | 0.0030905 | 0.0030905 | 0.0030905 | 0.0030905 | 0.0030905 | 0.00071372 | 0.00071372 | 0.00071372 | 0.00071373 | 0.00071373 | 0.00071373 | 0.00057599 | 0.00024208 | -0.0006745 | -0.00057594 | -0.00024204 | 0.00067456 | 0.0005789 | -0.00067478 | 0.00023971 | -0.00057882 | 0.00067488 | -0.00023962 | -45.1858 | -45.1858 | -45.1858 | 134.8138 | 134.8138 | 134.8138 |  | 1.1442 | 1.0044 | 1.003 | 1.1441 | 1.0045 | 1.003 | -0.041167 | -115.4503 | 115.2493 | -0.043518 | -115.4564 | 115.2577
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2388e-09 | -2.2098e-08 | 2.1098e-08 | -1.2204e-09 | 1.4888e-08 | -1.3906e-08 | -2.724e-08 | 9.3051e-09 | 1.1211e-08 | 1.8157e-08 | -5.897e-09 | -7.7935e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1441 | 1.0045 | 1.003 | 1.1441 | 1.0045 | 1.003 | -0.043518 | -115.4564 | 115.2577 | -0.043518 | -115.4564 | 115.2577
Line13_13_14 | 0.0030906 | 0.0030906 | 0.0030906 | 0.0030906 | 0.0030906 | 0.0030906 | 0.00071374 | 0.00071374 | 0.00071374 | 0.00071375 | 0.00071375 | 0.00071375 | 0.00057594 | 0.00024206 | -0.00067458 | -0.00057589 | -0.00024202 | 0.00067463 | 0.00057885 | -0.00067489 | 0.0002396 | -0.00057876 | 0.00067498 | -0.0002395 | -45.1877 | -45.1877 | -45.1877 | 134.8119 | 134.8119 | 134.8119 |  | 1.1441 | 1.0045 | 1.003 | 1.1439 | 1.0046 | 1.003 | -0.043518 | -115.4564 | 115.2577 | -0.04587 | -115.4626 | 115.2662
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.2588e-10 | -1.4732e-08 | 1.4066e-08 | -8.0748e-10 | 7.5214e-09 | -6.873e-09 | -1.816e-08 | 6.2034e-09 | 7.4743e-09 | 9.0767e-09 | -2.7953e-09 | -4.0564e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1441 | 1.0045 | 1.003 | 1.1441 | 1.0045 | 1.003 | -0.043518 | -115.4564 | 115.2577 | -0.043518 | -115.4564 | 115.2577
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1294e-10 | -7.3661e-09 | 7.0328e-09 | -3.9455e-10 | 1.5528e-10 | 1.5971e-10 | -9.08e-09 | 3.1017e-09 | 3.7371e-09 | -3.3454e-12 | 3.0637e-10 | -3.1924e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1441 | 1.0045 | 1.003 | 1.1441 | 1.0045 | 1.003 | -0.043518 | -115.4564 | 115.2577 | -0.043518 | -115.4564 | 115.2577
Line16_4_18 | 0 | 0.032623 | 0.032563 | 0 | 0.032623 | 0.032563 | 0 | 0.0075339 | 0.0075202 | 0 | 0.0075339 | 0.0075202 | 3.7727e-10 | 0.0053284 | 0.0053146 | -3.9259e-10 | -0.0053212 | -0.0053019 | -9.1816e-09 | 0.0053425 | 0.0053204 | -3.9001e-12 | -0.0053212 | -0.0053019 | 0 | -160.5891 | 70.1696 | 0 | 19.411 | -109.8304 |  | 1.1441 | 1.0015 | 0.99998 | 1.1436 | 0.99886 | 0.99705 | -0.043631 | -115.5133 | 115.2011 | -0.050753 | -115.589 | 115.1696
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9902e-10 | -7.4024e-09 | 7.0841e-09 | -3.9713e-10 | 1.5661e-10 | 1.5978e-10 | -9.1397e-09 | 3.1304e-09 | 3.741e-09 | -2.6239e-12 | 3.079e-10 | -3.215e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1446 | 1.0041 | 1.0029 | 1.1446 | 1.0041 | 1.0029 | -0.034115 | -115.4318 | 115.2238 | -0.034115 | -115.4318 | 115.2238
Line1_1_3 | 0.0030904 | 0.0030904 | 0.0030904 | 0.0030905 | 0.0030905 | 0.0030905 | 0.0007137 | 0.0007137 | 0.0007137 | 0.00071371 | 0.00071371 | 0.00071371 | 0.00057613 | 0.0002422 | -0.00067434 | -0.00057609 | -0.00024216 | 0.00067439 | 0.00057916 | -0.00067448 | 0.00024001 | -0.00057908 | 0.00067458 | -0.00023991 | -45.1844 | -45.1844 | -45.1844 | 134.8152 | 134.8152 | 134.8152 |  | 1.1446 | 1.0041 | 1.0029 | 1.1445 | 1.0042 | 1.0029 | -0.034115 | -115.4318 | 115.2238 | -0.036465 | -115.4379 | 115.2323
Line2_1_4 | 0.003123 | 0.0314 | 0.031363 | 0.0031231 | 0.0314 | 0.031363 | 0.00072124 | 0.0072515 | 0.0072431 | 0.00072124 | 0.0072515 | 0.0072431 | 0.00058421 | 0.005577 | 0.0046474 | -0.00058402 | -0.0055693 | -0.004636 | 0.00058328 | 0.0046815 | 0.0055829 | -0.0005829 | -0.0046615 | -0.0055648 | -44.9886 | -155.4429 | 64.9985 | 135.011 | 24.5572 | -115.0015 |  | 1.1446 | 1.0041 | 1.0029 | 1.1441 | 1.0015 | 0.99998 | -0.034115 | -115.4318 | 115.2238 | -0.043631 | -115.5133 | 115.2011
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.9803e-10 | -1.4805e-08 | 1.4168e-08 | -7.9614e-10 | 7.559e-09 | -6.9243e-09 | -1.8279e-08 | 6.2609e-09 | 7.482e-09 | 9.1371e-09 | -2.8225e-09 | -4.0625e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1446 | 1.0041 | 1.0029 | 1.1446 | 1.0041 | 1.0029 | -0.034115 | -115.4318 | 115.2238 | -0.034115 | -115.4318 | 115.2238
Line4_2_6 | 0.0030997 | 0.0030997 | 0.0030997 | 0.0030998 | 0.0030998 | 0.0030998 | 0.00071585 | 0.00071585 | 0.00071585 | 0.00071586 | 0.00071586 | 0.00071586 | 0.00057838 | 0.00024223 | -0.00067618 | -0.00057833 | -0.00024219 | 0.00067624 | 0.00058025 | -0.00067684 | 0.00024129 | -0.00058017 | 0.00067694 | -0.00024119 | -45.1292 | -45.1292 | -45.1292 | 134.8704 | 134.8704 | 134.8704 |  | 1.1445 | 1.0042 | 1.0029 | 1.1443 | 1.0043 | 1.0029 | -0.036479 | -115.4379 | 115.2323 | -0.038844 | -115.4441 | 115.2408
Line5_6_7 | 0.0030998 | 0.0030998 | 0.0030998 | 0.0030998 | 0.0030998 | 0.0030998 | 0.00071586 | 0.00071586 | 0.00071586 | 0.00071586 | 0.00071586 | 0.00071586 | 0.00057833 | 0.00024219 | -0.00067624 | -0.00057828 | -0.00024215 | 0.00067629 | 0.00058017 | -0.00067694 | 0.00024119 | -0.00058008 | 0.00067704 | -0.00024109 | -45.1296 | -45.1296 | -45.1296 | 134.8699 | 134.8699 | 134.8699 |  | 1.1443 | 1.0043 | 1.0029 | 1.1442 | 1.0044 | 1.003 | -0.038844 | -115.4441 | 115.2408 | -0.041209 | -115.4503 | 115.2493
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2286e-09 | -2.2125e-08 | 2.1136e-08 | -1.2142e-09 | 1.4906e-08 | -1.3931e-08 | -2.7284e-08 | 9.3264e-09 | 1.1214e-08 | 1.8186e-08 | -5.9109e-09 | -7.7961e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1442 | 1.0044 | 1.003 | 1.1442 | 1.0044 | 1.003 | -0.041209 | -115.4503 | 115.2493 | -0.041209 | -115.4503 | 115.2493
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0953e-10 | -7.3751e-09 | 7.0455e-09 | -3.9518e-10 | 1.5561e-10 | 1.5973e-10 | -9.0948e-09 | 3.1088e-09 | 3.7381e-09 | -3.1683e-12 | 3.0675e-10 | -3.198e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1442 | 1.0044 | 1.003 | 1.1442 | 1.0044 | 1.003 | -0.041209 | -115.4503 | 115.2493 | -0.041209 | -115.4503 | 115.2493
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0953e-10 | -7.3751e-09 | 7.0455e-09 | -3.9518e-10 | 1.5561e-10 | 1.5973e-10 | -9.0948e-09 | 3.1088e-09 | 3.7381e-09 | -3.1683e-12 | 3.0675e-10 | -3.198e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1442 | 1.0044 | 1.003 | 1.1442 | 1.0044 | 1.003 | -0.041209 | -115.4503 | 115.2493 | -0.041209 | -115.4503 | 115.2493
Line9_3_11 | 0.0030905 | 0.0030905 | 0.0030905 | 0.0030905 | 0.0030905 | 0.0030905 | 0.00071371 | 0.00071371 | 0.00071371 | 0.00071371 | 0.00071371 | 0.00071371 | 0.00057609 | 0.00024216 | -0.00067439 | -0.00057604 | -0.00024212 | 0.00067445 | 0.00057908 | -0.00067458 | 0.00023991 | -0.00057899 | 0.00067468 | -0.00023981 | -45.1849 | -45.1849 | -45.1849 | 134.8147 | 134.8147 | 134.8147 |  | 1.1445 | 1.0042 | 1.0029 | 1.1443 | 1.0043 | 1.0029 | -0.036465 | -115.4379 | 115.2323 | -0.038816 | -115.4441 | 115.2408

## LLG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.0032472 | 0.0032472 | 0.0032472 | 0.0032472 | 0.0032472 | 0.0032472 | 0.00074991 | 0.00074991 | 0.00074991 | 0.00074992 | 0.00074992 | 0.00074992 | 0.00063479 | 0.00026579 | -0.00074193 | -0.00063473 | -0.00026575 | 0.00074199 | 0.00063689 | -0.00074268 | 0.0002649 | -0.00063679 | 0.00074278 | -0.00026479 | -45.1303 | -45.1303 | -45.1303 | 134.8693 | 134.8693 | 134.8693 |  | 1.1991 | 1.0519 | 1.0505 | 1.1989 | 1.052 | 1.0505 | -0.035676 | -115.4386 | 115.2208 | -0.03804 | -115.4448 | 115.2293
Line10_11_12 | 0.0032375 | 0.0032375 | 0.0032375 | 0.0032376 | 0.0032376 | 0.0032376 | 0.00074768 | 0.00074768 | 0.00074768 | 0.00074768 | 0.00074768 | 0.00074768 | 0.00063216 | 0.00026563 | -0.00074008 | -0.00063211 | -0.00026558 | 0.00074014 | 0.0006354 | -0.00074041 | 0.00026317 | -0.00063531 | 0.00074052 | -0.00026306 | -45.1869 | -45.1869 | -45.1869 | 134.8127 | 134.8127 | 134.8127 |  | 1.1988 | 1.0521 | 1.0506 | 1.1986 | 1.0522 | 1.0506 | -0.040376 | -115.4509 | 115.2378 | -0.042727 | -115.4571 | 115.2462
Line11_12_13 | 0.0032376 | 0.0032376 | 0.0032376 | 0.0032376 | 0.0032376 | 0.0032376 | 0.00074768 | 0.00074768 | 0.00074768 | 0.00074769 | 0.00074769 | 0.00074769 | 0.00063211 | 0.00026559 | -0.00074014 | -0.00063206 | -0.00026554 | 0.0007402 | 0.00063531 | -0.00074052 | 0.00026306 | -0.00063521 | 0.00074063 | -0.00026296 | -45.1874 | -45.1874 | -45.1874 | 134.8122 | 134.8122 | 134.8122 |  | 1.1986 | 1.0522 | 1.0506 | 1.1985 | 1.0523 | 1.0506 | -0.042727 | -115.4571 | 115.2462 | -0.045079 | -115.4633 | 115.2547
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3591e-09 | -2.4251e-08 | 2.315e-08 | -1.3389e-09 | 1.6338e-08 | -1.5258e-08 | -2.9894e-08 | 1.0215e-08 | 1.2303e-08 | 1.9925e-08 | -6.4743e-09 | -8.5523e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1985 | 1.0523 | 1.0506 | 1.1985 | 1.0523 | 1.0506 | -0.045079 | -115.4633 | 115.2547 | -0.045079 | -115.4633 | 115.2547
Line13_13_14 | 0.0032377 | 0.0032377 | 0.0032377 | 0.0032377 | 0.0032377 | 0.0032377 | 0.0007477 | 0.0007477 | 0.0007477 | 0.00074771 | 0.00074771 | 0.00074771 | 0.00063206 | 0.00026557 | -0.00074023 | -0.000632 | -0.00026552 | 0.00074029 | 0.00063524 | -0.00074064 | 0.00026294 | -0.00063515 | 0.00074075 | -0.00026283 | -45.1892 | -45.1892 | -45.1892 | 134.8103 | 134.8103 | 134.8103 |  | 1.1985 | 1.0523 | 1.0506 | 1.1983 | 1.0524 | 1.0506 | -0.045079 | -115.4633 | 115.2547 | -0.047431 | -115.4694 | 115.2632
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0604e-10 | -1.6167e-08 | 1.5434e-08 | -8.8585e-10 | 8.2543e-09 | -7.541e-09 | -1.9929e-08 | 6.81e-09 | 8.2018e-09 | 9.9608e-09 | -3.0693e-09 | -4.4514e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1985 | 1.0523 | 1.0506 | 1.1985 | 1.0523 | 1.0506 | -0.045079 | -115.4633 | 115.2547 | -0.045079 | -115.4633 | 115.2547
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5302e-10 | -8.0835e-09 | 7.7168e-09 | -4.3283e-10 | 1.7076e-10 | 1.7577e-10 | -9.9646e-09 | 3.405e-09 | 4.1009e-09 | -3.8032e-12 | 3.3571e-10 | -3.5055e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1985 | 1.0523 | 1.0506 | 1.1985 | 1.0523 | 1.0506 | -0.045079 | -115.4633 | 115.2547 | -0.045079 | -115.4633 | 115.2547
Line16_4_18 | 0 | 0.034174 | 0.03411 | 0 | 0.034174 | 0.03411 | 0 | 0.0078921 | 0.0078773 | 0 | 0.0078921 | 0.0078773 | 4.1387e-10 | 0.0058471 | 0.0058313 | -4.3069e-10 | -0.0058392 | -0.0058173 | -1.0076e-08 | 0.0058626 | 0.0058377 | -4.412e-12 | -0.0058392 | -0.0058173 | 0 | -160.5959 | 70.1666 | 0 | 19.4042 | -109.8334 |  | 1.1985 | 1.0492 | 1.0475 | 1.198 | 1.0463 | 1.0444 | -0.045192 | -115.5201 | 115.1981 | -0.052314 | -115.5958 | 115.1666
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3774e-10 | -8.1233e-09 | 7.7732e-09 | -4.3566e-10 | 1.7221e-10 | 1.7584e-10 | -1.003e-08 | 3.4365e-09 | 4.1051e-09 | -3.0112e-12 | 3.374e-10 | -3.5302e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1991 | 1.0519 | 1.0505 | 1.1991 | 1.0519 | 1.0505 | -0.035676 | -115.4386 | 115.2208 | -0.035676 | -115.4386 | 115.2208
Line1_1_3 | 0.0032375 | 0.0032375 | 0.0032375 | 0.0032375 | 0.0032375 | 0.0032375 | 0.00074767 | 0.00074767 | 0.00074767 | 0.00074767 | 0.00074767 | 0.00074767 | 0.00063227 | 0.00026572 | -0.00073996 | -0.00063222 | -0.00026567 | 0.00074002 | 0.00063559 | -0.00074019 | 0.00026339 | -0.0006355 | 0.0007403 | -0.00026328 | -45.1859 | -45.1859 | -45.1859 | 134.8136 | 134.8136 | 134.8136 |  | 1.1991 | 1.0519 | 1.0505 | 1.1989 | 1.052 | 1.0505 | -0.035676 | -115.4386 | 115.2208 | -0.038026 | -115.4448 | 115.2293
Line2_1_4 | 0.0032717 | 0.032892 | 0.032853 | 0.0032717 | 0.032892 | 0.032853 | 0.00075556 | 0.0075961 | 0.007587 | 0.00075556 | 0.0075961 | 0.007587 | 0.00064113 | 0.0061198 | 0.0050991 | -0.00064092 | -0.0061113 | -0.0050867 | 0.00064012 | 0.0051371 | 0.0061258 | -0.0006397 | -0.0051152 | -0.0061059 | -44.9901 | -155.4496 | 64.9949 | 135.0094 | 24.5504 | -115.0051 |  | 1.1991 | 1.0519 | 1.0505 | 1.1985 | 1.0492 | 1.0475 | -0.035676 | -115.4386 | 115.2208 | -0.045192 | -115.5201 | 115.1981
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.7548e-10 | -1.6247e-08 | 1.5546e-08 | -8.734e-10 | 8.2955e-09 | -7.5973e-09 | -2.006e-08 | 6.8731e-09 | 8.2102e-09 | 1.0027e-08 | -3.0991e-09 | -4.4581e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1991 | 1.0519 | 1.0505 | 1.1991 | 1.0519 | 1.0505 | -0.035676 | -115.4386 | 115.2208 | -0.035676 | -115.4386 | 115.2208
Line4_2_6 | 0.0032472 | 0.0032472 | 0.0032472 | 0.0032473 | 0.0032473 | 0.0032473 | 0.00074992 | 0.00074992 | 0.00074992 | 0.00074992 | 0.00074992 | 0.00074992 | 0.00063473 | 0.00026575 | -0.00074199 | -0.00063468 | -0.00026571 | 0.00074205 | 0.00063679 | -0.00074278 | 0.00026479 | -0.0006367 | 0.00074289 | -0.00026468 | -45.1307 | -45.1307 | -45.1307 | 134.8688 | 134.8688 | 134.8688 |  | 1.1989 | 1.052 | 1.0505 | 1.1988 | 1.0521 | 1.0506 | -0.03804 | -115.4448 | 115.2293 | -0.040404 | -115.451 | 115.2378
Line5_6_7 | 0.0032473 | 0.0032473 | 0.0032473 | 0.0032473 | 0.0032473 | 0.0032473 | 0.00074992 | 0.00074992 | 0.00074992 | 0.00074993 | 0.00074993 | 0.00074993 | 0.00063468 | 0.00026571 | -0.00074205 | -0.00063463 | -0.00026566 | 0.00074211 | 0.0006367 | -0.00074289 | 0.00026468 | -0.0006366 | 0.000743 | -0.00026457 | -45.1312 | -45.1312 | -45.1312 | 134.8683 | 134.8683 | 134.8683 |  | 1.1988 | 1.0521 | 1.0506 | 1.1986 | 1.0522 | 1.0506 | -0.040404 | -115.451 | 115.2378 | -0.042769 | -115.4571 | 115.2463
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3478e-09 | -2.428e-08 | 2.3192e-08 | -1.3321e-09 | 1.6358e-08 | -1.5286e-08 | -2.9942e-08 | 1.0238e-08 | 1.2306e-08 | 1.9958e-08 | -6.4894e-09 | -8.5551e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1986 | 1.0522 | 1.0506 | 1.1986 | 1.0522 | 1.0506 | -0.042769 | -115.4571 | 115.2463 | -0.042769 | -115.4571 | 115.2463
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4927e-10 | -8.0934e-09 | 7.7308e-09 | -4.3353e-10 | 1.7112e-10 | 1.7579e-10 | -9.9808e-09 | 3.4128e-09 | 4.102e-09 | -3.6088e-12 | 3.3613e-10 | -3.5116e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1986 | 1.0522 | 1.0506 | 1.1986 | 1.0522 | 1.0506 | -0.042769 | -115.4571 | 115.2463 | -0.042769 | -115.4571 | 115.2463
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4927e-10 | -8.0934e-09 | 7.7308e-09 | -4.3353e-10 | 1.7112e-10 | 1.7579e-10 | -9.9808e-09 | 3.4128e-09 | 4.102e-09 | -3.6088e-12 | 3.3613e-10 | -3.5116e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1986 | 1.0522 | 1.0506 | 1.1986 | 1.0522 | 1.0506 | -0.042769 | -115.4571 | 115.2463 | -0.042769 | -115.4571 | 115.2463
Line9_3_11 | 0.0032375 | 0.0032375 | 0.0032375 | 0.0032375 | 0.0032375 | 0.0032375 | 0.00074767 | 0.00074767 | 0.00074767 | 0.00074768 | 0.00074768 | 0.00074768 | 0.00063222 | 0.00026567 | -0.00074002 | -0.00063216 | -0.00026563 | 0.00074008 | 0.0006355 | -0.0007403 | 0.00026328 | -0.0006354 | 0.00074041 | -0.00026317 | -45.1864 | -45.1864 | -45.1864 | 134.8131 | 134.8131 | 134.8131 |  | 1.1989 | 1.052 | 1.0505 | 1.1988 | 1.0521 | 1.0506 | -0.038026 | -115.4448 | 115.2293 | -0.040376 | -115.4509 | 115.2378

## LLG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.01504 | 0.01504 | 0.01504 | 0.015041 | 0.015041 | 0.015041 | 0.0034734 | 0.0034734 | 0.0034734 | 0.0034735 | 0.0034735 | 0.0034735 | 0.0034609 | 0.0011333 | -0.0011812 | -0.0034588 | -0.0011312 | 0.0011834 | 0.0034634 | -0.001766 | 0.0017162 | -0.0034612 | 0.0017683 | -0.001714 | -45.2129 | -45.2129 | -45.2129 | 134.7866 | 134.7867 | 134.7866 |  | 1.4096 | 0.60413 | 0.59981 | 1.4087 | 0.60434 | 0.59962 | -0.19243 | -102.5231 | 79.3245 | -0.19316 | -102.6063 | 79.409
Line10_11_12 | 0.014982 | 0.014982 | 0.014982 | 0.014982 | 0.014982 | 0.014982 | 0.00346 | 0.00346 | 0.00346 | 0.00346 | 0.00346 | 0.00346 | 0.0034429 | 0.0011248 | -0.001181 | -0.0034408 | -0.0011226 | 0.0011832 | 0.0034457 | -0.0017636 | 0.001705 | -0.0034436 | 0.0017658 | -0.0017027 | -45.2174 | -45.2174 | -45.2175 | 134.7821 | 134.7821 | 134.7821 |  | 1.4078 | 0.60455 | 0.59945 | 1.4069 | 0.60476 | 0.59927 | -0.19389 | -102.6888 | 79.4929 | -0.19462 | -102.7716 | 79.5772
Line11_12_13 | 0.014982 | 0.014982 | 0.014982 | 0.014982 | 0.014982 | 0.014982 | 0.00346 | 0.00346 | 0.00346 | 0.00346 | 0.00346 | 0.00346 | 0.0034408 | 0.0011226 | -0.0011832 | -0.0034386 | -0.0011205 | 0.0011854 | 0.0034436 | -0.0017658 | 0.0017027 | -0.0034414 | 0.0017681 | -0.0017005 | -45.2179 | -45.2179 | -45.2179 | 134.7816 | 134.7817 | 134.7816 |  | 1.4069 | 0.60476 | 0.59927 | 1.406 | 0.60498 | 0.59909 | -0.19462 | -102.7716 | 79.5772 | -0.19536 | -102.8544 | 79.6615
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.1172e-09 | -7.0211e-08 | 6.7308e-08 | -7.0959e-09 | 4.7479e-08 | -4.4597e-08 | -1.6238e-07 | 1.3425e-08 | -8.1088e-09 | 1.0824e-07 | -8.329e-09 | 4.0551e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.406 | 0.60498 | 0.59909 | 1.406 | 0.60498 | 0.59909 | -0.19536 | -102.8544 | 79.6615 | -0.19536 | -102.8544 | 79.6615
Line13_13_14 | 0.014983 | 0.014983 | 0.014983 | 0.014983 | 0.014983 | 0.014983 | 0.0034601 | 0.0034601 | 0.0034601 | 0.0034601 | 0.0034601 | 0.0034601 | 0.0034386 | 0.0011206 | -0.0011855 | -0.0034364 | -0.0011184 | 0.0011876 | 0.0034415 | -0.0017681 | 0.0017005 | -0.0034393 | 0.0017703 | -0.0016982 | -45.2198 | -45.2198 | -45.2198 | 134.7798 | 134.7798 | 134.7798 |  | 1.406 | 0.60498 | 0.59909 | 1.4051 | 0.60519 | 0.59892 | -0.19536 | -102.8544 | 79.6615 | -0.19609 | -102.9371 | 79.7459
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7448e-09 | -4.6807e-08 | 4.4872e-08 | -4.7234e-09 | 2.4075e-08 | -2.2161e-08 | -1.0825e-07 | 8.9502e-09 | -5.4059e-09 | 5.4109e-08 | -3.8539e-09 | 1.3521e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.406 | 0.60498 | 0.59909 | 1.406 | 0.60498 | 0.59909 | -0.19536 | -102.8544 | 79.6615 | -0.19536 | -102.8544 | 79.6615
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3724e-09 | -2.3404e-08 | 2.2436e-08 | -2.351e-09 | 6.7169e-10 | 2.7465e-10 | -5.4126e-08 | 4.4751e-09 | -2.703e-09 | -1.6699e-11 | 6.2125e-10 | -1.3508e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.406 | 0.60498 | 0.59909 | 1.406 | 0.60498 | 0.59909 | -0.19536 | -102.8544 | 79.6615 | -0.19536 | -102.8544 | 79.6615
Line16_4_18 | 0 | 2.5224 | 2.493 | 0 | 2.5224 | 2.493 | 0 | 0.58253 | 0.57572 | 0 | 0.58253 | 0.57572 | 2.3422e-09 | 0.12079 | 0.12064 | -2.3323e-09 | -1.1569e-14 | -2.008e-14 | -5.492e-08 | 0.12804 | 0.12345 | -1.686e-11 | -1.1741e-15 | 3.9093e-14 | 0 | -149.2754 | 33.7498 | 0 | 30.7246 | -146.2503 |  | 1.406 | 0.30217 | 0.29981 | 1.4033 | 0 | 0 | -0.1954 | -102.6071 | 79.4099 | -0.19763 | 0 | 0
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3914e-09 | -2.3575e-08 | 2.2625e-08 | -2.3756e-09 | 6.6901e-10 | 2.6543e-10 | -5.4689e-08 | 4.3683e-09 | -2.8669e-09 | -1.6491e-11 | 6.3199e-10 | -1.3618e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.4096 | 0.60413 | 0.59981 | 1.4096 | 0.60413 | 0.59981 | -0.19243 | -102.5231 | 79.3245 | -0.19243 | -102.5231 | 79.3245
Line1_1_3 | 0.014982 | 0.014982 | 0.014982 | 0.014982 | 0.014982 | 0.014982 | 0.0034599 | 0.0034599 | 0.0034599 | 0.0034599 | 0.0034599 | 0.0034599 | 0.0034472 | 0.001129 | -0.0011767 | -0.0034451 | -0.0011269 | 0.0011789 | 0.0034501 | -0.0017591 | 0.0017094 | -0.0034479 | 0.0017613 | -0.0017072 | -45.2165 | -45.2164 | -45.2165 | 134.7831 | 134.7831 | 134.783 |  | 1.4096 | 0.60413 | 0.59981 | 1.4087 | 0.60434 | 0.59963 | -0.19243 | -102.5231 | 79.3245 | -0.19316 | -102.606 | 79.4087
Line2_1_4 | 0.015188 | 2.5188 | 2.4959 | 0.015188 | 2.5188 | 2.4959 | 0.0035076 | 0.58169 | 0.57641 | 0.0035076 | 0.58169 | 0.57641 | 0.0034955 | 0.24227 | 0.24053 | -0.0034867 | -0.12136 | -0.12004 | 0.0034968 | 0.25456 | 0.24835 | -0.0034877 | -0.12715 | -0.12432 | -45.2034 | -148.9403 | 33.4076 | 134.7961 | 31.0597 | -146.5925 |  | 1.4096 | 0.60413 | 0.59981 | 1.406 | 0.30217 | 0.29981 | -0.19243 | -102.5231 | 79.3245 | -0.1954 | -102.6071 | 79.4099
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7827e-09 | -4.715e-08 | 4.525e-08 | -4.767e-09 | 2.4244e-08 | -2.236e-08 | -1.0938e-07 | 8.7366e-09 | -5.7338e-09 | 5.4673e-08 | -3.7363e-09 | 1.5052e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.4096 | 0.60413 | 0.59981 | 1.4096 | 0.60413 | 0.59981 | -0.19243 | -102.5231 | 79.3245 | -0.19243 | -102.5231 | 79.3245
Line4_2_6 | 0.015041 | 0.015041 | 0.015041 | 0.015041 | 0.015041 | 0.015041 | 0.0034735 | 0.0034735 | 0.0034735 | 0.0034735 | 0.0034735 | 0.0034735 | 0.0034588 | 0.0011312 | -0.0011834 | -0.0034566 | -0.001129 | 0.0011856 | 0.0034612 | -0.0017683 | 0.0017139 | -0.003459 | 0.0017706 | -0.0017117 | -45.2134 | -45.2134 | -45.2134 | 134.7862 | 134.7862 | 134.7861 |  | 1.4087 | 0.60434 | 0.59962 | 1.4078 | 0.60455 | 0.59944 | -0.19316 | -102.6063 | 79.409 | -0.1939 | -102.6895 | 79.4936
Line5_6_7 | 0.015041 | 0.015041 | 0.015041 | 0.015041 | 0.015041 | 0.015041 | 0.0034735 | 0.0034735 | 0.0034735 | 0.0034735 | 0.0034735 | 0.0034735 | 0.0034566 | 0.001129 | -0.0011856 | -0.0034544 | -0.0011269 | 0.0011878 | 0.003459 | -0.0017706 | 0.0017117 | -0.0034568 | 0.0017728 | -0.0017094 | -45.2139 | -45.2138 | -45.2139 | 134.7857 | 134.7857 | 134.7857 |  | 1.4078 | 0.60455 | 0.59944 | 1.4069 | 0.60477 | 0.59927 | -0.1939 | -102.6895 | 79.4936 | -0.19464 | -102.7726 | 79.5782
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.1313e-09 | -7.0338e-08 | 6.7448e-08 | -7.1113e-09 | 4.7563e-08 | -4.4693e-08 | -1.6279e-07 | 1.3347e-08 | -8.2298e-09 | 1.0851e-07 | -8.2739e-09 | 4.133e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.4069 | 0.60477 | 0.59927 | 1.4069 | 0.60477 | 0.59927 | -0.19464 | -102.7726 | 79.5782 | -0.19464 | -102.7726 | 79.5782
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3771e-09 | -2.3446e-08 | 2.2483e-08 | -2.3571e-09 | 6.7104e-10 | 2.7238e-10 | -5.4265e-08 | 4.4489e-09 | -2.7433e-09 | -1.6648e-11 | 6.239e-10 | -1.3535e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.4069 | 0.60477 | 0.59927 | 1.4069 | 0.60477 | 0.59927 | -0.19464 | -102.7726 | 79.5782 | -0.19464 | -102.7726 | 79.5782
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3771e-09 | -2.3446e-08 | 2.2483e-08 | -2.3571e-09 | 6.7104e-10 | 2.7238e-10 | -5.4265e-08 | 4.4489e-09 | -2.7433e-09 | -1.6648e-11 | 6.239e-10 | -1.3535e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.4069 | 0.60477 | 0.59927 | 1.4069 | 0.60477 | 0.59927 | -0.19464 | -102.7726 | 79.5782 | -0.19464 | -102.7726 | 79.5782
Line9_3_11 | 0.014982 | 0.014982 | 0.014982 | 0.014982 | 0.014982 | 0.014982 | 0.0034599 | 0.0034599 | 0.0034599 | 0.00346 | 0.00346 | 0.00346 | 0.0034451 | 0.0011269 | -0.0011789 | -0.0034429 | -0.0011248 | 0.001181 | 0.0034479 | -0.0017613 | 0.0017072 | -0.0034457 | 0.0017636 | -0.001705 | -45.217 | -45.2169 | -45.217 | 134.7826 | 134.7826 | 134.7826 |  | 1.4087 | 0.60434 | 0.59963 | 1.4078 | 0.60455 | 0.59945 | -0.19316 | -102.606 | 79.4087 | -0.19389 | -102.6888 | 79.4929

## LLG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.014249 | 0.014249 | 0.014249 | 0.014249 | 0.014249 | 0.014249 | 0.0032906 | 0.0032906 | 0.0032906 | 0.0032907 | 0.0032907 | 0.0032907 | 0.0031062 | 0.0010172 | -0.0010601 | -0.0031043 | -0.0010152 | 0.0010621 | 0.0031084 | -0.001585 | 0.0015403 | -0.0031064 | 0.0015871 | -0.0015383 | -45.2129 | -45.2129 | -45.2129 | 134.7866 | 134.7867 | 134.7866 |  | 1.3354 | 0.57233 | 0.56824 | 1.3346 | 0.57253 | 0.56807 | -0.19243 | -102.5231 | 79.3245 | -0.19316 | -102.6063 | 79.409
Line10_11_12 | 0.014194 | 0.014194 | 0.014194 | 0.014194 | 0.014194 | 0.014194 | 0.0032779 | 0.0032779 | 0.0032779 | 0.0032779 | 0.0032779 | 0.0032779 | 0.00309 | 0.0010095 | -0.00106 | -0.0030881 | -0.0010076 | 0.0010619 | 0.0030926 | -0.0015828 | 0.0015302 | -0.0030906 | 0.0015848 | -0.0015282 | -45.2174 | -45.2174 | -45.2175 | 134.7821 | 134.7821 | 134.7821 |  | 1.3337 | 0.57273 | 0.5679 | 1.3329 | 0.57293 | 0.56773 | -0.19389 | -102.6888 | 79.4929 | -0.19462 | -102.7716 | 79.5772
Line11_12_13 | 0.014194 | 0.014194 | 0.014194 | 0.014194 | 0.014194 | 0.014194 | 0.0032779 | 0.0032779 | 0.0032779 | 0.0032779 | 0.0032779 | 0.0032779 | 0.0030881 | 0.0010076 | -0.0010619 | -0.0030862 | -0.0010057 | 0.0010639 | 0.0030906 | -0.0015848 | 0.0015282 | -0.0030886 | 0.0015869 | -0.0015262 | -45.2179 | -45.2179 | -45.2179 | 134.7816 | 134.7817 | 134.7816 |  | 1.3329 | 0.57293 | 0.56773 | 1.332 | 0.57314 | 0.56756 | -0.19462 | -102.7716 | 79.5772 | -0.19536 | -102.8544 | 79.6615
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.3878e-09 | -6.3015e-08 | 6.0409e-08 | -6.3686e-09 | 4.2613e-08 | -4.0026e-08 | -1.4574e-07 | 1.2049e-08 | -7.2777e-09 | 9.7142e-08 | -7.4753e-09 | 3.6395e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.332 | 0.57314 | 0.56756 | 1.332 | 0.57314 | 0.56756 | -0.19536 | -102.8544 | 79.6615 | -0.19536 | -102.8544 | 79.6615
Line13_13_14 | 0.014194 | 0.014194 | 0.014194 | 0.014194 | 0.014194 | 0.014194 | 0.003278 | 0.003278 | 0.003278 | 0.003278 | 0.003278 | 0.003278 | 0.0030862 | 0.0010057 | -0.001064 | -0.0030842 | -0.0010038 | 0.0010659 | 0.0030888 | -0.0015869 | 0.0015262 | -0.0030868 | 0.0015889 | -0.0015242 | -45.2198 | -45.2198 | -45.2198 | 134.7798 | 134.7798 | 134.7798 |  | 1.332 | 0.57314 | 0.56756 | 1.3312 | 0.57334 | 0.56739 | -0.19536 | -102.8544 | 79.6615 | -0.19609 | -102.9371 | 79.7459
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2585e-09 | -4.201e-08 | 4.0273e-08 | -4.2393e-09 | 2.1608e-08 | -1.989e-08 | -9.7157e-08 | 8.0329e-09 | -4.8518e-09 | 4.8563e-08 | -3.4589e-09 | 1.2136e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.332 | 0.57314 | 0.56756 | 1.332 | 0.57314 | 0.56756 | -0.19536 | -102.8544 | 79.6615 | -0.19536 | -102.8544 | 79.6615
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1293e-09 | -2.1005e-08 | 2.0136e-08 | -2.1101e-09 | 6.0285e-10 | 2.465e-10 | -4.8578e-08 | 4.0164e-09 | -2.4259e-09 | -1.4987e-11 | 5.5757e-10 | -1.2124e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.332 | 0.57314 | 0.56756 | 1.332 | 0.57314 | 0.56756 | -0.19536 | -102.8544 | 79.6615 | -0.19536 | -102.8544 | 79.6615
Line16_4_18 | 0 | 2.3897 | 2.3618 | 0 | 2.3897 | 2.3618 | 0 | 0.55187 | 0.54542 | 0 | 0.55187 | 0.54542 | 2.1022e-09 | 0.10841 | 0.10827 | -2.0933e-09 | -1.0555e-14 | -1.7561e-14 | -4.9291e-08 | 0.11492 | 0.1108 | -1.5132e-11 | -3.8479e-15 | 3.7806e-14 | 0 | -149.2754 | 33.7498 | 0 | 30.7246 | -146.2503 |  | 1.332 | 0.28627 | 0.28403 | 1.3294 | 0 | 0 | -0.1954 | -102.6071 | 79.4099 | -0.19763 | 0 | 0
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1463e-09 | -2.1159e-08 | 2.0306e-08 | -2.1322e-09 | 6.0044e-10 | 2.3822e-10 | -4.9084e-08 | 3.9206e-09 | -2.5731e-09 | -1.4801e-11 | 5.6722e-10 | -1.2222e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3354 | 0.57233 | 0.56824 | 1.3354 | 0.57233 | 0.56824 | -0.19243 | -102.5231 | 79.3245 | -0.19243 | -102.5231 | 79.3245
Line1_1_3 | 0.014193 | 0.014193 | 0.014193 | 0.014193 | 0.014193 | 0.014193 | 0.0032778 | 0.0032778 | 0.0032778 | 0.0032778 | 0.0032778 | 0.0032778 | 0.0030939 | 0.0010133 | -0.0010561 | -0.003092 | -0.0010114 | 0.001058 | 0.0030965 | -0.0015788 | 0.0015342 | -0.0030945 | 0.0015808 | -0.0015322 | -45.2165 | -45.2164 | -45.2165 | 134.7831 | 134.7831 | 134.783 |  | 1.3354 | 0.57233 | 0.56824 | 1.3346 | 0.57253 | 0.56807 | -0.19243 | -102.5231 | 79.3245 | -0.19316 | -102.606 | 79.4087
Line2_1_4 | 0.014389 | 2.3862 | 2.3646 | 0.014389 | 2.3862 | 2.3646 | 0.003323 | 0.55108 | 0.54607 | 0.003323 | 0.55108 | 0.54607 | 0.0031372 | 0.21744 | 0.21587 | -0.0031293 | -0.10892 | -0.10774 | 0.0031384 | 0.22847 | 0.2229 | -0.0031303 | -0.11412 | -0.11157 | -45.2034 | -148.9403 | 33.4076 | 134.7961 | 31.0597 | -146.5925 |  | 1.3354 | 0.57233 | 0.56824 | 1.332 | 0.28627 | 0.28403 | -0.19243 | -102.5231 | 79.3245 | -0.1954 | -102.6071 | 79.4099
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2925e-09 | -4.2318e-08 | 4.0612e-08 | -4.2784e-09 | 2.1759e-08 | -2.0068e-08 | -9.8168e-08 | 7.8412e-09 | -5.1462e-09 | 4.9069e-08 | -3.3534e-09 | 1.3509e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3354 | 0.57233 | 0.56824 | 1.3354 | 0.57233 | 0.56824 | -0.19243 | -102.5231 | 79.3245 | -0.19243 | -102.5231 | 79.3245
Line4_2_6 | 0.014249 | 0.014249 | 0.014249 | 0.014249 | 0.014249 | 0.014249 | 0.0032907 | 0.0032907 | 0.0032907 | 0.0032907 | 0.0032907 | 0.0032907 | 0.0031043 | 0.0010152 | -0.0010621 | -0.0031023 | -0.0010133 | 0.001064 | 0.0031064 | -0.0015871 | 0.0015383 | -0.0031045 | 0.0015891 | -0.0015363 | -45.2134 | -45.2134 | -45.2134 | 134.7862 | 134.7862 | 134.7861 |  | 1.3346 | 0.57253 | 0.56807 | 1.3337 | 0.57273 | 0.56789 | -0.19316 | -102.6063 | 79.409 | -0.1939 | -102.6895 | 79.4936
Line5_6_7 | 0.014249 | 0.014249 | 0.014249 | 0.014249 | 0.014249 | 0.014249 | 0.0032907 | 0.0032907 | 0.0032907 | 0.0032907 | 0.0032907 | 0.0032907 | 0.0031023 | 0.0010133 | -0.001064 | -0.0031004 | -0.0010114 | 0.001066 | 0.0031045 | -0.0015891 | 0.0015363 | -0.0031025 | 0.0015911 | -0.0015342 | -45.2139 | -45.2138 | -45.2139 | 134.7857 | 134.7857 | 134.7857 |  | 1.3337 | 0.57273 | 0.56789 | 1.3329 | 0.57294 | 0.56773 | -0.1939 | -102.6895 | 79.4936 | -0.19464 | -102.7726 | 79.5782
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.4004e-09 | -6.3129e-08 | 6.0535e-08 | -6.3824e-09 | 4.2688e-08 | -4.0112e-08 | -1.4611e-07 | 1.1979e-08 | -7.3863e-09 | 9.7391e-08 | -7.4259e-09 | 3.7094e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3329 | 0.57294 | 0.56773 | 1.3329 | 0.57294 | 0.56773 | -0.19464 | -102.7726 | 79.5782 | -0.19464 | -102.7726 | 79.5782
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1335e-09 | -2.1043e-08 | 2.0178e-08 | -2.1155e-09 | 6.0226e-10 | 2.4446e-10 | -4.8703e-08 | 3.9929e-09 | -2.4621e-09 | -1.4942e-11 | 5.5996e-10 | -1.2148e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3329 | 0.57294 | 0.56773 | 1.3329 | 0.57294 | 0.56773 | -0.19464 | -102.7726 | 79.5782 | -0.19464 | -102.7726 | 79.5782
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1335e-09 | -2.1043e-08 | 2.0178e-08 | -2.1155e-09 | 6.0226e-10 | 2.4446e-10 | -4.8703e-08 | 3.9929e-09 | -2.4621e-09 | -1.4942e-11 | 5.5996e-10 | -1.2148e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3329 | 0.57294 | 0.56773 | 1.3329 | 0.57294 | 0.56773 | -0.19464 | -102.7726 | 79.5782 | -0.19464 | -102.7726 | 79.5782
Line9_3_11 | 0.014193 | 0.014193 | 0.014193 | 0.014194 | 0.014194 | 0.014194 | 0.0032778 | 0.0032778 | 0.0032778 | 0.0032779 | 0.0032779 | 0.0032779 | 0.003092 | 0.0010114 | -0.001058 | -0.00309 | -0.0010095 | 0.00106 | 0.0030945 | -0.0015808 | 0.0015322 | -0.0030926 | 0.0015828 | -0.0015302 | -45.217 | -45.2169 | -45.217 | 134.7826 | 134.7826 | 134.7826 |  | 1.3346 | 0.57253 | 0.56807 | 1.3337 | 0.57273 | 0.5679 | -0.19316 | -102.606 | 79.4087 | -0.19389 | -102.6888 | 79.4929

## LLG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.0028001 | 0.0028001 | 0.0028001 | 0.0028001 | 0.0028001 | 0.0028001 | 0.00064666 | 0.00064666 | 0.00064666 | 0.00064666 | 0.00064666 | 0.00064666 | 0.00047346 | 0.00019709 | -0.00055225 | -0.00047339 | -0.00019702 | 0.00055234 | 0.00047358 | -0.0005534 | 0.00019814 | -0.00047351 | 0.00055348 | -0.00019806 | -45.0415 | -45.0415 | -45.0415 | 134.958 | 134.958 | 134.958 |  | 1.0356 | 0.90844 | 0.90732 | 1.0354 | 0.90852 | 0.90739 | -0.034603 | -115.4385 | 115.2215 | -0.034792 | -115.448 | 115.2312
Line10_11_12 | 0.0027892 | 0.0027892 | 0.0027892 | 0.0027893 | 0.0027893 | 0.0027893 | 0.00064415 | 0.00064415 | 0.00064415 | 0.00064415 | 0.00064415 | 0.00064415 | 0.00047144 | 0.00019622 | -0.00055028 | -0.00047136 | -0.00019615 | 0.00055036 | 0.00047162 | -0.00055139 | 0.00019717 | -0.00047155 | 0.00055147 | -0.00019709 | -45.046 | -45.046 | -45.046 | 134.9535 | 134.9535 | 134.9535 |  | 1.0352 | 0.90859 | 0.90745 | 1.0351 | 0.90866 | 0.90752 | -0.034978 | -115.4574 | 115.2408 | -0.035165 | -115.4669 | 115.2505
Line11_12_13 | 0.0027893 | 0.0027893 | 0.0027893 | 0.0027893 | 0.0027893 | 0.0027893 | 0.00064415 | 0.00064415 | 0.00064415 | 0.00064416 | 0.00064416 | 0.00064416 | 0.00047136 | 0.00019615 | -0.00055036 | -0.00047129 | -0.00019608 | 0.00055044 | 0.00047155 | -0.00055147 | 0.00019709 | -0.00047148 | 0.00055155 | -0.00019701 | -45.0465 | -45.0465 | -45.0465 | 134.953 | 134.953 | 134.953 |  | 1.0351 | 0.90866 | 0.90752 | 1.0349 | 0.90874 | 0.90759 | -0.035165 | -115.4669 | 115.2505 | -0.035352 | -115.4763 | 115.2601
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.7086e-10 | -1.8034e-08 | 1.7255e-08 | -9.6941e-10 | 1.215e-08 | -1.1373e-08 | -2.2251e-08 | 7.6434e-09 | 9.1276e-09 | 1.4832e-08 | -4.8459e-09 | -6.3463e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0349 | 0.90874 | 0.90759 | 1.0349 | 0.90874 | 0.90759 | -0.035352 | -115.4763 | 115.2601 | -0.035353 | -115.4763 | 115.2601
Line13_13_14 | 0.0027893 | 0.0027893 | 0.0027893 | 0.0027894 | 0.0027894 | 0.0027894 | 0.00064417 | 0.00064417 | 0.00064417 | 0.00064418 | 0.00064418 | 0.00064418 | 0.00047129 | 0.0001961 | -0.00055045 | -0.00047121 | -0.00019603 | 0.00055053 | 0.0004715 | -0.00055156 | 0.000197 | -0.00047143 | 0.00055164 | -0.00019692 | -45.0484 | -45.0484 | -45.0484 | 134.9511 | 134.9511 | 134.9511 |  | 1.0349 | 0.90874 | 0.90759 | 1.0347 | 0.90881 | 0.90766 | -0.035352 | -115.4763 | 115.2601 | -0.035539 | -115.4857 | 115.2698
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.4724e-10 | -1.2022e-08 | 1.1504e-08 | -6.4579e-10 | 6.1388e-09 | -5.6215e-09 | -1.4834e-08 | 5.0956e-09 | 6.0851e-09 | 7.4148e-09 | -2.2981e-09 | -3.3038e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0349 | 0.90874 | 0.90759 | 1.0349 | 0.90874 | 0.90759 | -0.035353 | -115.4763 | 115.2601 | -0.035353 | -115.4763 | 115.2601
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2362e-10 | -6.0112e-09 | 5.7518e-09 | -3.2217e-10 | 1.2762e-10 | 1.3032e-10 | -7.417e-09 | 2.5478e-09 | 3.0425e-09 | -2.2243e-12 | 2.4966e-10 | -2.6124e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0349 | 0.90874 | 0.90759 | 1.0349 | 0.90874 | 0.90759 | -0.035353 | -115.4763 | 115.2601 | -0.035353 | -115.4763 | 115.2601
Line16_4_18 | 0 | 0.029456 | 0.029418 | 0 | 0.029456 | 0.029418 | 0 | 0.0068025 | 0.0067938 | 0 | 0.0068025 | 0.0067938 | 3.1947e-10 | 0.0043516 | 0.0043449 | -3.2007e-10 | -0.0043382 | -0.0043271 | -7.5259e-09 | 0.0043567 | 0.0043412 | -2.2596e-12 | -0.0043382 | -0.0043271 | 0 | -160.5142 | 70.2805 | 0 | 19.4858 | -109.7196 |  | 1.0349 | 0.90521 | 0.90406 | 1.0344 | 0.9019 | 0.90074 | -0.035364 | -115.481 | 115.2558 | -0.035933 | -115.5142 | 115.2805
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2529e-10 | -6.0575e-09 | 5.7977e-09 | -3.2492e-10 | 1.2841e-10 | 1.3101e-10 | -7.4799e-09 | 2.5638e-09 | 3.0606e-09 | -2.1786e-12 | 2.5166e-10 | -2.6328e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0356 | 0.90844 | 0.90732 | 1.0356 | 0.90844 | 0.90732 | -0.034603 | -115.4385 | 115.2215 | -0.034603 | -115.4385 | 115.2215
Line1_1_3 | 0.0027892 | 0.0027892 | 0.0027892 | 0.0027892 | 0.0027892 | 0.0027892 | 0.00064414 | 0.00064414 | 0.00064414 | 0.00064414 | 0.00064414 | 0.00064414 | 0.00047159 | 0.00019636 | -0.00055011 | -0.00047151 | -0.00019629 | 0.0005502 | 0.00047176 | -0.00055123 | 0.00019733 | -0.00047169 | 0.00055131 | -0.00019725 | -45.0451 | -45.0451 | -45.0451 | 134.9544 | 134.9544 | 134.9544 |  | 1.0356 | 0.90844 | 0.90732 | 1.0354 | 0.90852 | 0.90739 | -0.034603 | -115.4385 | 115.2215 | -0.034791 | -115.448 | 115.2312
Line2_1_4 | 0.0028276 | 0.028354 | 0.028325 | 0.0028276 | 0.028354 | 0.028325 | 0.00065301 | 0.0065482 | 0.0065413 | 0.00065301 | 0.0065482 | 0.0065413 | 0.00047819 | 0.0045629 | 0.0038055 | -0.00047789 | -0.0045495 | -0.0037892 | 0.00047815 | 0.0038166 | 0.0045544 | -0.00047784 | -0.0037996 | -0.0045403 | -45.0321 | -155.3493 | 65.1028 | 134.9675 | 24.6508 | -114.8972 |  | 1.0356 | 0.90844 | 0.90732 | 1.0349 | 0.90521 | 0.90406 | -0.034603 | -115.4385 | 115.2215 | -0.035364 | -115.481 | 115.2558
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.5059e-10 | -1.2115e-08 | 1.1595e-08 | -6.5021e-10 | 6.1859e-09 | -5.6667e-09 | -1.496e-08 | 5.1276e-09 | 6.1211e-09 | 7.4777e-09 | -2.3121e-09 | -3.3238e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0356 | 0.90844 | 0.90732 | 1.0356 | 0.90844 | 0.90732 | -0.034603 | -115.4385 | 115.2215 | -0.034603 | -115.4385 | 115.2215
Line4_2_6 | 0.0028001 | 0.0028001 | 0.0028001 | 0.0028001 | 0.0028001 | 0.0028001 | 0.00064666 | 0.00064666 | 0.00064666 | 0.00064667 | 0.00064667 | 0.00064667 | 0.00047339 | 0.00019702 | -0.00055234 | -0.00047331 | -0.00019695 | 0.00055242 | 0.00047351 | -0.00055348 | 0.00019806 | -0.00047343 | 0.00055356 | -0.00019797 | -45.042 | -45.042 | -45.042 | 134.9575 | 134.9575 | 134.9575 |  | 1.0354 | 0.90852 | 0.90739 | 1.0352 | 0.90859 | 0.90745 | -0.034792 | -115.448 | 115.2312 | -0.03498 | -115.4575 | 115.2409
Line5_6_7 | 0.0028001 | 0.0028001 | 0.0028001 | 0.0028002 | 0.0028002 | 0.0028002 | 0.00064667 | 0.00064667 | 0.00064667 | 0.00064667 | 0.00064667 | 0.00064667 | 0.00047331 | 0.00019695 | -0.00055242 | -0.00047324 | -0.00019688 | 0.0005525 | 0.00047343 | -0.00055356 | 0.00019797 | -0.00047336 | 0.00055364 | -0.00019789 | -45.0425 | -45.0425 | -45.0425 | 134.9571 | 134.9571 | 134.9571 |  | 1.0352 | 0.90859 | 0.90745 | 1.0351 | 0.90867 | 0.90752 | -0.03498 | -115.4575 | 115.2409 | -0.035169 | -115.467 | 115.2506
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.7211e-10 | -1.8068e-08 | 1.7289e-08 | -9.7092e-10 | 1.2173e-08 | -1.1396e-08 | -2.2298e-08 | 7.6553e-09 | 9.141e-09 | 1.4863e-08 | -4.8534e-09 | -6.3558e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0351 | 0.90867 | 0.90752 | 1.0351 | 0.90867 | 0.90752 | -0.035169 | -115.467 | 115.2506 | -0.035169 | -115.467 | 115.2506
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2404e-10 | -6.0226e-09 | 5.7631e-09 | -3.2284e-10 | 1.2782e-10 | 1.3049e-10 | -7.4325e-09 | 2.5518e-09 | 3.047e-09 | -2.2131e-12 | 2.5016e-10 | -2.6174e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0351 | 0.90867 | 0.90752 | 1.0351 | 0.90867 | 0.90752 | -0.035169 | -115.467 | 115.2506 | -0.035169 | -115.467 | 115.2506
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2404e-10 | -6.0226e-09 | 5.7631e-09 | -3.2284e-10 | 1.2781e-10 | 1.3049e-10 | -7.4325e-09 | 2.5518e-09 | 3.047e-09 | -2.213e-12 | 2.5016e-10 | -2.6174e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0351 | 0.90867 | 0.90752 | 1.0351 | 0.90867 | 0.90752 | -0.035169 | -115.467 | 115.2506 | -0.035169 | -115.467 | 115.2506
Line9_3_11 | 0.0027892 | 0.0027892 | 0.0027892 | 0.0027892 | 0.0027892 | 0.0027892 | 0.00064414 | 0.00064414 | 0.00064414 | 0.00064415 | 0.00064415 | 0.00064415 | 0.00047151 | 0.00019629 | -0.0005502 | -0.00047144 | -0.00019622 | 0.00055028 | 0.00047169 | -0.00055131 | 0.00019725 | -0.00047162 | 0.00055139 | -0.00019717 | -45.0456 | -45.0456 | -45.0456 | 134.954 | 134.954 | 134.954 |  | 1.0354 | 0.90852 | 0.90739 | 1.0352 | 0.90859 | 0.90745 | -0.034791 | -115.448 | 115.2312 | -0.034978 | -115.4574 | 115.2408

## LLG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.0026527 | 0.0026527 | 0.0026527 | 0.0026528 | 0.0026528 | 0.0026528 | 0.00061262 | 0.00061262 | 0.00061262 | 0.00061263 | 0.00061263 | 0.00061263 | 0.00042494 | 0.00017689 | -0.00049565 | -0.00042487 | -0.00017683 | 0.00049572 | 0.00042504 | -0.00049668 | 0.00017783 | -0.00042497 | 0.00049675 | -0.00017776 | -45.0415 | -45.0415 | -45.0415 | 134.958 | 134.958 | 134.958 |  | 0.98107 | 0.86063 | 0.85956 | 0.98091 | 0.8607 | 0.85963 | -0.034603 | -115.4385 | 115.2215 | -0.034792 | -115.448 | 115.2312
Line10_11_12 | 0.0026424 | 0.0026424 | 0.0026424 | 0.0026425 | 0.0026425 | 0.0026425 | 0.00061024 | 0.00061024 | 0.00061024 | 0.00061025 | 0.00061025 | 0.00061025 | 0.00042312 | 0.00017611 | -0.00049388 | -0.00042305 | -0.00017605 | 0.00049395 | 0.00042328 | -0.00049488 | 0.00017696 | -0.00042322 | 0.00049495 | -0.00017689 | -45.046 | -45.046 | -45.046 | 134.9535 | 134.9535 | 134.9535 |  | 0.98075 | 0.86077 | 0.85969 | 0.98059 | 0.86084 | 0.85976 | -0.034978 | -115.4574 | 115.2408 | -0.035165 | -115.4669 | 115.2505
Line11_12_13 | 0.0026425 | 0.0026425 | 0.0026425 | 0.0026425 | 0.0026425 | 0.0026425 | 0.00061025 | 0.00061025 | 0.00061025 | 0.00061025 | 0.00061025 | 0.00061025 | 0.00042305 | 0.00017605 | -0.00049395 | -0.00042298 | -0.00017598 | 0.00049402 | 0.00042322 | -0.00049495 | 0.00017689 | -0.00042316 | 0.00049502 | -0.00017682 | -45.0465 | -45.0465 | -45.0465 | 134.953 | 134.953 | 134.953 |  | 0.98059 | 0.86084 | 0.85976 | 0.98043 | 0.86091 | 0.85982 | -0.035165 | -115.4669 | 115.2505 | -0.035352 | -115.4763 | 115.2601
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.7135e-10 | -1.6185e-08 | 1.5487e-08 | -8.7005e-10 | 1.0905e-08 | -1.0208e-08 | -1.997e-08 | 6.86e-09 | 8.1921e-09 | 1.3312e-08 | -4.3493e-09 | -5.6959e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.98043 | 0.86091 | 0.85982 | 0.98043 | 0.86091 | 0.85982 | -0.035352 | -115.4763 | 115.2601 | -0.035353 | -115.4763 | 115.2601
Line13_13_14 | 0.0026425 | 0.0026425 | 0.0026425 | 0.0026426 | 0.0026426 | 0.0026426 | 0.00061027 | 0.00061027 | 0.00061027 | 0.00061027 | 0.00061027 | 0.00061027 | 0.00042298 | 0.000176 | -0.00049404 | -0.00042292 | -0.00017594 | 0.00049411 | 0.00042318 | -0.00049503 | 0.00017681 | -0.00042311 | 0.0004951 | -0.00017674 | -45.0484 | -45.0484 | -45.0484 | 134.9511 | 134.9511 | 134.9511 |  | 0.98043 | 0.86091 | 0.85982 | 0.98027 | 0.86098 | 0.85989 | -0.035352 | -115.4763 | 115.2601 | -0.035539 | -115.4857 | 115.2698
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.809e-10 | -1.079e-08 | 1.0325e-08 | -5.796e-10 | 5.5096e-09 | -5.0453e-09 | -1.3314e-08 | 4.5733e-09 | 5.4614e-09 | 6.6548e-09 | -2.0626e-09 | -2.9652e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.98043 | 0.86091 | 0.85982 | 0.98043 | 0.86091 | 0.85982 | -0.035353 | -115.4763 | 115.2601 | -0.035353 | -115.4763 | 115.2601
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9045e-10 | -5.3951e-09 | 5.1623e-09 | -2.8915e-10 | 1.1454e-10 | 1.1696e-10 | -6.6568e-09 | 2.2867e-09 | 2.7307e-09 | -1.9963e-12 | 2.2407e-10 | -2.3446e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.98043 | 0.86091 | 0.85982 | 0.98043 | 0.86091 | 0.85982 | -0.035353 | -115.4763 | 115.2601 | -0.035353 | -115.4763 | 115.2601
Line16_4_18 | 0 | 0.027906 | 0.02787 | 0 | 0.027906 | 0.02787 | 0 | 0.0064445 | 0.0064362 | 0 | 0.0064445 | 0.0064362 | 2.8673e-10 | 0.0039056 | 0.0038996 | -2.8727e-10 | -0.0038936 | -0.0038836 | -6.7546e-09 | 0.0039101 | 0.0038962 | -2.0281e-12 | -0.0038936 | -0.0038836 | 0 | -160.5142 | 70.2805 | 0 | 19.4858 | -109.7196 |  | 0.98043 | 0.85756 | 0.85648 | 0.97995 | 0.85443 | 0.85333 | -0.035364 | -115.481 | 115.2558 | -0.035933 | -115.5142 | 115.2805
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9195e-10 | -5.4366e-09 | 5.2034e-09 | -2.9161e-10 | 1.1525e-10 | 1.1758e-10 | -6.7133e-09 | 2.301e-09 | 2.7469e-09 | -1.9552e-12 | 2.2587e-10 | -2.3629e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.98107 | 0.86063 | 0.85956 | 0.98107 | 0.86063 | 0.85956 | -0.034603 | -115.4385 | 115.2215 | -0.034603 | -115.4385 | 115.2215
Line1_1_3 | 0.0026424 | 0.0026424 | 0.0026424 | 0.0026424 | 0.0026424 | 0.0026424 | 0.00061023 | 0.00061023 | 0.00061023 | 0.00061024 | 0.00061024 | 0.00061024 | 0.00042325 | 0.00017623 | -0.00049373 | -0.00042319 | -0.00017617 | 0.0004938 | 0.00042341 | -0.00049473 | 0.00017711 | -0.00042335 | 0.00049481 | -0.00017703 | -45.0451 | -45.0451 | -45.0451 | 134.9544 | 134.9544 | 134.9544 |  | 0.98107 | 0.86063 | 0.85956 | 0.98091 | 0.8607 | 0.85963 | -0.034603 | -115.4385 | 115.2215 | -0.034791 | -115.448 | 115.2312
Line2_1_4 | 0.0026788 | 0.026862 | 0.026834 | 0.0026788 | 0.026862 | 0.026834 | 0.00061864 | 0.0062035 | 0.006197 | 0.00061864 | 0.0062035 | 0.006197 | 0.00042918 | 0.0040952 | 0.0034155 | -0.00042891 | -0.0040832 | -0.0034008 | 0.00042914 | 0.0034254 | 0.0040876 | -0.00042886 | -0.0034102 | -0.004075 | -45.0321 | -155.3493 | 65.1028 | 134.9675 | 24.6508 | -114.8972 |  | 0.98107 | 0.86063 | 0.85956 | 0.98043 | 0.85756 | 0.85648 | -0.034603 | -115.4385 | 115.2215 | -0.035364 | -115.481 | 115.2558
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.8391e-10 | -1.0873e-08 | 1.0407e-08 | -5.8357e-10 | 5.5519e-09 | -5.0859e-09 | -1.3427e-08 | 4.602e-09 | 5.4938e-09 | 6.7113e-09 | -2.0752e-09 | -2.9832e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.98107 | 0.86063 | 0.85956 | 0.98107 | 0.86063 | 0.85956 | -0.034603 | -115.4385 | 115.2215 | -0.034603 | -115.4385 | 115.2215
Line4_2_6 | 0.0026527 | 0.0026527 | 0.0026527 | 0.0026528 | 0.0026528 | 0.0026528 | 0.00061263 | 0.00061263 | 0.00061263 | 0.00061263 | 0.00061263 | 0.00061263 | 0.00042487 | 0.00017683 | -0.00049572 | -0.0004248 | -0.00017676 | 0.0004958 | 0.00042497 | -0.00049675 | 0.00017776 | -0.00042491 | 0.00049683 | -0.00017768 | -45.042 | -45.042 | -45.042 | 134.9575 | 134.9575 | 134.9575 |  | 0.98091 | 0.8607 | 0.85963 | 0.98075 | 0.86077 | 0.85969 | -0.034792 | -115.448 | 115.2312 | -0.03498 | -115.4575 | 115.2409
Line5_6_7 | 0.0026528 | 0.0026528 | 0.0026528 | 0.0026528 | 0.0026528 | 0.0026528 | 0.00061263 | 0.00061263 | 0.00061263 | 0.00061264 | 0.00061264 | 0.00061264 | 0.0004248 | 0.00017676 | -0.0004958 | -0.00042473 | -0.0001767 | 0.00049587 | 0.00042491 | -0.00049683 | 0.00017768 | -0.00042485 | 0.0004969 | -0.00017761 | -45.0425 | -45.0425 | -45.0425 | 134.9571 | 134.9571 | 134.9571 |  | 0.98075 | 0.86077 | 0.85969 | 0.98059 | 0.86084 | 0.85976 | -0.03498 | -115.4575 | 115.2409 | -0.035169 | -115.467 | 115.2506
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.7247e-10 | -1.6216e-08 | 1.5517e-08 | -8.714e-10 | 1.0925e-08 | -1.0228e-08 | -2.0012e-08 | 6.8707e-09 | 8.2041e-09 | 1.334e-08 | -4.3559e-09 | -5.7043e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.98059 | 0.86084 | 0.85976 | 0.98059 | 0.86084 | 0.85976 | -0.035169 | -115.467 | 115.2506 | -0.035169 | -115.467 | 115.2506
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9082e-10 | -5.4053e-09 | 5.1724e-09 | -2.8976e-10 | 1.1471e-10 | 1.1712e-10 | -6.6707e-09 | 2.2902e-09 | 2.7347e-09 | -1.9863e-12 | 2.2452e-10 | -2.3491e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.98059 | 0.86084 | 0.85976 | 0.98059 | 0.86084 | 0.85976 | -0.035169 | -115.467 | 115.2506 | -0.035169 | -115.467 | 115.2506
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9082e-10 | -5.4053e-09 | 5.1724e-09 | -2.8975e-10 | 1.1471e-10 | 1.1712e-10 | -6.6707e-09 | 2.2902e-09 | 2.7347e-09 | -1.9863e-12 | 2.2452e-10 | -2.3491e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.98059 | 0.86084 | 0.85976 | 0.98059 | 0.86084 | 0.85976 | -0.035169 | -115.467 | 115.2506 | -0.035169 | -115.467 | 115.2506
Line9_3_11 | 0.0026424 | 0.0026424 | 0.0026424 | 0.0026424 | 0.0026424 | 0.0026424 | 0.00061024 | 0.00061024 | 0.00061024 | 0.00061024 | 0.00061024 | 0.00061024 | 0.00042319 | 0.00017617 | -0.0004938 | -0.00042312 | -0.00017611 | 0.00049388 | 0.00042335 | -0.00049481 | 0.00017703 | -0.00042328 | 0.00049488 | -0.00017696 | -45.0456 | -45.0456 | -45.0456 | 134.954 | 134.954 | 134.954 |  | 0.98091 | 0.8607 | 0.85963 | 0.98075 | 0.86077 | 0.85969 | -0.034791 | -115.448 | 115.2312 | -0.034978 | -115.4574 | 115.2408