## LLL_max_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 2.1767 | 2.1767 | 0 | 0 | 1.508 | 1.508 | 0.56854 | -0.42641 | 1.1371 | -0.85282 | -67.8829 | 112.1171 | 0.84302 | 0.63226 | -4.4479 | -4.4479
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84302 | 0.84302 | -4.4479 | -4.4479
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84302 | 0.84302 | -4.4479 | -4.4479
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84302 | 0.84302 | -4.4479 | -4.4479
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84302 | 0.84302 | -4.4479 | -4.4479
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84302 | 0.84302 | -4.4479 | -4.4479
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84302 | 0.84302 | -4.4479 | -4.4479
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84302 | 0.84302 | -4.4479 | -4.4479
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84302 | 0.84302 | -4.4479 | -4.4479
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84302 | 0.84302 | -4.4479 | -4.4479
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84302 | 0.84302 | -4.4479 | -4.4479
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84302 | 0.84302 | -4.4479 | -4.4479
Line4_2_6 | 2.1767 | 2.1767 | 0 | 0 | 1.508 | 1.508 | 0.42641 | -0.28427 | 0.85282 | -0.56854 | -67.8829 | 112.1171 | 0.63226 | 0.42151 | -4.4479 | -4.4479
Line5_6_7 | 2.1767 | 2.1767 | 0 | 0 | 1.508 | 1.508 | 0.28427 | -0.14214 | 0.56854 | -0.28427 | -67.8829 | 112.1171 | 0.42151 | 0.21075 | -4.4479 | -4.4479
Line6_7_8 | 2.1767 | 2.1767 | 0 | 4.0311 | 1.508 | 1.508 | 0.14214 | -1e-07 | 0.28427 | -1e-07 | -67.8829 | 112.1171 | 0.21075 | 0 | -4.4479 | 0
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4632e-22 | 0 | 4.2265e-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4632e-22 | 0 | 4.2265e-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84302 | 0.84302 | -4.4479 | -4.4479

## LLL_max_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 2.259 | 2.259 | 0 | 0 | 1.5651 | 1.5651 | 0.61237 | -0.45928 | 1.2247 | -0.91856 | -68.05 | 111.95 | 0.87491 | 0.65618 | -4.615 | -4.615
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87491 | 0.87491 | -4.615 | -4.615
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87491 | 0.87491 | -4.615 | -4.615
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87491 | 0.87491 | -4.615 | -4.615
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87491 | 0.87491 | -4.615 | -4.615
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87491 | 0.87491 | -4.615 | -4.615
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87491 | 0.87491 | -4.615 | -4.615
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87491 | 0.87491 | -4.615 | -4.615
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87491 | 0.87491 | -4.615 | -4.615
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87491 | 0.87491 | -4.615 | -4.615
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87491 | 0.87491 | -4.615 | -4.615
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87491 | 0.87491 | -4.615 | -4.615
Line4_2_6 | 2.259 | 2.259 | 0 | 0 | 1.5651 | 1.5651 | 0.45928 | -0.30619 | 0.91856 | -0.61237 | -68.05 | 111.95 | 0.65618 | 0.43745 | -4.615 | -4.615
Line5_6_7 | 2.259 | 2.259 | 0 | 0 | 1.5651 | 1.5651 | 0.30619 | -0.15309 | 0.61237 | -0.30619 | -68.05 | 111.95 | 0.43745 | 0.21873 | -4.615 | -4.615
Line6_7_8 | 2.259 | 2.259 | 0 | 4.1931 | 1.5651 | 1.5651 | 0.15309 | -1e-07 | 0.30619 | -1e-07 | -68.05 | 111.95 | 0.21873 | 0 | -4.615 | 0
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1499e-21 | 0 | -5.8009e-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1499e-21 | 0 | -5.8009e-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87491 | 0.87491 | -4.615 | -4.615

## LLL_max_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 0.033802 | 0.033802 | 0 | 0 | 0.023418 | 0.023418 | 0.017275 | -0.017241 | 0.017412 | -0.017344 | -45.346 | 134.654 | 1.0474 | 1.0443 | -0.11952 | -0.17563
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.11952 | -0.11952
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.11952 | -0.11952
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.11952 | -0.11952
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.11952 | -0.11952
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.11952 | -0.11952
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.11952 | -0.11952
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.11952 | -0.11952
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.11952 | -0.11952
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.11952 | -0.11952
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.11952 | -0.11952
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.11952 | -0.11952
Line4_2_6 | 0.033802 | 0.033802 | 0 | 0 | 0.023418 | 0.023418 | 0.017241 | -0.017207 | 0.017344 | -0.017275 | -45.346 | 134.654 | 1.0443 | 1.0412 | -0.17563 | -0.23207
Line5_6_7 | 0.033802 | 0.033802 | 0 | 0 | 0.023418 | 0.023418 | 0.017207 | -0.017173 | 0.017275 | -0.017207 | -45.346 | 134.654 | 1.0412 | 1.0381 | -0.23207 | -0.28886
Line6_7_8 | 0.033802 | 0.033802 | 0 | 0.0626 | 0.023418 | 0.023418 | 0.017173 | -0.017138 | 0.017207 | -0.017138 | -45.346 | 134.654 | 1.0381 | 1.035 | -0.28886 | -0.34598
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | -1.7102e-10 | 0 | 7.2182e-11 | 0 | 0 | 0 | 1.035 | 1.035 | -0.34598 | -0.34598
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | -1.7102e-10 | 0 | 7.2182e-11 | 0 | 0 | 0 | 1.035 | 1.035 | -0.34598 | -0.34598
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.11952 | -0.11952

## LLL_max_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 0.035407 | 0.035407 | 0 | 0 | 0.024531 | 0.024531 | 0.018955 | -0.018918 | 0.019106 | -0.019031 | -45.3516 | 134.6484 | 1.0971 | 1.0939 | -0.12515 | -0.18126
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12515 | -0.12515
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12515 | -0.12515
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12515 | -0.12515
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12515 | -0.12515
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12515 | -0.12515
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12515 | -0.12515
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12515 | -0.12515
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12515 | -0.12515
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12515 | -0.12515
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12515 | -0.12515
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12515 | -0.12515
Line4_2_6 | 0.035407 | 0.035407 | 0 | 0 | 0.024531 | 0.024531 | 0.018918 | -0.01888 | 0.019031 | -0.018955 | -45.3516 | 134.6484 | 1.0939 | 1.0906 | -0.18126 | -0.23771
Line5_6_7 | 0.035407 | 0.035407 | 0 | 0 | 0.024531 | 0.024531 | 0.01888 | -0.018842 | 0.018955 | -0.01888 | -45.3516 | 134.6484 | 1.0906 | 1.0874 | -0.23771 | -0.29449
Line6_7_8 | 0.035407 | 0.035407 | 0 | 0.065722 | 0.024531 | 0.024531 | 0.018842 | -0.018805 | 0.01888 | -0.018805 | -45.3516 | 134.6484 | 1.0874 | 1.0841 | -0.29449 | -0.35161
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | -1.8919e-10 | 0 | 8.0501e-11 | 0 | 0 | 0 | 1.0841 | 1.0841 | -0.35161 | -0.35161
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | -1.8919e-10 | 0 | 8.0501e-11 | 0 | 0 | 0 | 1.0841 | 1.0841 | -0.35161 | -0.35161
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12515 | -0.12515

## LLL_min_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 1.6801 | 1.6801 | 0 | 0 | 1.164 | 1.164 | 0.65034 | -0.48775 | 0.67743 | -0.50807 | -52.8727 | 127.1273 | 0.80677 | 0.60508 | -6.7036 | -6.7036
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80677 | 0.80677 | -6.7036 | -6.7036
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80677 | 0.80677 | -6.7036 | -6.7036
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80677 | 0.80677 | -6.7036 | -6.7036
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80677 | 0.80677 | -6.7036 | -6.7036
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80677 | 0.80677 | -6.7036 | -6.7036
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80677 | 0.80677 | -6.7036 | -6.7036
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80677 | 0.80677 | -6.7036 | -6.7036
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80677 | 0.80677 | -6.7036 | -6.7036
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80677 | 0.80677 | -6.7036 | -6.7036
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80677 | 0.80677 | -6.7036 | -6.7036
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80677 | 0.80677 | -6.7036 | -6.7036
Line4_2_6 | 1.6801 | 1.6801 | 0 | 0 | 1.164 | 1.164 | 0.48775 | -0.32517 | 0.50807 | -0.33872 | -52.8727 | 127.1273 | 0.60508 | 0.40338 | -6.7036 | -6.7036
Line5_6_7 | 1.6801 | 1.6801 | 0 | 0 | 1.164 | 1.164 | 0.32517 | -0.16258 | 0.33872 | -0.16936 | -52.8727 | 127.1273 | 0.40338 | 0.20169 | -6.7036 | -6.7036
Line6_7_8 | 1.6801 | 1.6801 | 0 | 2.6638 | 1.164 | 1.164 | 0.16258 | -1e-07 | 0.16936 | -1e-07 | -52.8727 | 127.1273 | 0.20169 | 0 | -6.7036 | 0
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 7.0075e-22 | 0 | 9.1561e-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 7.0075e-22 | 0 | 9.1561e-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80677 | 0.80677 | -6.7036 | -6.7036

## LLL_min_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 1.5916 | 1.5916 | 0 | 0 | 1.1027 | 1.1027 | 0.58368 | -0.43776 | 0.608 | -0.456 | -52.8727 | 127.1273 | 0.76431 | 0.57323 | -6.7036 | -6.7036
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76431 | 0.76431 | -6.7036 | -6.7036
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76431 | 0.76431 | -6.7036 | -6.7036
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76431 | 0.76431 | -6.7036 | -6.7036
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76431 | 0.76431 | -6.7036 | -6.7036
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76431 | 0.76431 | -6.7036 | -6.7036
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76431 | 0.76431 | -6.7036 | -6.7036
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76431 | 0.76431 | -6.7036 | -6.7036
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76431 | 0.76431 | -6.7036 | -6.7036
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76431 | 0.76431 | -6.7036 | -6.7036
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76431 | 0.76431 | -6.7036 | -6.7036
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76431 | 0.76431 | -6.7036 | -6.7036
Line4_2_6 | 1.5916 | 1.5916 | 0 | 0 | 1.1027 | 1.1027 | 0.43776 | -0.29184 | 0.456 | -0.304 | -52.8727 | 127.1273 | 0.57323 | 0.38215 | -6.7036 | -6.7036
Line5_6_7 | 1.5916 | 1.5916 | 0 | 0 | 1.1027 | 1.1027 | 0.29184 | -0.14592 | 0.304 | -0.152 | -52.8727 | 127.1273 | 0.38215 | 0.19108 | -6.7036 | -6.7036
Line6_7_8 | 1.5916 | 1.5916 | 0 | 2.5236 | 1.1027 | 1.1027 | 0.14592 | -1e-07 | 0.152 | -1e-07 | -52.8727 | 127.1273 | 0.19108 | 0 | -6.7036 | 0
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 6.276e-22 | 0 | 8.2153e-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 6.276e-22 | 0 | 8.2153e-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76431 | 0.76431 | -6.7036 | -6.7036

## LLL_min_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 0.030469 | 0.030469 | 0 | 0 | 0.02111 | 0.02111 | 0.01414 | -0.014086 | 0.014149 | -0.014093 | -45.1423 | 134.8577 | 0.94756 | 0.9439 | -0.12428 | -0.12874
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94756 | 0.94756 | -0.12428 | -0.12428
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94756 | 0.94756 | -0.12428 | -0.12428
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94756 | 0.94756 | -0.12428 | -0.12428
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94756 | 0.94756 | -0.12428 | -0.12428
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94756 | 0.94756 | -0.12428 | -0.12428
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94756 | 0.94756 | -0.12428 | -0.12428
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94756 | 0.94756 | -0.12428 | -0.12428
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94756 | 0.94756 | -0.12428 | -0.12428
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94756 | 0.94756 | -0.12428 | -0.12428
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94756 | 0.94756 | -0.12428 | -0.12428
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94756 | 0.94756 | -0.12428 | -0.12428
Line4_2_6 | 0.030469 | 0.030469 | 0 | 0 | 0.02111 | 0.02111 | 0.014086 | -0.014033 | 0.014093 | -0.014037 | -45.1423 | 134.8577 | 0.9439 | 0.94024 | -0.12874 | -0.13323
Line5_6_7 | 0.030469 | 0.030469 | 0 | 0 | 0.02111 | 0.02111 | 0.014033 | -0.013979 | 0.014037 | -0.013981 | -45.1423 | 134.8577 | 0.94024 | 0.93659 | -0.13323 | -0.13776
Line6_7_8 | 0.030469 | 0.030469 | 0 | 0.04831 | 0.02111 | 0.02111 | 0.013979 | -0.013926 | 0.013981 | -0.013926 | -45.1423 | 134.8577 | 0.93659 | 0.93293 | -0.13776 | -0.14233
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | -1.7514e-10 | 0 | 2.4218e-11 | 0 | 0 | 0 | 0.93293 | 0.93293 | -0.14233 | -0.14233
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | -1.7514e-10 | 0 | 2.4218e-11 | 0 | 0 | 0 | 0.93293 | 0.93293 | -0.14233 | -0.14233
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94756 | 0.94756 | -0.12428 | -0.12428

## LLL_min_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 0.028866 | 0.028866 | 0 | 0 | 0.019999 | 0.019999 | 0.01269 | -0.012642 | 0.012698 | -0.012648 | -45.1423 | 134.8577 | 0.89769 | 0.89422 | -0.12428 | -0.12874
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89769 | 0.89769 | -0.12428 | -0.12428
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89769 | 0.89769 | -0.12428 | -0.12428
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89769 | 0.89769 | -0.12428 | -0.12428
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89769 | 0.89769 | -0.12428 | -0.12428
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89769 | 0.89769 | -0.12428 | -0.12428
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89769 | 0.89769 | -0.12428 | -0.12428
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89769 | 0.89769 | -0.12428 | -0.12428
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89769 | 0.89769 | -0.12428 | -0.12428
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89769 | 0.89769 | -0.12428 | -0.12428
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89769 | 0.89769 | -0.12428 | -0.12428
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89769 | 0.89769 | -0.12428 | -0.12428
Line4_2_6 | 0.028866 | 0.028866 | 0 | 0 | 0.019999 | 0.019999 | 0.012642 | -0.012594 | 0.012648 | -0.012598 | -45.1423 | 134.8577 | 0.89422 | 0.89076 | -0.12874 | -0.13323
Line5_6_7 | 0.028866 | 0.028866 | 0 | 0 | 0.019999 | 0.019999 | 0.012594 | -0.012546 | 0.012598 | -0.012548 | -45.1423 | 134.8577 | 0.89076 | 0.88729 | -0.13323 | -0.13776
Line6_7_8 | 0.028866 | 0.028866 | 0 | 0.045767 | 0.019999 | 0.019999 | 0.012546 | -0.012498 | 0.012548 | -0.012498 | -45.1423 | 134.8577 | 0.88729 | 0.88383 | -0.13776 | -0.14233
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | -1.5719e-10 | 0 | 2.1736e-11 | 0 | 0 | 0 | 0.88383 | 0.88383 | -0.14233 | -0.14233
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | -1.5719e-10 | 0 | 2.1736e-11 | 0 | 0 | 0 | 0.88383 | 0.88383 | -0.14233 | -0.14233
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89769 | 0.89769 | -0.12428 | -0.12428

## LL_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 1.885 | 1.885 | 0 | 1.885 | 1.885 | 0 | 0.43533 | 0.43533 | 0 | 0.43533 | 0.43533 | 1.0492e-15 | 0.35387 | -0.069596 | -1.088e-15 | -0.31833 | 0.10513 | -4.0801e-16 | 0.19822 | 0.37032 | 3.6915e-16 | -0.12715 | -0.29925 | 0 | -157.8829 | 22.1171 | 0 | 22.1171 | -157.8829 | 1.05 | 0.93171 | 0.86555 | 1.05 | 0.78742 | 0.7286 | -3.6265e-12 | -128.6271 | 122.7608 | -3.6397e-12 | -136.1092 | 131.4739
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9143e-16 | -2.1811e-09 | -3.489e-09 | -2.9143e-16 | 2.1811e-09 | 3.489e-09 | 3.8858e-17 | 3.2284e-09 | -9.6307e-10 | -3.8858e-17 | -3.2284e-09 | 9.6307e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.93171 | 0.86555 | 1.05 | 0.93171 | 0.86555 | -3.64e-12 | -128.6271 | 122.7608 | -3.6455e-12 | -128.6271 | 122.7608
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9143e-16 | -1.8176e-09 | -2.9075e-09 | -2.9143e-16 | 1.8176e-09 | 2.9075e-09 | -1.9429e-17 | 2.6904e-09 | -8.0256e-10 | 1.8565e-29 | -2.6904e-09 | 8.0256e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.93171 | 0.86555 | 1.05 | 0.93171 | 0.86555 | -3.6455e-12 | -128.6271 | 122.7608 | -3.6498e-12 | -128.6271 | 122.7608
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.36e-16 | -1.0906e-09 | -1.7445e-09 | -1.1657e-16 | 1.0906e-09 | 1.7445e-09 | 3.8858e-17 | 1.6142e-09 | -4.8153e-10 | -1.9429e-17 | -1.6142e-09 | 4.8153e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.93171 | 0.86555 | 1.05 | 0.93171 | 0.86555 | -3.6498e-12 | -128.6271 | 122.7608 | -3.652e-12 | -128.6271 | 122.7608
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.8858e-17 | -3.6352e-10 | -5.8151e-10 | 1.9429e-17 | 3.6352e-10 | 5.8151e-10 | 1.9429e-17 | 5.3807e-10 | -1.6051e-10 | -1.2379e-30 | -5.3807e-10 | 1.6051e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.93171 | 0.86555 | 1.05 | 0.93171 | 0.86555 | -3.6498e-12 | -128.6271 | 122.7608 | -3.6505e-12 | -128.6271 | 122.7608
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1657e-16 | -7.2704e-10 | -1.163e-09 | -1.1657e-16 | 7.2704e-10 | 1.163e-09 | -7.4303e-30 | 1.0761e-09 | -3.2102e-10 | 7.4324e-30 | -1.0761e-09 | 3.2102e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.93171 | 0.86555 | 1.05 | 0.93171 | 0.86555 | -3.652e-12 | -128.6271 | 122.7608 | -3.653e-12 | -128.6271 | 122.7608
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.8287e-17 | -3.6352e-10 | -5.8151e-10 | 5.8287e-17 | 3.6352e-10 | 5.8151e-10 | 1.9429e-17 | 5.3807e-10 | -1.6051e-10 | -1.9429e-17 | -5.3807e-10 | 1.6051e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.93171 | 0.86555 | 1.05 | 0.93171 | 0.86555 | -3.653e-12 | -128.6271 | 122.7608 | -3.6534e-12 | -128.6271 | 122.7608
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.8287e-17 | -3.6352e-10 | -5.8151e-10 | -3.8858e-17 | 3.6352e-10 | 5.8151e-10 | -5.8287e-17 | 5.3807e-10 | -1.6051e-10 | 3.8858e-17 | -5.3807e-10 | 1.6051e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.93171 | 0.86555 | 1.05 | 0.93171 | 0.86555 | -3.6276e-12 | -128.6271 | 122.7608 | -3.628e-12 | -128.6271 | 122.7608
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.8287e-17 | -3.6352e-10 | -5.8151e-10 | -3.8858e-17 | 3.6352e-10 | 5.8151e-10 | -5.8287e-17 | 5.3807e-10 | -1.6051e-10 | 3.8858e-17 | -5.3807e-10 | 1.6051e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.93171 | 0.86555 | 1.05 | 0.93171 | 0.86555 | -3.6276e-12 | -128.6271 | 122.7608 | -3.628e-12 | -128.6271 | 122.7608
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8858e-16 | -2.9082e-09 | -4.6521e-09 | -3.6915e-16 | 2.9082e-09 | 4.6521e-09 | 9.7145e-17 | 4.3046e-09 | -1.2841e-09 | -1.1657e-16 | -4.3046e-09 | 1.2841e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.93171 | 0.86555 | 1.05 | 0.93171 | 0.86555 | -3.6265e-12 | -128.6271 | 122.7608 | -3.6337e-12 | -128.6271 | 122.7608
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9429e-17 | -7.2704e-10 | -1.163e-09 | -1.9429e-17 | 7.2704e-10 | 1.163e-09 | 1.9429e-17 | 1.0761e-09 | -3.2102e-10 | -3.8858e-17 | -1.0761e-09 | 3.2102e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.93171 | 0.86555 | 1.05 | 0.93171 | 0.86555 | -3.6265e-12 | -128.6271 | 122.7608 | -3.6276e-12 | -128.6271 | 122.7608
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9429e-17 | -7.2704e-10 | -1.163e-09 | -1.9429e-17 | 7.2704e-10 | 1.163e-09 | 1.9429e-17 | 1.0761e-09 | -3.2102e-10 | -3.8858e-17 | -1.0761e-09 | 3.2102e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.93171 | 0.86555 | 1.05 | 0.93171 | 0.86555 | -3.6265e-12 | -128.6271 | 122.7608 | -3.6276e-12 | -128.6271 | 122.7608
Line4_2_6 | 0 | 1.885 | 1.885 | 0 | 1.885 | 1.885 | 0 | 0.43533 | 0.43533 | 0 | 0.43533 | 0.43533 | 9.3259e-16 | 0.31833 | -0.10513 | -9.3259e-16 | -0.2828 | 0.14066 | -3.4972e-16 | 0.12715 | 0.29925 | 3.8858e-16 | -0.056087 | -0.22819 | 0 | -157.8829 | 22.1171 | 0 | 22.1171 | -157.8829 | 1.05 | 0.78742 | 0.7286 | 1.05 | 0.66227 | 0.61575 | -3.6397e-12 | -136.1092 | 131.4739 | -3.6493e-12 | -146.6652 | 143.7688
Line5_6_7 | 0 | 1.885 | 1.885 | 0 | 1.885 | 1.885 | 0 | 0.43533 | 0.43533 | 0 | 0.43533 | 0.43533 | 6.9944e-16 | 0.2828 | -0.14066 | -6.9944e-16 | -0.24727 | 0.1762 | -3.4972e-16 | 0.056087 | 0.22819 | 3.4972e-16 | 0.014981 | -0.15712 | 0 | -157.8829 | 22.1171 | 0 | 22.1171 | -157.8829 | 1.05 | 0.66227 | 0.61575 | 1.05 | 0.56903 | 0.54229 | -3.6493e-12 | -146.6652 | 143.7688 | -3.659e-12 | -161.35 | 160.3935
Line6_7_8 | 0 | 1.885 | 1.885 | 0 | 1.885 | 1.885 | 0 | 0.43533 | 0.43533 | 0 | 0.43533 | 0.43533 | 4.6629e-16 | 0.24727 | -0.1762 | -4.6629e-16 | -0.21173 | 0.21173 | -3.4972e-16 | -0.014981 | 0.15712 | 3.8858e-16 | 0.086049 | -0.086049 | 0 | -157.8829 | 22.1171 | 0 | 22.1171 | -157.8829 | 1.05 | 0.56903 | 0.54229 | 1.05 | 0.525 | 0.525 | -3.659e-12 | -161.35 | 160.3935 | -3.6672e-12 | -180 | -180
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5543e-16 | 2.3315e-16 | -3.1086e-16 | -1.5543e-16 | 1.1866e-16 | 2.0841e-18 | -7.7716e-17 | 1.7505e-09 | -1.7505e-09 | 7.7716e-17 | -1.7505e-09 | 1.7505e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.525 | 0.525 | 1.05 | 0.525 | 0.525 | -3.6672e-12 | -180 | -180 | -3.6703e-12 | -180 | 180
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5543e-16 | 3.4972e-16 | -3.1086e-16 | -1.5543e-16 | 2.0845e-18 | 1.5752e-16 | -1.1657e-16 | 1.7505e-09 | -1.7505e-09 | 1.1657e-16 | -1.7505e-09 | 1.7505e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.525 | 0.525 | 1.05 | 0.525 | 0.525 | -3.6672e-12 | -180 | -180 | -3.6704e-12 | -180 | 180
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4972e-16 | -2.5447e-09 | -4.0705e-09 | -3.6915e-16 | 2.5447e-09 | 4.0705e-09 | 7.7716e-17 | 3.7665e-09 | -1.1236e-09 | -7.7716e-17 | -3.7665e-09 | 1.1236e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.93171 | 0.86555 | 1.05 | 0.93171 | 0.86555 | -3.6337e-12 | -128.6271 | 122.7608 | -3.64e-12 | -128.6271 | 122.7608

## LL_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 1.9564 | 1.9564 | 0 | 1.9564 | 1.9564 | 0 | 0.4518 | 0.4518 | 0 | 0.4518 | 0.4518 | 1.0177e-15 | 0.38357 | -0.077384 | -1.0177e-15 | -0.3453 | 0.11566 | -2.4425e-16 | 0.2133 | 0.39907 | 2.4425e-16 | -0.13675 | -0.32252 | 0 | -158.05 | 21.95 | 0 | 21.95 | -158.05 | 1.1 | 0.97142 | 0.89974 | 1.1 | 0.82203 | 0.75838 | 3.8235e-12 | -128.9719 | 122.9242 | 3.8071e-12 | -136.444 | 131.678
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6637e-16 | -2.4603e-09 | -3.9356e-09 | -3.4602e-16 | 2.4603e-09 | 3.9356e-09 | 4.0708e-17 | 3.6661e-09 | -1.1108e-09 | -2.2971e-29 | -3.6661e-09 | 1.1108e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.97142 | 0.89974 | 1.1 | 0.97142 | 0.89974 | 3.8095e-12 | -128.9719 | 122.9242 | 3.8037e-12 | -128.9719 | 122.9242
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8496e-16 | -2.0502e-09 | -3.2797e-09 | -3.0531e-16 | 2.0502e-09 | 3.2797e-09 | 1.8918e-29 | 3.0551e-09 | -9.2564e-10 | 2.0354e-17 | -3.0551e-09 | 9.2564e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.97142 | 0.89974 | 1.1 | 0.97142 | 0.89974 | 3.8037e-12 | -128.9719 | 122.9242 | 3.7992e-12 | -128.9719 | 122.9242
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8319e-16 | -1.2301e-09 | -1.9678e-09 | -1.6283e-16 | 1.2301e-09 | 1.9678e-09 | 4.0708e-17 | 1.8331e-09 | -5.5539e-10 | -6.1062e-17 | -1.8331e-09 | 5.5539e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.97142 | 0.89974 | 1.1 | 0.97142 | 0.89974 | 3.7992e-12 | -128.9719 | 122.9242 | 3.797e-12 | -128.9719 | 122.9242
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0354e-17 | -4.1005e-10 | -6.5593e-10 | 2.0354e-17 | 4.1005e-10 | 6.5593e-10 | -2.0354e-17 | 6.1102e-10 | -1.8513e-10 | 1.3494e-30 | -6.1102e-10 | 1.8513e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.97142 | 0.89974 | 1.1 | 0.97142 | 0.89974 | 3.7992e-12 | -128.9719 | 122.9242 | 3.7986e-12 | -128.9719 | 122.9242
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.1416e-17 | -8.2009e-10 | -1.3119e-09 | -1.2212e-16 | 8.2009e-10 | 1.3119e-09 | 4.0708e-17 | 1.222e-09 | -3.7026e-10 | -8.091e-30 | -1.222e-09 | 3.7026e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.97142 | 0.89974 | 1.1 | 0.97142 | 0.89974 | 3.797e-12 | -128.9719 | 122.9242 | 3.7959e-12 | -128.9719 | 122.9242
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0354e-17 | -4.1005e-10 | -6.5593e-10 | -1.3484e-30 | 4.1005e-10 | 6.5593e-10 | 1.3485e-30 | 6.1102e-10 | -1.8513e-10 | 2.0354e-17 | -6.1102e-10 | 1.8513e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.97142 | 0.89974 | 1.1 | 0.97142 | 0.89974 | 3.7959e-12 | -128.9719 | 122.9242 | 3.7956e-12 | -128.9719 | 122.9242
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.0354e-17 | -4.1005e-10 | -6.5593e-10 | 2.0354e-17 | 4.1005e-10 | 6.5593e-10 | -1.3579e-30 | 6.1102e-10 | -1.8513e-10 | 1.3578e-30 | -6.1102e-10 | 1.8513e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.97142 | 0.89974 | 1.1 | 0.97142 | 0.89974 | 3.8225e-12 | -128.9719 | 122.9242 | 3.8221e-12 | -128.9719 | 122.9242
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.0354e-17 | -4.1005e-10 | -6.5593e-10 | 2.0354e-17 | 4.1005e-10 | 6.5593e-10 | -1.3579e-30 | 6.1102e-10 | -1.8513e-10 | 1.3578e-30 | -6.1102e-10 | 1.8513e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.97142 | 0.89974 | 1.1 | 0.97142 | 0.89974 | 3.8225e-12 | -128.9719 | 122.9242 | 3.8221e-12 | -128.9719 | 122.9242
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.0885e-16 | -3.2804e-09 | -5.2475e-09 | -5.0885e-16 | 3.2804e-09 | 5.2475e-09 | 1.4248e-16 | 4.8882e-09 | -1.481e-09 | -1.4248e-16 | -4.8882e-09 | 1.481e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.97142 | 0.89974 | 1.1 | 0.97142 | 0.89974 | 3.8235e-12 | -128.9719 | 122.9242 | 3.816e-12 | -128.9719 | 122.9242
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0177e-16 | -8.2009e-10 | -1.3119e-09 | -8.1416e-17 | 8.2009e-10 | 1.3119e-09 | 2.0354e-17 | 1.222e-09 | -3.7026e-10 | -5.4317e-30 | -1.222e-09 | 3.7026e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.97142 | 0.89974 | 1.1 | 0.97142 | 0.89974 | 3.8235e-12 | -128.9719 | 122.9242 | 3.8225e-12 | -128.9719 | 122.9242
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0177e-16 | -8.2009e-10 | -1.3119e-09 | -8.1416e-17 | 8.2009e-10 | 1.3119e-09 | 2.0354e-17 | 1.222e-09 | -3.7026e-10 | -5.4317e-30 | -1.222e-09 | 3.7026e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.97142 | 0.89974 | 1.1 | 0.97142 | 0.89974 | 3.8235e-12 | -128.9719 | 122.9242 | 3.8225e-12 | -128.9719 | 122.9242
Line4_2_6 | 0 | 1.9564 | 1.9564 | 0 | 1.9564 | 1.9564 | 0 | 0.4518 | 0.4518 | 0 | 0.4518 | 0.4518 | 8.9558e-16 | 0.3453 | -0.11566 | -8.1416e-16 | -0.30702 | 0.15393 | -2.8496e-16 | 0.13675 | 0.32252 | 2.8496e-16 | -0.060208 | -0.24598 | 0 | -158.05 | 21.95 | 0 | 21.95 | -158.05 | 1.1 | 0.82203 | 0.75838 | 1.1 | 0.6925 | 0.64226 | 3.8071e-12 | -136.444 | 131.678 | 3.7903e-12 | -146.955 | 143.988
Line5_6_7 | 0 | 1.9564 | 1.9564 | 0 | 1.9564 | 1.9564 | 0 | 0.4518 | 0.4518 | 0 | 0.4518 | 0.4518 | 8.1416e-16 | 0.30702 | -0.15393 | -8.1416e-16 | -0.26875 | 0.1922 | -3.2567e-16 | 0.060208 | 0.24598 | 3.2567e-16 | 0.016339 | -0.16943 | 0 | -158.05 | 21.95 | 0 | 21.95 | -158.05 | 1.1 | 0.6925 | 0.64226 | 1.1 | 0.59594 | 0.56711 | 3.7903e-12 | -146.955 | 143.988 | 3.7765e-12 | -161.529 | 160.5532
Line6_7_8 | 0 | 1.9564 | 1.9564 | 0 | 1.9564 | 1.9564 | 0 | 0.4518 | 0.4518 | 0 | 0.4518 | 0.4518 | 1.0733e-29 | 0.26875 | -0.1922 | -1.0714e-29 | -0.23048 | 0.23048 | -1.6283e-16 | -0.016339 | 0.16943 | 1.6283e-16 | 0.092885 | -0.092885 | 0 | -158.05 | 21.95 | 0 | 21.95 | -158.05 | 1.1 | 0.59594 | 0.56711 | 1.1 | 0.55 | 0.55 | 3.7765e-12 | -161.529 | 160.5532 | 3.77e-12 | 180 | 180
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.5133e-16 | 2.6913e-22 | -6.5133e-16 | -6.5133e-16 | 4.0937e-16 | 9.7928e-16 | -2.4425e-16 | 1.9211e-09 | -1.9211e-09 | 2.4425e-16 | -1.9211e-09 | 1.9211e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.55 | 0.55 | 1.1 | 0.55 | 0.55 | 3.77e-12 | 180 | 180 | 3.7668e-12 | -180 | 180
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2567e-16 | 8.1417e-17 | -3.2567e-16 | -3.2567e-16 | 3.2795e-16 | 6.5362e-16 | -8.1416e-17 | 1.9211e-09 | -1.9211e-09 | 1.6283e-16 | -1.9211e-09 | 1.9211e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.55 | 0.55 | 1.1 | 0.55 | 0.55 | 3.77e-12 | 180 | 180 | 3.7664e-12 | -180 | 180
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2744e-16 | -2.8703e-09 | -4.5915e-09 | -4.2744e-16 | 2.8703e-09 | 4.5915e-09 | 4.0708e-17 | 4.2771e-09 | -1.2959e-09 | -8.1416e-17 | -4.2771e-09 | 1.2959e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.97142 | 0.89974 | 1.1 | 0.97142 | 0.89974 | 3.816e-12 | -128.9719 | 122.9242 | 3.8095e-12 | -128.9719 | 122.9242

## LL_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0.057717 | 0.057717 | 0 | 0.057717 | 0.057717 | 0 | 0.013329 | 0.013329 | 0 | 0.013329 | 0.013329 | 2.7322e-17 | 0.013468 | 0.0034547 | -2.8536e-17 | -0.013435 | -0.0034214 | -2.4286e-18 | 0.0037057 | 0.013484 | -4.5484e-32 | -0.0036391 | -0.013417 | 0 | -135.6822 | 44.3178 | 0 | 44.3178 | -135.6822 | 1.05 | 1.048 | 1.0443 | 1.05 | 1.0443 | 1.0388 | 9.1613e-14 | -120.2981 | 119.9471 | 9.1325e-14 | -120.5262 | 120.0122
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.6787e-18 | -4.627e-11 | -1.3184e-10 | -7.2858e-18 | 4.627e-11 | 1.3184e-10 | 2.4286e-18 | 1.2595e-10 | 2.226e-11 | -3.6429e-18 | -1.2595e-10 | -2.226e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0443 | 1.05 | 1.048 | 1.0443 | 9.1263e-14 | -120.2981 | 119.9471 | 9.1113e-14 | -120.2981 | 119.9471
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.9823e-18 | -3.8558e-11 | -1.0987e-10 | -6.3751e-18 | 3.8558e-11 | 1.0987e-10 | 1.1103e-32 | 1.0496e-10 | 1.855e-11 | -1.0124e-32 | -1.0496e-10 | -1.855e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0443 | 1.05 | 1.048 | 1.0443 | 9.1113e-14 | -120.2981 | 119.9471 | 9.0992e-14 | -120.2981 | 119.9471
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2501e-18 | -2.3135e-11 | -6.592e-11 | -4.8572e-18 | 2.3135e-11 | 6.592e-11 | 1.8215e-18 | 6.2976e-11 | 1.113e-11 | -1.2143e-18 | -6.2976e-11 | -1.113e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0443 | 1.05 | 1.048 | 1.0443 | 9.0992e-14 | -120.2981 | 119.9471 | 9.0932e-14 | -120.2981 | 119.9471
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.0715e-19 | -7.7116e-12 | -2.1973e-11 | 1.9281e-33 | 7.7116e-12 | 2.1973e-11 | 6.0715e-19 | 2.0992e-11 | 3.71e-12 | -1.2143e-18 | -2.0992e-11 | -3.71e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0443 | 1.05 | 1.048 | 1.0443 | 9.0992e-14 | -120.2981 | 119.9471 | 9.0977e-14 | -120.2981 | 119.9471
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4286e-18 | -1.5423e-11 | -4.3946e-11 | -2.4286e-18 | 1.5423e-11 | 4.3946e-11 | 1.8215e-18 | 4.1984e-11 | 7.42e-12 | -3.8531e-33 | -4.1984e-11 | -7.42e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0443 | 1.05 | 1.048 | 1.0443 | 9.0932e-14 | -120.2981 | 119.9471 | 9.0903e-14 | -120.2981 | 119.9471
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.1073e-19 | -7.7116e-12 | -2.1973e-11 | 3.0358e-19 | 7.7116e-12 | 2.1973e-11 | -1.2143e-18 | 2.0992e-11 | 3.71e-12 | 1.2143e-18 | -2.0992e-11 | -3.71e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0443 | 1.05 | 1.048 | 1.0443 | 9.0903e-14 | -120.2981 | 119.9471 | 9.0885e-14 | -120.2981 | 119.9471
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -9.1073e-19 | -7.7116e-12 | -2.1973e-11 | 3.0358e-19 | 7.7116e-12 | 2.1973e-11 | 6.0715e-19 | 2.0992e-11 | 3.71e-12 | -6.0715e-19 | -2.0992e-11 | -3.71e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0443 | 1.05 | 1.048 | 1.0443 | 9.1579e-14 | -120.2981 | 119.9471 | 9.156e-14 | -120.2981 | 119.9471
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -9.1073e-19 | -7.7116e-12 | -2.1973e-11 | 3.0358e-19 | 7.7116e-12 | 2.1973e-11 | 6.0715e-19 | 2.0992e-11 | 3.71e-12 | -6.0715e-19 | -2.0992e-11 | -3.71e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0443 | 1.05 | 1.048 | 1.0443 | 9.1579e-14 | -120.2981 | 119.9471 | 9.156e-14 | -120.2981 | 119.9471
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0625e-17 | -6.1693e-11 | -1.7579e-10 | -1.0018e-17 | 6.1693e-11 | 1.7579e-10 | 5.4644e-18 | 1.6794e-10 | 2.968e-11 | -7.2858e-18 | -1.6794e-10 | -2.968e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0443 | 1.05 | 1.048 | 1.0443 | 9.1613e-14 | -120.2981 | 119.9471 | 9.1427e-14 | -120.2981 | 119.9471
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2143e-18 | -1.5423e-11 | -4.3946e-11 | -1.2143e-18 | 1.5423e-11 | 4.3946e-11 | 1.9416e-33 | 4.1984e-11 | 7.42e-12 | -1.2143e-18 | -4.1984e-11 | -7.42e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0443 | 1.05 | 1.048 | 1.0443 | 9.1613e-14 | -120.2981 | 119.9471 | 9.1579e-14 | -120.2981 | 119.9471
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2143e-18 | -1.5423e-11 | -4.3946e-11 | -1.2143e-18 | 1.5423e-11 | 4.3946e-11 | 1.9416e-33 | 4.1984e-11 | 7.42e-12 | -1.2143e-18 | -4.1984e-11 | -7.42e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0443 | 1.05 | 1.048 | 1.0443 | 9.1613e-14 | -120.2981 | 119.9471 | 9.1579e-14 | -120.2981 | 119.9471
Line4_2_6 | 0 | 0.057717 | 0.057717 | 0 | 0.057717 | 0.057717 | 0 | 0.013329 | 0.013329 | 0 | 0.013329 | 0.013329 | 2.3072e-17 | 0.013435 | 0.0034214 | -2.3072e-17 | -0.013402 | -0.003388 | -2.4286e-18 | 0.0036391 | 0.013417 | 2.4286e-18 | -0.0035725 | -0.01335 | 0 | -135.6822 | 44.3178 | 0 | 44.3178 | -135.6822 | 1.05 | 1.0443 | 1.0388 | 1.05 | 1.0405 | 1.0333 | 9.1325e-14 | -120.5262 | 120.0122 | 9.1142e-14 | -120.7558 | 120.078
Line5_6_7 | 0 | 0.057717 | 0.057717 | 0 | 0.057717 | 0.057717 | 0 | 0.013329 | 0.013329 | 0 | 0.013329 | 0.013329 | 1.4572e-17 | 0.013402 | 0.003388 | -1.4572e-17 | -0.013368 | -0.0033547 | 2.318e-32 | 0.0035725 | 0.01335 | -2.3125e-32 | -0.0035059 | -0.013284 | 0 | -135.6822 | 44.3178 | 0 | 44.3178 | -135.6822 | 1.05 | 1.0405 | 1.0333 | 1.05 | 1.0368 | 1.0279 | 9.1142e-14 | -120.7558 | 120.078 | 9.0929e-14 | -120.9872 | 120.1445
Line6_7_8 | 0 | 0.057717 | 0.057717 | 0 | 0.057717 | 0.057717 | 0 | 0.013329 | 0.013329 | 0 | 0.013329 | 0.013329 | 4.8572e-18 | 0.013368 | 0.0033547 | -4.8572e-18 | -0.013335 | -0.0033214 | -4.8572e-18 | 0.0035059 | 0.013284 | 7.2858e-18 | -0.0034392 | -0.013217 | 0 | -135.6822 | 44.3178 | 0 | 44.3178 | -135.6822 | 1.05 | 1.0368 | 1.0279 | 1.05 | 1.0332 | 1.0224 | 9.0929e-14 | -120.9872 | 120.1445 | 9.071e-14 | -121.2201 | 120.2117
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4286e-18 | -6.2856e-11 | -1.0336e-10 | -2.4286e-18 | 6.2856e-11 | 1.0336e-10 | 7.2858e-18 | 8.4699e-11 | -1.4546e-11 | -7.2858e-18 | -8.4699e-11 | 1.4546e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.0332 | 1.0224 | 1.05 | 1.0332 | 1.0224 | 9.071e-14 | -121.2201 | 120.2117 | 9.0624e-14 | -121.2201 | 120.2117
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4286e-18 | -6.2856e-11 | -1.0336e-10 | -4.8572e-18 | 6.2856e-11 | 1.0336e-10 | 3.845e-33 | 8.4699e-11 | -1.4546e-11 | -7.6834e-33 | -8.4699e-11 | 1.4546e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.0332 | 1.0224 | 1.05 | 1.0332 | 1.0224 | 9.071e-14 | -121.2201 | 120.2117 | 9.0634e-14 | -121.2201 | 120.2117
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.1073e-18 | -5.3981e-11 | -1.5381e-10 | -8.5001e-18 | 5.3981e-11 | 1.5381e-10 | 5.4644e-18 | 1.4694e-10 | 2.597e-11 | -4.8572e-18 | -1.4694e-10 | -2.597e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0443 | 1.05 | 1.048 | 1.0443 | 9.1427e-14 | -120.2981 | 119.9471 | 9.1263e-14 | -120.2981 | 119.9471

## LL_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0.060452 | 0.060452 | 0 | 0.060452 | 0.060452 | 0 | 0.013961 | 0.013961 | 0 | 0.013961 | 0.013961 | 3.3075e-17 | 0.014777 | 0.0037874 | -3.3075e-17 | -0.01474 | -0.0037509 | 3.8164e-18 | 0.004065 | 0.014792 | -6.3607e-18 | -0.0039919 | -0.014719 | 0 | -135.6932 | 44.3068 | 0 | 44.3068 | -135.6932 | 1.1 | 1.0978 | 1.0937 | 1.1 | 1.0939 | 1.088 | 3.0238e-13 | -120.3121 | 119.9447 | 3.018e-13 | -120.5402 | 120.0098
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6328e-18 | -5.3155e-11 | -1.5146e-10 | -7.6328e-18 | 5.3155e-11 | 1.5146e-10 | 3.1803e-18 | 1.4472e-10 | 2.555e-11 | -3.8164e-18 | -1.4472e-10 | -2.555e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0937 | 1.1 | 1.0978 | 1.0937 | 3.0201e-13 | -120.3121 | 119.9447 | 3.0186e-13 | -120.3121 | 119.9447
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.6787e-18 | -4.4296e-11 | -1.2622e-10 | -6.6787e-18 | 4.4296e-11 | 1.2622e-10 | 6.3607e-19 | 1.206e-10 | 2.1292e-11 | -1.9082e-18 | -1.206e-10 | -2.1292e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0937 | 1.1 | 1.0978 | 1.0937 | 3.0186e-13 | -120.3121 | 119.9447 | 3.0173e-13 | -120.3121 | 119.9447
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.0885e-18 | -2.6578e-11 | -7.5731e-11 | -3.8164e-18 | 2.6578e-11 | 7.5731e-11 | 6.3607e-19 | 7.2361e-11 | 1.2775e-11 | -1.2721e-18 | -7.2361e-11 | -1.2775e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0937 | 1.1 | 1.0978 | 1.0937 | 3.0173e-13 | -120.3121 | 119.9447 | 3.0167e-13 | -120.3121 | 119.9447
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.541e-19 | -8.8592e-12 | -2.5244e-11 | -3.1803e-19 | 8.8592e-12 | 2.5244e-11 | -1.2721e-18 | 2.412e-11 | 4.2584e-12 | 2.5443e-18 | -2.412e-11 | -4.2584e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0937 | 1.1 | 1.0978 | 1.0937 | 3.0173e-13 | -120.3121 | 119.9447 | 3.0171e-13 | -120.3121 | 119.9447
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5443e-18 | -1.7718e-11 | -5.0487e-11 | -2.5443e-18 | 1.7718e-11 | 5.0487e-11 | 2.5443e-18 | 4.824e-11 | 8.5168e-12 | -2.5443e-18 | -4.824e-11 | -8.5168e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0937 | 1.1 | 1.0978 | 1.0937 | 3.0167e-13 | -120.3121 | 119.9447 | 3.0164e-13 | -120.3121 | 119.9447
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9082e-18 | -8.8592e-12 | -2.5244e-11 | -1.2721e-18 | 8.8592e-12 | 2.5244e-11 | -6.3607e-19 | 2.412e-11 | 4.2584e-12 | 1.2721e-18 | -2.412e-11 | -4.2584e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0937 | 1.1 | 1.0978 | 1.0937 | 3.0164e-13 | -120.3121 | 119.9447 | 3.0162e-13 | -120.3121 | 119.9447
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.1803e-19 | -8.8592e-12 | -2.5244e-11 | 3.1803e-19 | 8.8592e-12 | 2.5244e-11 | -1.6783e-33 | 2.412e-11 | 4.2584e-12 | 1.6782e-33 | -2.412e-11 | -4.2584e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0937 | 1.1 | 1.0978 | 1.0937 | 3.0235e-13 | -120.3121 | 119.9447 | 3.0233e-13 | -120.3121 | 119.9447
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.1803e-19 | -8.8592e-12 | -2.5244e-11 | 3.1803e-19 | 8.8592e-12 | 2.5244e-11 | -1.6783e-33 | 2.412e-11 | 4.2584e-12 | 1.6782e-33 | -2.412e-11 | -4.2584e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0937 | 1.1 | 1.0978 | 1.0937 | 3.0235e-13 | -120.3121 | 119.9447 | 3.0233e-13 | -120.3121 | 119.9447
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2085e-17 | -7.0874e-11 | -2.0195e-10 | -1.2721e-17 | 7.0874e-11 | 2.0195e-10 | 5.7246e-18 | 1.9296e-10 | 3.4067e-11 | -6.9967e-18 | -1.9296e-10 | -3.4067e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0937 | 1.1 | 1.0978 | 1.0937 | 3.0238e-13 | -120.3121 | 119.9447 | 3.0219e-13 | -120.3121 | 119.9447
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9082e-18 | -1.7718e-11 | -5.0487e-11 | -1.9082e-18 | 1.7718e-11 | 5.0487e-11 | 1.2721e-18 | 4.8241e-11 | 8.5168e-12 | -1.2721e-18 | -4.824e-11 | -8.5168e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0937 | 1.1 | 1.0978 | 1.0937 | 3.0238e-13 | -120.3121 | 119.9447 | 3.0235e-13 | -120.3121 | 119.9447
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9082e-18 | -1.7718e-11 | -5.0487e-11 | -1.9082e-18 | 1.7718e-11 | 5.0487e-11 | 1.2721e-18 | 4.8241e-11 | 8.5168e-12 | -1.2721e-18 | -4.824e-11 | -8.5168e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0937 | 1.1 | 1.0978 | 1.0937 | 3.0238e-13 | -120.3121 | 119.9447 | 3.0235e-13 | -120.3121 | 119.9447
Line4_2_6 | 0 | 0.060452 | 0.060452 | 0 | 0.060452 | 0.060452 | 0 | 0.013961 | 0.013961 | 0 | 0.013961 | 0.013961 | 3.6892e-17 | 0.01474 | 0.0037509 | -3.6892e-17 | -0.014704 | -0.0037143 | 2.5443e-18 | 0.0039919 | 0.014719 | -5.0885e-18 | -0.0039188 | -0.014646 | 0 | -135.6932 | 44.3068 | 0 | 44.3068 | -135.6932 | 1.1 | 1.0939 | 1.088 | 1.1 | 1.09 | 1.0823 | 3.018e-13 | -120.5402 | 120.0098 | 3.0122e-13 | -120.7698 | 120.0757
Line5_6_7 | 0 | 0.060452 | 0.060452 | 0 | 0.060452 | 0.060452 | 0 | 0.013961 | 0.013961 | 0 | 0.013961 | 0.013961 | 2.5443e-17 | 0.014704 | 0.0037143 | -2.5443e-17 | -0.014667 | -0.0036778 | -5.0885e-18 | 0.0039188 | 0.014646 | 7.6328e-18 | -0.0038457 | -0.014572 | 0 | -135.6932 | 44.3068 | 0 | 44.3068 | -135.6932 | 1.1 | 1.09 | 1.0823 | 1.1 | 1.0861 | 1.0765 | 3.0122e-13 | -120.7698 | 120.0757 | 3.0068e-13 | -121.0011 | 120.1422
Line6_7_8 | 0 | 0.060452 | 0.060452 | 0 | 0.060452 | 0.060452 | 0 | 0.013961 | 0.013961 | 0 | 0.013961 | 0.013961 | 1.5266e-17 | 0.014667 | 0.0036778 | -1.781e-17 | -0.014631 | -0.0036413 | -5.0885e-18 | 0.0038457 | 0.014572 | 2.5443e-18 | -0.0037726 | -0.014499 | 0 | -135.6932 | 44.3068 | 0 | 44.3068 | -135.6932 | 1.1 | 1.0861 | 1.0765 | 1.1 | 1.0823 | 1.0708 | 3.0068e-13 | -121.0011 | 120.1422 | 3.0037e-13 | -121.2341 | 120.2095
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6328e-18 | -6.9334e-11 | -1.1449e-10 | -7.6328e-18 | 6.9334e-11 | 1.1449e-10 | -5.0885e-18 | 9.4011e-11 | -1.5791e-11 | 5.0885e-18 | -9.4011e-11 | 1.5791e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0823 | 1.0708 | 1.1 | 1.0823 | 1.0708 | 3.0037e-13 | -121.2341 | 120.2095 | 3.0029e-13 | -121.2341 | 120.2095
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.0885e-18 | -6.9334e-11 | -1.1449e-10 | -5.0885e-18 | 6.9334e-11 | 1.1449e-10 | -2.5443e-18 | 9.4011e-11 | -1.5791e-11 | 2.5443e-18 | -9.4011e-11 | 1.5791e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0823 | 1.0708 | 1.1 | 1.0823 | 1.0708 | 3.0037e-13 | -121.2341 | 120.2095 | 3.0028e-13 | -121.2341 | 120.2095
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0813e-17 | -6.2015e-11 | -1.7671e-10 | -1.0177e-17 | 6.2015e-11 | 1.7671e-10 | 6.3607e-18 | 1.6884e-10 | 2.9809e-11 | -5.0885e-18 | -1.6884e-10 | -2.9809e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0937 | 1.1 | 1.0978 | 1.0937 | 3.0219e-13 | -120.3121 | 119.9447 | 3.0201e-13 | -120.3121 | 119.9447

## LL_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 1.455 | 1.455 | 0 | 1.455 | 1.455 | 0 | 0.33601 | 0.33601 | 0 | 0.33601 | 0.33601 | -1.0547e-16 | 0.28984 | 0.03533 | 7.0314e-17 | -0.24919 | 0.005316 | 2.461e-16 | 0.073022 | 0.26569 | -2.461e-16 | -0.030682 | -0.22336 | 0 | -142.8727 | 37.1273 | 0 | 37.1273 | -142.8727 | 0.95 | 0.88953 | 0.79769 | 0.95 | 0.74721 | 0.66491 | 1.6524e-12 | -128.7319 | 119.553 | 1.6631e-12 | -135.8534 | 128.4907
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.0167e-30 | -9.6789e-10 | -2.6725e-09 | -8.7893e-18 | 9.6789e-10 | 2.6725e-09 | 3.5157e-17 | 2.8224e-09 | 1.3007e-10 | -5.2736e-17 | -2.8224e-09 | -1.3007e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.88953 | 0.79769 | 0.95 | 0.88953 | 0.79769 | 1.6569e-12 | -128.7319 | 119.553 | 1.6591e-12 | -128.7319 | 119.553
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.7579e-17 | -8.0657e-10 | -2.2271e-09 | 8.7893e-18 | 8.0657e-10 | 2.2271e-09 | 1.0547e-16 | 2.352e-09 | 1.0839e-10 | -8.7893e-17 | -2.352e-09 | -1.0839e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.88953 | 0.79769 | 0.95 | 0.88953 | 0.79769 | 1.6591e-12 | -128.7319 | 119.553 | 1.6612e-12 | -128.7319 | 119.553
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.7579e-17 | -4.8394e-10 | -1.3362e-09 | 8.7893e-18 | 4.8394e-10 | 1.3362e-09 | 1.7579e-17 | 1.4112e-09 | 6.5035e-11 | -1.7579e-17 | -1.4112e-09 | -6.5035e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.88953 | 0.79769 | 0.95 | 0.88953 | 0.79769 | 1.6612e-12 | -128.7319 | 119.553 | 1.6622e-12 | -128.7319 | 119.553
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.3946e-18 | -1.6131e-10 | -4.4541e-10 | 4.3946e-18 | 1.6131e-10 | 4.4541e-10 | -1.2742e-31 | 4.7039e-10 | 2.1678e-11 | 1.2741e-31 | -4.7039e-10 | -2.1678e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.88953 | 0.79769 | 0.95 | 0.88953 | 0.79769 | 1.6612e-12 | -128.7319 | 119.553 | 1.6612e-12 | -128.7319 | 119.553
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.1973e-17 | -3.2263e-10 | -8.9083e-10 | 2.1973e-17 | 3.2263e-10 | 8.9083e-10 | 1.7579e-17 | 9.4079e-10 | 4.3357e-11 | 6.3777e-31 | -9.4079e-10 | -4.3357e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.88953 | 0.79769 | 0.95 | 0.88953 | 0.79769 | 1.6622e-12 | -128.7319 | 119.553 | 1.663e-12 | -128.7319 | 119.553
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.3946e-18 | -1.6131e-10 | -4.4541e-10 | 4.3946e-18 | 1.6131e-10 | 4.4541e-10 | 5.2736e-17 | 4.7039e-10 | 2.1678e-11 | -3.5157e-17 | -4.7039e-10 | -2.1678e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.88953 | 0.79769 | 0.95 | 0.88953 | 0.79769 | 1.663e-12 | -128.7319 | 119.553 | 1.6632e-12 | -128.7319 | 119.553
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.0762e-17 | -1.6131e-10 | -4.4541e-10 | 3.0762e-17 | 1.6131e-10 | 4.4541e-10 | 3.5157e-17 | 4.7039e-10 | 2.1678e-11 | -3.5157e-17 | -4.7039e-10 | -2.1678e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.88953 | 0.79769 | 0.95 | 0.88953 | 0.79769 | 1.6532e-12 | -128.7319 | 119.553 | 1.6535e-12 | -128.7319 | 119.553
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.0762e-17 | -1.6131e-10 | -4.4541e-10 | 3.0762e-17 | 1.6131e-10 | 4.4541e-10 | 3.5157e-17 | 4.7039e-10 | 2.1678e-11 | -3.5157e-17 | -4.7039e-10 | -2.1678e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.88953 | 0.79769 | 0.95 | 0.88953 | 0.79769 | 1.6532e-12 | -128.7319 | 119.553 | 1.6535e-12 | -128.7319 | 119.553
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5157e-17 | -1.2905e-09 | -3.5633e-09 | -4.3946e-17 | 1.2905e-09 | 3.5633e-09 | 5.2736e-17 | 3.7632e-09 | 1.7343e-10 | -3.5157e-17 | -3.7632e-09 | -1.7343e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.88953 | 0.79769 | 0.95 | 0.88953 | 0.79769 | 1.6524e-12 | -128.7319 | 119.553 | 1.6546e-12 | -128.7319 | 119.553
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.3946e-18 | -3.2263e-10 | -8.9083e-10 | -4.3946e-18 | 3.2263e-10 | 8.9083e-10 | 1.7579e-17 | 9.4079e-10 | 4.3357e-11 | 1.7579e-17 | -9.4079e-10 | -4.3357e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.88953 | 0.79769 | 0.95 | 0.88953 | 0.79769 | 1.6524e-12 | -128.7319 | 119.553 | 1.6532e-12 | -128.7319 | 119.553
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.3946e-18 | -3.2263e-10 | -8.9083e-10 | -4.3946e-18 | 3.2263e-10 | 8.9083e-10 | 1.7579e-17 | 9.4079e-10 | 4.3357e-11 | 1.7579e-17 | -9.4079e-10 | -4.3357e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.88953 | 0.79769 | 0.95 | 0.88953 | 0.79769 | 1.6524e-12 | -128.7319 | 119.553 | 1.6532e-12 | -128.7319 | 119.553
Line4_2_6 | 0 | 1.455 | 1.455 | 0 | 1.455 | 1.455 | 0 | 0.33601 | 0.33601 | 0 | 0.33601 | 0.33601 | -1.0547e-16 | 0.24919 | -0.005316 | 1.4063e-16 | -0.20855 | 0.045962 | 3.1641e-16 | 0.030682 | 0.22336 | -2.8126e-16 | 0.011658 | -0.18102 | 0 | -142.8727 | 37.1273 | 0 | 37.1273 | -142.8727 | 0.95 | 0.74721 | 0.66491 | 0.95 | 0.62161 | 0.55581 | 1.6631e-12 | -135.8534 | 128.4907 | 1.672e-12 | -146.0722 | 141.3743
Line5_6_7 | 0 | 1.455 | 1.455 | 0 | 1.455 | 1.455 | 0 | 0.33601 | 0.33601 | 0 | 0.33601 | 0.33601 | -1.4063e-16 | 0.20855 | -0.045962 | 1.0547e-16 | -0.1679 | 0.086608 | 2.8126e-16 | -0.011658 | 0.18102 | -2.8126e-16 | 0.053997 | -0.13868 | 0 | -142.8727 | 37.1273 | 0 | 37.1273 | -142.8727 | 0.95 | 0.62161 | 0.55581 | 0.95 | 0.52489 | 0.48658 | 1.672e-12 | -146.0722 | 141.3743 | 1.6809e-12 | -160.7007 | 159.1134
Line6_7_8 | 0 | 1.455 | 1.455 | 0 | 1.455 | 1.455 | 0 | 0.33601 | 0.33601 | 0 | 0.33601 | 0.33601 | -1.4063e-16 | 0.1679 | -0.086608 | 2.1094e-16 | -0.12725 | 0.12725 | 3.5157e-16 | -0.053997 | 0.13868 | -3.5157e-16 | 0.096337 | -0.096337 | 0 | -142.8727 | 37.1273 | 0 | 37.1273 | -142.8727 | 0.95 | 0.52489 | 0.48658 | 0.95 | 0.475 | 0.475 | 1.6809e-12 | -160.7007 | 159.1134 | 1.688e-12 | 180 | 180
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.0314e-17 | 6.4974e-23 | -1.1555e-22 | -4.1403e-30 | -1.022e-16 | 3.2762e-18 | -1.4063e-16 | 1.4329e-09 | -1.4329e-09 | 1.4063e-16 | -1.4329e-09 | 1.4329e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.475 | 0.475 | 0.95 | 0.475 | 0.475 | 1.688e-12 | 180 | 180 | 1.6869e-12 | -180 | 180
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.461e-16 | 1.4063e-16 | -7.0314e-17 | 1.7906e-16 | 3.2762e-18 | 0 | 1.4329e-09 | -1.4329e-09 | 7.0314e-17 | -1.4329e-09 | 1.4329e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.475 | 0.475 | 0.95 | 0.475 | 0.475 | 1.688e-12 | 180 | 180 | 1.6908e-12 | -180 | 180
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.7893e-18 | -1.1292e-09 | -3.1179e-09 | 2.0333e-30 | 1.1292e-09 | 3.1179e-09 | 7.0314e-17 | 3.2928e-09 | 1.5175e-10 | -7.0314e-17 | -3.2928e-09 | -1.5175e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.88953 | 0.79769 | 0.95 | 0.88953 | 0.79769 | 1.6546e-12 | -128.7319 | 119.553 | 1.6569e-12 | -128.7319 | 119.553

## LL_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 1.3784 | 1.3784 | 0 | 1.3784 | 1.3784 | 0 | 0.31833 | 0.31833 | 0 | 0.31833 | 0.31833 | -9.992e-17 | 0.26013 | 0.031709 | 9.992e-17 | -0.22365 | 0.0047711 | 1.8319e-16 | 0.065537 | 0.23846 | -2.1649e-16 | -0.027537 | -0.20046 | 0 | -142.8727 | 37.1273 | 0 | 37.1273 | -142.8727 | 0.9 | 0.84271 | 0.7557 | 0.9 | 0.70788 | 0.62991 | 2.7715e-12 | -128.7319 | 119.553 | 2.7804e-12 | -135.8534 | 128.4907
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.4205e-30 | -8.6869e-10 | -2.3986e-09 | -8.3267e-18 | 8.6869e-10 | 2.3986e-09 | 4.996e-17 | 2.5331e-09 | 1.1674e-10 | -4.996e-17 | -2.5331e-09 | -1.1674e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.84271 | 0.7557 | 0.9 | 0.84271 | 0.7557 | 2.7759e-12 | -128.7319 | 119.553 | 2.7782e-12 | -128.7319 | 119.553
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.9143e-17 | -7.2391e-10 | -1.9988e-09 | 2.0817e-17 | 7.2391e-10 | 1.9988e-09 | 8.3267e-17 | 2.1109e-09 | 9.7283e-11 | -8.3267e-17 | -2.1109e-09 | -9.7283e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.84271 | 0.7557 | 0.9 | 0.84271 | 0.7557 | 2.7782e-12 | -128.7319 | 119.553 | 2.7803e-12 | -128.7319 | 119.553
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.6653e-17 | -4.3434e-10 | -1.1993e-09 | 1.6653e-17 | 4.3434e-10 | 1.1993e-09 | 1.6653e-17 | 1.2665e-09 | 5.837e-11 | -1.6653e-17 | -1.2665e-09 | -5.837e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.84271 | 0.7557 | 0.9 | 0.84271 | 0.7557 | 2.7803e-12 | -128.7319 | 119.553 | 2.7813e-12 | -128.7319 | 119.553
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.3267e-18 | -1.4478e-10 | -3.9976e-10 | 8.3267e-18 | 1.4478e-10 | 3.9976e-10 | -4.0405e-31 | 4.2218e-10 | 1.9457e-11 | 4.0404e-31 | -4.2218e-10 | -1.9457e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.84271 | 0.7557 | 0.9 | 0.84271 | 0.7557 | 2.7803e-12 | -128.7319 | 119.553 | 2.7802e-12 | -128.7319 | 119.553
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.1633e-18 | -2.8956e-10 | -7.9952e-10 | 1.249e-17 | 2.8956e-10 | 7.9952e-10 | 3.3307e-17 | 8.4436e-10 | 3.8913e-11 | -3.3307e-17 | -8.4436e-10 | -3.8913e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.84271 | 0.7557 | 0.9 | 0.84271 | 0.7557 | 2.7813e-12 | -128.7319 | 119.553 | 2.7821e-12 | -128.7319 | 119.553
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.1633e-18 | -1.4478e-10 | -3.9976e-10 | 1.249e-17 | 1.4478e-10 | 3.9976e-10 | -1.6653e-17 | 4.2218e-10 | 1.9457e-11 | 1.6653e-17 | -4.2218e-10 | -1.9457e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.84271 | 0.7557 | 0.9 | 0.84271 | 0.7557 | 2.7821e-12 | -128.7319 | 119.553 | 2.7823e-12 | -128.7319 | 119.553
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.6653e-17 | -1.4478e-10 | -3.9976e-10 | 1.6653e-17 | 1.4478e-10 | 3.9976e-10 | -1.6653e-17 | 4.2218e-10 | 1.9457e-11 | 8.0586e-31 | -4.2218e-10 | -1.9457e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.84271 | 0.7557 | 0.9 | 0.84271 | 0.7557 | 2.7723e-12 | -128.7319 | 119.553 | 2.7725e-12 | -128.7319 | 119.553
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.6653e-17 | -1.4478e-10 | -3.9976e-10 | 1.6653e-17 | 1.4478e-10 | 3.9976e-10 | -1.6653e-17 | 4.2218e-10 | 1.9457e-11 | 8.0586e-31 | -4.2218e-10 | -1.9457e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.84271 | 0.7557 | 0.9 | 0.84271 | 0.7557 | 2.7723e-12 | -128.7319 | 119.553 | 2.7725e-12 | -128.7319 | 119.553
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1633e-18 | -1.1582e-09 | -3.1981e-09 | -4.1633e-18 | 1.1582e-09 | 3.1981e-09 | 6.6613e-17 | 3.3775e-09 | 1.5565e-10 | -9.992e-17 | -3.3775e-09 | -1.5565e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.84271 | 0.7557 | 0.9 | 0.84271 | 0.7557 | 2.7715e-12 | -128.7319 | 119.553 | 2.7737e-12 | -128.7319 | 119.553
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.0555e-31 | -2.8956e-10 | -7.9952e-10 | 1.6116e-30 | 2.8956e-10 | 7.9952e-10 | 1.6653e-17 | 8.4436e-10 | 3.8913e-11 | -3.3307e-17 | -8.4436e-10 | -3.8913e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.84271 | 0.7557 | 0.9 | 0.84271 | 0.7557 | 2.7715e-12 | -128.7319 | 119.553 | 2.7723e-12 | -128.7319 | 119.553
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.0555e-31 | -2.8956e-10 | -7.9952e-10 | 1.6116e-30 | 2.8956e-10 | 7.9952e-10 | 1.6653e-17 | 8.4436e-10 | 3.8913e-11 | -3.3307e-17 | -8.4436e-10 | -3.8913e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.84271 | 0.7557 | 0.9 | 0.84271 | 0.7557 | 2.7715e-12 | -128.7319 | 119.553 | 2.7723e-12 | -128.7319 | 119.553
Line4_2_6 | 0 | 1.3784 | 1.3784 | 0 | 1.3784 | 1.3784 | 0 | 0.31833 | 0.31833 | 0 | 0.31833 | 0.31833 | -1.6653e-16 | 0.22365 | -0.0047711 | 1.3323e-16 | -0.18717 | 0.041251 | 2.6645e-16 | 0.027537 | 0.20046 | -2.6645e-16 | 0.010463 | -0.16246 | 0 | -142.8727 | 37.1273 | 0 | 37.1273 | -142.8727 | 0.9 | 0.70788 | 0.62991 | 0.9 | 0.5889 | 0.52656 | 2.7804e-12 | -135.8534 | 128.4907 | 2.7881e-12 | -146.0722 | 141.3743
Line5_6_7 | 0 | 1.3784 | 1.3784 | 0 | 1.3784 | 1.3784 | 0 | 0.31833 | 0.31833 | 0 | 0.31833 | 0.31833 | -3.3307e-17 | 0.18717 | -0.041251 | 4.8758e-30 | -0.15069 | 0.077731 | 1.3323e-16 | -0.010463 | 0.16246 | -9.992e-17 | 0.048463 | -0.12446 | 0 | -142.8727 | 37.1273 | 0 | 37.1273 | -142.8727 | 0.9 | 0.5889 | 0.52656 | 0.9 | 0.49726 | 0.46097 | 2.7881e-12 | -146.0722 | 141.3743 | 2.7958e-12 | -160.7007 | 159.1134
Line6_7_8 | 0 | 1.3784 | 1.3784 | 0 | 1.3784 | 1.3784 | 0 | 0.31833 | 0.31833 | 0 | 0.31833 | 0.31833 | -1.3323e-16 | 0.15069 | -0.077731 | 1.3323e-16 | -0.11421 | 0.11421 | 2.6645e-16 | -0.048463 | 0.12446 | -2.6645e-16 | 0.086463 | -0.086463 | 0 | -142.8727 | 37.1273 | 0 | 37.1273 | -142.8727 | 0.9 | 0.49726 | 0.46097 | 0.9 | 0.45 | 0.45 | 2.7958e-12 | -160.7007 | 159.1134 | 2.802e-12 | 180 | 180
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3323e-16 | -9.992e-17 | -1.3323e-16 | -1.3323e-16 | 1.0286e-16 | 1.3617e-16 | 6.6613e-17 | 1.286e-09 | -1.286e-09 | -6.5128e-30 | -1.286e-09 | 1.286e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.45 | 0.45 | 0.9 | 0.45 | 0.45 | 2.802e-12 | 180 | 180 | 2.8009e-12 | -180 | 180
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.6613e-17 | -2.6645e-16 | -1.542e-22 | -6.6613e-17 | 2.6939e-16 | 2.9405e-18 | 3.2577e-30 | 1.286e-09 | -1.286e-09 | -3.2608e-30 | -1.286e-09 | 1.286e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.45 | 0.45 | 0.9 | 0.45 | 0.45 | 2.802e-12 | 180 | 180 | 2.8047e-12 | -180 | 180
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6653e-17 | -1.0135e-09 | -2.7983e-09 | -1.6653e-17 | 1.0135e-09 | 2.7983e-09 | 4.996e-17 | 2.9553e-09 | 1.362e-10 | -6.6613e-17 | -2.9553e-09 | -1.362e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.84271 | 0.7557 | 0.9 | 0.84271 | 0.7557 | 2.7737e-12 | -128.7319 | 119.553 | 2.7759e-12 | -128.7319 | 119.553

## LL_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0.051843 | 0.051843 | 0 | 0.051843 | 0.051843 | 0 | 0.011973 | 0.011973 | 0 | 0.011973 | 0.011973 | -1.648e-18 | 0.010966 | 0.0028847 | 1.648e-18 | -0.010915 | -0.0028331 | 1.0987e-17 | 0.0029326 | 0.010936 | -1.0987e-17 | -0.0028788 | -0.010882 | 0 | -135.2796 | 44.7204 | 0 | 44.7204 | -135.2796 | 0.95 | 0.94815 | 0.94465 | 0.95 | 0.94283 | 0.93921 | 1.1828e-14 | -120.3084 | 119.9432 | 1.2247e-14 | -120.5043 | 120.1275
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.8666e-20 | -3.8309e-11 | -1.1119e-10 | -2.06e-19 | 3.8309e-11 | 1.1119e-10 | 2.7466e-18 | 1.0665e-10 | 1.9584e-11 | -1.648e-18 | -1.0665e-10 | -1.9584e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94815 | 0.94465 | 0.95 | 0.94815 | 0.94465 | 1.197e-14 | -120.3084 | 119.9432 | 1.2044e-14 | -120.3084 | 119.9432
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.8666e-20 | -3.1925e-11 | -9.2658e-11 | 2.06e-19 | 3.1925e-11 | 9.2658e-11 | 3.296e-18 | 8.8872e-11 | 1.632e-11 | -2.7466e-18 | -8.8872e-11 | -1.632e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94815 | 0.94465 | 0.95 | 0.94815 | 0.94465 | 1.2044e-14 | -120.3084 | 119.9432 | 1.2114e-14 | -120.3084 | 119.9432
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.8666e-20 | -1.9155e-11 | -5.5595e-11 | 3.4333e-19 | 1.9155e-11 | 5.5595e-11 | 1.0987e-18 | 5.3323e-11 | 9.7921e-12 | -1.0987e-18 | -5.3323e-11 | -9.7921e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94815 | 0.94465 | 0.95 | 0.94815 | 0.94465 | 1.2114e-14 | -120.3084 | 119.9432 | 1.2151e-14 | -120.3084 | 119.9432
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.06e-19 | -6.3849e-12 | -1.8532e-11 | 6.8666e-20 | 6.3849e-12 | 1.8532e-11 | 5.4933e-19 | 1.7774e-11 | 3.264e-12 | -5.4933e-19 | -1.7775e-11 | -3.264e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94815 | 0.94465 | 0.95 | 0.94815 | 0.94465 | 1.2114e-14 | -120.3084 | 119.9432 | 1.2113e-14 | -120.3084 | 119.9432
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.8066e-19 | -1.277e-11 | -3.7063e-11 | 4.8066e-19 | 1.277e-11 | 3.7063e-11 | -1.0193e-34 | 3.5549e-11 | 6.5281e-12 | -1.0987e-18 | -3.5549e-11 | -6.5281e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94815 | 0.94465 | 0.95 | 0.94815 | 0.94465 | 1.2151e-14 | -120.3084 | 119.9432 | 1.2183e-14 | -120.3084 | 119.9432
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.5533e-19 | -6.3849e-12 | -1.8532e-11 | 7.5533e-19 | 6.3849e-12 | 1.8532e-11 | 1.0987e-18 | 1.7774e-11 | 3.264e-12 | -1.0987e-18 | -1.7774e-11 | -3.264e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94815 | 0.94465 | 0.95 | 0.94815 | 0.94465 | 1.2183e-14 | -120.3084 | 119.9432 | 1.2195e-14 | -120.3084 | 119.9432
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.8066e-19 | -6.3849e-12 | -1.8532e-11 | 7.5533e-19 | 6.3849e-12 | 1.8532e-11 | 1.0987e-18 | 1.7774e-11 | 3.264e-12 | -1.0987e-18 | -1.7774e-11 | -3.264e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94815 | 0.94465 | 0.95 | 0.94815 | 0.94465 | 1.1858e-14 | -120.3084 | 119.9432 | 1.187e-14 | -120.3084 | 119.9432
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.8066e-19 | -6.3849e-12 | -1.8532e-11 | 7.5533e-19 | 6.3849e-12 | 1.8532e-11 | 1.0987e-18 | 1.7774e-11 | 3.264e-12 | -1.0987e-18 | -1.7774e-11 | -3.264e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94815 | 0.94465 | 0.95 | 0.94815 | 0.94465 | 1.1858e-14 | -120.3084 | 119.9432 | 1.187e-14 | -120.3084 | 119.9432
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7167e-18 | -5.1079e-11 | -1.4825e-10 | -1.7167e-18 | 5.1079e-11 | 1.4825e-10 | 2.7466e-18 | 1.422e-10 | 2.6112e-11 | -3.296e-18 | -1.422e-10 | -2.6112e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94815 | 0.94465 | 0.95 | 0.94815 | 0.94465 | 1.1828e-14 | -120.3084 | 119.9432 | 1.1897e-14 | -120.3084 | 119.9432
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.12e-19 | -1.277e-11 | -3.7063e-11 | -4.12e-19 | 1.277e-11 | 3.7063e-11 | 1.0987e-18 | 3.5549e-11 | 6.5281e-12 | -1.0987e-18 | -3.5549e-11 | -6.5281e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94815 | 0.94465 | 0.95 | 0.94815 | 0.94465 | 1.1828e-14 | -120.3084 | 119.9432 | 1.1858e-14 | -120.3084 | 119.9432
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.12e-19 | -1.277e-11 | -3.7063e-11 | -4.12e-19 | 1.277e-11 | 3.7063e-11 | 1.0987e-18 | 3.5549e-11 | 6.5281e-12 | -1.0987e-18 | -3.5549e-11 | -6.5281e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94815 | 0.94465 | 0.95 | 0.94815 | 0.94465 | 1.1828e-14 | -120.3084 | 119.9432 | 1.1858e-14 | -120.3084 | 119.9432
Line4_2_6 | 0 | 0.051843 | 0.051843 | 0 | 0.051843 | 0.051843 | 0 | 0.011973 | 0.011973 | 0 | 0.011973 | 0.011973 | -3.296e-18 | 0.010915 | 0.0028331 | 1.0987e-18 | -0.010863 | -0.0027815 | 8.7893e-18 | 0.0028788 | 0.010882 | -9.8879e-18 | -0.0028251 | -0.010828 | 0 | -135.2796 | 44.7204 | 0 | 44.7204 | -135.2796 | 0.95 | 0.94283 | 0.93921 | 0.95 | 0.93752 | 0.93379 | 1.2247e-14 | -120.5043 | 120.1275 | 1.2604e-14 | -120.7024 | 120.3141
Line5_6_7 | 0 | 0.051843 | 0.051843 | 0 | 0.051843 | 0.051843 | 0 | 0.011973 | 0.011973 | 0 | 0.011973 | 0.011973 | -1.4501e-33 | 0.010863 | 0.0027815 | 1.4923e-33 | -0.010812 | -0.0027299 | 6.5919e-18 | 0.0028251 | 0.010828 | -6.5919e-18 | -0.0027713 | -0.010775 | 0 | -135.2796 | 44.7204 | 0 | 44.7204 | -135.2796 | 0.95 | 0.93752 | 0.93379 | 0.95 | 0.93223 | 0.92837 | 1.2604e-14 | -120.7024 | 120.3141 | 1.2971e-14 | -120.9028 | 120.5028
Line6_7_8 | 0 | 0.051843 | 0.051843 | 0 | 0.051843 | 0.051843 | 0 | 0.011973 | 0.011973 | 0 | 0.011973 | 0.011973 | -6.5919e-18 | 0.010812 | 0.0027299 | 4.3946e-18 | -0.01076 | -0.0026783 | 1.3184e-17 | 0.0027713 | 0.010775 | -1.5381e-17 | -0.0027175 | -0.010721 | 0 | -135.2796 | 44.7204 | 0 | 44.7204 | -135.2796 | 0.95 | 0.93223 | 0.92837 | 0.95 | 0.92694 | 0.92297 | 1.2971e-14 | -120.9028 | 120.5028 | 1.3234e-14 | -121.1055 | 120.6937
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1973e-18 | -7.7759e-11 | -9.1252e-11 | -4.3946e-18 | 7.7759e-11 | 9.1252e-11 | -2.1973e-18 | 6.2294e-11 | -3.8923e-11 | -1.0125e-33 | -6.2294e-11 | 3.8923e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.92694 | 0.92297 | 0.95 | 0.92694 | 0.92297 | 1.3234e-14 | -121.1055 | 120.6937 | 1.3201e-14 | -121.1055 | 120.6937
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.1973e-18 | -7.7759e-11 | -9.1252e-11 | -5.1237e-34 | 7.7759e-11 | 9.1252e-11 | -4.3946e-18 | 6.2294e-11 | -3.8923e-11 | 2.1973e-18 | -6.2294e-11 | 3.8923e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.92694 | 0.92297 | 0.95 | 0.92694 | 0.92297 | 1.3234e-14 | -121.1055 | 120.6937 | 1.336e-14 | -121.1055 | 120.6937
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.5533e-19 | -4.4694e-11 | -1.2972e-10 | -7.5533e-19 | 4.4694e-11 | 1.2972e-10 | 2.7466e-18 | 1.2442e-10 | 2.2848e-11 | -2.7466e-18 | -1.2442e-10 | -2.2848e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94815 | 0.94465 | 0.95 | 0.94815 | 0.94465 | 1.1897e-14 | -120.3084 | 119.9432 | 1.197e-14 | -120.3084 | 119.9432

## LL_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0.049114 | 0.049114 | 0 | 0.049114 | 0.049114 | 0 | 0.011342 | 0.011342 | 0 | 0.011342 | 0.011342 | -2.0817e-18 | 0.0098425 | 0.002589 | 1.5613e-18 | -0.0097961 | -0.0025427 | 1.0408e-17 | 0.002632 | 0.009815 | -1.1449e-17 | -0.0025837 | -0.0097667 | 0 | -135.2796 | 44.7204 | 0 | 44.7204 | -135.2796 | 0.9 | 0.89825 | 0.89493 | 0.9 | 0.89321 | 0.88978 | 8.7138e-15 | -120.3084 | 119.9432 | 9.1786e-15 | -120.5043 | 120.1275
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.301e-19 | -3.4383e-11 | -9.9793e-11 | -3.9031e-19 | 3.4383e-11 | 9.9793e-11 | 3.1225e-18 | 9.5716e-11 | 1.7577e-11 | -3.6429e-18 | -9.5716e-11 | -1.7577e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89825 | 0.89493 | 0.9 | 0.89825 | 0.89493 | 8.8558e-15 | -120.3084 | 119.9432 | 8.9297e-15 | -120.3084 | 119.9432
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.5052e-20 | -2.8652e-11 | -8.3161e-11 | -6.5052e-20 | 2.8652e-11 | 8.3161e-11 | 2.0817e-18 | 7.9764e-11 | 1.4648e-11 | -2.6021e-18 | -7.9764e-11 | -1.4648e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89825 | 0.89493 | 0.9 | 0.89825 | 0.89493 | 8.9297e-15 | -120.3084 | 119.9432 | 9.0001e-15 | -120.3084 | 119.9432
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.301e-19 | -1.7191e-11 | -4.9896e-11 | -1.301e-19 | 1.7191e-11 | 4.9896e-11 | 5.2042e-19 | 4.7858e-11 | 8.7885e-12 | -5.2042e-19 | -4.7858e-11 | -8.7885e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89825 | 0.89493 | 0.9 | 0.89825 | 0.89493 | 9.0001e-15 | -120.3084 | 119.9432 | 9.0366e-15 | -120.3084 | 119.9432
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.5052e-19 | -5.7305e-12 | -1.6632e-11 | -6.5052e-19 | 5.7305e-12 | 1.6632e-11 | 1.0218e-34 | 1.5953e-11 | 2.9295e-12 | 5.2042e-19 | -1.5953e-11 | -2.9295e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89825 | 0.89493 | 0.9 | 0.89825 | 0.89493 | 9.0001e-15 | -120.3084 | 119.9432 | 8.999e-15 | -120.3084 | 119.9432
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.9031e-19 | -1.1461e-11 | -3.3264e-11 | 6.5052e-19 | 1.1461e-11 | 3.3264e-11 | 5.2042e-19 | 3.1905e-11 | 5.859e-12 | -1.0408e-18 | -3.1905e-11 | -5.859e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89825 | 0.89493 | 0.9 | 0.89825 | 0.89493 | 9.0366e-15 | -120.3084 | 119.9432 | 9.0689e-15 | -120.3084 | 119.9432
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.2042e-19 | -5.7305e-12 | -1.6632e-11 | 7.8063e-19 | 5.7305e-12 | 1.6632e-11 | 5.2042e-19 | 1.5953e-11 | 2.9295e-12 | -1.0408e-18 | -1.5953e-11 | -2.9295e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89825 | 0.89493 | 0.9 | 0.89825 | 0.89493 | 9.0689e-15 | -120.3084 | 119.9432 | 9.0809e-15 | -120.3084 | 119.9432
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.5052e-20 | -5.7305e-12 | -1.6632e-11 | 1.9516e-19 | 5.7305e-12 | 1.6632e-11 | 5.2042e-19 | 1.5953e-11 | 2.9295e-12 | -5.2042e-19 | -1.5953e-11 | -2.9295e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89825 | 0.89493 | 0.9 | 0.89825 | 0.89493 | 8.7434e-15 | -120.3084 | 119.9432 | 8.7555e-15 | -120.3084 | 119.9432
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.5052e-20 | -5.7305e-12 | -1.6632e-11 | 1.9516e-19 | 5.7305e-12 | 1.6632e-11 | 5.2042e-19 | 1.5953e-11 | 2.9295e-12 | -5.2042e-19 | -1.5953e-11 | -2.9295e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89825 | 0.89493 | 0.9 | 0.89825 | 0.89493 | 8.7434e-15 | -120.3084 | 119.9432 | 8.7555e-15 | -120.3084 | 119.9432
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1709e-18 | -4.5844e-11 | -1.3306e-10 | -1.4311e-18 | 4.5844e-11 | 1.3306e-10 | 3.1225e-18 | 1.2762e-10 | 2.3436e-11 | -2.6021e-18 | -1.2762e-10 | -2.3436e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89825 | 0.89493 | 0.9 | 0.89825 | 0.89493 | 8.7138e-15 | -120.3084 | 119.9432 | 8.7832e-15 | -120.3084 | 119.9432
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.9031e-19 | -1.1461e-11 | -3.3264e-11 | 3.9031e-19 | 1.1461e-11 | 3.3264e-11 | -5.9361e-35 | 3.1905e-11 | 5.859e-12 | -5.2042e-19 | -3.1905e-11 | -5.859e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89825 | 0.89493 | 0.9 | 0.89825 | 0.89493 | 8.7138e-15 | -120.3084 | 119.9432 | 8.7434e-15 | -120.3084 | 119.9432
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.9031e-19 | -1.1461e-11 | -3.3264e-11 | 3.9031e-19 | 1.1461e-11 | 3.3264e-11 | -5.9361e-35 | 3.1905e-11 | 5.859e-12 | -5.2042e-19 | -3.1905e-11 | -5.859e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89825 | 0.89493 | 0.9 | 0.89825 | 0.89493 | 8.7138e-15 | -120.3084 | 119.9432 | 8.7434e-15 | -120.3084 | 119.9432
Line4_2_6 | 0 | 0.049114 | 0.049114 | 0 | 0.049114 | 0.049114 | 0 | 0.011342 | 0.011342 | 0 | 0.011342 | 0.011342 | -2.0817e-18 | 0.0097961 | 0.0025427 | 3.1225e-18 | -0.0097498 | -0.0024964 | 9.3675e-18 | 0.0025837 | 0.0097667 | -1.1449e-17 | -0.0025355 | -0.0097185 | 0 | -135.2796 | 44.7204 | 0 | 44.7204 | -135.2796 | 0.9 | 0.89321 | 0.88978 | 0.9 | 0.88818 | 0.88464 | 9.1786e-15 | -120.5043 | 120.1275 | 9.5594e-15 | -120.7024 | 120.3141
Line5_6_7 | 0 | 0.049114 | 0.049114 | 0 | 0.049114 | 0.049114 | 0 | 0.011342 | 0.011342 | 0 | 0.011342 | 0.011342 | -2.0817e-18 | 0.0097498 | 0.0024964 | 2.0817e-18 | -0.0097035 | -0.0024501 | 1.249e-17 | 0.0025355 | 0.0097185 | -1.4572e-17 | -0.0024873 | -0.0096702 | 0 | -135.2796 | 44.7204 | 0 | 44.7204 | -135.2796 | 0.9 | 0.88818 | 0.88464 | 0.9 | 0.88316 | 0.87951 | 9.5594e-15 | -120.7024 | 120.3141 | 9.9099e-15 | -120.9028 | 120.5028
Line6_7_8 | 0 | 0.049114 | 0.049114 | 0 | 0.049114 | 0.049114 | 0 | 0.011342 | 0.011342 | 0 | 0.011342 | 0.011342 | -4.1633e-18 | 0.0097035 | 0.0024501 | 2.0817e-18 | -0.0096572 | -0.0024038 | 8.3267e-18 | 0.0024873 | 0.0096702 | -8.3267e-18 | -0.002439 | -0.009622 | 0 | -135.2796 | 44.7204 | 0 | 44.7204 | -135.2796 | 0.9 | 0.88316 | 0.87951 | 0.9 | 0.87816 | 0.87439 | 9.9099e-15 | -120.9028 | 120.5028 | 1.019e-14 | -121.1055 | 120.6937
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1633e-18 | -6.9789e-11 | -8.1899e-11 | -6.245e-18 | 6.9789e-11 | 8.1899e-11 | 7.4048e-34 | 5.5909e-11 | -3.4934e-11 | -1.1071e-33 | -5.5909e-11 | 3.4934e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.87816 | 0.87439 | 0.9 | 0.87816 | 0.87439 | 1.019e-14 | -121.1055 | 120.6937 | 1.0157e-14 | -121.1055 | 120.6937
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.7024e-34 | -6.9789e-11 | -8.1899e-11 | -2.0817e-18 | 6.9789e-11 | 8.1899e-11 | 2.0817e-18 | 5.5909e-11 | -3.4934e-11 | -3.7418e-34 | -5.5909e-11 | 3.4934e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.87816 | 0.87439 | 0.9 | 0.87816 | 0.87439 | 1.019e-14 | -121.1055 | 120.6937 | 1.0299e-14 | -121.1055 | 120.6937
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2526e-19 | -4.0113e-11 | -1.1643e-10 | -8.4568e-19 | 4.0113e-11 | 1.1643e-10 | 2.0817e-18 | 1.1167e-10 | 2.0507e-11 | -2.0817e-18 | -1.1167e-10 | -2.0507e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89825 | 0.89493 | 0.9 | 0.89825 | 0.89493 | 8.7832e-15 | -120.3084 | 119.9432 | 8.8558e-15 | -120.3084 | 119.9432

## LG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.044184 | 2.2572e-06 | 2.2572e-06 | 0.044184 | 1.8823e-06 | 1.8823e-06 | 0.010204 | 5.2127e-07 | 5.2127e-07 | 0.010204 | 4.347e-07 | 4.347e-07 | 6.5073e-05 | 5.08e-07 | -4.3933e-07 | -4.8804e-05 | -4.2956e-07 | 3.6013e-07 | 0.00013015 | -7.9327e-07 | -8.2932e-07 | -9.7608e-05 | 6.5748e-07 | 6.945e-07 | -89.624 | -92.1793 | -92.1793 | 90.376 | 87.3161 | 87.3161 | 0.01426 | 1.8071 | 1.8004 | 0.010695 | 1.8067 | 1.7997 | -26.189 | -149.5445 | 149.9086 | -26.189 | -149.5256 | 149.9071
Line10_11_12 | 2.2533e-06 | 2.2533e-06 | 2.2533e-06 | 1.8785e-06 | 1.8785e-06 | 1.8785e-06 | 5.2037e-07 | 5.2038e-07 | 5.2038e-07 | 4.3383e-07 | 4.3383e-07 | 4.3383e-07 | 3.0225e-09 | 5.066e-07 | -4.3912e-07 | -2.4702e-09 | -4.2809e-07 | 3.6006e-07 | 6.7769e-09 | -7.9225e-07 | -8.2761e-07 | -5.6716e-09 | 6.5678e-07 | 6.9313e-07 | -92.152 | -92.1412 | -92.1412 | 87.3462 | 87.3591 | 87.3591 | 0.01426 | 1.8071 | 1.8004 | 0.01426 | 1.8071 | 1.8004 | -26.1889 | -149.5445 | 149.9086 | -26.1889 | -149.5445 | 149.9086
Line11_12_13 | 1.8777e-06 | 1.8777e-06 | 1.8777e-06 | 1.503e-06 | 1.503e-06 | 1.503e-06 | 4.3364e-07 | 4.3365e-07 | 4.3365e-07 | 3.471e-07 | 3.471e-07 | 3.471e-07 | 2.5187e-09 | 4.2217e-07 | -3.6594e-07 | -1.9665e-09 | -3.4365e-07 | 2.8687e-07 | 5.6474e-09 | -6.6021e-07 | -6.8967e-07 | -4.5421e-09 | 5.2473e-07 | 5.5519e-07 | -92.152 | -92.1412 | -92.1412 | 87.2208 | 87.2343 | 87.2343 | 0.01426 | 1.8071 | 1.8004 | 0.01426 | 1.8071 | 1.8004 | -26.1889 | -149.5445 | 149.9086 | -26.1889 | -149.5445 | 149.9086
Line12_13_15 | 1.1266e-06 | 1.1266e-06 | 1.1266e-06 | 0 | 0 | 0 | 2.6019e-07 | 2.6019e-07 | 2.6019e-07 | 0 | 0 | 0 | 1.5112e-09 | 2.533e-07 | -2.1956e-07 | -9.5897e-10 | -1.7479e-07 | 1.405e-07 | 3.3884e-09 | -3.9612e-07 | -4.138e-07 | -2.2832e-09 | 2.6065e-07 | 2.7933e-07 | -92.152 | -92.1412 | -92.1412 | 0 | 0 | 0 | 0.01426 | 1.8071 | 1.8004 | 0.014259 | 1.8071 | 1.8004 | -26.1889 | -149.5445 | 149.9086 | -26.1889 | -149.5445 | 149.9086
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.0374e-10 | 8.4433e-08 | -7.3187e-08 | 4.8518e-11 | -5.9212e-09 | -5.877e-09 | 1.1295e-09 | -1.3204e-07 | -1.3793e-07 | -2.4229e-11 | -3.4307e-09 | 3.4562e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01426 | 1.8071 | 1.8004 | 0.01426 | 1.8071 | 1.8004 | -26.1889 | -149.5445 | 149.9086 | -26.1889 | -149.5445 | 149.9086
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0075e-09 | 1.6887e-07 | -1.4637e-07 | -4.5522e-10 | -9.0354e-08 | 6.731e-08 | 2.2589e-09 | -2.6408e-07 | -2.7587e-07 | -1.1537e-09 | 1.2861e-07 | 1.4139e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014259 | 1.8071 | 1.8004 | 0.014259 | 1.8071 | 1.8004 | -26.1889 | -149.5445 | 149.9086 | -26.1889 | -149.5445 | 149.9086
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.0374e-10 | 8.4433e-08 | -7.3187e-08 | 4.8518e-11 | -5.9212e-09 | -5.877e-09 | 1.1295e-09 | -1.3204e-07 | -1.3793e-07 | -2.4229e-11 | -3.4307e-09 | 3.4562e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014259 | 1.8071 | 1.8004 | 0.014259 | 1.8071 | 1.8004 | -26.1889 | -149.5445 | 149.9086 | -26.1889 | -149.5445 | 149.9086
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.0376e-10 | 8.4433e-08 | -7.3187e-08 | 4.8519e-11 | -5.9212e-09 | -5.877e-09 | 1.1295e-09 | -1.3204e-07 | -1.3793e-07 | -2.423e-11 | -3.4307e-09 | 3.4562e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01426 | 1.8071 | 1.8004 | 0.01426 | 1.8071 | 1.8004 | -26.189 | -149.5445 | 149.9086 | -26.189 | -149.5445 | 149.9086
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.0376e-10 | 8.4433e-08 | -7.3187e-08 | 4.8519e-11 | -5.9212e-09 | -5.877e-09 | 1.1295e-09 | -1.3204e-07 | -1.3793e-07 | -2.423e-11 | -3.4307e-09 | 3.4562e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01426 | 1.8071 | 1.8004 | 0.01426 | 1.8071 | 1.8004 | -26.189 | -149.5445 | 149.9086 | -26.189 | -149.5445 | 149.9086
Line1_1_3 | 3.0044e-06 | 3.0044e-06 | 3.0044e-06 | 2.6296e-06 | 2.6296e-06 | 2.6296e-06 | 6.9383e-07 | 6.9384e-07 | 6.9384e-07 | 6.0728e-07 | 6.0728e-07 | 6.0728e-07 | 4.0301e-09 | 6.7547e-07 | -5.855e-07 | -3.4778e-09 | -5.9695e-07 | 5.0643e-07 | 9.036e-09 | -1.0563e-06 | -1.1035e-06 | -7.9307e-09 | 9.2086e-07 | 9.69e-07 | -92.152 | -92.1412 | -92.1412 | 87.4895 | 87.5018 | 87.5018 | 0.01426 | 1.8071 | 1.8004 | 0.01426 | 1.8071 | 1.8004 | -26.189 | -149.5445 | 149.9086 | -26.1889 | -149.5445 | 149.9086
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0075e-09 | 1.6887e-07 | -1.4637e-07 | -4.5524e-10 | -9.0354e-08 | 6.731e-08 | 2.259e-09 | -2.6408e-07 | -2.7587e-07 | -1.1537e-09 | 1.2861e-07 | 1.4139e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01426 | 1.8071 | 1.8004 | 0.01426 | 1.8071 | 1.8004 | -26.189 | -149.5445 | 149.9086 | -26.189 | -149.5445 | 149.9086
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0075e-09 | 1.6887e-07 | -1.4637e-07 | -4.5524e-10 | -9.0354e-08 | 6.731e-08 | 2.259e-09 | -2.6408e-07 | -2.7587e-07 | -1.1537e-09 | 1.2861e-07 | 1.4139e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01426 | 1.8071 | 1.8004 | 0.01426 | 1.8071 | 1.8004 | -26.189 | -149.5445 | 149.9086 | -26.189 | -149.5445 | 149.9086
Line4_2_6 | 0.044184 | 1.8815e-06 | 1.8815e-06 | 0.044184 | 1.5064e-06 | 1.5064e-06 | 0.010204 | 4.3451e-07 | 4.3451e-07 | 0.010204 | 3.4789e-07 | 3.4789e-07 | 4.8804e-05 | 4.2365e-07 | -3.66e-07 | -3.2536e-05 | -3.4507e-07 | 2.8686e-07 | 9.7608e-05 | -6.6091e-07 | -6.9105e-07 | -6.5072e-05 | 5.2518e-07 | 5.5624e-07 | -89.624 | -92.1856 | -92.1856 | 90.376 | 87.1862 | 87.1862 | 0.010695 | 1.8067 | 1.7997 | 0.00713 | 1.8063 | 1.799 | -26.189 | -149.5256 | 149.9071 | -26.189 | -149.5067 | 149.9055
Line5_6_7 | 0.044184 | 1.5056e-06 | 1.5056e-06 | 0.044183 | 1.1303e-06 | 1.1303e-06 | 0.010204 | 3.477e-07 | 3.477e-07 | 0.010204 | 2.6103e-07 | 2.6103e-07 | 3.2536e-05 | 3.3916e-07 | -2.9272e-07 | -1.6268e-05 | -2.6044e-07 | 2.1362e-07 | 6.5072e-05 | -5.286e-07 | -5.5278e-07 | -3.2535e-05 | 3.9292e-07 | 4.1798e-07 | -89.624 | -92.1915 | -92.1915 | 90.3761 | 86.9747 | 86.9747 | 0.00713 | 1.8063 | 1.799 | 0.003565 | 1.8059 | 1.7983 | -26.189 | -149.5067 | 149.9055 | -26.189 | -149.4878 | 149.904
Line6_7_8 | 0.044183 | 1.1294e-06 | 1.1294e-06 | 0.044183 | 0 | 0 | 0.010204 | 2.6083e-07 | 2.6083e-07 | 0.010204 | 0 | 0 | 1.6268e-05 | 2.5453e-07 | -2.1948e-07 | -1.9854e-14 | -1.7567e-07 | 1.4042e-07 | 3.2535e-05 | -3.9634e-07 | -4.1452e-07 | 1.3822e-14 | 2.6072e-07 | 2.7972e-07 | -89.6239 | -92.1964 | -92.1964 | 90.3761 | 0 | 0 | 0.003565 | 1.8059 | 1.7983 | 0 | 1.8055 | 1.7976 | -26.189 | -149.4878 | 149.904 | 0 | -149.4689 | 149.9024
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7435e-19 | 8.4884e-08 | -7.3135e-08 | -3.0014e-17 | -5.9012e-09 | -5.8485e-09 | -1.0989e-19 | -1.3207e-07 | -1.3814e-07 | 1.8316e-17 | -3.4197e-09 | 3.4501e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8055 | 1.7976 | 0 | 1.8055 | 1.7976 | 0 | -149.4689 | 149.9024 | 0 | -149.4689 | 149.9024
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7435e-19 | 8.4884e-08 | -7.3135e-08 | -3.0014e-17 | -5.9012e-09 | -5.8485e-09 | -1.0989e-19 | -1.3207e-07 | -1.3814e-07 | 1.8316e-17 | -3.4197e-09 | 3.4501e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8055 | 1.7976 | 0 | 1.8055 | 1.7976 | 0 | -149.4689 | 149.9024 | 0 | -149.4689 | 149.9024
Line9_3_11 | 2.6288e-06 | 2.6288e-06 | 2.6288e-06 | 2.2541e-06 | 2.2541e-06 | 2.2541e-06 | 6.071e-07 | 6.0711e-07 | 6.0711e-07 | 5.2055e-07 | 5.2056e-07 | 5.2056e-07 | 3.5263e-09 | 5.9103e-07 | -5.1231e-07 | -2.974e-09 | -5.1252e-07 | 4.3325e-07 | 7.9064e-09 | -9.2429e-07 | -9.6554e-07 | -6.8011e-09 | 7.8882e-07 | 8.3106e-07 | -92.152 | -92.1412 | -92.1412 | 87.4298 | 87.4424 | 87.4424 | 0.01426 | 1.8071 | 1.8004 | 0.01426 | 1.8071 | 1.8004 | -26.1889 | -149.5445 | 149.9086 | -26.1889 | -149.5445 | 149.9086

## LG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.046281 | 2.3643e-06 | 2.3643e-06 | 0.04628 | 1.9717e-06 | 1.9717e-06 | 0.010688 | 5.4602e-07 | 5.4602e-07 | 0.010688 | 4.5534e-07 | 4.5534e-07 | 7.1394e-05 | 5.5745e-07 | -4.8211e-07 | -5.3545e-05 | -4.7138e-07 | 3.952e-07 | 0.00014279 | -8.7039e-07 | -9.0994e-07 | -0.00010709 | 7.214e-07 | 7.6201e-07 | -89.6228 | -92.1786 | -92.1786 | 90.3772 | 87.3168 | 87.3168 | 0.014937 | 1.893 | 1.8859 | 0.011202 | 1.8926 | 1.8852 | -26.1878 | -149.5408 | 149.9057 | -26.1878 | -149.5219 | 149.9042
Line10_11_12 | 2.3603e-06 | 2.3603e-06 | 2.3603e-06 | 1.9677e-06 | 1.9677e-06 | 1.9677e-06 | 5.4508e-07 | 5.4508e-07 | 5.4508e-07 | 4.5442e-07 | 4.5443e-07 | 4.5443e-07 | 3.3161e-09 | 5.5592e-07 | -4.8189e-07 | -2.7102e-09 | -4.6976e-07 | 3.9512e-07 | 7.4355e-09 | -8.6927e-07 | -9.0806e-07 | -6.2228e-09 | 7.2063e-07 | 7.6051e-07 | -92.1518 | -92.1405 | -92.1405 | 87.3463 | 87.3599 | 87.3599 | 0.014936 | 1.893 | 1.8859 | 0.014936 | 1.893 | 1.8859 | -26.1877 | -149.5408 | 149.9057 | -26.1877 | -149.5408 | 149.9057
Line11_12_13 | 1.9669e-06 | 1.9669e-06 | 1.9669e-06 | 1.5744e-06 | 1.5744e-06 | 1.5744e-06 | 4.5423e-07 | 4.5424e-07 | 4.5424e-07 | 3.6358e-07 | 3.6358e-07 | 3.6358e-07 | 2.7634e-09 | 4.6326e-07 | -4.0157e-07 | -2.1575e-09 | -3.7711e-07 | 3.1481e-07 | 6.1962e-09 | -7.2439e-07 | -7.5672e-07 | -4.9835e-09 | 5.7575e-07 | 6.0917e-07 | -92.1518 | -92.1405 | -92.1405 | 87.2209 | 87.2351 | 87.2351 | 0.014936 | 1.893 | 1.8859 | 0.014936 | 1.893 | 1.8859 | -26.1877 | -149.5408 | 149.9057 | -26.1877 | -149.5408 | 149.9057
Line12_13_15 | 1.1801e-06 | 1.1801e-06 | 1.1801e-06 | 0 | 0 | 0 | 2.7254e-07 | 2.7254e-07 | 2.7254e-07 | 0 | 0 | 0 | 1.658e-09 | 2.7796e-07 | -2.4094e-07 | -1.0521e-09 | -1.918e-07 | 1.5418e-07 | 3.7177e-09 | -4.3464e-07 | -4.5403e-07 | -2.5051e-09 | 2.8599e-07 | 3.0648e-07 | -92.1518 | -92.1405 | -92.1405 | 0 | 0 | 0 | 0.014936 | 1.893 | 1.8859 | 0.014936 | 1.893 | 1.8859 | -26.1877 | -149.5408 | 149.9057 | -26.1877 | -149.5408 | 149.9057
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5268e-10 | 9.2653e-08 | -8.0314e-08 | 5.3241e-11 | -6.4965e-09 | -6.4478e-09 | 1.2392e-09 | -1.4488e-07 | -1.5134e-07 | -2.6586e-11 | -3.7644e-09 | 3.7925e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014936 | 1.893 | 1.8859 | 0.014936 | 1.893 | 1.8859 | -26.1877 | -149.5408 | 149.9057 | -26.1877 | -149.5408 | 149.9057
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1053e-09 | 1.8531e-07 | -1.6063e-07 | -4.9943e-10 | -9.9149e-08 | 7.3866e-08 | 2.4785e-09 | -2.8976e-07 | -3.0269e-07 | -1.2658e-09 | 1.4111e-07 | 1.5514e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014936 | 1.893 | 1.8859 | 0.014936 | 1.893 | 1.8859 | -26.1877 | -149.5408 | 149.9057 | -26.1877 | -149.5408 | 149.9057
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5267e-10 | 9.2653e-08 | -8.0314e-08 | 5.324e-11 | -6.4965e-09 | -6.4478e-09 | 1.2392e-09 | -1.4488e-07 | -1.5134e-07 | -2.6586e-11 | -3.7644e-09 | 3.7925e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014936 | 1.893 | 1.8859 | 0.014936 | 1.893 | 1.8859 | -26.1877 | -149.5408 | 149.9057 | -26.1877 | -149.5408 | 149.9057
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5269e-10 | 9.2652e-08 | -8.0314e-08 | 5.3242e-11 | -6.4965e-09 | -6.4478e-09 | 1.2393e-09 | -1.4488e-07 | -1.5134e-07 | -2.6587e-11 | -3.7644e-09 | 3.7925e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014937 | 1.893 | 1.8859 | 0.014937 | 1.893 | 1.8859 | -26.1878 | -149.5408 | 149.9057 | -26.1877 | -149.5408 | 149.9057
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5269e-10 | 9.2652e-08 | -8.0314e-08 | 5.3242e-11 | -6.4965e-09 | -6.4478e-09 | 1.2393e-09 | -1.4488e-07 | -1.5134e-07 | -2.6587e-11 | -3.7644e-09 | 3.7925e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014937 | 1.893 | 1.8859 | 0.014937 | 1.893 | 1.8859 | -26.1878 | -149.5408 | 149.9057 | -26.1877 | -149.5408 | 149.9057
Line1_1_3 | 3.147e-06 | 3.147e-06 | 3.147e-06 | 2.7544e-06 | 2.7545e-06 | 2.7545e-06 | 7.2677e-07 | 7.2678e-07 | 7.2678e-07 | 6.3611e-07 | 6.3612e-07 | 6.3612e-07 | 4.4216e-09 | 7.4122e-07 | -6.4251e-07 | -3.8156e-09 | -6.5506e-07 | 5.5575e-07 | 9.9142e-09 | -1.159e-06 | -1.2107e-06 | -8.7014e-09 | 1.0104e-06 | 1.0632e-06 | -92.1518 | -92.1405 | -92.1405 | 87.4897 | 87.5026 | 87.5026 | 0.014937 | 1.893 | 1.8859 | 0.014936 | 1.893 | 1.8859 | -26.1878 | -149.5408 | 149.9057 | -26.1877 | -149.5408 | 149.9057
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1054e-09 | 1.853e-07 | -1.6063e-07 | -4.9945e-10 | -9.9149e-08 | 7.3866e-08 | 2.4786e-09 | -2.8976e-07 | -3.0269e-07 | -1.2659e-09 | 1.4111e-07 | 1.5514e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014937 | 1.893 | 1.8859 | 0.014937 | 1.893 | 1.8859 | -26.1878 | -149.5408 | 149.9057 | -26.1878 | -149.5408 | 149.9057
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1054e-09 | 1.853e-07 | -1.6063e-07 | -4.9945e-10 | -9.9149e-08 | 7.3866e-08 | 2.4786e-09 | -2.8976e-07 | -3.0269e-07 | -1.2659e-09 | 1.4111e-07 | 1.5514e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014937 | 1.893 | 1.8859 | 0.014937 | 1.893 | 1.8859 | -26.1878 | -149.5408 | 149.9057 | -26.1878 | -149.5408 | 149.9057
Line4_2_6 | 0.04628 | 1.9708e-06 | 1.9708e-06 | 0.04628 | 1.5779e-06 | 1.5779e-06 | 0.010688 | 4.5514e-07 | 4.5514e-07 | 0.010688 | 3.6441e-07 | 3.6441e-07 | 5.3545e-05 | 4.6489e-07 | -4.0164e-07 | -3.5696e-05 | -3.7866e-07 | 3.1479e-07 | 0.00010709 | -7.2516e-07 | -7.5822e-07 | -7.1393e-05 | 5.7623e-07 | 6.1031e-07 | -89.6228 | -92.1849 | -92.1849 | 90.3772 | 87.187 | 87.187 | 0.011202 | 1.8926 | 1.8852 | 0.0074682 | 1.8922 | 1.8845 | -26.1878 | -149.5219 | 149.9042 | -26.1877 | -149.503 | 149.9026
Line5_6_7 | 0.04628 | 1.5771e-06 | 1.5771e-06 | 0.046279 | 1.184e-06 | 1.184e-06 | 0.010688 | 3.6421e-07 | 3.6421e-07 | 0.010688 | 2.7342e-07 | 2.7342e-07 | 3.5696e-05 | 3.7217e-07 | -3.2123e-07 | -1.7848e-05 | -2.8579e-07 | 2.3442e-07 | 7.1393e-05 | -5.7999e-07 | -6.0652e-07 | -3.5696e-05 | 4.3112e-07 | 4.5861e-07 | -89.6227 | -92.1907 | -92.1907 | 90.3773 | 86.9755 | 86.9755 | 0.0074682 | 1.8922 | 1.8845 | 0.0037341 | 1.8917 | 1.8837 | -26.1877 | -149.503 | 149.9026 | -26.1877 | -149.4841 | 149.9011
Line6_7_8 | 0.046279 | 1.183e-06 | 1.183e-06 | 0.046279 | 0 | 0 | 0.010688 | 2.7321e-07 | 2.7321e-07 | 0.010688 | 0 | 0 | 1.7848e-05 | 2.7931e-07 | -2.4085e-07 | -1.8216e-14 | -1.9277e-07 | 1.541e-07 | 3.5696e-05 | -4.3488e-07 | -4.5482e-07 | 5.2959e-15 | 2.8606e-07 | 3.0691e-07 | -89.6227 | -92.1957 | -92.1957 | 90.3773 | 0 | 0 | 0.0037341 | 1.8917 | 1.8837 | 0 | 1.8913 | 1.883 | -26.1877 | -149.4841 | 149.9011 | 0 | -149.4652 | 149.8995
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5709e-19 | 9.3147e-08 | -8.0256e-08 | -3.2933e-17 | -6.4745e-09 | -6.4166e-09 | -3.7964e-20 | -1.4491e-07 | -1.5156e-07 | 2.0101e-17 | -3.7524e-09 | 3.7858e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8913 | 1.883 | 0 | 1.8913 | 1.883 | 0 | -149.4652 | 149.8995 | 0 | -149.4652 | 149.8995
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5709e-19 | 9.3147e-08 | -8.0256e-08 | -3.2933e-17 | -6.4745e-09 | -6.4166e-09 | -3.7964e-20 | -1.4491e-07 | -1.5156e-07 | 2.0101e-17 | -3.7524e-09 | 3.7858e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8913 | 1.883 | 0 | 1.8913 | 1.883 | 0 | -149.4652 | 149.8995 | 0 | -149.4652 | 149.8995
Line9_3_11 | 2.7536e-06 | 2.7537e-06 | 2.7537e-06 | 2.3611e-06 | 2.3611e-06 | 2.3611e-06 | 6.3593e-07 | 6.3593e-07 | 6.3593e-07 | 5.4527e-07 | 5.4527e-07 | 5.4527e-07 | 3.8688e-09 | 6.4857e-07 | -5.622e-07 | -3.2629e-09 | -5.6241e-07 | 4.7544e-07 | 8.6749e-09 | -1.0141e-06 | -1.0594e-06 | -7.4621e-09 | 8.6551e-07 | 9.1185e-07 | -92.1518 | -92.1405 | -92.1405 | 87.43 | 87.4431 | 87.4431 | 0.014936 | 1.893 | 1.8859 | 0.014936 | 1.893 | 1.8859 | -26.1877 | -149.5408 | 149.9057 | -26.1877 | -149.5408 | 149.9057

## LG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.020843 | 1.0648e-06 | 1.0648e-06 | 0.020843 | 0 | 0 | 0.0048135 | 2.459e-07 | 2.459e-07 | 0.0048134 | 0 | 0 | 0.0021865 | 1.6037e-07 | -2.5099e-07 | -0.0021829 | -1.3616e-07 | 2.0817e-07 | 0.002201 | -3.2613e-07 | -1.5073e-07 | -0.0021937 | 2.7072e-07 | 1.2747e-07 | -64.3517 | -66.907 | -66.907 | 115.6483 | 0 | 0 | 0.64453 | 1.478 | 1.1906 | 0.64294 | 1.4778 | 1.1904 | -19.1625 | -130.7217 | 144.0792 | -19.2094 | -130.7117 | 144.07
Line10_11_12 | 1.0629e-06 | 1.0629e-06 | 1.0629e-06 | 0 | 0 | 0 | 2.4547e-07 | 2.4548e-07 | 2.4548e-07 | 0 | 0 | 0 | 1.0645e-07 | 1.5988e-07 | -2.5066e-07 | -8.7884e-08 | -1.3565e-07 | 2.0787e-07 | 1.1705e-07 | -3.2568e-07 | -1.5031e-07 | -9.8359e-08 | 2.7034e-07 | 1.2712e-07 | -66.8797 | -66.8689 | -66.8689 | 0 | 0 | 0 | 0.64453 | 1.478 | 1.1906 | 0.64453 | 1.478 | 1.1906 | -19.1625 | -130.7217 | 144.0793 | -19.1625 | -130.7217 | 144.0793
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.8705e-08 | 1.3324e-07 | -2.0889e-07 | -7.0143e-08 | -1.0901e-07 | 1.661e-07 | 9.7544e-08 | -2.714e-07 | -1.2525e-07 | -7.885e-08 | 2.1606e-07 | 1.0207e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0.64453 | 1.478 | 1.1906 | 0.64453 | 1.478 | 1.1906 | -19.1625 | -130.7217 | 144.0793 | -19.1625 | -130.7217 | 144.0793
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3223e-08 | 7.9941e-08 | -1.2533e-07 | -3.4661e-08 | -5.5713e-08 | 8.2541e-08 | 5.8527e-08 | -1.6284e-07 | -7.5153e-08 | -3.9832e-08 | 1.075e-07 | 5.1972e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0.64453 | 1.478 | 1.1906 | 0.64453 | 1.478 | 1.1906 | -19.1625 | -130.7217 | 144.0793 | -19.1625 | -130.7217 | 144.0793
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7741e-08 | 2.6647e-08 | -4.1777e-08 | 8.2074e-10 | -2.4187e-09 | -1.0129e-09 | 1.9509e-08 | -5.428e-08 | -2.5051e-08 | -8.1453e-10 | -1.0586e-09 | 1.8703e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.64453 | 1.478 | 1.1906 | 0.64453 | 1.478 | 1.1906 | -19.1625 | -130.7217 | 144.0793 | -19.1625 | -130.7217 | 144.0793
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5482e-08 | 5.3294e-08 | -8.3554e-08 | -1.692e-08 | -2.9066e-08 | 4.0764e-08 | 3.9018e-08 | -1.0856e-07 | -5.0102e-08 | -2.0323e-08 | 5.3221e-08 | 2.6921e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0.64453 | 1.478 | 1.1906 | 0.64453 | 1.478 | 1.1906 | -19.1625 | -130.7217 | 144.0793 | -19.1625 | -130.7217 | 144.0793
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7741e-08 | 2.6647e-08 | -4.1777e-08 | 8.2074e-10 | -2.4187e-09 | -1.0129e-09 | 1.9509e-08 | -5.428e-08 | -2.5051e-08 | -8.1453e-10 | -1.0586e-09 | 1.8703e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.64453 | 1.478 | 1.1906 | 0.64453 | 1.478 | 1.1906 | -19.1625 | -130.7217 | 144.0793 | -19.1625 | -130.7217 | 144.0793
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7741e-08 | 2.6647e-08 | -4.1777e-08 | 8.2074e-10 | -2.4187e-09 | -1.0129e-09 | 1.9509e-08 | -5.428e-08 | -2.5051e-08 | -8.1453e-10 | -1.0586e-09 | 1.8703e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.64453 | 1.478 | 1.1906 | 0.64453 | 1.478 | 1.1906 | -19.1625 | -130.7217 | 144.0792 | -19.1625 | -130.7217 | 144.0792
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7741e-08 | 2.6647e-08 | -4.1777e-08 | 8.2074e-10 | -2.4187e-09 | -1.0129e-09 | 1.9509e-08 | -5.428e-08 | -2.5051e-08 | -8.1453e-10 | -1.0586e-09 | 1.8703e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.64453 | 1.478 | 1.1906 | 0.64453 | 1.478 | 1.1906 | -19.1625 | -130.7217 | 144.0792 | -19.1625 | -130.7217 | 144.0792
Line1_1_3 | 1.4172e-06 | 1.4173e-06 | 1.4173e-06 | 1.2404e-06 | 1.2405e-06 | 1.2405e-06 | 3.273e-07 | 3.273e-07 | 3.273e-07 | 2.8647e-07 | 2.8647e-07 | 2.8647e-07 | 1.4193e-07 | 2.1318e-07 | -3.3422e-07 | -1.2337e-07 | -1.8895e-07 | 2.9143e-07 | 1.5607e-07 | -4.3424e-07 | -2.0041e-07 | -1.3738e-07 | 3.789e-07 | 1.7723e-07 | -66.8797 | -66.8689 | -66.8689 | 112.7618 | 112.7741 | 112.7741 | 0.64453 | 1.478 | 1.1906 | 0.64453 | 1.478 | 1.1906 | -19.1625 | -130.7217 | 144.0792 | -19.1625 | -130.7217 | 144.0792
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5482e-08 | 5.3294e-08 | -8.3554e-08 | -1.692e-08 | -2.9066e-08 | 4.0764e-08 | 3.9018e-08 | -1.0856e-07 | -5.0102e-08 | -2.0323e-08 | 5.3221e-08 | 2.6921e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0.64453 | 1.478 | 1.1906 | 0.64453 | 1.478 | 1.1906 | -19.1625 | -130.7217 | 144.0792 | -19.1625 | -130.7217 | 144.0792
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5482e-08 | 5.3294e-08 | -8.3554e-08 | -1.692e-08 | -2.9066e-08 | 4.0764e-08 | 3.9018e-08 | -1.0856e-07 | -5.0102e-08 | -2.0323e-08 | 5.3221e-08 | 2.6921e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0.64453 | 1.478 | 1.1906 | 0.64453 | 1.478 | 1.1906 | -19.1625 | -130.7217 | 144.0792 | -19.1625 | -130.7217 | 144.0792
Line4_2_6 | 0.020843 | 0 | 0 | 0.020843 | 0 | 0 | 0.0048134 | 0 | 0 | 0.0048134 | 0 | 0 | 0.0021829 | 1.3374e-07 | -2.0918e-07 | -0.0021792 | -1.0948e-07 | 1.6634e-07 | 0.0021937 | -2.7177e-07 | -1.256e-07 | -0.0021865 | 2.1636e-07 | 1.0234e-07 | -64.3517 | 0 | 0 | 115.6483 | 0 | 0 | 0.64294 | 1.4778 | 1.1904 | 0.64134 | 1.4776 | 1.1901 | -19.2094 | -130.7117 | 144.07 | -19.2566 | -130.7017 | 144.0607
Line5_6_7 | 0.020843 | 0 | 0 | 0.020842 | 0 | 0 | 0.0048134 | 0 | 0 | 0.0048133 | 0 | 0 | 0.0021792 | 1.0706e-07 | -1.6735e-07 | -0.0021756 | -8.2759e-08 | 1.2451e-07 | 0.0021865 | -2.1741e-07 | -1.0047e-07 | -0.0021792 | 1.62e-07 | 7.7212e-08 | -64.3517 | 0 | 0 | 115.6483 | 0 | 0 | 0.64134 | 1.4776 | 1.1901 | 0.63974 | 1.4773 | 1.1898 | -19.2566 | -130.7017 | 144.0607 | -19.3039 | -130.6917 | 144.0514
Line6_7_8 | 0.020842 | 0 | 0 | 0.020842 | 0 | 0 | 0.0048133 | 0 | 0 | 0.0048133 | 0 | 0 | 0.0021756 | 8.0345e-08 | -1.2552e-07 | -0.0021719 | -5.5997e-08 | 8.2667e-08 | 0.0021792 | -1.6305e-07 | -7.5345e-08 | -0.0021719 | 1.0763e-07 | 5.208e-08 | -64.3516 | 0 | 0 | 115.6484 | 0 | 0 | 0.63974 | 1.4773 | 1.1898 | 0.63815 | 1.4771 | 1.1895 | -19.3039 | -130.6917 | 144.0514 | -19.3516 | -130.6816 | 144.0421
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7637e-08 | 2.6793e-08 | -4.1836e-08 | 8.2488e-10 | -2.4119e-09 | -1.0059e-09 | 1.9331e-08 | -5.4342e-08 | -2.5107e-08 | -8.1412e-10 | -1.0541e-09 | 1.8658e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.63815 | 1.4771 | 1.1895 | 0.63815 | 1.4771 | 1.1895 | -19.3516 | -130.6816 | 144.0421 | -19.3516 | -130.6816 | 144.0421
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7637e-08 | 2.6793e-08 | -4.1836e-08 | 8.2488e-10 | -2.4119e-09 | -1.0059e-09 | 1.9331e-08 | -5.4342e-08 | -2.5107e-08 | -8.1412e-10 | -1.0541e-09 | 1.8658e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.63815 | 1.4771 | 1.1895 | 0.63815 | 1.4771 | 1.1895 | -19.3516 | -130.6816 | 144.0421 | -19.3516 | -130.6816 | 144.0421
Line9_3_11 | 1.2401e-06 | 1.2401e-06 | 1.2401e-06 | 1.0633e-06 | 1.0633e-06 | 1.0633e-06 | 2.8639e-07 | 2.8639e-07 | 2.8639e-07 | 2.4556e-07 | 2.4556e-07 | 2.4556e-07 | 1.2419e-07 | 1.8653e-07 | -2.9244e-07 | -1.0563e-07 | -1.623e-07 | 2.4965e-07 | 1.3656e-07 | -3.7996e-07 | -1.7536e-07 | -1.1787e-07 | 3.2462e-07 | 1.5218e-07 | -66.8797 | -66.8689 | -66.8689 | 112.7021 | 112.7147 | 112.7147 | 0.64453 | 1.478 | 1.1906 | 0.64453 | 1.478 | 1.1906 | -19.1625 | -130.7217 | 144.0792 | -19.1625 | -130.7217 | 144.0793

## LG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.021834 | 1.1154e-06 | 1.1154e-06 | 0.021834 | 0 | 0 | 0.0050423 | 2.5759e-07 | 2.5759e-07 | 0.0050422 | 0 | 0 | 0.0023993 | 1.7601e-07 | -2.7545e-07 | -0.0023953 | -1.4943e-07 | 2.2845e-07 | 0.0024152 | -3.579e-07 | -1.6541e-07 | -0.0024073 | 2.9708e-07 | 1.3989e-07 | -64.3531 | -66.9089 | -66.9089 | 115.6469 | 0 | 0 | 0.67517 | 1.5483 | 1.2473 | 0.6735 | 1.5481 | 1.247 | -19.1639 | -130.7214 | 144.0766 | -19.2108 | -130.7114 | 144.0674
Line10_11_12 | 1.1135e-06 | 1.1135e-06 | 1.1135e-06 | 0 | 0 | 0 | 2.5715e-07 | 2.5715e-07 | 2.5715e-07 | 0 | 0 | 0 | 1.1681e-07 | 1.7547e-07 | -2.7509e-07 | -9.644e-08 | -1.4888e-07 | 2.2813e-07 | 1.2845e-07 | -3.574e-07 | -1.6495e-07 | -1.0794e-07 | 2.9667e-07 | 1.3951e-07 | -66.8821 | -66.8708 | -66.8708 | 0 | 0 | 0 | 0.67517 | 1.5483 | 1.2473 | 0.67517 | 1.5483 | 1.2473 | -19.1639 | -130.7214 | 144.0766 | -19.1639 | -130.7214 | 144.0766
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.7341e-08 | 1.4623e-07 | -2.2924e-07 | -7.6972e-08 | -1.1963e-07 | 1.8228e-07 | 1.0704e-07 | -2.9783e-07 | -1.3746e-07 | -8.653e-08 | 2.3711e-07 | 1.1202e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67517 | 1.5483 | 1.2473 | 0.67517 | 1.5483 | 1.2473 | -19.1639 | -130.7214 | 144.0766 | -19.1639 | -130.7214 | 144.0766
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.8405e-08 | 8.7736e-08 | -1.3755e-07 | -3.8036e-08 | -6.1144e-08 | 9.0586e-08 | 6.4227e-08 | -1.787e-07 | -8.2474e-08 | -4.3712e-08 | 1.1797e-07 | 5.7035e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67517 | 1.5483 | 1.2473 | 0.67517 | 1.5483 | 1.2473 | -19.1639 | -130.7214 | 144.0766 | -19.1639 | -130.7214 | 144.0766
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9468e-08 | 2.9245e-08 | -4.5849e-08 | 9.008e-10 | -2.6541e-09 | -1.1115e-09 | 2.1409e-08 | -5.9567e-08 | -2.7491e-08 | -8.9395e-10 | -1.1618e-09 | 2.0524e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67517 | 1.5483 | 1.2473 | 0.67517 | 1.5483 | 1.2473 | -19.1639 | -130.7214 | 144.0766 | -19.1639 | -130.7214 | 144.0766
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8936e-08 | 5.849e-08 | -9.1697e-08 | -1.8567e-08 | -3.1899e-08 | 4.4737e-08 | 4.2818e-08 | -1.1913e-07 | -5.4983e-08 | -2.2303e-08 | 5.8405e-08 | 2.9544e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67517 | 1.5483 | 1.2473 | 0.67517 | 1.5483 | 1.2473 | -19.1639 | -130.7214 | 144.0766 | -19.1639 | -130.7214 | 144.0766
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9468e-08 | 2.9245e-08 | -4.5849e-08 | 9.008e-10 | -2.6541e-09 | -1.1115e-09 | 2.1409e-08 | -5.9567e-08 | -2.7491e-08 | -8.9395e-10 | -1.1618e-09 | 2.0524e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67517 | 1.5483 | 1.2473 | 0.67517 | 1.5483 | 1.2473 | -19.1639 | -130.7214 | 144.0766 | -19.1639 | -130.7214 | 144.0766
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9468e-08 | 2.9245e-08 | -4.5849e-08 | 9.008e-10 | -2.6541e-09 | -1.1115e-09 | 2.1409e-08 | -5.9567e-08 | -2.7491e-08 | -8.9395e-10 | -1.1618e-09 | 2.0524e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67517 | 1.5483 | 1.2473 | 0.67517 | 1.5483 | 1.2473 | -19.1639 | -130.7214 | 144.0766 | -19.1639 | -130.7214 | 144.0766
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9468e-08 | 2.9245e-08 | -4.5849e-08 | 9.008e-10 | -2.6541e-09 | -1.1115e-09 | 2.1409e-08 | -5.9567e-08 | -2.7491e-08 | -8.9395e-10 | -1.1618e-09 | 2.0524e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67517 | 1.5483 | 1.2473 | 0.67517 | 1.5483 | 1.2473 | -19.1639 | -130.7214 | 144.0766 | -19.1639 | -130.7214 | 144.0766
Line1_1_3 | 1.4847e-06 | 1.4847e-06 | 1.4847e-06 | 1.2995e-06 | 1.2995e-06 | 1.2995e-06 | 3.4287e-07 | 3.4287e-07 | 3.4287e-07 | 3.001e-07 | 3.001e-07 | 3.001e-07 | 1.5575e-07 | 2.3396e-07 | -3.6679e-07 | -1.3538e-07 | -2.0737e-07 | 3.1983e-07 | 1.7127e-07 | -4.7653e-07 | -2.1993e-07 | -1.5076e-07 | 4.1581e-07 | 1.9449e-07 | -66.8821 | -66.8708 | -66.8708 | 112.7594 | 112.7723 | 112.7723 | 0.67517 | 1.5483 | 1.2473 | 0.67517 | 1.5483 | 1.2473 | -19.1639 | -130.7214 | 144.0766 | -19.1639 | -130.7214 | 144.0766
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8936e-08 | 5.849e-08 | -9.1697e-08 | -1.8567e-08 | -3.1899e-08 | 4.4737e-08 | 4.2818e-08 | -1.1913e-07 | -5.4983e-08 | -2.2303e-08 | 5.8405e-08 | 2.9544e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67517 | 1.5483 | 1.2473 | 0.67517 | 1.5483 | 1.2473 | -19.1639 | -130.7214 | 144.0766 | -19.1639 | -130.7214 | 144.0766
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8936e-08 | 5.849e-08 | -9.1697e-08 | -1.8567e-08 | -3.1899e-08 | 4.4737e-08 | 4.2818e-08 | -1.1913e-07 | -5.4983e-08 | -2.2303e-08 | 5.8405e-08 | 2.9544e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67517 | 1.5483 | 1.2473 | 0.67517 | 1.5483 | 1.2473 | -19.1639 | -130.7214 | 144.0766 | -19.1639 | -130.7214 | 144.0766
Line4_2_6 | 0.021834 | 0 | 0 | 0.021833 | 0 | 0 | 0.0050422 | 0 | 0 | 0.0050422 | 0 | 0 | 0.0023953 | 1.4678e-07 | -2.2956e-07 | -0.0023913 | -1.2015e-07 | 1.8255e-07 | 0.0024073 | -2.9824e-07 | -1.3784e-07 | -0.0023993 | 2.3743e-07 | 1.1231e-07 | -64.3531 | 0 | 0 | 115.6469 | 0 | 0 | 0.6735 | 1.5481 | 1.247 | 0.67183 | 1.5479 | 1.2467 | -19.2108 | -130.7114 | 144.0674 | -19.2579 | -130.7014 | 144.0581
Line5_6_7 | 0.021833 | 0 | 0 | 0.021833 | 0 | 0 | 0.0050422 | 0 | 0 | 0.0050422 | 0 | 0 | 0.0023913 | 1.175e-07 | -1.8366e-07 | -0.0023874 | -9.0828e-08 | 1.3664e-07 | 0.0023993 | -2.3859e-07 | -1.1026e-07 | -0.0023913 | 1.7777e-07 | 8.4734e-08 | -64.3531 | 0 | 0 | 115.6469 | 0 | 0 | 0.67183 | 1.5479 | 1.2467 | 0.67016 | 1.5476 | 1.2465 | -19.2579 | -130.7014 | 144.0581 | -19.3053 | -130.6914 | 144.0488
Line6_7_8 | 0.021833 | 0 | 0 | 0.021833 | 0 | 0 | 0.0050422 | 0 | 0 | 0.0050421 | 0 | 0 | 0.0023874 | 8.8179e-08 | -1.3775e-07 | -0.0023834 | -6.1457e-08 | 9.0724e-08 | 0.0023913 | -1.7893e-07 | -8.2685e-08 | -0.0023834 | 1.1811e-07 | 5.7154e-08 | -64.353 | 0 | 0 | 115.647 | 0 | 0 | 0.67016 | 1.5476 | 1.2465 | 0.66849 | 1.5474 | 1.2462 | -19.3053 | -130.6914 | 144.0488 | -19.353 | -130.6813 | 144.0395
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9354e-08 | 2.9405e-08 | -4.5914e-08 | 9.0534e-10 | -2.6466e-09 | -1.1038e-09 | 2.1213e-08 | -5.9635e-08 | -2.7553e-08 | -8.9349e-10 | -1.1568e-09 | 2.0475e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.66849 | 1.5474 | 1.2462 | 0.66849 | 1.5474 | 1.2462 | -19.353 | -130.6813 | 144.0395 | -19.353 | -130.6813 | 144.0395
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9354e-08 | 2.9405e-08 | -4.5914e-08 | 9.0534e-10 | -2.6466e-09 | -1.1038e-09 | 2.1213e-08 | -5.9635e-08 | -2.7553e-08 | -8.9349e-10 | -1.1568e-09 | 2.0475e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.66849 | 1.5474 | 1.2462 | 0.66849 | 1.5474 | 1.2462 | -19.353 | -130.6813 | 144.0395 | -19.353 | -130.6813 | 144.0395
Line9_3_11 | 1.2991e-06 | 1.2991e-06 | 1.2991e-06 | 1.1139e-06 | 1.1139e-06 | 1.1139e-06 | 3.0001e-07 | 3.0001e-07 | 3.0001e-07 | 2.5724e-07 | 2.5724e-07 | 2.5724e-07 | 1.3628e-07 | 2.0472e-07 | -3.2094e-07 | -1.1591e-07 | -1.7813e-07 | 2.7398e-07 | 1.4986e-07 | -4.1697e-07 | -1.9244e-07 | -1.2935e-07 | 3.5624e-07 | 1.67e-07 | -66.8821 | -66.8708 | -66.8708 | 112.6996 | 112.7128 | 112.7128 | 0.67517 | 1.5483 | 1.2473 | 0.67517 | 1.5483 | 1.2473 | -19.1639 | -130.7214 | 144.0766 | -19.1639 | -130.7214 | 144.0766

## LG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.039969 | 2.042e-06 | 2.042e-06 | 0.039968 | 1.7029e-06 | 1.7029e-06 | 0.0092304 | 4.7158e-07 | 4.7158e-07 | 0.0092303 | 3.9327e-07 | 3.9327e-07 | 0.00010224 | 4.1511e-07 | -3.6042e-07 | -7.6677e-05 | -3.5122e-07 | 2.9531e-07 | 0.0001065 | -6.5111e-07 | -6.7686e-07 | -7.9872e-05 | 5.3964e-07 | 5.6688e-07 | -89.3029 | -91.9017 | -91.9017 | 90.6971 | 87.5868 | 87.5868 | 0.015994 | 1.6374 | 1.6261 | 0.011995 | 1.6372 | 1.6253 | -43.1337 | -149.3823 | 150.0636 | -43.1337 | -149.3554 | 150.07
Line10_11_12 | 2.0384e-06 | 2.0384e-06 | 2.0384e-06 | 1.6993e-06 | 1.6994e-06 | 1.6994e-06 | 4.7074e-07 | 4.7074e-07 | 4.7074e-07 | 3.9245e-07 | 3.9245e-07 | 3.9245e-07 | 4.9691e-09 | 4.1345e-07 | -3.6073e-07 | -4.1012e-09 | -3.4941e-07 | 2.9582e-07 | 5.6559e-09 | -6.5054e-07 | -6.7515e-07 | -4.7513e-09 | 5.3932e-07 | 5.6546e-07 | -91.8317 | -91.8205 | -91.8205 | 87.6664 | 87.6798 | 87.6798 | 0.015993 | 1.6374 | 1.6261 | 0.015993 | 1.6374 | 1.6261 | -43.1336 | -149.3823 | 150.0636 | -43.1336 | -149.3823 | 150.0636
Line11_12_13 | 1.6986e-06 | 1.6986e-06 | 1.6986e-06 | 1.3596e-06 | 1.3596e-06 | 1.3596e-06 | 3.9228e-07 | 3.9228e-07 | 3.9228e-07 | 3.1399e-07 | 3.14e-07 | 3.14e-07 | 4.1409e-09 | 3.4454e-07 | -3.0061e-07 | -3.273e-09 | -2.805e-07 | 2.357e-07 | 4.7132e-09 | -5.4211e-07 | -5.6262e-07 | -3.8086e-09 | 4.3089e-07 | 4.5293e-07 | -91.8317 | -91.8205 | -91.8205 | 87.541 | 87.555 | 87.555 | 0.015993 | 1.6374 | 1.6261 | 0.015993 | 1.6374 | 1.6261 | -43.1336 | -149.3823 | 150.0636 | -43.1336 | -149.3823 | 150.0636
Line12_13_15 | 1.0192e-06 | 1.0192e-06 | 1.0192e-06 | 0 | 0 | 0 | 2.3537e-07 | 2.3537e-07 | 2.3537e-07 | 0 | 0 | 0 | 2.4845e-09 | 2.0673e-07 | -1.8037e-07 | -1.6166e-09 | -1.4268e-07 | 1.1545e-07 | 2.8279e-09 | -3.2527e-07 | -3.3757e-07 | -1.9233e-09 | 2.1405e-07 | 2.2789e-07 | -91.8317 | -91.8205 | -91.8205 | 0 | 0 | 0 | 0.015993 | 1.6374 | 1.6261 | 0.015993 | 1.6374 | 1.6261 | -43.1336 | -149.3823 | 150.0636 | -43.1336 | -149.3823 | 150.0636
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.2818e-10 | 6.8909e-08 | -6.0122e-08 | 3.9717e-11 | -4.861e-09 | -4.7932e-09 | 9.4263e-10 | -1.0842e-07 | -1.1252e-07 | -3.8089e-11 | -2.7984e-09 | 2.8376e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.015993 | 1.6374 | 1.6261 | 0.015993 | 1.6374 | 1.6261 | -43.1336 | -149.3823 | 150.0636 | -43.1336 | -149.3823 | 150.0636
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6563e-09 | 1.3782e-07 | -1.2024e-07 | -7.8845e-10 | -7.377e-08 | 5.5329e-08 | 1.8853e-09 | -2.1685e-07 | -2.2505e-07 | -9.8071e-10 | 1.0562e-07 | 1.1536e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0.015993 | 1.6374 | 1.6261 | 0.015993 | 1.6374 | 1.6261 | -43.1336 | -149.3823 | 150.0636 | -43.1336 | -149.3823 | 150.0636
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.2817e-10 | 6.8909e-08 | -6.0122e-08 | 3.9717e-11 | -4.861e-09 | -4.7932e-09 | 9.4263e-10 | -1.0842e-07 | -1.1252e-07 | -3.8088e-11 | -2.7984e-09 | 2.8376e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.015993 | 1.6374 | 1.6261 | 0.015993 | 1.6374 | 1.6261 | -43.1336 | -149.3823 | 150.0636 | -43.1336 | -149.3823 | 150.0636
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.282e-10 | 6.8909e-08 | -6.0122e-08 | 3.9718e-11 | -4.861e-09 | -4.7932e-09 | 9.4266e-10 | -1.0842e-07 | -1.1252e-07 | -3.809e-11 | -2.7984e-09 | 2.8376e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.015994 | 1.6374 | 1.6261 | 0.015994 | 1.6374 | 1.6261 | -43.1337 | -149.3823 | 150.0636 | -43.1337 | -149.3823 | 150.0636
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.282e-10 | 6.8909e-08 | -6.0122e-08 | 3.9718e-11 | -4.861e-09 | -4.7932e-09 | 9.4266e-10 | -1.0842e-07 | -1.1252e-07 | -3.809e-11 | -2.7984e-09 | 2.8376e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.015994 | 1.6374 | 1.6261 | 0.015994 | 1.6374 | 1.6261 | -43.1337 | -149.3823 | 150.0636 | -43.1337 | -149.3823 | 150.0636
Line1_1_3 | 2.7178e-06 | 2.7178e-06 | 2.7178e-06 | 2.3788e-06 | 2.3788e-06 | 2.3788e-06 | 6.2765e-07 | 6.2765e-07 | 6.2765e-07 | 5.4935e-07 | 5.4936e-07 | 5.4936e-07 | 6.6256e-09 | 5.5127e-07 | -4.8098e-07 | -5.7576e-09 | -4.8722e-07 | 4.1606e-07 | 7.5413e-09 | -8.6738e-07 | -9.0019e-07 | -6.6366e-09 | 7.5616e-07 | 7.9051e-07 | -91.8317 | -91.8205 | -91.8205 | 87.8097 | 87.8225 | 87.8225 | 0.015994 | 1.6374 | 1.6261 | 0.015994 | 1.6374 | 1.6261 | -43.1337 | -149.3823 | 150.0636 | -43.1337 | -149.3823 | 150.0636
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6564e-09 | 1.3782e-07 | -1.2024e-07 | -7.8848e-10 | -7.377e-08 | 5.5329e-08 | 1.8853e-09 | -2.1685e-07 | -2.2505e-07 | -9.8075e-10 | 1.0562e-07 | 1.1536e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0.015994 | 1.6374 | 1.6261 | 0.015994 | 1.6374 | 1.6261 | -43.1337 | -149.3823 | 150.0636 | -43.1337 | -149.3823 | 150.0636
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6564e-09 | 1.3782e-07 | -1.2024e-07 | -7.8848e-10 | -7.377e-08 | 5.5329e-08 | 1.8853e-09 | -2.1685e-07 | -2.2505e-07 | -9.8075e-10 | 1.0562e-07 | 1.1536e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0.015994 | 1.6374 | 1.6261 | 0.015994 | 1.6374 | 1.6261 | -43.1337 | -149.3823 | 150.0636 | -43.1337 | -149.3823 | 150.0636
Line4_2_6 | 0.039968 | 1.7022e-06 | 1.7022e-06 | 0.039968 | 1.3629e-06 | 1.3629e-06 | 0.0092303 | 3.931e-07 | 3.931e-07 | 0.0092302 | 3.1474e-07 | 3.1474e-07 | 7.6677e-05 | 3.4636e-07 | -3.001e-07 | -5.1117e-05 | -2.8228e-07 | 2.351e-07 | 7.9872e-05 | -5.4243e-07 | -5.6405e-07 | -5.3247e-05 | 4.3102e-07 | 4.5406e-07 | -89.3029 | -91.915 | -91.915 | 90.6971 | 87.4506 | 87.4506 | 0.011995 | 1.6372 | 1.6253 | 0.0079968 | 1.637 | 1.6245 | -43.1337 | -149.3554 | 150.07 | -43.1337 | -149.3286 | 150.0764
Line5_6_7 | 0.039968 | 1.3621e-06 | 1.3621e-06 | 0.039968 | 1.0226e-06 | 1.0226e-06 | 0.0092302 | 3.1456e-07 | 3.1456e-07 | 0.0092301 | 2.3616e-07 | 2.3616e-07 | 5.1117e-05 | 2.7742e-07 | -2.3988e-07 | -2.5558e-05 | -2.1315e-07 | 1.7499e-07 | 5.3247e-05 | -4.3381e-07 | -4.5122e-07 | -2.6623e-05 | 3.2246e-07 | 3.4121e-07 | -89.3029 | -91.9273 | -91.9273 | 90.6971 | 87.2338 | 87.2338 | 0.0079968 | 1.637 | 1.6245 | 0.0039984 | 1.6368 | 1.6238 | -43.1337 | -149.3286 | 150.0764 | -43.1337 | -149.3017 | 150.0829
Line6_7_8 | 0.039968 | 1.0218e-06 | 1.0218e-06 | 0.039967 | 0 | 0 | 0.0092301 | 2.3597e-07 | 2.3597e-07 | 0.0092301 | 0 | 0 | 2.5558e-05 | 2.0829e-07 | -1.7976e-07 | 6.8249e-15 | -1.4383e-07 | 1.1498e-07 | 2.6623e-05 | -3.2525e-07 | -3.3838e-07 | 2.8691e-16 | 2.1396e-07 | 2.2836e-07 | -89.3028 | -91.9376 | -91.9376 | 90.6972 | 0 | 0 | 0.0039984 | 1.6368 | 1.6238 | 0 | 1.6365 | 1.623 | -43.1337 | -149.3017 | 150.0829 | 0 | -149.2748 | 150.0893
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.7954e-20 | 6.949e-08 | -5.9876e-08 | -2.366e-17 | -4.8478e-09 | -4.7668e-09 | -5.1693e-21 | -1.0837e-07 | -1.1276e-07 | 2.6673e-17 | -2.7876e-09 | 2.8343e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6365 | 1.623 | 0 | 1.6365 | 1.623 | 0 | -149.2748 | 150.0893 | 0 | -149.2748 | 150.0893
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.7954e-20 | 6.949e-08 | -5.9876e-08 | -2.366e-17 | -4.8478e-09 | -4.7668e-09 | -5.1693e-21 | -1.0837e-07 | -1.1276e-07 | 2.6673e-17 | -2.7876e-09 | 2.8343e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6365 | 1.623 | 0 | 1.6365 | 1.623 | 0 | -149.2748 | 150.0893 | 0 | -149.2748 | 150.0893
Line9_3_11 | 2.3781e-06 | 2.3781e-06 | 2.3781e-06 | 2.0391e-06 | 2.0391e-06 | 2.0391e-06 | 5.4919e-07 | 5.492e-07 | 5.492e-07 | 4.709e-07 | 4.709e-07 | 4.709e-07 | 5.7974e-09 | 4.8236e-07 | -4.2086e-07 | -4.9294e-09 | -4.1831e-07 | 3.5594e-07 | 6.5985e-09 | -7.5896e-07 | -7.8767e-07 | -5.6939e-09 | 6.4774e-07 | 6.7798e-07 | -91.8317 | -91.8205 | -91.8205 | 87.75 | 87.7631 | 87.7631 | 0.015994 | 1.6374 | 1.6261 | 0.015993 | 1.6374 | 1.6261 | -43.1337 | -149.3823 | 150.0636 | -43.1336 | -149.3823 | 150.0636

## LG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.037865 | 1.9345e-06 | 1.9345e-06 | 0.037865 | 1.6133e-06 | 1.6133e-06 | 0.0087446 | 4.4676e-07 | 4.4676e-07 | 0.0087445 | 3.7257e-07 | 3.7257e-07 | 9.1758e-05 | 3.7257e-07 | -3.2348e-07 | -6.8818e-05 | -3.1522e-07 | 2.6504e-07 | 9.5582e-05 | -5.8438e-07 | -6.0749e-07 | -7.1685e-05 | 4.8433e-07 | 5.0878e-07 | -89.3029 | -91.9017 | -91.9017 | 90.6971 | 87.5868 | 87.5868 | 0.015152 | 1.5513 | 1.5405 | 0.011364 | 1.551 | 1.5398 | -43.1337 | -149.3823 | 150.0636 | -43.1337 | -149.3554 | 150.07
Line10_11_12 | 1.9311e-06 | 1.9311e-06 | 1.9311e-06 | 1.6099e-06 | 1.6099e-06 | 1.6099e-06 | 4.4596e-07 | 4.4596e-07 | 4.4596e-07 | 3.7179e-07 | 3.7179e-07 | 3.7179e-07 | 4.4598e-09 | 3.7108e-07 | -3.2376e-07 | -3.6808e-09 | -3.1359e-07 | 2.655e-07 | 5.0762e-09 | -5.8386e-07 | -6.0595e-07 | -4.2643e-09 | 4.8404e-07 | 5.075e-07 | -91.8317 | -91.8205 | -91.8205 | 87.6664 | 87.6798 | 87.6798 | 0.015152 | 1.5513 | 1.5405 | 0.015152 | 1.5513 | 1.5405 | -43.1336 | -149.3823 | 150.0636 | -43.1336 | -149.3823 | 150.0636
Line11_12_13 | 1.6092e-06 | 1.6092e-06 | 1.6092e-06 | 1.2881e-06 | 1.2881e-06 | 1.2881e-06 | 3.7163e-07 | 3.7164e-07 | 3.7164e-07 | 2.9747e-07 | 2.9747e-07 | 2.9747e-07 | 3.7165e-09 | 3.0923e-07 | -2.698e-07 | -2.9375e-09 | -2.5175e-07 | 2.1154e-07 | 4.2301e-09 | -4.8655e-07 | -5.0496e-07 | -3.4183e-09 | 3.8673e-07 | 4.0651e-07 | -91.8317 | -91.8205 | -91.8205 | 87.541 | 87.555 | 87.555 | 0.015152 | 1.5513 | 1.5405 | 0.015151 | 1.5513 | 1.5405 | -43.1336 | -149.3823 | 150.0636 | -43.1336 | -149.3823 | 150.0636
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2299e-09 | 1.8554e-07 | -1.6188e-07 | -1.4509e-09 | -1.2806e-07 | 1.0362e-07 | 2.5381e-09 | -2.9193e-07 | -3.0297e-07 | -1.7262e-09 | 1.9211e-07 | 2.0453e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0.015151 | 1.5513 | 1.5405 | 0.015151 | 1.5513 | 1.5405 | -43.1336 | -149.3823 | 150.0636 | -43.1336 | -149.3823 | 150.0636
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4329e-10 | 6.1846e-08 | -5.396e-08 | 3.5646e-11 | -4.3628e-09 | -4.302e-09 | 8.4602e-10 | -9.731e-08 | -1.0099e-07 | -3.4185e-11 | -2.5116e-09 | 2.5467e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.015151 | 1.5513 | 1.5405 | 0.015151 | 1.5513 | 1.5405 | -43.1336 | -149.3823 | 150.0636 | -43.1336 | -149.3823 | 150.0636
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4866e-09 | 1.2369e-07 | -1.0792e-07 | -7.0764e-10 | -6.6209e-08 | 4.9658e-08 | 1.692e-09 | -1.9462e-07 | -2.0198e-07 | -8.802e-10 | 9.4799e-08 | 1.0354e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0.015151 | 1.5513 | 1.5405 | 0.015151 | 1.5513 | 1.5405 | -43.1336 | -149.3823 | 150.0636 | -43.1336 | -149.3823 | 150.0636
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4329e-10 | 6.1846e-08 | -5.396e-08 | 3.5646e-11 | -4.3628e-09 | -4.302e-09 | 8.4601e-10 | -9.731e-08 | -1.0099e-07 | -3.4185e-11 | -2.5116e-09 | 2.5467e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.015151 | 1.5513 | 1.5405 | 0.015151 | 1.5513 | 1.5405 | -43.1336 | -149.3823 | 150.0636 | -43.1336 | -149.3823 | 150.0636
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4332e-10 | 6.1846e-08 | -5.396e-08 | 3.5647e-11 | -4.3628e-09 | -4.302e-09 | 8.4604e-10 | -9.731e-08 | -1.0099e-07 | -3.4186e-11 | -2.5116e-09 | 2.5467e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.015152 | 1.5513 | 1.5405 | 0.015152 | 1.5513 | 1.5405 | -43.1337 | -149.3823 | 150.0636 | -43.1337 | -149.3823 | 150.0636
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4332e-10 | 6.1846e-08 | -5.396e-08 | 3.5647e-11 | -4.3628e-09 | -4.302e-09 | 8.4604e-10 | -9.731e-08 | -1.0099e-07 | -3.4186e-11 | -2.5116e-09 | 2.5467e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.015152 | 1.5513 | 1.5405 | 0.015152 | 1.5513 | 1.5405 | -43.1337 | -149.3823 | 150.0636 | -43.1337 | -149.3823 | 150.0636
Line1_1_3 | 2.5748e-06 | 2.5748e-06 | 2.5748e-06 | 2.2536e-06 | 2.2536e-06 | 2.2536e-06 | 5.9461e-07 | 5.9462e-07 | 5.9462e-07 | 5.2044e-07 | 5.2044e-07 | 5.2044e-07 | 5.9465e-09 | 4.9477e-07 | -4.3168e-07 | -5.1675e-09 | -4.3729e-07 | 3.7342e-07 | 6.7683e-09 | -7.7848e-07 | -8.0793e-07 | -5.9564e-09 | 6.7866e-07 | 7.0949e-07 | -91.8317 | -91.8205 | -91.8205 | 87.8097 | 87.8225 | 87.8225 | 0.015152 | 1.5513 | 1.5405 | 0.015152 | 1.5513 | 1.5405 | -43.1337 | -149.3823 | 150.0636 | -43.1337 | -149.3823 | 150.0636
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4866e-09 | 1.2369e-07 | -1.0792e-07 | -7.0767e-10 | -6.6209e-08 | 4.9658e-08 | 1.6921e-09 | -1.9462e-07 | -2.0198e-07 | -8.8023e-10 | 9.4799e-08 | 1.0354e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0.015152 | 1.5513 | 1.5405 | 0.015152 | 1.5513 | 1.5405 | -43.1337 | -149.3823 | 150.0636 | -43.1337 | -149.3823 | 150.0636
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4866e-09 | 1.2369e-07 | -1.0792e-07 | -7.0767e-10 | -6.6209e-08 | 4.9658e-08 | 1.6921e-09 | -1.9462e-07 | -2.0198e-07 | -8.8023e-10 | 9.4799e-08 | 1.0354e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0.015152 | 1.5513 | 1.5405 | 0.015152 | 1.5513 | 1.5405 | -43.1337 | -149.3823 | 150.0636 | -43.1337 | -149.3823 | 150.0636
Line4_2_6 | 0.037865 | 1.6126e-06 | 1.6126e-06 | 0.037864 | 1.2911e-06 | 1.2911e-06 | 0.0087445 | 3.7241e-07 | 3.7241e-07 | 0.0087444 | 2.9817e-07 | 2.9817e-07 | 6.8818e-05 | 3.1086e-07 | -2.6934e-07 | -4.5878e-05 | -2.5334e-07 | 2.11e-07 | 7.1685e-05 | -4.8684e-07 | -5.0624e-07 | -4.779e-05 | 3.8684e-07 | 4.0752e-07 | -89.3029 | -91.915 | -91.915 | 90.6971 | 87.4506 | 87.4506 | 0.011364 | 1.551 | 1.5398 | 0.0075759 | 1.5508 | 1.539 | -43.1337 | -149.3554 | 150.07 | -43.1337 | -149.3286 | 150.0764
Line5_6_7 | 0.037864 | 1.2904e-06 | 1.2904e-06 | 0.037864 | 0 | 0 | 0.0087444 | 2.9801e-07 | 2.9801e-07 | 0.0087443 | 0 | 0 | 4.5878e-05 | 2.4899e-07 | -2.1529e-07 | -2.2939e-05 | -1.913e-07 | 1.5706e-07 | 4.779e-05 | -3.8935e-07 | -4.0497e-07 | -2.3895e-05 | 2.8941e-07 | 3.0624e-07 | -89.3029 | -91.9273 | -91.9273 | 90.6971 | 0 | 0 | 0.0075759 | 1.5508 | 1.539 | 0.0037879 | 1.5506 | 1.5383 | -43.1337 | -149.3286 | 150.0764 | -43.1337 | -149.3017 | 150.0829
Line6_7_8 | 0.037864 | 0 | 0 | 0.037864 | 0 | 0 | 0.0087443 | 0 | 0 | 0.0087443 | 0 | 0 | 2.2939e-05 | 1.8695e-07 | -1.6134e-07 | 6.1244e-15 | -1.2909e-07 | 1.032e-07 | 2.3895e-05 | -2.9192e-07 | -3.037e-07 | 2.5461e-16 | 1.9203e-07 | 2.0496e-07 | -89.3028 | 0 | 0 | 90.6972 | 0 | 0 | 0.0037879 | 1.5506 | 1.5383 | 0 | 1.5504 | 1.5376 | -43.1337 | -149.3017 | 150.0829 | 0 | -149.2748 | 150.0893
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.2006e-20 | 6.2368e-08 | -5.3739e-08 | -2.1235e-17 | -4.3509e-09 | -4.2782e-09 | -4.6144e-21 | -9.7267e-08 | -1.0121e-07 | 2.394e-17 | -2.5019e-09 | 2.5438e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5504 | 1.5376 | 0 | 1.5504 | 1.5376 | 0 | -149.2748 | 150.0893 | 0 | -149.2748 | 150.0893
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.2006e-20 | 6.2368e-08 | -5.3739e-08 | -2.1235e-17 | -4.3509e-09 | -4.2782e-09 | -4.6144e-21 | -9.7267e-08 | -1.0121e-07 | 2.394e-17 | -2.5019e-09 | 2.5438e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5504 | 1.5376 | 0 | 1.5504 | 1.5376 | 0 | -149.2748 | 150.0893 | 0 | -149.2748 | 150.0893
Line9_3_11 | 2.2529e-06 | 2.2529e-06 | 2.2529e-06 | 1.9317e-06 | 1.9317e-06 | 1.9317e-06 | 5.2029e-07 | 5.2029e-07 | 5.2029e-07 | 4.4612e-07 | 4.4612e-07 | 4.4612e-07 | 5.2032e-09 | 4.3292e-07 | -3.7772e-07 | -4.4242e-09 | -3.7544e-07 | 3.1946e-07 | 5.9222e-09 | -6.8117e-07 | -7.0694e-07 | -5.1104e-09 | 5.8135e-07 | 6.0849e-07 | -91.8317 | -91.8205 | -91.8205 | 87.75 | 87.7631 | 87.7631 | 0.015152 | 1.5513 | 1.5405 | 0.015152 | 1.5513 | 1.5405 | -43.1337 | -149.3823 | 150.0636 | -43.1336 | -149.3823 | 150.0636

## LG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.018835 | 0 | 0 | 0.018835 | 0 | 0 | 0.0043498 | 0 | 0 | 0.0043498 | 0 | 0 | 0.0017964 | 1.3093e-07 | -2.0521e-07 | -0.0017907 | -1.1122e-07 | 1.7016e-07 | 0.0017974 | -2.6675e-07 | -1.2279e-07 | -0.0017914 | 2.2142e-07 | 1.0387e-07 | -64.2169 | 0 | 0 | 115.7831 | 0 | 0 | 0.58421 | 1.3371 | 1.0761 | 0.58233 | 1.337 | 1.0757 | -19.2017 | -130.6718 | 144.0799 | -19.2054 | -130.6569 | 144.0738
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.7481e-08 | 1.3032e-07 | -2.0501e-07 | -7.2231e-08 | -1.1058e-07 | 1.7002e-07 | 9.5617e-08 | -2.6646e-07 | -1.2228e-07 | -8.035e-08 | 2.2119e-07 | 1.0343e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0.58421 | 1.3371 | 1.0761 | 0.58421 | 1.3371 | 1.0761 | -19.2017 | -130.6718 | 144.0799 | -19.2017 | -130.6718 | 144.0799
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.2901e-08 | 1.086e-07 | -1.7084e-07 | -5.7651e-08 | -8.8861e-08 | 1.3585e-07 | 7.9681e-08 | -2.2205e-07 | -1.019e-07 | -6.4414e-08 | 1.7678e-07 | 8.3051e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0.58421 | 1.3371 | 1.0761 | 0.58421 | 1.3371 | 1.0761 | -19.2017 | -130.6718 | 144.0799 | -19.2017 | -130.6718 | 144.0799
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3741e-08 | 6.5162e-08 | -1.0251e-07 | -2.849e-08 | -4.542e-08 | 6.7514e-08 | 4.7808e-08 | -1.3323e-07 | -6.1141e-08 | -3.2542e-08 | 8.7958e-08 | 4.229e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0.58421 | 1.3371 | 1.0761 | 0.58421 | 1.3371 | 1.0761 | -19.2017 | -130.6718 | 144.0799 | -19.2017 | -130.6718 | 144.0799
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.458e-08 | 2.1721e-08 | -3.4169e-08 | 6.7034e-10 | -1.9786e-09 | -8.2365e-10 | 1.5936e-08 | -4.441e-08 | -2.038e-08 | -6.693e-10 | -8.6253e-10 | 1.5294e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.58421 | 1.3371 | 1.0761 | 0.58421 | 1.3371 | 1.0761 | -19.2017 | -130.6718 | 144.0799 | -19.2017 | -130.6718 | 144.0799
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.916e-08 | 4.3441e-08 | -6.8338e-08 | -1.391e-08 | -2.3699e-08 | 3.3345e-08 | 3.1872e-08 | -8.8821e-08 | -4.0761e-08 | -1.6605e-08 | 4.3548e-08 | 2.191e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0.58421 | 1.3371 | 1.0761 | 0.58421 | 1.3371 | 1.0761 | -19.2017 | -130.6718 | 144.0799 | -19.2017 | -130.6718 | 144.0799
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.458e-08 | 2.1721e-08 | -3.4169e-08 | 6.7034e-10 | -1.9786e-09 | -8.2365e-10 | 1.5936e-08 | -4.441e-08 | -2.038e-08 | -6.693e-10 | -8.6253e-10 | 1.5294e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.58421 | 1.3371 | 1.0761 | 0.58421 | 1.3371 | 1.0761 | -19.2017 | -130.6718 | 144.0799 | -19.2017 | -130.6718 | 144.0799
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.458e-08 | 2.1721e-08 | -3.4169e-08 | 6.7034e-10 | -1.9786e-09 | -8.2365e-10 | 1.5936e-08 | -4.441e-08 | -2.038e-08 | -6.693e-10 | -8.6253e-10 | 1.5294e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.58421 | 1.3371 | 1.0761 | 0.58421 | 1.3371 | 1.0761 | -19.2017 | -130.6718 | 144.0799 | -19.2017 | -130.6718 | 144.0799
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.458e-08 | 2.1721e-08 | -3.4169e-08 | 6.7034e-10 | -1.9786e-09 | -8.2365e-10 | 1.5936e-08 | -4.441e-08 | -2.038e-08 | -6.693e-10 | -8.6253e-10 | 1.5294e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.58421 | 1.3371 | 1.0761 | 0.58421 | 1.3371 | 1.0761 | -19.2017 | -130.6718 | 144.0799 | -19.2017 | -130.6718 | 144.0799
Line1_1_3 | 1.2808e-06 | 1.2808e-06 | 1.2808e-06 | 1.121e-06 | 1.121e-06 | 1.121e-06 | 2.9578e-07 | 2.9578e-07 | 2.9578e-07 | 2.5888e-07 | 2.5888e-07 | 2.5888e-07 | 1.1664e-07 | 1.7376e-07 | -2.7335e-07 | -1.0139e-07 | -1.5402e-07 | 2.3836e-07 | 1.2749e-07 | -3.5528e-07 | -1.6304e-07 | -1.1222e-07 | 3.1001e-07 | 1.4419e-07 | -66.7457 | -66.7345 | -66.7345 | 112.8958 | 112.9086 | 112.9086 | 0.58421 | 1.3371 | 1.0761 | 0.58421 | 1.3371 | 1.0761 | -19.2017 | -130.6718 | 144.0799 | -19.2017 | -130.6718 | 144.0799
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.916e-08 | 4.3441e-08 | -6.8338e-08 | -1.391e-08 | -2.3699e-08 | 3.3345e-08 | 3.1872e-08 | -8.8821e-08 | -4.0761e-08 | -1.6605e-08 | 4.3548e-08 | 2.191e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0.58421 | 1.3371 | 1.0761 | 0.58421 | 1.3371 | 1.0761 | -19.2017 | -130.6718 | 144.0799 | -19.2017 | -130.6718 | 144.0799
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.916e-08 | 4.3441e-08 | -6.8338e-08 | -1.391e-08 | -2.3699e-08 | 3.3345e-08 | 3.1872e-08 | -8.8821e-08 | -4.0761e-08 | -1.6605e-08 | 4.3548e-08 | 2.191e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0.58421 | 1.3371 | 1.0761 | 0.58421 | 1.3371 | 1.0761 | -19.2017 | -130.6718 | 144.0799 | -19.2017 | -130.6718 | 144.0799
Line4_2_6 | 0.018835 | 0 | 0 | 0.018835 | 0 | 0 | 0.0043498 | 0 | 0 | 0.0043497 | 0 | 0 | 0.0017907 | 1.0924e-07 | -1.7098e-07 | -0.001785 | -8.9467e-08 | 1.3595e-07 | 0.0017914 | -2.2228e-07 | -1.0234e-07 | -0.0017855 | 1.7695e-07 | 8.3411e-08 | -64.2169 | 0 | 0 | 115.7831 | 0 | 0 | 0.58233 | 1.337 | 1.0757 | 0.58044 | 1.3368 | 1.0754 | -19.2054 | -130.6569 | 144.0738 | -19.2091 | -130.642 | 144.0676
Line5_6_7 | 0.018835 | 0 | 0 | 0.018835 | 0 | 0 | 0.0043497 | 0 | 0 | 0.0043497 | 0 | 0 | 0.001785 | 8.7491e-08 | -1.3677e-07 | -0.0017793 | -6.7659e-08 | 1.0174e-07 | 0.0017855 | -1.7781e-07 | -8.1883e-08 | -0.0017796 | 1.3248e-07 | 6.294e-08 | -64.2168 | 0 | 0 | 115.7832 | 0 | 0 | 0.58044 | 1.3368 | 1.0754 | 0.57856 | 1.3367 | 1.075 | -19.2091 | -130.642 | 144.0676 | -19.2129 | -130.627 | 144.0615
Line6_7_8 | 0.018835 | 0 | 0 | 0.018834 | 0 | 0 | 0.0043497 | 0 | 0 | 0.0043496 | 0 | 0 | 0.0017794 | 6.5684e-08 | -1.0256e-07 | -0.0017737 | -4.5795e-08 | 6.7543e-08 | 0.0017796 | -1.3334e-07 | -6.1413e-08 | -0.0017737 | 8.8023e-08 | 4.2458e-08 | -64.2168 | 0 | 0 | 115.7832 | 0 | 0 | 0.57856 | 1.3367 | 1.075 | 0.57668 | 1.3366 | 1.0746 | -19.2129 | -130.627 | 144.0615 | -19.2167 | -130.6121 | 144.0553
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4382e-08 | 2.191e-08 | -3.4179e-08 | 6.7746e-10 | -1.9741e-09 | -8.1624e-10 | 1.58e-08 | -4.444e-08 | -2.0466e-08 | -6.6117e-10 | -8.5739e-10 | 1.5259e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.57668 | 1.3366 | 1.0746 | 0.57668 | 1.3366 | 1.0746 | -19.2167 | -130.6121 | 144.0553 | -19.2167 | -130.6121 | 144.0553
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4382e-08 | 2.191e-08 | -3.4179e-08 | 6.7746e-10 | -1.9741e-09 | -8.1624e-10 | 1.58e-08 | -4.444e-08 | -2.0466e-08 | -6.6117e-10 | -8.5739e-10 | 1.5259e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.57668 | 1.3366 | 1.0746 | 0.57668 | 1.3366 | 1.0746 | -19.2167 | -130.6121 | 144.0553 | -19.2167 | -130.6121 | 144.0553
Line9_3_11 | 1.1207e-06 | 1.1207e-06 | 1.1207e-06 | 0 | 0 | 0 | 2.5881e-07 | 2.5881e-07 | 2.5881e-07 | 0 | 0 | 0 | 1.0206e-07 | 1.5204e-07 | -2.3918e-07 | -8.6811e-08 | -1.323e-07 | 2.0419e-07 | 1.1155e-07 | -3.1087e-07 | -1.4266e-07 | -9.6286e-08 | 2.656e-07 | 1.2381e-07 | -66.7457 | -66.7345 | -66.7345 | 0 | 0 | 0 | 0.58421 | 1.3371 | 1.0761 | 0.58421 | 1.3371 | 1.0761 | -19.2017 | -130.6718 | 144.0799 | -19.2017 | -130.6718 | 144.0799

## LG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.017844 | 0 | 0 | 0.017844 | 0 | 0 | 0.0041209 | 0 | 0 | 0.0041208 | 0 | 0 | 0.0016123 | 1.1751e-07 | -1.8417e-07 | -0.0016072 | -9.9819e-08 | 1.5272e-07 | 0.0016132 | -2.3941e-07 | -1.1021e-07 | -0.0016078 | 1.9872e-07 | 9.3225e-08 | -64.2169 | 0 | 0 | 115.7831 | 0 | 0 | 0.55346 | 1.2668 | 1.0194 | 0.55168 | 1.2666 | 1.0191 | -19.2017 | -130.6718 | 144.0799 | -19.2054 | -130.6569 | 144.0738
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.8515e-08 | 1.1697e-07 | -1.84e-07 | -6.4828e-08 | -9.9248e-08 | 1.5259e-07 | 8.5817e-08 | -2.3915e-07 | -1.0975e-07 | -7.2115e-08 | 1.9852e-07 | 9.283e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0.55346 | 1.2668 | 1.0194 | 0.55346 | 1.2668 | 1.0194 | -19.2017 | -130.6718 | 144.0799 | -19.2017 | -130.6718 | 144.0799
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.5429e-08 | 9.7472e-08 | -1.5333e-07 | -5.1742e-08 | -7.9753e-08 | 1.2193e-07 | 7.1514e-08 | -1.9929e-07 | -9.1458e-08 | -5.7812e-08 | 1.5866e-07 | 7.4539e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0.55346 | 1.2668 | 1.0194 | 0.55346 | 1.2668 | 1.0194 | -19.2017 | -130.6718 | 144.0799 | -19.2017 | -130.6718 | 144.0799
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9258e-08 | 5.8483e-08 | -9.2e-08 | -2.557e-08 | -4.0765e-08 | 6.0594e-08 | 4.2908e-08 | -1.1958e-07 | -5.4875e-08 | -2.9206e-08 | 7.8943e-08 | 3.7956e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0.55346 | 1.2668 | 1.0194 | 0.55346 | 1.2668 | 1.0194 | -19.2017 | -130.6718 | 144.0799 | -19.2017 | -130.6718 | 144.0799
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3086e-08 | 1.9494e-08 | -3.0667e-08 | 6.0164e-10 | -1.7758e-09 | -7.3923e-10 | 1.4303e-08 | -3.9859e-08 | -1.8292e-08 | -6.007e-10 | -7.7412e-10 | 1.3726e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.55346 | 1.2668 | 1.0194 | 0.55346 | 1.2668 | 1.0194 | -19.2017 | -130.6718 | 144.0799 | -19.2017 | -130.6718 | 144.0799
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6172e-08 | 3.8989e-08 | -6.1334e-08 | -1.2484e-08 | -2.127e-08 | 2.9928e-08 | 2.8606e-08 | -7.9717e-08 | -3.6583e-08 | -1.4903e-08 | 3.9084e-08 | 1.9664e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0.55346 | 1.2668 | 1.0194 | 0.55346 | 1.2668 | 1.0194 | -19.2017 | -130.6718 | 144.0799 | -19.2017 | -130.6718 | 144.0799
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3086e-08 | 1.9494e-08 | -3.0667e-08 | 6.0164e-10 | -1.7758e-09 | -7.3923e-10 | 1.4303e-08 | -3.9859e-08 | -1.8292e-08 | -6.007e-10 | -7.7412e-10 | 1.3726e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.55346 | 1.2668 | 1.0194 | 0.55346 | 1.2668 | 1.0194 | -19.2017 | -130.6718 | 144.0799 | -19.2017 | -130.6718 | 144.0799
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3086e-08 | 1.9494e-08 | -3.0667e-08 | 6.0164e-10 | -1.7758e-09 | -7.3923e-10 | 1.4303e-08 | -3.9859e-08 | -1.8292e-08 | -6.007e-10 | -7.7412e-10 | 1.3726e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.55346 | 1.2668 | 1.0194 | 0.55346 | 1.2668 | 1.0194 | -19.2017 | -130.6718 | 144.0799 | -19.2017 | -130.6718 | 144.0799
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3086e-08 | 1.9494e-08 | -3.0667e-08 | 6.0164e-10 | -1.7758e-09 | -7.3923e-10 | 1.4303e-08 | -3.9859e-08 | -1.8292e-08 | -6.007e-10 | -7.7412e-10 | 1.3726e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.55346 | 1.2668 | 1.0194 | 0.55346 | 1.2668 | 1.0194 | -19.2017 | -130.6718 | 144.0799 | -19.2017 | -130.6718 | 144.0799
Line1_1_3 | 1.2133e-06 | 1.2134e-06 | 1.2134e-06 | 1.062e-06 | 1.062e-06 | 1.062e-06 | 2.8021e-07 | 2.8021e-07 | 2.8021e-07 | 2.4526e-07 | 2.4526e-07 | 2.4526e-07 | 1.0469e-07 | 1.5595e-07 | -2.4533e-07 | -9.0999e-08 | -1.3824e-07 | 2.1393e-07 | 1.1442e-07 | -3.1887e-07 | -1.4633e-07 | -1.0072e-07 | 2.7824e-07 | 1.2941e-07 | -66.7457 | -66.7345 | -66.7345 | 112.8958 | 112.9086 | 112.9086 | 0.55346 | 1.2668 | 1.0194 | 0.55346 | 1.2668 | 1.0194 | -19.2017 | -130.6718 | 144.0799 | -19.2017 | -130.6718 | 144.0799
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6172e-08 | 3.8989e-08 | -6.1334e-08 | -1.2484e-08 | -2.127e-08 | 2.9928e-08 | 2.8606e-08 | -7.9717e-08 | -3.6583e-08 | -1.4903e-08 | 3.9084e-08 | 1.9664e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0.55346 | 1.2668 | 1.0194 | 0.55346 | 1.2668 | 1.0194 | -19.2017 | -130.6718 | 144.0799 | -19.2017 | -130.6718 | 144.0799
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6172e-08 | 3.8989e-08 | -6.1334e-08 | -1.2484e-08 | -2.127e-08 | 2.9928e-08 | 2.8606e-08 | -7.9717e-08 | -3.6583e-08 | -1.4903e-08 | 3.9084e-08 | 1.9664e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0.55346 | 1.2668 | 1.0194 | 0.55346 | 1.2668 | 1.0194 | -19.2017 | -130.6718 | 144.0799 | -19.2017 | -130.6718 | 144.0799
Line4_2_6 | 0.017844 | 0 | 0 | 0.017844 | 0 | 0 | 0.0041208 | 0 | 0 | 0.0041208 | 0 | 0 | 0.0016072 | 9.8044e-08 | -1.5346e-07 | -0.0016021 | -8.0297e-08 | 1.2202e-07 | 0.0016078 | -1.995e-07 | -9.1853e-08 | -0.0016025 | 1.5881e-07 | 7.4862e-08 | -64.2169 | 0 | 0 | 115.7831 | 0 | 0 | 0.55168 | 1.2666 | 1.0191 | 0.54989 | 1.2665 | 1.0188 | -19.2054 | -130.6569 | 144.0738 | -19.2091 | -130.642 | 144.0676
Line5_6_7 | 0.017844 | 0 | 0 | 0.017843 | 0 | 0 | 0.0041208 | 0 | 0 | 0.0041207 | 0 | 0 | 0.0016021 | 7.8523e-08 | -1.2275e-07 | -0.001597 | -6.0725e-08 | 9.1315e-08 | 0.0016025 | -1.5959e-07 | -7.3491e-08 | -0.0015972 | 1.1891e-07 | 5.6489e-08 | -64.2168 | 0 | 0 | 115.7832 | 0 | 0 | 0.54989 | 1.2665 | 1.0188 | 0.54811 | 1.2664 | 1.0184 | -19.2091 | -130.642 | 144.0676 | -19.2129 | -130.627 | 144.0615
Line6_7_8 | 0.017843 | 0 | 0 | 0.017843 | 0 | 0 | 0.0041207 | 0 | 0 | 0.0041207 | 0 | 0 | 0.001597 | 5.8952e-08 | -9.2049e-08 | -0.0015919 | -4.1101e-08 | 6.062e-08 | 0.0015972 | -1.1968e-07 | -5.5119e-08 | -0.0015919 | 7.9001e-08 | 3.8106e-08 | -64.2168 | 0 | 0 | 115.7832 | 0 | 0 | 0.54811 | 1.2664 | 1.0184 | 0.54633 | 1.2662 | 1.0181 | -19.2129 | -130.627 | 144.0615 | -19.2167 | -130.6121 | 144.0553
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2908e-08 | 1.9665e-08 | -3.0676e-08 | 6.0802e-10 | -1.7717e-09 | -7.3258e-10 | 1.4181e-08 | -3.9885e-08 | -1.8368e-08 | -5.934e-10 | -7.6951e-10 | 1.3695e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.54633 | 1.2662 | 1.0181 | 0.54633 | 1.2662 | 1.0181 | -19.2167 | -130.6121 | 144.0553 | -19.2167 | -130.6121 | 144.0553
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2908e-08 | 1.9665e-08 | -3.0676e-08 | 6.0802e-10 | -1.7717e-09 | -7.3258e-10 | 1.4181e-08 | -3.9885e-08 | -1.8368e-08 | -5.934e-10 | -7.6951e-10 | 1.3695e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.54633 | 1.2662 | 1.0181 | 0.54633 | 1.2662 | 1.0181 | -19.2167 | -130.6121 | 144.0553 | -19.2167 | -130.6121 | 144.0553
Line9_3_11 | 1.0617e-06 | 1.0617e-06 | 1.0617e-06 | 0 | 0 | 0 | 2.4518e-07 | 2.4519e-07 | 2.4519e-07 | 0 | 0 | 0 | 9.1601e-08 | 1.3646e-07 | -2.1467e-07 | -7.7914e-08 | -1.1874e-07 | 1.8326e-07 | 1.0012e-07 | -2.7901e-07 | -1.2804e-07 | -8.6417e-08 | 2.3838e-07 | 1.1112e-07 | -66.7457 | -66.7345 | -66.7345 | 0 | 0 | 0 | 0.55346 | 1.2668 | 1.0194 | 0.55346 | 1.2668 | 1.0194 | -19.2017 | -130.6718 | 144.0799 | -19.2017 | -130.6718 | 144.0799

## LLG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 1.1393e-06 | 1.8809 | 1.8892 | 0 | 1.8809 | 1.8892 | 2.6311e-07 | 0.43438 | 0.4363 | 0 | 0.43438 | 0.4363 | 1.765e-08 | 0.1411 | 0.14318 | -1.7783e-08 | -0.10582 | -0.10739 | -4.1305e-07 | 0.28349 | 0.28507 | 3.4424e-07 | -0.21262 | -0.2138 | 87.6033 | -158.1979 | 22.4308 | 0 | 21.8021 | -157.5692 | 1.5713 | 0.729 | 0.73116 | 1.571 | 0.54675 | 0.54837 | 0.05 | -94.6578 | 85.7613 | 0.055847 | -94.6578 | 85.7613
Line10_11_12 | 1.1374e-06 | 1.1544e-06 | 1.1203e-06 | 0 | 0 | 0 | 2.6266e-07 | 2.666e-07 | 2.5873e-07 | 0 | 0 | 0 | 1.7345e-08 | -1.9415e-07 | 1.891e-07 | -1.7458e-08 | 1.6238e-07 | -1.5722e-07 | -4.1236e-07 | 8.8049e-09 | -5.1583e-09 | 3.4364e-07 | -6.1361e-09 | 2.7148e-09 | 87.6413 | 87.9388 | 87.3239 | 0 | 0 | 0 | 1.5713 | 0.729 | 0.73116 | 1.5713 | 0.729 | 0.73116 | 0.049998 | -94.6578 | 85.7613 | 0.049997 | -94.6578 | 85.7613
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4454e-08 | -1.618e-07 | 1.5758e-07 | -1.4567e-08 | 1.3002e-07 | -1.257e-07 | -3.4363e-07 | 7.3374e-09 | -4.2986e-09 | 2.7491e-07 | -4.6686e-09 | 1.8551e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5713 | 0.729 | 0.73116 | 1.5713 | 0.729 | 0.73116 | 0.049997 | -94.6578 | 85.7613 | 0.049996 | -94.6578 | 85.7613
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.6727e-09 | -9.7077e-08 | 9.455e-08 | -8.7852e-09 | 6.5306e-08 | -6.2667e-08 | -2.0618e-07 | 4.4024e-09 | -2.5792e-09 | 1.3746e-07 | -1.7336e-09 | 1.3564e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5713 | 0.729 | 0.73116 | 1.5713 | 0.729 | 0.73116 | 0.049996 | -94.6578 | 85.7613 | 0.049996 | -94.6578 | 85.7613
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8909e-09 | -3.2359e-08 | 3.1517e-08 | -3.0034e-09 | 5.8794e-10 | 3.6696e-10 | -6.8726e-08 | 1.4675e-09 | -8.5972e-10 | 5.2794e-12 | 1.2013e-09 | -1.5838e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5713 | 0.729 | 0.73116 | 1.5713 | 0.729 | 0.73116 | 0.049996 | -94.6578 | 85.7613 | 0.049996 | -94.6578 | 85.7613
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.7818e-09 | -6.4718e-08 | 6.3034e-08 | -5.8943e-09 | 3.2947e-08 | -3.115e-08 | -1.3745e-07 | 2.935e-09 | -1.7194e-09 | 6.8732e-08 | -2.6616e-10 | -7.2408e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5713 | 0.729 | 0.73116 | 1.5713 | 0.729 | 0.73116 | 0.049996 | -94.6578 | 85.7613 | 0.049995 | -94.6578 | 85.7613
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8909e-09 | -3.2359e-08 | 3.1517e-08 | -3.0034e-09 | 5.8794e-10 | 3.6696e-10 | -6.8726e-08 | 1.4675e-09 | -8.5972e-10 | 5.279e-12 | 1.2013e-09 | -1.5838e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5713 | 0.729 | 0.73116 | 1.5713 | 0.729 | 0.73116 | 0.049995 | -94.6578 | 85.7613 | 0.049995 | -94.6578 | 85.7613
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8909e-09 | -3.2359e-08 | 3.1517e-08 | -3.0034e-09 | 5.8794e-10 | 3.6696e-10 | -6.8726e-08 | 1.4675e-09 | -8.5972e-10 | 5.2802e-12 | 1.2013e-09 | -1.5838e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5713 | 0.729 | 0.73116 | 1.5713 | 0.729 | 0.73116 | 0.05 | -94.6578 | 85.7613 | 0.05 | -94.6578 | 85.7613
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8909e-09 | -3.2359e-08 | 3.1517e-08 | -3.0034e-09 | 5.8794e-10 | 3.6696e-10 | -6.8726e-08 | 1.4675e-09 | -8.5972e-10 | 5.2802e-12 | 1.2013e-09 | -1.5838e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5713 | 0.729 | 0.73116 | 1.5713 | 0.729 | 0.73116 | 0.05 | -94.6578 | 85.7613 | 0.05 | -94.6578 | 85.7613
Line1_1_3 | 1.5165e-06 | 1.5392e-06 | 1.4938e-06 | 1.3273e-06 | 1.35e-06 | 1.3047e-06 | 3.5022e-07 | 3.5547e-07 | 3.4497e-07 | 3.0653e-07 | 3.1177e-07 | 3.013e-07 | 2.3127e-08 | -2.5887e-07 | 2.5213e-07 | -2.324e-08 | 2.271e-07 | -2.2025e-07 | -5.4981e-07 | 1.174e-08 | -6.8777e-09 | 4.8109e-07 | -9.0711e-09 | 4.4342e-09 | 87.6413 | 87.9388 | 87.3239 | -92.7156 | -92.3704 | -93.0853 | 1.5713 | 0.729 | 0.73116 | 1.5713 | 0.729 | 0.73116 | 0.05 | -94.6578 | 85.7613 | 0.049999 | -94.6578 | 85.7613
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.7818e-09 | -6.4718e-08 | 6.3034e-08 | -5.8943e-09 | 3.2947e-08 | -3.115e-08 | -1.3745e-07 | 2.935e-09 | -1.7194e-09 | 6.8731e-08 | -2.6618e-10 | -7.2409e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5713 | 0.729 | 0.73116 | 1.5713 | 0.729 | 0.73116 | 0.05 | -94.6578 | 85.7613 | 0.05 | -94.6578 | 85.7613
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.7818e-09 | -6.4718e-08 | 6.3034e-08 | -5.8943e-09 | 3.2947e-08 | -3.115e-08 | -1.3745e-07 | 2.935e-09 | -1.7194e-09 | 6.8731e-08 | -2.6618e-10 | -7.2409e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5713 | 0.729 | 0.73116 | 1.5713 | 0.729 | 0.73116 | 0.05 | -94.6578 | 85.7613 | 0.05 | -94.6578 | 85.7613
Line4_2_6 | 0 | 1.8809 | 1.8892 | 0 | 1.8809 | 1.8892 | 0 | 0.43438 | 0.4363 | 0 | 0.43438 | 0.4363 | 1.4782e-08 | 0.10582 | 0.10739 | -1.4881e-08 | -0.070548 | -0.071592 | -3.4423e-07 | 0.21262 | 0.2138 | 2.754e-07 | -0.14175 | -0.14253 | 0 | -158.1979 | 22.4308 | 0 | 21.8021 | -157.5692 | 1.571 | 0.54675 | 0.54837 | 1.5707 | 0.3645 | 0.36558 | 0.055847 | -94.6578 | 85.7613 | 0.061696 | -94.6578 | 85.7613
Line5_6_7 | 0 | 1.8809 | 1.8892 | 0 | 1.8809 | 1.8892 | 0 | 0.43438 | 0.4363 | 0 | 0.43438 | 0.4363 | 1.1883e-08 | 0.070548 | 0.071592 | -1.1947e-08 | -0.035274 | -0.035796 | -2.754e-07 | 0.14175 | 0.14253 | 2.0655e-07 | -0.070873 | -0.071267 | 0 | -158.1979 | 22.4308 | 0 | 21.8021 | -157.5692 | 1.5707 | 0.3645 | 0.36558 | 1.5703 | 0.18225 | 0.18279 | 0.061696 | -94.6578 | 85.7613 | 0.067548 | -94.6578 | 85.7613
Line6_7_8 | 0 | 1.8809 | 1.8892 | 0 | 1.8809 | 1.8892 | 0 | 0.43438 | 0.4363 | 0 | 0.43438 | 0.4363 | 8.9509e-09 | 0.035274 | 0.035796 | -8.9807e-09 | 4.5098e-13 | -3.8352e-13 | -2.0655e-07 | 0.070873 | 0.071267 | 1.3769e-07 | 2.3185e-13 | -2.3073e-13 | 0 | -158.1979 | 22.4308 | 0 | 21.8021 | -157.5692 | 1.5703 | 0.18225 | 0.18279 | 1.57 | 0 | 0 | 0.067548 | -94.6578 | 85.7613 | 0.073402 | 0 | 0
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9936e-09 | 4.3003e-20 | 3.453e-20 | -2.9936e-09 | 1.4632e-19 | -1.1116e-17 | -6.8842e-08 | -3.4478e-20 | -2.32e-20 | 7.7438e-12 | 2.3124e-17 | -5.5038e-18 | 0 | 0 | 0 | 0 | 0 | 0 | 1.57 | 0 | 0 | 1.57 | 0 | 0 | 0.073402 | 0 | 0 | 0.073402 | 0 | 0
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9936e-09 | 4.3003e-20 | 3.453e-20 | -2.9936e-09 | 1.4632e-19 | -1.1116e-17 | -6.8842e-08 | -3.4478e-20 | -2.32e-20 | 7.744e-12 | 2.3124e-17 | -5.5038e-18 | 0 | 0 | 0 | 0 | 0 | 0 | 1.57 | 0 | 0 | 1.57 | 0 | 0 | 0.073402 | 0 | 0 | 0.073402 | 0 | 0
Line9_3_11 | 1.3269e-06 | 1.3468e-06 | 1.307e-06 | 1.1378e-06 | 1.1576e-06 | 1.1179e-06 | 3.0644e-07 | 3.1104e-07 | 3.0185e-07 | 2.6275e-07 | 2.6734e-07 | 2.5818e-07 | 2.0236e-08 | -2.2651e-07 | 2.2062e-07 | -2.0349e-08 | 1.9474e-07 | -1.8873e-07 | -4.8108e-07 | 1.0272e-08 | -6.018e-09 | 4.1236e-07 | -7.6036e-09 | 3.5745e-09 | 87.6413 | 87.9388 | 87.3239 | -92.7751 | -92.4218 | -93.1536 | 1.5713 | 0.729 | 0.73116 | 1.5713 | 0.729 | 0.73116 | 0.049999 | -94.6578 | 85.7613 | 0.049998 | -94.6578 | 85.7613

## LLG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 1.1935e-06 | 1.952 | 1.9607 | 0 | 1.952 | 1.9607 | 2.7563e-07 | 0.45081 | 0.45281 | 0 | 0.45081 | 0.45281 | 1.9368e-08 | 0.15196 | 0.15423 | -1.9514e-08 | -0.11397 | -0.11567 | -4.533e-07 | 0.30534 | 0.30704 | 3.7778e-07 | -0.22901 | -0.23028 | 87.6036 | -158.3683 | 22.267 | 0 | 21.6317 | -157.733 | 1.6461 | 0.75658 | 0.75882 | 1.6457 | 0.56743 | 0.56911 | 0.050153 | -94.8271 | 85.5965 | 0.055999 | -94.8271 | 85.5965
Line10_11_12 | 1.1915e-06 | 1.21e-06 | 1.1729e-06 | 0 | 1.0118e-06 | 0 | 2.7516e-07 | 2.7945e-07 | 2.7088e-07 | 0 | 2.3367e-07 | 0 | 1.9034e-08 | -2.1118e-07 | 2.0546e-07 | -1.9158e-08 | 1.7664e-07 | -1.708e-07 | -4.5253e-07 | 1.0234e-08 | -6.1632e-09 | 3.7712e-07 | -7.2306e-09 | 3.4067e-09 | 87.6417 | 87.9475 | 87.3147 | 0 | -92.4831 | 0 | 1.6461 | 0.75658 | 0.75882 | 1.6461 | 0.75658 | 0.75882 | 0.05015 | -94.8271 | 85.5964 | 0.050149 | -94.8271 | 85.5964
Line11_12_13 | 0 | 1.0084e-06 | 0 | 0 | 0 | 0 | 0 | 2.3287e-07 | 0 | 0 | 0 | 0 | 1.5862e-08 | -1.7598e-07 | 1.7121e-07 | -1.5985e-08 | 1.4145e-07 | -1.3656e-07 | -3.7711e-07 | 8.5286e-09 | -5.136e-09 | 3.017e-07 | -5.5249e-09 | 2.3795e-09 | 0 | 87.9475 | 0 | 0 | 0 | 0 | 1.6461 | 0.75658 | 0.75882 | 1.6461 | 0.75658 | 0.75882 | 0.050149 | -94.8271 | 85.5964 | 0.050149 | -94.8271 | 85.5964
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.517e-09 | -1.0559e-07 | 1.0273e-07 | -9.6405e-09 | 7.1055e-08 | -6.8072e-08 | -2.2627e-07 | 5.1171e-09 | -3.0816e-09 | 1.5085e-07 | -2.1135e-09 | 3.2514e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6461 | 0.75658 | 0.75882 | 1.6461 | 0.75658 | 0.75882 | 0.050149 | -94.8271 | 85.5964 | 0.050148 | -94.8271 | 85.5964
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1723e-09 | -3.5196e-08 | 3.4243e-08 | -3.2959e-09 | 6.6288e-10 | 4.1393e-10 | -7.5422e-08 | 1.7057e-09 | -1.0272e-09 | 5.8118e-12 | 1.298e-09 | -1.7293e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6461 | 0.75658 | 0.75882 | 1.6461 | 0.75658 | 0.75882 | 0.050149 | -94.8271 | 85.5964 | 0.050149 | -94.8271 | 85.5964
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.3447e-09 | -7.0392e-08 | 6.8486e-08 | -6.4682e-09 | 3.5859e-08 | -3.3829e-08 | -1.5084e-07 | 3.4114e-09 | -2.0544e-09 | 7.5428e-08 | -4.0774e-10 | -7.0207e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6461 | 0.75658 | 0.75882 | 1.6461 | 0.75658 | 0.75882 | 0.050148 | -94.8271 | 85.5964 | 0.050148 | -94.8271 | 85.5964
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1723e-09 | -3.5196e-08 | 3.4243e-08 | -3.2959e-09 | 6.6288e-10 | 4.1392e-10 | -7.5422e-08 | 1.7057e-09 | -1.0272e-09 | 5.8107e-12 | 1.298e-09 | -1.7293e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6461 | 0.75658 | 0.75882 | 1.6461 | 0.75658 | 0.75882 | 0.050148 | -94.8271 | 85.5964 | 0.050148 | -94.8271 | 85.5964
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1723e-09 | -3.5196e-08 | 3.4243e-08 | -3.2959e-09 | 6.6288e-10 | 4.1393e-10 | -7.5422e-08 | 1.7057e-09 | -1.0272e-09 | 5.812e-12 | 1.298e-09 | -1.7293e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6461 | 0.75658 | 0.75882 | 1.6461 | 0.75658 | 0.75882 | 0.050152 | -94.8271 | 85.5965 | 0.050152 | -94.8271 | 85.5965
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1723e-09 | -3.5196e-08 | 3.4243e-08 | -3.2959e-09 | 6.6288e-10 | 4.1393e-10 | -7.5422e-08 | 1.7057e-09 | -1.0272e-09 | 5.812e-12 | 1.298e-09 | -1.7293e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6461 | 0.75658 | 0.75882 | 1.6461 | 0.75658 | 0.75882 | 0.050152 | -94.8271 | 85.5965 | 0.050152 | -94.8271 | 85.5965
Line1_1_3 | 1.5886e-06 | 1.6134e-06 | 1.5639e-06 | 1.3905e-06 | 1.4152e-06 | 1.3658e-06 | 3.6688e-07 | 3.726e-07 | 3.6117e-07 | 3.2112e-07 | 3.2682e-07 | 3.1542e-07 | 2.5379e-08 | -2.8157e-07 | 2.7394e-07 | -2.5502e-08 | 2.4704e-07 | -2.3929e-07 | -6.0338e-07 | 1.3646e-08 | -8.2176e-09 | 5.2796e-07 | -1.0642e-08 | 5.4611e-09 | 87.6417 | 87.9475 | 87.3147 | -92.7153 | -92.3604 | -93.0961 | 1.6461 | 0.75658 | 0.75882 | 1.6461 | 0.75658 | 0.75882 | 0.050153 | -94.8271 | 85.5965 | 0.050151 | -94.8271 | 85.5965
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.3446e-09 | -7.0392e-08 | 6.8485e-08 | -6.4682e-09 | 3.5859e-08 | -3.3829e-08 | -1.5084e-07 | 3.4115e-09 | -2.0544e-09 | 7.5428e-08 | -4.0776e-10 | -7.0207e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6461 | 0.75658 | 0.75882 | 1.6461 | 0.75658 | 0.75882 | 0.050153 | -94.8271 | 85.5965 | 0.050152 | -94.8271 | 85.5965
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.3446e-09 | -7.0392e-08 | 6.8485e-08 | -6.4682e-09 | 3.5859e-08 | -3.3829e-08 | -1.5084e-07 | 3.4115e-09 | -2.0544e-09 | 7.5428e-08 | -4.0776e-10 | -7.0207e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6461 | 0.75658 | 0.75882 | 1.6461 | 0.75658 | 0.75882 | 0.050153 | -94.8271 | 85.5965 | 0.050152 | -94.8271 | 85.5965
Line4_2_6 | 0 | 1.952 | 1.9607 | 0 | 1.952 | 1.9607 | 0 | 0.45081 | 0.45281 | 0 | 0.45081 | 0.45281 | 1.6221e-08 | 0.11397 | 0.11567 | -1.633e-08 | -0.075982 | -0.077114 | -3.7777e-07 | 0.22901 | 0.23028 | 3.0224e-07 | -0.15267 | -0.15352 | 0 | -158.3683 | 22.267 | 0 | 21.6317 | -157.733 | 1.6457 | 0.56743 | 0.56911 | 1.6454 | 0.37829 | 0.37941 | 0.055999 | -94.8271 | 85.5965 | 0.061848 | -94.8271 | 85.5965
Line5_6_7 | 0 | 1.952 | 1.9607 | 0 | 1.952 | 1.9607 | 0 | 0.45081 | 0.45281 | 0 | 0.45081 | 0.45281 | 1.3039e-08 | 0.075982 | 0.077114 | -1.311e-08 | -0.037991 | -0.038557 | -3.0223e-07 | 0.15267 | 0.15352 | 2.2668e-07 | -0.076336 | -0.07676 | 0 | -158.3683 | 22.267 | 0 | 21.6317 | -157.733 | 1.6454 | 0.37829 | 0.37941 | 1.6451 | 0.18914 | 0.1897 | 0.061848 | -94.8271 | 85.5965 | 0.067699 | -94.8271 | 85.5965
Line6_7_8 | 0 | 1.952 | 1.9607 | 0 | 1.952 | 1.9607 | 0 | 0.45081 | 0.45281 | 0 | 0.45081 | 0.45281 | 9.8223e-09 | 0.037991 | 0.038557 | -9.855e-09 | 2.7993e-13 | -1.9393e-13 | -2.2667e-07 | 0.076336 | 0.07676 | 1.5111e-07 | 2.501e-13 | -2.7886e-13 | 0 | -158.3683 | 22.267 | 0 | 21.6317 | -157.733 | 1.6451 | 0.18914 | 0.1897 | 1.6447 | 0 | 0 | 0.067699 | -94.8271 | 85.5965 | 0.073553 | 0 | 0
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.285e-09 | 3.7531e-20 | 3.1391e-20 | -3.285e-09 | 1.6213e-19 | -1.2199e-17 | -7.5549e-08 | -1.6962e-20 | -5.4829e-21 | 8.5172e-12 | 2.5377e-17 | -6.0381e-18 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6447 | 0 | 0 | 1.6447 | 0 | 0 | 0.073553 | 0 | 0 | 0.073553 | 0 | 0
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.285e-09 | 3.7531e-20 | 3.1391e-20 | -3.285e-09 | 1.6213e-19 | -1.2199e-17 | -7.5549e-08 | -1.6962e-20 | -5.4829e-21 | 8.5172e-12 | 2.5377e-17 | -6.0381e-18 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6447 | 0 | 0 | 1.6447 | 0 | 0 | 0.073553 | 0 | 0 | 0.073553 | 0 | 0
Line9_3_11 | 1.3901e-06 | 1.4117e-06 | 1.3684e-06 | 1.1919e-06 | 1.2135e-06 | 1.1703e-06 | 3.2102e-07 | 3.2602e-07 | 3.1603e-07 | 2.7526e-07 | 2.8025e-07 | 2.7028e-07 | 2.2206e-08 | -2.4637e-07 | 2.397e-07 | -2.233e-08 | 2.1184e-07 | -2.0504e-07 | -5.2796e-07 | 1.194e-08 | -7.1904e-09 | 4.5254e-07 | -8.9364e-09 | 4.4339e-09 | 87.6417 | 87.9475 | 87.3147 | -92.7747 | -92.4115 | -93.1648 | 1.6461 | 0.75658 | 0.75882 | 1.6461 | 0.75658 | 0.75882 | 0.050151 | -94.8271 | 85.5965 | 0.05015 | -94.8271 | 85.5964

## LLG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0.026757 | 0.033226 | 0 | 0.026757 | 0.033226 | 0 | 0.0061792 | 0.0076732 | 0 | 0.0061792 | 0.0076732 | -4.4176e-08 | 0.0036037 | 0.0055671 | 3.5116e-08 | -0.0035976 | -0.0055552 | -2.3266e-07 | 0.0036407 | 0.0056014 | 1.9431e-07 | -0.0036254 | -0.005581 | 0 | -149.3709 | 55.9079 | 0 | 30.6294 | -124.0923 | 1.3784 | 0.82901 | 1.0292 | 1.3781 | 0.82657 | 1.0262 | 4.2767 | -104.0782 | 101.0843 | 4.2789 | -104.1503 | 101.0403
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.4255e-08 | -1.2423e-07 | 1.7605e-07 | 3.5205e-08 | 1.0407e-07 | -1.4684e-07 | -2.3224e-07 | 6.9279e-08 | -1.2208e-08 | 1.9393e-07 | -5.6857e-08 | 8.8888e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3784 | 0.82901 | 1.0292 | 1.3784 | 0.82901 | 1.0292 | 4.2767 | -104.0782 | 101.0843 | 4.2767 | -104.0782 | 101.0843
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.6879e-08 | -1.0352e-07 | 1.4671e-07 | 2.7829e-08 | 8.3368e-08 | -1.175e-07 | -1.9353e-07 | 5.7733e-08 | -1.0173e-08 | 1.5522e-07 | -4.5311e-08 | 6.8542e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3784 | 0.82901 | 1.0292 | 1.3784 | 0.82901 | 1.0292 | 4.2767 | -104.0782 | 101.0843 | 4.2767 | -104.0782 | 101.0843
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.2128e-08 | -6.2114e-08 | 8.8023e-08 | 1.3077e-08 | 4.1959e-08 | -5.8818e-08 | -1.1612e-07 | 3.464e-08 | -6.104e-09 | 7.7808e-08 | -2.2218e-08 | 2.7848e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3784 | 0.82901 | 1.0292 | 1.3784 | 0.82901 | 1.0292 | 4.2767 | -104.0782 | 101.0843 | 4.2767 | -104.0782 | 101.0843
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.3759e-09 | -2.0705e-08 | 2.9341e-08 | -1.6743e-09 | 5.493e-10 | -1.3554e-10 | -3.8706e-08 | 1.1547e-08 | -2.0347e-09 | 3.9574e-10 | 8.7556e-10 | -1.2845e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3784 | 0.82901 | 1.0292 | 1.3784 | 0.82901 | 1.0292 | 4.2767 | -104.0782 | 101.0843 | 4.2767 | -104.0782 | 101.0843
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.4752e-08 | -4.1409e-08 | 5.8682e-08 | 5.7015e-09 | 2.1254e-08 | -2.9477e-08 | -7.7412e-08 | 2.3093e-08 | -4.0694e-09 | 3.9102e-08 | -1.0671e-08 | 7.5014e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3784 | 0.82901 | 1.0292 | 1.3784 | 0.82901 | 1.0292 | 4.2767 | -104.0782 | 101.0843 | 4.2767 | -104.0782 | 101.0843
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.3759e-09 | -2.0705e-08 | 2.9341e-08 | -1.6743e-09 | 5.493e-10 | -1.3554e-10 | -3.8706e-08 | 1.1547e-08 | -2.0347e-09 | 3.9574e-10 | 8.7556e-10 | -1.2845e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3784 | 0.82901 | 1.0292 | 1.3784 | 0.82901 | 1.0292 | 4.2767 | -104.0782 | 101.0843 | 4.2767 | -104.0782 | 101.0843
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.3759e-09 | -2.0705e-08 | 2.9341e-08 | -1.6743e-09 | 5.493e-10 | -1.3554e-10 | -3.8706e-08 | 1.1547e-08 | -2.0347e-09 | 3.9574e-10 | 8.7556e-10 | -1.2845e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3784 | 0.82901 | 1.0292 | 1.3784 | 0.82901 | 1.0292 | 4.2767 | -104.0782 | 101.0843 | 4.2767 | -104.0782 | 101.0843
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.3759e-09 | -2.0705e-08 | 2.9341e-08 | -1.6743e-09 | 5.493e-10 | -1.3554e-10 | -3.8706e-08 | 1.1547e-08 | -2.0347e-09 | 3.9574e-10 | 8.7556e-10 | -1.2845e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3784 | 0.82901 | 1.0292 | 1.3784 | 0.82901 | 1.0292 | 4.2767 | -104.0782 | 101.0843 | 4.2767 | -104.0782 | 101.0843
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.9007e-08 | -1.6564e-07 | 2.3473e-07 | 4.9957e-08 | 1.4548e-07 | -2.0552e-07 | -3.0965e-07 | 9.2372e-08 | -1.6277e-08 | 2.7134e-07 | -7.995e-08 | 1.2958e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3784 | 0.82901 | 1.0292 | 1.3784 | 0.82901 | 1.0292 | 4.2767 | -104.0782 | 101.0843 | 4.2767 | -104.0782 | 101.0843
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.4752e-08 | -4.1409e-08 | 5.8682e-08 | 5.7015e-09 | 2.1254e-08 | -2.9477e-08 | -7.7412e-08 | 2.3093e-08 | -4.0694e-09 | 3.9102e-08 | -1.0671e-08 | 7.5014e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3784 | 0.82901 | 1.0292 | 1.3784 | 0.82901 | 1.0292 | 4.2767 | -104.0782 | 101.0843 | 4.2767 | -104.0782 | 101.0843
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.4752e-08 | -4.1409e-08 | 5.8682e-08 | 5.7015e-09 | 2.1254e-08 | -2.9477e-08 | -7.7412e-08 | 2.3093e-08 | -4.0694e-09 | 3.9102e-08 | -1.0671e-08 | 7.5014e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3784 | 0.82901 | 1.0292 | 1.3784 | 0.82901 | 1.0292 | 4.2767 | -104.0782 | 101.0843 | 4.2767 | -104.0782 | 101.0843
Line4_2_6 | 0 | 0.026757 | 0.033226 | 0 | 0.026757 | 0.033226 | 0 | 0.0061792 | 0.0076732 | 0 | 0.0061792 | 0.0076732 | -3.6789e-08 | 0.0035976 | 0.0055552 | 2.774e-08 | -0.0035916 | -0.0055434 | -1.9391e-07 | 0.0036254 | 0.005581 | 1.5555e-07 | -0.0036102 | -0.0055606 | 0 | -149.3706 | 55.9077 | 0 | 30.6296 | -124.0924 | 1.3781 | 0.82657 | 1.0262 | 1.3779 | 0.82413 | 1.0233 | 4.2789 | -104.1503 | 101.0403 | 4.2812 | -104.2229 | 100.9961
Line5_6_7 | 0 | 0.026757 | 0.033226 | 0 | 0.026757 | 0.033226 | 0 | 0.0061792 | 0.0076732 | 0 | 0.0061792 | 0.0076732 | -2.9412e-08 | 0.0035916 | 0.0055434 | 2.0375e-08 | -0.0035856 | -0.0055316 | -1.5515e-07 | 0.0036102 | 0.0055606 | 1.1677e-07 | -0.0035949 | -0.0055401 | 0 | -149.3704 | 55.9076 | 0 | 30.6299 | -124.0926 | 1.3779 | 0.82413 | 1.0233 | 1.3777 | 0.82169 | 1.0203 | 4.2812 | -104.2229 | 100.9961 | 4.2834 | -104.2959 | 100.9517
Line6_7_8 | 0 | 0.026757 | 0.033226 | 0 | 0.026757 | 0.033226 | 0 | 0.0061792 | 0.0076732 | 0 | 0.0061792 | 0.0076731 | -2.2045e-08 | 0.0035856 | 0.0055316 | 1.3021e-08 | -0.0035796 | -0.0055197 | -1.1637e-07 | 0.0035949 | 0.0055401 | 7.7973e-08 | -0.0035796 | -0.0055197 | 0 | -149.3701 | 55.9074 | 0 | 30.6301 | -124.0927 | 1.3777 | 0.82169 | 1.0203 | 1.3774 | 0.81926 | 1.0173 | 4.2834 | -104.2959 | 100.9517 | 4.2857 | -104.3693 | 100.9069
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.3446e-09 | -2.0496e-08 | 2.9027e-08 | -1.6686e-09 | 5.765e-10 | -9.3557e-11 | -3.8788e-08 | 1.1533e-08 | -2.0618e-09 | 3.963e-10 | 8.4983e-10 | -1.2812e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3774 | 0.81926 | 1.0173 | 1.3774 | 0.81926 | 1.0173 | 4.2857 | -104.3693 | 100.9069 | 4.2857 | -104.3693 | 100.9069
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.3446e-09 | -2.0496e-08 | 2.9027e-08 | -1.6686e-09 | 5.765e-10 | -9.3557e-11 | -3.8788e-08 | 1.1533e-08 | -2.0618e-09 | 3.963e-10 | 8.4983e-10 | -1.2812e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3774 | 0.81926 | 1.0173 | 1.3774 | 0.81926 | 1.0173 | 4.2857 | -104.3693 | 100.9069 | 4.2857 | -104.3693 | 100.9069
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.1631e-08 | -1.4493e-07 | 2.0539e-07 | 4.2581e-08 | 1.2478e-07 | -1.7618e-07 | -2.7094e-07 | 8.0826e-08 | -1.4243e-08 | 2.3263e-07 | -6.8404e-08 | 1.0924e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3784 | 0.82901 | 1.0292 | 1.3784 | 0.82901 | 1.0292 | 4.2767 | -104.0782 | 101.0843 | 4.2767 | -104.0782 | 101.0843

## LLG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0.028028 | 0.034804 | 0 | 0.028028 | 0.034804 | 0 | 0.0064728 | 0.0080376 | 0 | 0.0064728 | 0.0080376 | -4.8481e-08 | 0.0039543 | 0.0061084 | 3.8538e-08 | -0.0039477 | -0.0060954 | -2.5534e-07 | 0.0039949 | 0.0061461 | 2.1325e-07 | -0.0039781 | -0.0061237 | 0 | -149.378 | 55.9037 | 0 | 30.6223 | -124.0964 | 1.444 | 0.8684 | 1.0781 | 1.4437 | 0.86584 | 1.075 | 4.2763 | -104.0853 | 101.0801 | 4.2786 | -104.1574 | 101.0361
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.8567e-08 | -1.3632e-07 | 1.9318e-07 | 3.8635e-08 | 1.142e-07 | -1.6113e-07 | -2.5487e-07 | 7.6043e-08 | -1.3406e-08 | 2.1283e-07 | -6.2409e-08 | 9.7615e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.444 | 0.8684 | 1.0781 | 1.444 | 0.8684 | 1.0781 | 4.2763 | -104.0853 | 101.0801 | 4.2763 | -104.0853 | 101.0801
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.0473e-08 | -1.136e-07 | 1.6098e-07 | 3.0541e-08 | 9.1483e-08 | -1.2894e-07 | -2.124e-07 | 6.3369e-08 | -1.1171e-08 | 1.7035e-07 | -4.9735e-08 | 7.5272e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.444 | 0.8684 | 1.0781 | 1.444 | 0.8684 | 1.0781 | 4.2763 | -104.0853 | 101.0801 | 4.2763 | -104.0853 | 101.0801
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.4284e-08 | -6.816e-08 | 9.6591e-08 | 1.4352e-08 | 4.6043e-08 | -6.4542e-08 | -1.2744e-07 | 3.8021e-08 | -6.7029e-09 | 8.5392e-08 | -2.4387e-08 | 3.0587e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.444 | 0.8684 | 1.0781 | 1.444 | 0.8684 | 1.0781 | 4.2763 | -104.0853 | 101.0801 | 4.2763 | -104.0853 | 101.0801
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.0946e-09 | -2.272e-08 | 3.2197e-08 | -1.8374e-09 | 6.0319e-10 | -1.4831e-10 | -4.2479e-08 | 1.2674e-08 | -2.2343e-09 | 4.3428e-10 | 9.6042e-10 | -1.4099e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.444 | 0.8684 | 1.0781 | 1.444 | 0.8684 | 1.0781 | 4.2763 | -104.0853 | 101.0801 | 4.2763 | -104.0853 | 101.0801
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.6189e-08 | -4.544e-08 | 6.4394e-08 | 6.2572e-09 | 2.3323e-08 | -3.2345e-08 | -8.4958e-08 | 2.5348e-08 | -4.4686e-09 | 4.2913e-08 | -1.1713e-08 | 8.2437e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.444 | 0.8684 | 1.0781 | 1.444 | 0.8684 | 1.0781 | 4.2763 | -104.0853 | 101.0801 | 4.2763 | -104.0853 | 101.0801
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.0946e-09 | -2.272e-08 | 3.2197e-08 | -1.8374e-09 | 6.0319e-10 | -1.4831e-10 | -4.2479e-08 | 1.2674e-08 | -2.2343e-09 | 4.3428e-10 | 9.6042e-10 | -1.4099e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.444 | 0.8684 | 1.0781 | 1.444 | 0.8684 | 1.0781 | 4.2763 | -104.0853 | 101.0801 | 4.2763 | -104.0853 | 101.0801
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.0946e-09 | -2.272e-08 | 3.2197e-08 | -1.8374e-09 | 6.0319e-10 | -1.4831e-10 | -4.2479e-08 | 1.2674e-08 | -2.2343e-09 | 4.3428e-10 | 9.6042e-10 | -1.4099e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.444 | 0.8684 | 1.0781 | 1.444 | 0.8684 | 1.0781 | 4.2763 | -104.0853 | 101.0801 | 4.2763 | -104.0853 | 101.0801
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.0946e-09 | -2.272e-08 | 3.2197e-08 | -1.8374e-09 | 6.0319e-10 | -1.4831e-10 | -4.2479e-08 | 1.2674e-08 | -2.2343e-09 | 4.3428e-10 | 9.6042e-10 | -1.4099e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.444 | 0.8684 | 1.0781 | 1.444 | 0.8684 | 1.0781 | 4.2763 | -104.0853 | 101.0801 | 4.2763 | -104.0853 | 101.0801
Line1_1_3 | 1.0374e-06 | 1.0378e-06 | 1.037e-06 | 0 | 0 | 0 | 2.3958e-07 | 2.3967e-07 | 2.3949e-07 | 0 | 0 | 0 | -6.4756e-08 | -1.8176e-07 | 2.5758e-07 | 5.4825e-08 | 1.5964e-07 | -2.2553e-07 | -3.3983e-07 | 1.0139e-07 | -1.7874e-08 | 2.9779e-07 | -8.7756e-08 | 1.423e-08 | 105.0649 | 105.0688 | 105.0497 | 0 | 0 | 0 | 1.444 | 0.8684 | 1.0781 | 1.444 | 0.8684 | 1.0781 | 4.2763 | -104.0853 | 101.0801 | 4.2763 | -104.0853 | 101.0801
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.6189e-08 | -4.544e-08 | 6.4394e-08 | 6.2572e-09 | 2.3323e-08 | -3.2345e-08 | -8.4958e-08 | 2.5348e-08 | -4.4686e-09 | 4.2913e-08 | -1.1713e-08 | 8.2438e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.444 | 0.8684 | 1.0781 | 1.444 | 0.8684 | 1.0781 | 4.2763 | -104.0853 | 101.0801 | 4.2763 | -104.0853 | 101.0801
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.6189e-08 | -4.544e-08 | 6.4394e-08 | 6.2572e-09 | 2.3323e-08 | -3.2345e-08 | -8.4958e-08 | 2.5348e-08 | -4.4686e-09 | 4.2913e-08 | -1.1713e-08 | 8.2438e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.444 | 0.8684 | 1.0781 | 1.444 | 0.8684 | 1.0781 | 4.2763 | -104.0853 | 101.0801 | 4.2763 | -104.0853 | 101.0801
Line4_2_6 | 0 | 0.028028 | 0.034804 | 0 | 0.028028 | 0.034804 | 0 | 0.0064728 | 0.0080376 | 0 | 0.0064728 | 0.0080376 | -4.0373e-08 | 0.0039477 | 0.0060954 | 3.0443e-08 | -0.0039411 | -0.0060824 | -2.1282e-07 | 0.0039781 | 0.0061237 | 1.7071e-07 | -0.0039614 | -0.0061012 | 0 | -149.3777 | 55.9036 | 0 | 30.6225 | -124.0966 | 1.4437 | 0.86584 | 1.075 | 1.4435 | 0.86329 | 1.0719 | 4.2786 | -104.1574 | 101.0361 | 4.2808 | -104.23 | 100.9919
Line5_6_7 | 0 | 0.028028 | 0.034804 | 0 | 0.028028 | 0.034804 | 0 | 0.0064728 | 0.0080376 | 0 | 0.0064728 | 0.0080376 | -3.2278e-08 | 0.0039411 | 0.0060824 | 2.2361e-08 | -0.0039345 | -0.0060694 | -1.7027e-07 | 0.0039614 | 0.0061012 | 1.2815e-07 | -0.0039447 | -0.0060788 | 0 | -149.3775 | 55.9034 | 0 | 30.6228 | -124.0968 | 1.4435 | 0.86329 | 1.0719 | 1.4433 | 0.86074 | 1.0687 | 4.2808 | -104.23 | 100.9919 | 4.283 | -104.303 | 100.9475
Line6_7_8 | 0 | 0.028028 | 0.034804 | 0 | 0.028028 | 0.034804 | 0 | 0.0064728 | 0.0080376 | 0 | 0.0064728 | 0.0080375 | -2.4193e-08 | 0.0039345 | 0.0060694 | 1.4289e-08 | -0.0039278 | -0.0060564 | -1.2771e-07 | 0.0039447 | 0.0060788 | 8.5573e-08 | -0.0039279 | -0.0060564 | 0 | -149.3772 | 55.9033 | 0 | 30.6231 | -124.0969 | 1.4433 | 0.86074 | 1.0687 | 1.443 | 0.85818 | 1.0656 | 4.283 | -104.303 | 100.9475 | 4.2853 | -104.3764 | 100.9028
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.0603e-09 | -2.2491e-08 | 3.1852e-08 | -1.8312e-09 | 6.3303e-10 | -1.0225e-10 | -4.2569e-08 | 1.2659e-08 | -2.264e-09 | 4.349e-10 | 9.322e-10 | -1.4062e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.443 | 0.85818 | 1.0656 | 1.443 | 0.85818 | 1.0656 | 4.2853 | -104.3764 | 100.9028 | 4.2853 | -104.3764 | 100.9028
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.0603e-09 | -2.2491e-08 | 3.1852e-08 | -1.8312e-09 | 6.3303e-10 | -1.0225e-10 | -4.2569e-08 | 1.2659e-08 | -2.264e-09 | 4.349e-10 | 9.3219e-10 | -1.4062e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.443 | 0.85818 | 1.0656 | 1.443 | 0.85818 | 1.0656 | 4.2853 | -104.3764 | 100.9028 | 4.2853 | -104.3764 | 100.9028
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.6662e-08 | -1.5904e-07 | 2.2538e-07 | 4.673e-08 | 1.3692e-07 | -1.9333e-07 | -2.9735e-07 | 8.8717e-08 | -1.564e-08 | 2.5531e-07 | -7.5083e-08 | 1.1996e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 1.444 | 0.8684 | 1.0781 | 1.444 | 0.8684 | 1.0781 | 4.2763 | -104.0853 | 101.0801 | 4.2763 | -104.0853 | 101.0801

## LLG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 1.0308e-06 | 1.449 | 1.4611 | 0 | 1.449 | 1.4611 | 2.3806e-07 | 0.33462 | 0.33742 | 0 | 0.33462 | 0.33742 | 1.4191e-08 | 0.16115 | 0.16403 | -1.4404e-08 | -0.12086 | -0.12302 | -3.3813e-07 | 0.16849 | 0.17024 | 2.8181e-07 | -0.12637 | -0.12768 | 87.6897 | -143.192 | 37.4439 | 0 | 36.808 | -142.5561 | 1.4216 | 0.69675 | 0.70062 | 1.4213 | 0.52256 | 0.52547 | 0.093013 | -96.9161 | 83.5078 | 0.10424 | -96.9161 | 83.5078
Line10_11_12 | 1.029e-06 | 1.041e-06 | 1.0171e-06 | 0 | 0 | 0 | 2.3764e-07 | 2.4041e-07 | 2.3488e-07 | 0 | 0 | 0 | 1.3688e-08 | -1.6683e-07 | 1.642e-07 | -1.3865e-08 | 1.3948e-07 | -1.3667e-07 | -3.3755e-07 | 1.4992e-08 | -1.0887e-08 | 2.813e-07 | -1.1542e-08 | 7.6209e-09 | 87.7709 | 88.2189 | 87.3009 | 0 | 0 | 0 | 1.4216 | 0.69675 | 0.70062 | 1.4216 | 0.69675 | 0.70062 | 0.093009 | -96.9161 | 83.5078 | 0.093007 | -96.9161 | 83.5078
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1407e-08 | -1.3903e-07 | 1.3684e-07 | -1.1584e-08 | 1.1167e-07 | -1.0931e-07 | -2.8129e-07 | 1.2493e-08 | -9.0723e-09 | 2.2504e-07 | -9.0432e-09 | 5.8064e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4216 | 0.69675 | 0.70062 | 1.4216 | 0.69675 | 0.70062 | 0.093007 | -96.9161 | 83.5078 | 0.093006 | -96.9161 | 83.5078
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.8441e-09 | -8.3416e-08 | 8.2102e-08 | -7.021e-09 | 5.6063e-08 | -5.4573e-08 | -1.6878e-07 | 7.4961e-09 | -5.4434e-09 | 1.1253e-07 | -4.0458e-09 | 2.1775e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4216 | 0.69675 | 0.70062 | 1.4216 | 0.69675 | 0.70062 | 0.093006 | -96.9161 | 83.5078 | 0.093005 | -96.9161 | 83.5078
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2813e-09 | -2.7805e-08 | 2.7367e-08 | -2.4583e-09 | 4.5266e-10 | 1.6214e-10 | -5.6259e-08 | 2.4987e-09 | -1.8145e-09 | 8.0384e-12 | 9.5158e-10 | -1.4514e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4216 | 0.69675 | 0.70062 | 1.4216 | 0.69675 | 0.70062 | 0.093006 | -96.9161 | 83.5078 | 0.093005 | -96.9161 | 83.5078
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5627e-09 | -5.5611e-08 | 5.4735e-08 | -4.7396e-09 | 2.8258e-08 | -2.7205e-08 | -1.1252e-07 | 4.9974e-09 | -3.6289e-09 | 5.6267e-08 | -1.5471e-09 | 3.6306e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4216 | 0.69675 | 0.70062 | 1.4216 | 0.69675 | 0.70062 | 0.093005 | -96.9161 | 83.5078 | 0.093004 | -96.9161 | 83.5078
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2814e-09 | -2.7805e-08 | 2.7367e-08 | -2.4583e-09 | 4.5266e-10 | 1.6214e-10 | -5.6259e-08 | 2.4987e-09 | -1.8145e-09 | 8.0386e-12 | 9.5158e-10 | -1.4514e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4216 | 0.69675 | 0.70062 | 1.4216 | 0.69675 | 0.70062 | 0.093004 | -96.9161 | 83.5078 | 0.093004 | -96.9161 | 83.5078
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2813e-09 | -2.7805e-08 | 2.7367e-08 | -2.4583e-09 | 4.5266e-10 | 1.6214e-10 | -5.6258e-08 | 2.4987e-09 | -1.8145e-09 | 8.0387e-12 | 9.5158e-10 | -1.4514e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4216 | 0.69675 | 0.70062 | 1.4216 | 0.69675 | 0.70062 | 0.093012 | -96.9161 | 83.5078 | 0.093012 | -96.9161 | 83.5078
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2813e-09 | -2.7805e-08 | 2.7367e-08 | -2.4583e-09 | 4.5266e-10 | 1.6214e-10 | -5.6258e-08 | 2.4987e-09 | -1.8145e-09 | 8.0387e-12 | 9.5158e-10 | -1.4514e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4216 | 0.69675 | 0.70062 | 1.4216 | 0.69675 | 0.70062 | 0.093012 | -96.9161 | 83.5078 | 0.093012 | -96.9161 | 83.5078
Line1_1_3 | 1.372e-06 | 1.388e-06 | 1.3561e-06 | 1.2009e-06 | 1.2168e-06 | 1.185e-06 | 3.1685e-07 | 3.2054e-07 | 3.1318e-07 | 2.7733e-07 | 2.81e-07 | 2.7367e-07 | 1.8251e-08 | -2.2244e-07 | 2.1894e-07 | -1.8428e-08 | 1.9509e-07 | -1.9141e-07 | -4.5007e-07 | 1.999e-08 | -1.4516e-08 | 3.9382e-07 | -1.6539e-08 | 1.125e-08 | 87.7709 | 88.2189 | 87.3009 | -92.5861 | -92.0703 | -93.1286 | 1.4216 | 0.69675 | 0.70062 | 1.4216 | 0.69675 | 0.70062 | 0.093013 | -96.9161 | 83.5078 | 0.093011 | -96.9161 | 83.5078
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5627e-09 | -5.5611e-08 | 5.4735e-08 | -4.7396e-09 | 2.8258e-08 | -2.7205e-08 | -1.1252e-07 | 4.9974e-09 | -3.6289e-09 | 5.6267e-08 | -1.5471e-09 | 3.6306e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4216 | 0.69675 | 0.70062 | 1.4216 | 0.69675 | 0.70062 | 0.093013 | -96.9161 | 83.5078 | 0.093012 | -96.9161 | 83.5078
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5627e-09 | -5.5611e-08 | 5.4735e-08 | -4.7396e-09 | 2.8258e-08 | -2.7205e-08 | -1.1252e-07 | 4.9974e-09 | -3.6289e-09 | 5.6267e-08 | -1.5471e-09 | 3.6306e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4216 | 0.69675 | 0.70062 | 1.4216 | 0.69675 | 0.70062 | 0.093013 | -96.9161 | 83.5078 | 0.093012 | -96.9161 | 83.5078
Line4_2_6 | 0 | 1.449 | 1.4611 | 0 | 1.449 | 1.4611 | 0 | 0.33462 | 0.33742 | 0 | 0.33462 | 0.33742 | 1.1948e-08 | 0.12086 | 0.12302 | -1.2106e-08 | -0.080575 | -0.082014 | -2.818e-07 | 0.12637 | 0.12768 | 2.2546e-07 | -0.084245 | -0.085118 | 0 | -143.192 | 37.4439 | 0 | 36.808 | -142.5561 | 1.4213 | 0.52256 | 0.52547 | 1.421 | 0.34838 | 0.35031 | 0.10424 | -96.9161 | 83.5078 | 0.11547 | -96.9161 | 83.5078
Line5_6_7 | 0 | 1.449 | 1.4611 | 0 | 1.449 | 1.4611 | 0 | 0.33462 | 0.33742 | 0 | 0.33462 | 0.33742 | 9.6515e-09 | 0.080575 | 0.082014 | -9.7545e-09 | -0.040287 | -0.041007 | -2.2545e-07 | 0.084245 | 0.085118 | 1.691e-07 | -0.042123 | -0.042559 | 0 | -143.192 | 37.4439 | 0 | 36.808 | -142.5561 | 1.421 | 0.34838 | 0.35031 | 1.4207 | 0.17419 | 0.17516 | 0.11547 | -96.9161 | 83.5078 | 0.12671 | -96.9161 | 83.5078
Line6_7_8 | 0 | 1.449 | 1.4611 | 0 | 1.449 | 1.4611 | 0 | 0.33462 | 0.33742 | 0 | 0.33462 | 0.33742 | 7.3023e-09 | 0.040287 | 0.041007 | -7.3506e-09 | -5.2097e-14 | 5.843e-14 | -1.6908e-07 | 0.042123 | 0.042559 | 1.1272e-07 | -1.8123e-13 | 1.7461e-13 | 0 | -143.192 | 37.4439 | 0 | 36.808 | -142.5561 | 1.4207 | 0.17419 | 0.17516 | 1.4204 | 0 | 0 | 0.12671 | -96.9161 | 83.5078 | 0.13795 | 0 | 0
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4502e-09 | -2.2161e-20 | -1.8625e-20 | -2.4502e-09 | 7.0928e-18 | -1.2426e-17 | -5.6355e-08 | -9.3971e-21 | -7.3416e-21 | 1.1913e-11 | 2.237e-17 | -2e-18 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4204 | 0 | 0 | 1.4204 | 0 | 0 | 0.13795 | 0 | 0 | 0.13795 | 0 | 0
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4502e-09 | -2.2161e-20 | -1.8625e-20 | -2.4502e-09 | 7.0928e-18 | -1.2426e-17 | -5.6355e-08 | -9.3971e-21 | -7.3416e-21 | 1.1913e-11 | 2.237e-17 | -2e-18 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4204 | 0 | 0 | 1.4204 | 0 | 0 | 0.13795 | 0 | 0 | 0.13795 | 0 | 0
Line9_3_11 | 1.2005e-06 | 1.2145e-06 | 1.1866e-06 | 1.0294e-06 | 1.0433e-06 | 1.0155e-06 | 2.7724e-07 | 2.8047e-07 | 2.7403e-07 | 2.3772e-07 | 2.4094e-07 | 2.3452e-07 | 1.5969e-08 | -1.9464e-07 | 1.9157e-07 | -1.6146e-08 | 1.6728e-07 | -1.6404e-07 | -3.9381e-07 | 1.7491e-08 | -1.2701e-08 | 3.3756e-07 | -1.4041e-08 | 9.4353e-09 | 87.7709 | 88.2189 | 87.3009 | -92.6455 | -92.1184 | -93.2003 | 1.4216 | 0.69675 | 0.70062 | 1.4216 | 0.69675 | 0.70062 | 0.093011 | -96.9161 | 83.5078 | 0.093009 | -96.9161 | 83.5078

## LLG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 1.3727 | 1.3842 | 0 | 1.3727 | 1.3842 | 0 | 0.31701 | 0.31966 | 0 | 0.31701 | 0.31966 | 1.2737e-08 | 0.14463 | 0.14722 | -1.2928e-08 | -0.10847 | -0.11041 | -3.0348e-07 | 0.15122 | 0.15279 | 2.5292e-07 | -0.11342 | -0.11459 | 0 | -143.192 | 37.4439 | 0 | 36.808 | -142.5561 | 1.3468 | 0.66008 | 0.66375 | 1.3465 | 0.49506 | 0.49781 | 0.093013 | -96.9161 | 83.5078 | 0.10424 | -96.9161 | 83.5078
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2285e-08 | -1.4973e-07 | 1.4737e-07 | -1.2444e-08 | 1.2518e-07 | -1.2267e-07 | -3.0295e-07 | 1.3456e-08 | -9.7709e-09 | 2.5247e-07 | -1.0359e-08 | 6.8398e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3468 | 0.66008 | 0.66375 | 1.3468 | 0.66008 | 0.66375 | 0.093009 | -96.9161 | 83.5078 | 0.093007 | -96.9161 | 83.5078
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0238e-08 | -1.2478e-07 | 1.2281e-07 | -1.0396e-08 | 1.0023e-07 | -9.8104e-08 | -2.5246e-07 | 1.1213e-08 | -8.1424e-09 | 2.0198e-07 | -8.1163e-09 | 5.2113e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3468 | 0.66008 | 0.66375 | 1.3468 | 0.66008 | 0.66375 | 0.093007 | -96.9161 | 83.5078 | 0.093006 | -96.9161 | 83.5078
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.1426e-09 | -7.4866e-08 | 7.3687e-08 | -6.3014e-09 | 5.0317e-08 | -4.8979e-08 | -1.5148e-07 | 6.7278e-09 | -4.8855e-09 | 1.0099e-07 | -3.6311e-09 | 1.9543e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3468 | 0.66008 | 0.66375 | 1.3468 | 0.66008 | 0.66375 | 0.093006 | -96.9161 | 83.5078 | 0.093005 | -96.9161 | 83.5078
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0475e-09 | -2.4955e-08 | 2.4562e-08 | -2.2063e-09 | 4.0627e-10 | 1.4553e-10 | -5.0492e-08 | 2.2426e-09 | -1.6285e-09 | 7.2145e-12 | 8.5405e-10 | -1.3026e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3468 | 0.66008 | 0.66375 | 1.3468 | 0.66008 | 0.66375 | 0.093006 | -96.9161 | 83.5078 | 0.093005 | -96.9161 | 83.5078
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0951e-09 | -4.9911e-08 | 4.9125e-08 | -4.2539e-09 | 2.5362e-08 | -2.4417e-08 | -1.0098e-07 | 4.4852e-09 | -3.257e-09 | 5.05e-08 | -1.3885e-09 | 3.2585e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3468 | 0.66008 | 0.66375 | 1.3468 | 0.66008 | 0.66375 | 0.093005 | -96.9161 | 83.5078 | 0.093004 | -96.9161 | 83.5078
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0475e-09 | -2.4955e-08 | 2.4562e-08 | -2.2063e-09 | 4.0627e-10 | 1.4553e-10 | -5.0492e-08 | 2.2426e-09 | -1.6285e-09 | 7.2144e-12 | 8.5405e-10 | -1.3026e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3468 | 0.66008 | 0.66375 | 1.3468 | 0.66008 | 0.66375 | 0.093004 | -96.9161 | 83.5078 | 0.093004 | -96.9161 | 83.5078
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0475e-09 | -2.4955e-08 | 2.4562e-08 | -2.2063e-09 | 4.0627e-10 | 1.4553e-10 | -5.0492e-08 | 2.2426e-09 | -1.6285e-09 | 7.2151e-12 | 8.5405e-10 | -1.3026e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3468 | 0.66008 | 0.66375 | 1.3468 | 0.66008 | 0.66375 | 0.093012 | -96.9161 | 83.5078 | 0.093012 | -96.9161 | 83.5078
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0475e-09 | -2.4955e-08 | 2.4562e-08 | -2.2063e-09 | 4.0627e-10 | 1.4553e-10 | -5.0492e-08 | 2.2426e-09 | -1.6285e-09 | 7.2151e-12 | 8.5405e-10 | -1.3026e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3468 | 0.66008 | 0.66375 | 1.3468 | 0.66008 | 0.66375 | 0.093012 | -96.9161 | 83.5078 | 0.093012 | -96.9161 | 83.5078
Line1_1_3 | 1.2998e-06 | 1.3149e-06 | 1.2847e-06 | 1.1377e-06 | 1.1527e-06 | 1.1227e-06 | 3.0017e-07 | 3.0367e-07 | 2.9669e-07 | 2.6273e-07 | 2.6621e-07 | 2.5927e-07 | 1.638e-08 | -1.9964e-07 | 1.965e-07 | -1.6539e-08 | 1.7509e-07 | -1.7179e-07 | -4.0394e-07 | 1.7941e-08 | -1.3028e-08 | 3.5345e-07 | -1.4844e-08 | 1.0097e-08 | 87.7709 | 88.2189 | 87.3009 | -92.5861 | -92.0703 | -93.1286 | 1.3468 | 0.66008 | 0.66375 | 1.3468 | 0.66008 | 0.66375 | 0.093013 | -96.9161 | 83.5078 | 0.093011 | -96.9161 | 83.5078
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.095e-09 | -4.9911e-08 | 4.9125e-08 | -4.2538e-09 | 2.5362e-08 | -2.4417e-08 | -1.0098e-07 | 4.4852e-09 | -3.257e-09 | 5.05e-08 | -1.3886e-09 | 3.2585e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3468 | 0.66008 | 0.66375 | 1.3468 | 0.66008 | 0.66375 | 0.093013 | -96.9161 | 83.5078 | 0.093012 | -96.9161 | 83.5078
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.095e-09 | -4.9911e-08 | 4.9125e-08 | -4.2538e-09 | 2.5362e-08 | -2.4417e-08 | -1.0098e-07 | 4.4852e-09 | -3.257e-09 | 5.05e-08 | -1.3886e-09 | 3.2585e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3468 | 0.66008 | 0.66375 | 1.3468 | 0.66008 | 0.66375 | 0.093013 | -96.9161 | 83.5078 | 0.093012 | -96.9161 | 83.5078
Line4_2_6 | 0 | 1.3727 | 1.3842 | 0 | 1.3727 | 1.3842 | 0 | 0.31701 | 0.31966 | 0 | 0.31701 | 0.31966 | 1.0723e-08 | 0.10847 | 0.11041 | -1.0865e-08 | -0.072316 | -0.073608 | -2.5291e-07 | 0.11342 | 0.11459 | 2.0235e-07 | -0.075611 | -0.076394 | 0 | -143.192 | 37.4439 | 0 | 36.808 | -142.5561 | 1.3465 | 0.49506 | 0.49781 | 1.3462 | 0.33004 | 0.33187 | 0.10424 | -96.9161 | 83.5078 | 0.11547 | -96.9161 | 83.5078
Line5_6_7 | 0 | 1.3727 | 1.3842 | 0 | 1.3727 | 1.3842 | 0 | 0.31701 | 0.31966 | 0 | 0.31701 | 0.31966 | 8.6623e-09 | 0.072316 | 0.073608 | -8.7548e-09 | -0.036158 | -0.036804 | -2.0234e-07 | 0.075611 | 0.076394 | 1.5176e-07 | -0.037805 | -0.038197 | 0 | -143.192 | 37.4439 | 0 | 36.808 | -142.5561 | 1.3462 | 0.33004 | 0.33187 | 1.346 | 0.16502 | 0.16594 | 0.11547 | -96.9161 | 83.5078 | 0.12671 | -96.9161 | 83.5078
Line6_7_8 | 0 | 1.3727 | 1.3842 | 0 | 1.3727 | 1.3842 | 0 | 0.31701 | 0.31966 | 0 | 0.31701 | 0.31966 | 6.5539e-09 | 0.036158 | 0.036804 | -6.5972e-09 | -4.6675e-14 | 5.2581e-14 | -1.5175e-07 | 0.037805 | 0.038197 | 1.0117e-07 | -1.7014e-13 | 1.6419e-13 | 0 | -143.192 | 37.4439 | 0 | 36.808 | -142.5561 | 1.346 | 0.16502 | 0.16594 | 1.3457 | 0 | 0 | 0.12671 | -96.9161 | 83.5078 | 0.13795 | 0 | 0
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1991e-09 | -2.0625e-20 | -1.7348e-20 | -2.1991e-09 | 6.3659e-18 | -1.1153e-17 | -5.0579e-08 | -9.0434e-21 | -7.1002e-21 | 1.0692e-11 | 2.0077e-17 | -1.795e-18 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3457 | 0 | 0 | 1.3457 | 0 | 0 | 0.13795 | 0 | 0 | 0.13795 | 0 | 0
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1991e-09 | -2.0625e-20 | -1.7348e-20 | -2.1991e-09 | 6.3659e-18 | -1.1153e-17 | -5.0579e-08 | -9.0434e-21 | -7.1002e-21 | 1.0692e-11 | 2.0077e-17 | -1.795e-18 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3457 | 0 | 0 | 1.3457 | 0 | 0 | 0.13795 | 0 | 0 | 0.13795 | 0 | 0
Line9_3_11 | 1.1373e-06 | 1.1506e-06 | 1.1241e-06 | 0 | 0 | 0 | 2.6265e-07 | 2.6571e-07 | 2.5961e-07 | 0 | 0 | 0 | 1.4333e-08 | -1.7469e-07 | 1.7194e-07 | -1.4492e-08 | 1.5014e-07 | -1.4723e-07 | -3.5345e-07 | 1.5698e-08 | -1.1399e-08 | 3.0296e-07 | -1.2602e-08 | 8.4683e-09 | 87.7709 | 88.2189 | 87.3009 | 0 | 0 | 0 | 1.3468 | 0.66008 | 0.66375 | 1.3468 | 0.66008 | 0.66375 | 0.093011 | -96.9161 | 83.5078 | 0.093009 | -96.9161 | 83.5078

## LLG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0.0241 | 0.029975 | 0 | 0.0241 | 0.029975 | 0 | 0.0055657 | 0.0069224 | 0 | 0.0055657 | 0.0069224 | -3.6205e-08 | 0.0029455 | 0.0045624 | 2.8752e-08 | -0.0029351 | -0.0045449 | -1.9033e-07 | 0.0029556 | 0.0045569 | 1.5896e-07 | -0.0029427 | -0.0045408 | 0 | -149.2086 | 56.1265 | 0 | 30.7916 | -123.8737 | 1.2468 | 0.74971 | 0.93152 | 1.2466 | 0.74677 | 0.92809 | 4.2943 | -104.1102 | 101.092 | 4.3004 | -104.1342 | 101.1003
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.641e-08 | -1.0149e-07 | 1.4408e-07 | 2.8972e-08 | 8.5025e-08 | -1.2018e-07 | -1.8994e-07 | 5.6859e-08 | -1.0172e-08 | 1.5861e-07 | -4.6668e-08 | 7.4254e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2468 | 0.74971 | 0.93152 | 1.2468 | 0.74971 | 0.93152 | 4.2943 | -104.1102 | 101.092 | 4.2943 | -104.1102 | 101.092
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.0341e-08 | -8.4575e-08 | 1.2007e-07 | 2.2904e-08 | 6.8111e-08 | -9.6167e-08 | -1.5829e-07 | 4.7383e-08 | -8.4769e-09 | 1.2695e-07 | -3.7191e-08 | 5.73e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2468 | 0.74971 | 0.93152 | 1.2468 | 0.74971 | 0.93152 | 4.2943 | -104.1102 | 101.092 | 4.2943 | -104.1102 | 101.092
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.8205e-08 | -5.0745e-08 | 7.2041e-08 | 1.0767e-08 | 3.4281e-08 | -4.8139e-08 | -9.4972e-08 | 2.843e-08 | -5.0861e-09 | 6.364e-08 | -1.8238e-08 | 2.3393e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2468 | 0.74971 | 0.93152 | 1.2468 | 0.74971 | 0.93152 | 4.2943 | -104.1102 | 101.092 | 4.2943 | -104.1102 | 101.092
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.0683e-09 | -1.6915e-08 | 2.4014e-08 | -1.3693e-09 | 4.5079e-10 | -1.1199e-10 | -3.1657e-08 | 9.4765e-09 | -1.6954e-09 | 3.2521e-10 | 7.15e-10 | -1.0515e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2468 | 0.74971 | 0.93152 | 1.2468 | 0.74971 | 0.93152 | 4.2943 | -104.1102 | 101.092 | 4.2943 | -104.1102 | 101.092
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.2137e-08 | -3.383e-08 | 4.8027e-08 | 4.699e-09 | 1.7366e-08 | -2.4126e-08 | -6.3315e-08 | 1.8953e-08 | -3.3907e-09 | 3.1982e-08 | -8.7615e-09 | 6.4389e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2468 | 0.74971 | 0.93152 | 1.2468 | 0.74971 | 0.93152 | 4.2943 | -104.1102 | 101.092 | 4.2943 | -104.1102 | 101.092
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.0683e-09 | -1.6915e-08 | 2.4014e-08 | -1.3693e-09 | 4.5079e-10 | -1.1199e-10 | -3.1657e-08 | 9.4765e-09 | -1.6954e-09 | 3.2521e-10 | 7.15e-10 | -1.0515e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2468 | 0.74971 | 0.93152 | 1.2468 | 0.74971 | 0.93152 | 4.2943 | -104.1102 | 101.092 | 4.2943 | -104.1102 | 101.092
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.0683e-09 | -1.6915e-08 | 2.4014e-08 | -1.3692e-09 | 4.5079e-10 | -1.1199e-10 | -3.1657e-08 | 9.4765e-09 | -1.6954e-09 | 3.2521e-10 | 7.15e-10 | -1.0515e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2468 | 0.74971 | 0.93152 | 1.2468 | 0.74971 | 0.93152 | 4.2943 | -104.1102 | 101.092 | 4.2943 | -104.1102 | 101.092
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.0683e-09 | -1.6915e-08 | 2.4014e-08 | -1.3692e-09 | 4.5079e-10 | -1.1199e-10 | -3.1657e-08 | 9.4765e-09 | -1.6954e-09 | 3.2521e-10 | 7.15e-10 | -1.0515e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2468 | 0.74971 | 0.93152 | 1.2468 | 0.74971 | 0.93152 | 4.2943 | -104.1102 | 101.092 | 4.2943 | -104.1102 | 101.092
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.8546e-08 | -1.3532e-07 | 1.9211e-07 | 4.1109e-08 | 1.1886e-07 | -1.6821e-07 | -2.5326e-07 | 7.5812e-08 | -1.3563e-08 | 2.2193e-07 | -6.5621e-08 | 1.0816e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2468 | 0.74971 | 0.93152 | 1.2468 | 0.74971 | 0.93152 | 4.2943 | -104.1102 | 101.092 | 4.2943 | -104.1102 | 101.092
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.2137e-08 | -3.383e-08 | 4.8027e-08 | 4.699e-09 | 1.7366e-08 | -2.4126e-08 | -6.3315e-08 | 1.8953e-08 | -3.3908e-09 | 3.1982e-08 | -8.7615e-09 | 6.439e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2468 | 0.74971 | 0.93152 | 1.2468 | 0.74971 | 0.93152 | 4.2943 | -104.1102 | 101.092 | 4.2943 | -104.1102 | 101.092
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.2137e-08 | -3.383e-08 | 4.8027e-08 | 4.699e-09 | 1.7366e-08 | -2.4126e-08 | -6.3315e-08 | 1.8953e-08 | -3.3908e-09 | 3.1982e-08 | -8.7615e-09 | 6.439e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2468 | 0.74971 | 0.93152 | 1.2468 | 0.74971 | 0.93152 | 4.2943 | -104.1102 | 101.092 | 4.2943 | -104.1102 | 101.092
Line4_2_6 | 0 | 0.0241 | 0.029975 | 0 | 0.0241 | 0.029975 | 0 | 0.0055657 | 0.0069224 | 0 | 0.0055657 | 0.0069223 | -3.012e-08 | 0.0029351 | 0.0045449 | 2.2691e-08 | -0.0029248 | -0.0045274 | -1.5864e-07 | 0.0029427 | 0.0045408 | 1.2726e-07 | -0.0029299 | -0.0045246 | 0 | -149.2084 | 56.1263 | 0 | 30.7919 | -123.8739 | 1.2466 | 0.74677 | 0.92809 | 1.2464 | 0.74382 | 0.92465 | 4.3004 | -104.1342 | 101.1003 | 4.3065 | -104.1583 | 101.1086
Line5_6_7 | 0 | 0.0241 | 0.029975 | 0 | 0.0241 | 0.029975 | 0 | 0.0055657 | 0.0069223 | 0 | 0.0055657 | 0.0069223 | -2.4057e-08 | 0.0029248 | 0.0045274 | 1.6651e-08 | -0.0029145 | -0.0045099 | -1.2693e-07 | 0.0029299 | 0.0045246 | 9.5532e-08 | -0.002917 | -0.0045085 | 0 | -149.2081 | 56.1262 | 0 | 30.7921 | -123.874 | 1.2464 | 0.74382 | 0.92465 | 1.2462 | 0.74087 | 0.92121 | 4.3065 | -104.1583 | 101.1086 | 4.3127 | -104.1826 | 101.117
Line6_7_8 | 0 | 0.0241 | 0.029975 | 0 | 0.0241 | 0.029974 | 0 | 0.0055657 | 0.0069223 | 0 | 0.0055657 | 0.0069223 | -1.8016e-08 | 0.0029145 | 0.0045099 | 1.0633e-08 | -0.0029041 | -0.0044923 | -9.5206e-08 | 0.002917 | 0.0045085 | 6.3795e-08 | -0.0029042 | -0.0044923 | 0 | -149.2079 | 56.126 | 0 | 30.7924 | -123.8742 | 1.2462 | 0.74087 | 0.92121 | 1.2459 | 0.73792 | 0.91777 | 4.3127 | -104.1826 | 101.117 | 4.3188 | -104.2071 | 101.1255
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.9986e-09 | -1.6729e-08 | 2.3678e-08 | -1.3642e-09 | 4.7679e-10 | -6.3449e-11 | -3.1734e-08 | 9.3456e-09 | -1.6092e-09 | 3.2683e-10 | 6.9957e-10 | -1.0342e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2459 | 0.73792 | 0.91777 | 1.2459 | 0.73792 | 0.91777 | 4.3188 | -104.2071 | 101.1255 | 4.3188 | -104.2071 | 101.1255
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.9986e-09 | -1.6729e-08 | 2.3678e-08 | -1.3642e-09 | 4.7679e-10 | -6.3449e-11 | -3.1734e-08 | 9.3456e-09 | -1.6092e-09 | 3.2683e-10 | 6.9957e-10 | -1.0342e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2459 | 0.73792 | 0.91777 | 1.2459 | 0.73792 | 0.91777 | 4.3188 | -104.2071 | 101.1255 | 4.3188 | -104.2071 | 101.1255
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.2478e-08 | -1.184e-07 | 1.681e-07 | 3.504e-08 | 1.0194e-07 | -1.4419e-07 | -2.216e-07 | 6.6336e-08 | -1.1868e-08 | 1.9027e-07 | -5.6144e-08 | 9.1207e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2468 | 0.74971 | 0.93152 | 1.2468 | 0.74971 | 0.93152 | 4.2943 | -104.1102 | 101.092 | 4.2943 | -104.1102 | 101.092

## LLG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0.022832 | 0.028397 | 0 | 0.022832 | 0.028397 | 0 | 0.0052728 | 0.006558 | 0 | 0.0052728 | 0.006558 | -3.2494e-08 | 0.0026436 | 0.0040948 | 2.5805e-08 | -0.0026343 | -0.0040791 | -1.7083e-07 | 0.0026527 | 0.0040899 | 1.4267e-07 | -0.0026411 | -0.0040754 | 0 | -149.2086 | 56.1265 | 0 | 30.7916 | -123.8737 | 1.1812 | 0.71025 | 0.8825 | 1.181 | 0.70746 | 0.87924 | 4.2943 | -104.1102 | 101.092 | 4.3004 | -104.1342 | 101.1003
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.2678e-08 | -9.1088e-08 | 1.2931e-07 | 2.6003e-08 | 7.6311e-08 | -1.0786e-07 | -1.7048e-07 | 5.1032e-08 | -9.1296e-09 | 1.4235e-07 | -4.1885e-08 | 6.6643e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1812 | 0.71025 | 0.8825 | 1.1812 | 0.71025 | 0.8825 | 4.2943 | -104.1102 | 101.092 | 4.2943 | -104.1102 | 101.092
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.7232e-08 | -7.5906e-08 | 1.0776e-07 | 2.0556e-08 | 6.113e-08 | -8.631e-08 | -1.4206e-07 | 4.2526e-08 | -7.608e-09 | 1.1394e-07 | -3.3379e-08 | 5.1427e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1812 | 0.71025 | 0.8825 | 1.1812 | 0.71025 | 0.8825 | 4.2943 | -104.1102 | 101.092 | 4.2943 | -104.1102 | 101.092
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.6339e-08 | -4.5544e-08 | 6.4657e-08 | 9.6637e-09 | 3.0767e-08 | -4.3205e-08 | -8.5238e-08 | 2.5516e-08 | -4.5648e-09 | 5.7117e-08 | -1.6369e-08 | 2.0995e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1812 | 0.71025 | 0.8825 | 1.1812 | 0.71025 | 0.8825 | 4.2943 | -104.1102 | 101.092 | 4.2943 | -104.1102 | 101.092
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.4463e-09 | -1.5181e-08 | 2.1552e-08 | -1.2289e-09 | 4.0459e-10 | -1.0051e-10 | -2.8413e-08 | 8.5052e-09 | -1.5216e-09 | 2.9188e-10 | 6.4171e-10 | -9.4371e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1812 | 0.71025 | 0.8825 | 1.1812 | 0.71025 | 0.8825 | 4.2943 | -104.1102 | 101.092 | 4.2943 | -104.1102 | 101.092
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.0893e-08 | -3.0363e-08 | 4.3105e-08 | 4.2174e-09 | 1.5586e-08 | -2.1653e-08 | -5.6825e-08 | 1.701e-08 | -3.0432e-09 | 2.8705e-08 | -7.8635e-09 | 5.779e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1812 | 0.71025 | 0.8825 | 1.1812 | 0.71025 | 0.8825 | 4.2943 | -104.1102 | 101.092 | 4.2943 | -104.1102 | 101.092
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.4463e-09 | -1.5181e-08 | 2.1552e-08 | -1.2289e-09 | 4.0459e-10 | -1.0051e-10 | -2.8413e-08 | 8.5052e-09 | -1.5216e-09 | 2.9188e-10 | 6.4171e-10 | -9.4371e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1812 | 0.71025 | 0.8825 | 1.1812 | 0.71025 | 0.8825 | 4.2943 | -104.1102 | 101.092 | 4.2943 | -104.1102 | 101.092
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.4463e-09 | -1.5181e-08 | 2.1552e-08 | -1.2289e-09 | 4.0459e-10 | -1.0051e-10 | -2.8413e-08 | 8.5053e-09 | -1.5216e-09 | 2.9188e-10 | 6.4171e-10 | -9.4371e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1812 | 0.71025 | 0.8825 | 1.1812 | 0.71025 | 0.8825 | 4.2943 | -104.1102 | 101.092 | 4.2943 | -104.1102 | 101.092
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.4463e-09 | -1.5181e-08 | 2.1552e-08 | -1.2289e-09 | 4.0459e-10 | -1.0051e-10 | -2.8413e-08 | 8.5053e-09 | -1.5216e-09 | 2.9188e-10 | 6.4171e-10 | -9.4371e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1812 | 0.71025 | 0.8825 | 1.1812 | 0.71025 | 0.8825 | 4.2943 | -104.1102 | 101.092 | 4.2943 | -104.1102 | 101.092
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.3571e-08 | -1.2145e-07 | 1.7242e-07 | 3.6895e-08 | 1.0667e-07 | -1.5097e-07 | -2.273e-07 | 6.8042e-08 | -1.2173e-08 | 1.9918e-07 | -5.8895e-08 | 9.7075e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1812 | 0.71025 | 0.8825 | 1.1812 | 0.71025 | 0.8825 | 4.2943 | -104.1102 | 101.092 | 4.2943 | -104.1102 | 101.092
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.0893e-08 | -3.0363e-08 | 4.3105e-08 | 4.2174e-09 | 1.5586e-08 | -2.1653e-08 | -5.6825e-08 | 1.7011e-08 | -3.0432e-09 | 2.8704e-08 | -7.8635e-09 | 5.779e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1812 | 0.71025 | 0.8825 | 1.1812 | 0.71025 | 0.8825 | 4.2943 | -104.1102 | 101.092 | 4.2943 | -104.1102 | 101.092
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.0893e-08 | -3.0363e-08 | 4.3105e-08 | 4.2174e-09 | 1.5586e-08 | -2.1653e-08 | -5.6825e-08 | 1.7011e-08 | -3.0432e-09 | 2.8704e-08 | -7.8635e-09 | 5.779e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1812 | 0.71025 | 0.8825 | 1.1812 | 0.71025 | 0.8825 | 4.2943 | -104.1102 | 101.092 | 4.2943 | -104.1102 | 101.092
Line4_2_6 | 0 | 0.022832 | 0.028397 | 0 | 0.022832 | 0.028397 | 0 | 0.0052728 | 0.006558 | 0 | 0.0052728 | 0.006558 | -2.7033e-08 | 0.0026343 | 0.0040791 | 2.0365e-08 | -0.002625 | -0.0040634 | -1.4238e-07 | 0.0026411 | 0.0040754 | 1.1421e-07 | -0.0026296 | -0.0040609 | 0 | -149.2084 | 56.1263 | 0 | 30.7919 | -123.8739 | 1.181 | 0.70746 | 0.87924 | 1.1808 | 0.70467 | 0.87598 | 4.3004 | -104.1342 | 101.1003 | 4.3065 | -104.1583 | 101.1086
Line5_6_7 | 0 | 0.022832 | 0.028397 | 0 | 0.022832 | 0.028397 | 0 | 0.0052728 | 0.006558 | 0 | 0.0052728 | 0.006558 | -2.1592e-08 | 0.002625 | 0.0040634 | 1.4944e-08 | -0.0026157 | -0.0040476 | -1.1392e-07 | 0.0026296 | 0.0040609 | 8.5741e-08 | -0.0026181 | -0.0040464 | 0 | -149.2081 | 56.1262 | 0 | 30.7921 | -123.874 | 1.1808 | 0.70467 | 0.87598 | 1.1806 | 0.70188 | 0.87273 | 4.3065 | -104.1583 | 101.1086 | 4.3127 | -104.1826 | 101.117
Line6_7_8 | 0 | 0.022832 | 0.028397 | 0 | 0.022832 | 0.028397 | 0 | 0.0052728 | 0.006558 | 0 | 0.0052728 | 0.006558 | -1.617e-08 | 0.0026157 | 0.0040476 | 9.5432e-09 | -0.0026065 | -0.0040319 | -8.5448e-08 | 0.0026181 | 0.0040464 | 5.7256e-08 | -0.0026065 | -0.0040319 | 0 | -149.2079 | 56.126 | 0 | 30.7924 | -123.8742 | 1.1806 | 0.70188 | 0.87273 | 1.1804 | 0.69908 | 0.86947 | 4.3127 | -104.1826 | 101.117 | 4.3188 | -104.2071 | 101.1255
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.3838e-09 | -1.5014e-08 | 2.1251e-08 | -1.2244e-09 | 4.2792e-10 | -5.6945e-11 | -2.8482e-08 | 8.3877e-09 | -1.4443e-09 | 2.9333e-10 | 6.2787e-10 | -9.2819e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1804 | 0.69908 | 0.86947 | 1.1804 | 0.69908 | 0.86947 | 4.3188 | -104.2071 | 101.1255 | 4.3188 | -104.2071 | 101.1255
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.3838e-09 | -1.5014e-08 | 2.1251e-08 | -1.2244e-09 | 4.2792e-10 | -5.6945e-11 | -2.8482e-08 | 8.3877e-09 | -1.4443e-09 | 2.9333e-10 | 6.2787e-10 | -9.2819e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1804 | 0.69908 | 0.86947 | 1.1804 | 0.69908 | 0.86947 | 4.3188 | -104.2071 | 101.1255 | 4.3188 | -104.2071 | 101.1255
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.8124e-08 | -1.0627e-07 | 1.5087e-07 | 3.1449e-08 | 9.1492e-08 | -1.2942e-07 | -1.9889e-07 | 5.9537e-08 | -1.0651e-08 | 1.7077e-07 | -5.039e-08 | 8.1859e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1812 | 0.71025 | 0.8825 | 1.1812 | 0.71025 | 0.8825 | 4.2943 | -104.1102 | 101.092 | 4.2943 | -104.1102 | 101.092