## LLL_max_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 2.1767 | 2.1767 | 0 | 0 | 1.508 | 1.508 | 0.56854 | -0.42641 | 1.1371 | -0.85282 | -67.8829 | 112.1171 | 0.84302 | 0.63226 | -4.4479 | -4.4479
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84302 | 0.84302 | -4.4479 | -4.4479
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84302 | 0.84302 | -4.4479 | -4.4479
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84302 | 0.84302 | -4.4479 | -4.4479
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84302 | 0.84302 | -4.4479 | -4.4479
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84302 | 0.84302 | -4.4479 | -4.4479
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84302 | 0.84302 | -4.4479 | -4.4479
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84302 | 0.84302 | -4.4479 | -4.4479
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84302 | 0.84302 | -4.4479 | -4.4479
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84302 | 0.84302 | -4.4479 | -4.4479
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84302 | 0.84302 | -4.4479 | -4.4479
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84302 | 0.84302 | -4.4479 | -4.4479
Line4_2_6 | 2.1767 | 2.1767 | 0 | 0 | 1.508 | 1.508 | 0.42641 | -0.28427 | 0.85282 | -0.56854 | -67.8829 | 112.1171 | 0.63226 | 0.42151 | -4.4479 | -4.4479
Line5_6_7 | 2.1767 | 2.1767 | 0 | 0 | 1.508 | 1.508 | 0.28427 | -0.14214 | 0.56854 | -0.28427 | -67.8829 | 112.1171 | 0.42151 | 0.21075 | -4.4479 | -4.4479
Line6_7_8 | 2.1767 | 2.1767 | 0 | 4.0311 | 1.508 | 1.508 | 0.14214 | -1e-07 | 0.28427 | -1e-07 | -67.8829 | 112.1171 | 0.21075 | 0 | -4.4479 | 0
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4632e-22 | 0 | 4.2265e-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4632e-22 | 0 | 4.2265e-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84302 | 0.84302 | -4.4479 | -4.4479

## LLL_max_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 2.259 | 2.259 | 0 | 0 | 1.5651 | 1.5651 | 0.61237 | -0.45928 | 1.2247 | -0.91856 | -68.05 | 111.95 | 0.87491 | 0.65618 | -4.615 | -4.615
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87491 | 0.87491 | -4.615 | -4.615
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87491 | 0.87491 | -4.615 | -4.615
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87491 | 0.87491 | -4.615 | -4.615
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87491 | 0.87491 | -4.615 | -4.615
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87491 | 0.87491 | -4.615 | -4.615
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87491 | 0.87491 | -4.615 | -4.615
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87491 | 0.87491 | -4.615 | -4.615
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87491 | 0.87491 | -4.615 | -4.615
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87491 | 0.87491 | -4.615 | -4.615
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87491 | 0.87491 | -4.615 | -4.615
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87491 | 0.87491 | -4.615 | -4.615
Line4_2_6 | 2.259 | 2.259 | 0 | 0 | 1.5651 | 1.5651 | 0.45928 | -0.30619 | 0.91856 | -0.61237 | -68.05 | 111.95 | 0.65618 | 0.43745 | -4.615 | -4.615
Line5_6_7 | 2.259 | 2.259 | 0 | 0 | 1.5651 | 1.5651 | 0.30619 | -0.15309 | 0.61237 | -0.30619 | -68.05 | 111.95 | 0.43745 | 0.21873 | -4.615 | -4.615
Line6_7_8 | 2.259 | 2.259 | 0 | 4.1931 | 1.5651 | 1.5651 | 0.15309 | -1e-07 | 0.30619 | -1e-07 | -68.05 | 111.95 | 0.21873 | 0 | -4.615 | 0
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1499e-21 | 0 | -5.8009e-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1499e-21 | 0 | -5.8009e-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87491 | 0.87491 | -4.615 | -4.615

## LLL_max_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 0.033802 | 0.033802 | 0 | 0 | 0.023418 | 0.023418 | 0.017275 | -0.017241 | 0.017412 | -0.017344 | -45.346 | 134.654 | 1.0474 | 1.0443 | -0.11952 | -0.17563
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.11952 | -0.11952
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.11952 | -0.11952
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.11952 | -0.11952
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.11952 | -0.11952
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.11952 | -0.11952
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.11952 | -0.11952
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.11952 | -0.11952
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.11952 | -0.11952
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.11952 | -0.11952
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.11952 | -0.11952
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.11952 | -0.11952
Line4_2_6 | 0.033802 | 0.033802 | 0 | 0 | 0.023418 | 0.023418 | 0.017241 | -0.017207 | 0.017344 | -0.017275 | -45.346 | 134.654 | 1.0443 | 1.0412 | -0.17563 | -0.23207
Line5_6_7 | 0.033802 | 0.033802 | 0 | 0 | 0.023418 | 0.023418 | 0.017207 | -0.017173 | 0.017275 | -0.017207 | -45.346 | 134.654 | 1.0412 | 1.0381 | -0.23207 | -0.28886
Line6_7_8 | 0.033802 | 0.033802 | 0 | 0.0626 | 0.023418 | 0.023418 | 0.017173 | -0.017138 | 0.017207 | -0.017138 | -45.346 | 134.654 | 1.0381 | 1.035 | -0.28886 | -0.34598
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | -1.7102e-10 | 0 | 7.2182e-11 | 0 | 0 | 0 | 1.035 | 1.035 | -0.34598 | -0.34598
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | -1.7102e-10 | 0 | 7.2182e-11 | 0 | 0 | 0 | 1.035 | 1.035 | -0.34598 | -0.34598
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.11952 | -0.11952

## LLL_max_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 0.035407 | 0.035407 | 0 | 0 | 0.024531 | 0.024531 | 0.018955 | -0.018918 | 0.019106 | -0.019031 | -45.3516 | 134.6484 | 1.0971 | 1.0939 | -0.12515 | -0.18126
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12515 | -0.12515
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12515 | -0.12515
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12515 | -0.12515
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12515 | -0.12515
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12515 | -0.12515
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12515 | -0.12515
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12515 | -0.12515
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12515 | -0.12515
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12515 | -0.12515
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12515 | -0.12515
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12515 | -0.12515
Line4_2_6 | 0.035407 | 0.035407 | 0 | 0 | 0.024531 | 0.024531 | 0.018918 | -0.01888 | 0.019031 | -0.018955 | -45.3516 | 134.6484 | 1.0939 | 1.0906 | -0.18126 | -0.23771
Line5_6_7 | 0.035407 | 0.035407 | 0 | 0 | 0.024531 | 0.024531 | 0.01888 | -0.018842 | 0.018955 | -0.01888 | -45.3516 | 134.6484 | 1.0906 | 1.0874 | -0.23771 | -0.29449
Line6_7_8 | 0.035407 | 0.035407 | 0 | 0.065722 | 0.024531 | 0.024531 | 0.018842 | -0.018805 | 0.01888 | -0.018805 | -45.3516 | 134.6484 | 1.0874 | 1.0841 | -0.29449 | -0.35161
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | -1.8919e-10 | 0 | 8.0501e-11 | 0 | 0 | 0 | 1.0841 | 1.0841 | -0.35161 | -0.35161
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | -1.8919e-10 | 0 | 8.0501e-11 | 0 | 0 | 0 | 1.0841 | 1.0841 | -0.35161 | -0.35161
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12515 | -0.12515

## LLL_min_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 1.6801 | 1.6801 | 0 | 0 | 1.164 | 1.164 | 0.65034 | -0.48775 | 0.67743 | -0.50807 | -52.8727 | 127.1273 | 0.80677 | 0.60508 | -6.7036 | -6.7036
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80677 | 0.80677 | -6.7036 | -6.7036
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80677 | 0.80677 | -6.7036 | -6.7036
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80677 | 0.80677 | -6.7036 | -6.7036
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80677 | 0.80677 | -6.7036 | -6.7036
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80677 | 0.80677 | -6.7036 | -6.7036
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80677 | 0.80677 | -6.7036 | -6.7036
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80677 | 0.80677 | -6.7036 | -6.7036
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80677 | 0.80677 | -6.7036 | -6.7036
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80677 | 0.80677 | -6.7036 | -6.7036
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80677 | 0.80677 | -6.7036 | -6.7036
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80677 | 0.80677 | -6.7036 | -6.7036
Line4_2_6 | 1.6801 | 1.6801 | 0 | 0 | 1.164 | 1.164 | 0.48775 | -0.32517 | 0.50807 | -0.33872 | -52.8727 | 127.1273 | 0.60508 | 0.40338 | -6.7036 | -6.7036
Line5_6_7 | 1.6801 | 1.6801 | 0 | 0 | 1.164 | 1.164 | 0.32517 | -0.16258 | 0.33872 | -0.16936 | -52.8727 | 127.1273 | 0.40338 | 0.20169 | -6.7036 | -6.7036
Line6_7_8 | 1.6801 | 1.6801 | 0 | 2.6638 | 1.164 | 1.164 | 0.16258 | -1e-07 | 0.16936 | -1e-07 | -52.8727 | 127.1273 | 0.20169 | 0 | -6.7036 | 0
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 7.0075e-22 | 0 | 9.1561e-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 7.0075e-22 | 0 | 9.1561e-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80677 | 0.80677 | -6.7036 | -6.7036

## LLL_min_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 1.5916 | 1.5916 | 0 | 0 | 1.1027 | 1.1027 | 0.58368 | -0.43776 | 0.608 | -0.456 | -52.8727 | 127.1273 | 0.76431 | 0.57323 | -6.7036 | -6.7036
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76431 | 0.76431 | -6.7036 | -6.7036
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76431 | 0.76431 | -6.7036 | -6.7036
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76431 | 0.76431 | -6.7036 | -6.7036
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76431 | 0.76431 | -6.7036 | -6.7036
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76431 | 0.76431 | -6.7036 | -6.7036
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76431 | 0.76431 | -6.7036 | -6.7036
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76431 | 0.76431 | -6.7036 | -6.7036
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76431 | 0.76431 | -6.7036 | -6.7036
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76431 | 0.76431 | -6.7036 | -6.7036
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76431 | 0.76431 | -6.7036 | -6.7036
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76431 | 0.76431 | -6.7036 | -6.7036
Line4_2_6 | 1.5916 | 1.5916 | 0 | 0 | 1.1027 | 1.1027 | 0.43776 | -0.29184 | 0.456 | -0.304 | -52.8727 | 127.1273 | 0.57323 | 0.38215 | -6.7036 | -6.7036
Line5_6_7 | 1.5916 | 1.5916 | 0 | 0 | 1.1027 | 1.1027 | 0.29184 | -0.14592 | 0.304 | -0.152 | -52.8727 | 127.1273 | 0.38215 | 0.19108 | -6.7036 | -6.7036
Line6_7_8 | 1.5916 | 1.5916 | 0 | 2.5236 | 1.1027 | 1.1027 | 0.14592 | -1e-07 | 0.152 | -1e-07 | -52.8727 | 127.1273 | 0.19108 | 0 | -6.7036 | 0
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 6.276e-22 | 0 | 8.2153e-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 6.276e-22 | 0 | 8.2153e-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76431 | 0.76431 | -6.7036 | -6.7036

## LLL_min_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 0.030469 | 0.030469 | 0 | 0 | 0.02111 | 0.02111 | 0.01414 | -0.014086 | 0.014149 | -0.014093 | -45.1423 | 134.8577 | 0.94756 | 0.9439 | -0.12428 | -0.12874
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94756 | 0.94756 | -0.12428 | -0.12428
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94756 | 0.94756 | -0.12428 | -0.12428
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94756 | 0.94756 | -0.12428 | -0.12428
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94756 | 0.94756 | -0.12428 | -0.12428
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94756 | 0.94756 | -0.12428 | -0.12428
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94756 | 0.94756 | -0.12428 | -0.12428
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94756 | 0.94756 | -0.12428 | -0.12428
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94756 | 0.94756 | -0.12428 | -0.12428
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94756 | 0.94756 | -0.12428 | -0.12428
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94756 | 0.94756 | -0.12428 | -0.12428
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94756 | 0.94756 | -0.12428 | -0.12428
Line4_2_6 | 0.030469 | 0.030469 | 0 | 0 | 0.02111 | 0.02111 | 0.014086 | -0.014033 | 0.014093 | -0.014037 | -45.1423 | 134.8577 | 0.9439 | 0.94024 | -0.12874 | -0.13323
Line5_6_7 | 0.030469 | 0.030469 | 0 | 0 | 0.02111 | 0.02111 | 0.014033 | -0.013979 | 0.014037 | -0.013981 | -45.1423 | 134.8577 | 0.94024 | 0.93659 | -0.13323 | -0.13776
Line6_7_8 | 0.030469 | 0.030469 | 0 | 0.04831 | 0.02111 | 0.02111 | 0.013979 | -0.013926 | 0.013981 | -0.013926 | -45.1423 | 134.8577 | 0.93659 | 0.93293 | -0.13776 | -0.14233
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | -1.7514e-10 | 0 | 2.4218e-11 | 0 | 0 | 0 | 0.93293 | 0.93293 | -0.14233 | -0.14233
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | -1.7514e-10 | 0 | 2.4218e-11 | 0 | 0 | 0 | 0.93293 | 0.93293 | -0.14233 | -0.14233
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94756 | 0.94756 | -0.12428 | -0.12428

## LLL_min_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 0.028866 | 0.028866 | 0 | 0 | 0.019999 | 0.019999 | 0.01269 | -0.012642 | 0.012698 | -0.012648 | -45.1423 | 134.8577 | 0.89769 | 0.89422 | -0.12428 | -0.12874
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89769 | 0.89769 | -0.12428 | -0.12428
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89769 | 0.89769 | -0.12428 | -0.12428
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89769 | 0.89769 | -0.12428 | -0.12428
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89769 | 0.89769 | -0.12428 | -0.12428
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89769 | 0.89769 | -0.12428 | -0.12428
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89769 | 0.89769 | -0.12428 | -0.12428
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89769 | 0.89769 | -0.12428 | -0.12428
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89769 | 0.89769 | -0.12428 | -0.12428
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89769 | 0.89769 | -0.12428 | -0.12428
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89769 | 0.89769 | -0.12428 | -0.12428
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89769 | 0.89769 | -0.12428 | -0.12428
Line4_2_6 | 0.028866 | 0.028866 | 0 | 0 | 0.019999 | 0.019999 | 0.012642 | -0.012594 | 0.012648 | -0.012598 | -45.1423 | 134.8577 | 0.89422 | 0.89076 | -0.12874 | -0.13323
Line5_6_7 | 0.028866 | 0.028866 | 0 | 0 | 0.019999 | 0.019999 | 0.012594 | -0.012546 | 0.012598 | -0.012548 | -45.1423 | 134.8577 | 0.89076 | 0.88729 | -0.13323 | -0.13776
Line6_7_8 | 0.028866 | 0.028866 | 0 | 0.045767 | 0.019999 | 0.019999 | 0.012546 | -0.012498 | 0.012548 | -0.012498 | -45.1423 | 134.8577 | 0.88729 | 0.88383 | -0.13776 | -0.14233
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | -1.5719e-10 | 0 | 2.1736e-11 | 0 | 0 | 0 | 0.88383 | 0.88383 | -0.14233 | -0.14233
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | -1.5719e-10 | 0 | 2.1736e-11 | 0 | 0 | 0 | 0.88383 | 0.88383 | -0.14233 | -0.14233
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89769 | 0.89769 | -0.12428 | -0.12428

## LL_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 1.885 | 1.885 | 0 | 1.885 | 1.885 | 0 | 0.43533 | 0.43533 | 0 | 0.43533 | 0.43533 | 3.4972e-16 | 0.35387 | -0.069596 | -3.4972e-16 | -0.31833 | 0.10513 | -9.7145e-17 | 0.19822 | 0.37032 | 1.1657e-16 | -0.12715 | -0.29925 | 0 | -157.8829 | 22.1171 | 0 | 22.1171 | -157.8829 | 1.05 | 0.93171 | 0.86555 | 1.05 | 0.78742 | 0.7286 | -4.2443e-10 | -128.6271 | 122.7608 | -4.2443e-10 | -136.1092 | 131.4739
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1086e-16 | -2.1811e-09 | -3.489e-09 | -2.9143e-16 | 2.1811e-09 | 3.489e-09 | -2.3028e-27 | 3.2284e-09 | -9.6307e-10 | -1.9429e-17 | -3.2284e-09 | 9.6307e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.93171 | 0.86555 | 1.05 | 0.93171 | 0.86555 | -4.2444e-10 | -128.6271 | 122.7608 | -4.2445e-10 | -128.6271 | 122.7608
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.72e-16 | -1.8176e-09 | -2.9075e-09 | -2.72e-16 | 1.8176e-09 | 2.9075e-09 | -1.9429e-17 | 2.6904e-09 | -8.0256e-10 | 3.8858e-17 | -2.6904e-09 | 8.0256e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.93171 | 0.86555 | 1.05 | 0.93171 | 0.86555 | -4.2445e-10 | -128.6271 | 122.7608 | -4.2445e-10 | -128.6271 | 122.7608
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5543e-16 | -1.0906e-09 | -1.7445e-09 | -1.36e-16 | 1.0906e-09 | 1.7445e-09 | 1.9429e-17 | 1.6142e-09 | -4.8153e-10 | -1.9429e-17 | -1.6142e-09 | 4.8153e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.93171 | 0.86555 | 1.05 | 0.93171 | 0.86555 | -4.2445e-10 | -128.6271 | 122.7608 | -4.2445e-10 | -128.6271 | 122.7608
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.6352e-10 | -5.8151e-10 | 1.9429e-17 | 3.6352e-10 | 5.8151e-10 | 0 | 5.3807e-10 | -1.6051e-10 | -1.4393e-28 | -5.3807e-10 | 1.6051e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.93171 | 0.86555 | 1.05 | 0.93171 | 0.86555 | -4.2445e-10 | -128.6271 | 122.7608 | -4.2445e-10 | -128.6271 | 122.7608
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7716e-17 | -7.2704e-10 | -1.163e-09 | -7.7716e-17 | 7.2704e-10 | 1.163e-09 | -5.7573e-28 | 1.0761e-09 | -3.2102e-10 | 1.9429e-17 | -1.0761e-09 | 3.2102e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.93171 | 0.86555 | 1.05 | 0.93171 | 0.86555 | -4.2445e-10 | -128.6271 | 122.7608 | -4.2446e-10 | -128.6271 | 122.7608
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.9429e-17 | -3.6352e-10 | -5.8151e-10 | 1.9429e-17 | 3.6352e-10 | 5.8151e-10 | -1.9429e-17 | 5.3807e-10 | -1.6051e-10 | -1.9429e-17 | -5.3807e-10 | 1.6051e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.93171 | 0.86555 | 1.05 | 0.93171 | 0.86555 | -4.2446e-10 | -128.6271 | 122.7608 | -4.2446e-10 | -128.6271 | 122.7608
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.6352e-10 | -5.8151e-10 | 1.4392e-28 | 3.6352e-10 | 5.8151e-10 | 0 | 5.3807e-10 | -1.6051e-10 | 1.9429e-17 | -5.3807e-10 | 1.6051e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.93171 | 0.86555 | 1.05 | 0.93171 | 0.86555 | -4.2443e-10 | -128.6271 | 122.7608 | -4.2443e-10 | -128.6271 | 122.7608
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.6352e-10 | -5.8151e-10 | 1.4392e-28 | 3.6352e-10 | 5.8151e-10 | 0 | 5.3807e-10 | -1.6051e-10 | 1.9429e-17 | -5.3807e-10 | 1.6051e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.93171 | 0.86555 | 1.05 | 0.93171 | 0.86555 | -4.2443e-10 | -128.6271 | 122.7608 | -4.2443e-10 | -128.6271 | 122.7608
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4686e-16 | -2.9082e-09 | -4.6521e-09 | -4.4686e-16 | 2.9082e-09 | 4.6521e-09 | 7.7716e-17 | 4.3046e-09 | -1.2841e-09 | -5.8287e-17 | -4.3046e-09 | 1.2841e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.93171 | 0.86555 | 1.05 | 0.93171 | 0.86555 | -4.2443e-10 | -128.6271 | 122.7608 | -4.2444e-10 | -128.6271 | 122.7608
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7716e-17 | -7.2704e-10 | -1.163e-09 | -5.8287e-17 | 7.2704e-10 | 1.163e-09 | -5.7569e-28 | 1.0761e-09 | -3.2102e-10 | -1.9429e-17 | -1.0761e-09 | 3.2102e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.93171 | 0.86555 | 1.05 | 0.93171 | 0.86555 | -4.2443e-10 | -128.6271 | 122.7608 | -4.2443e-10 | -128.6271 | 122.7608
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7716e-17 | -7.2704e-10 | -1.163e-09 | -5.8287e-17 | 7.2704e-10 | 1.163e-09 | -5.7569e-28 | 1.0761e-09 | -3.2102e-10 | -1.9429e-17 | -1.0761e-09 | 3.2102e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.93171 | 0.86555 | 1.05 | 0.93171 | 0.86555 | -4.2443e-10 | -128.6271 | 122.7608 | -4.2443e-10 | -128.6271 | 122.7608
Line4_2_6 | 0 | 1.885 | 1.885 | 0 | 1.885 | 1.885 | 0 | 0.43533 | 0.43533 | 0 | 0.43533 | 0.43533 | 3.8858e-16 | 0.31833 | -0.10513 | -3.8858e-16 | -0.2828 | 0.14066 | -1.9429e-16 | 0.12715 | 0.29925 | 1.9429e-16 | -0.056087 | -0.22819 | 0 | -157.8829 | 22.1171 | 0 | 22.1171 | -157.8829 | 1.05 | 0.78742 | 0.7286 | 1.05 | 0.66227 | 0.61575 | -4.2443e-10 | -136.1092 | 131.4739 | -4.2444e-10 | -146.6652 | 143.7688
Line5_6_7 | 0 | 1.885 | 1.885 | 0 | 1.885 | 1.885 | 0 | 0.43533 | 0.43533 | 0 | 0.43533 | 0.43533 | 3.1086e-16 | 0.2828 | -0.14066 | -3.1086e-16 | -0.24727 | 0.1762 | -1.1657e-16 | 0.056087 | 0.22819 | 1.5543e-16 | 0.014981 | -0.15712 | 0 | -157.8829 | 22.1171 | 0 | 22.1171 | -157.8829 | 1.05 | 0.66227 | 0.61575 | 1.05 | 0.56903 | 0.54229 | -4.2444e-10 | -146.6652 | 143.7688 | -4.2444e-10 | -161.35 | 160.3935
Line6_7_8 | 0 | 1.885 | 1.885 | 0 | 1.885 | 1.885 | 0 | 0.43533 | 0.43533 | 0 | 0.43533 | 0.43533 | 2.3315e-16 | 0.24727 | -0.1762 | -3.1086e-16 | -0.21173 | 0.21173 | -1.1657e-16 | -0.014981 | 0.15712 | 1.5543e-16 | 0.086049 | -0.086049 | 0 | -157.8829 | 22.1171 | 0 | 22.1171 | -157.8829 | 1.05 | 0.56903 | 0.54229 | 1.05 | 0.525 | 0.525 | -4.2444e-10 | -161.35 | 160.3935 | -4.2444e-10 | -180 | -180
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7716e-17 | 1.9427e-16 | -1.554e-16 | -1.5543e-16 | 1.5754e-16 | -1.5338e-16 | -1.1657e-16 | 1.7505e-09 | -1.7505e-09 | 1.1657e-16 | -1.7505e-09 | 1.7505e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.525 | 0.525 | 1.05 | 0.525 | 0.525 | -4.2444e-10 | -180 | -180 | -4.2445e-10 | -180 | 180
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.5543e-16 | 4.6627e-16 | -3.1083e-16 | 8.6358e-28 | -1.1447e-16 | 2.0556e-18 | -1.1657e-16 | 1.7505e-09 | -1.7505e-09 | 1.1657e-16 | -1.7505e-09 | 1.7505e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.525 | 0.525 | 1.05 | 0.525 | 0.525 | -4.2444e-10 | -180 | -180 | -4.2445e-10 | -180 | 180
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6915e-16 | -2.5447e-09 | -4.0705e-09 | -3.6915e-16 | 2.5447e-09 | 4.0705e-09 | 1.9429e-17 | 3.7665e-09 | -1.1236e-09 | -1.9429e-17 | -3.7665e-09 | 1.1236e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.93171 | 0.86555 | 1.05 | 0.93171 | 0.86555 | -4.2444e-10 | -128.6271 | 122.7608 | -4.2444e-10 | -128.6271 | 122.7608

## LL_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 1.9564 | 1.9564 | 0 | 1.9564 | 1.9564 | 0 | 0.4518 | 0.4518 | 0 | 0.4518 | 0.4518 | 1.0991e-15 | 0.38357 | -0.077384 | -1.0991e-15 | -0.3453 | 0.11566 | -2.4425e-16 | 0.2133 | 0.39907 | 2.4425e-16 | -0.13675 | -0.32252 | 0 | -158.05 | 21.95 | 0 | 21.95 | -158.05 | 1.1 | 0.97142 | 0.89974 | 1.1 | 0.82203 | 0.75838 | -1.3272e-09 | -128.9719 | 122.9242 | -1.3273e-09 | -136.444 | 131.678
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4602e-16 | -2.4603e-09 | -3.9356e-09 | -3.4602e-16 | 2.4603e-09 | 3.9356e-09 | 4.0708e-17 | 3.6661e-09 | -1.1108e-09 | 8.0156e-27 | -3.6661e-09 | 1.1108e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.97142 | 0.89974 | 1.1 | 0.97142 | 0.89974 | -1.3273e-09 | -128.9719 | 122.9242 | -1.3273e-09 | -128.9719 | 122.9242
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.646e-16 | -2.0502e-09 | -3.2797e-09 | -2.4425e-16 | 2.0502e-09 | 3.2797e-09 | -2.0354e-17 | 3.0551e-09 | -9.2564e-10 | 4.0708e-17 | -3.0551e-09 | 9.2564e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.97142 | 0.89974 | 1.1 | 0.97142 | 0.89974 | -1.3273e-09 | -128.9719 | 122.9242 | -1.3273e-09 | -128.9719 | 122.9242
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6283e-16 | -1.2301e-09 | -1.9678e-09 | -1.6283e-16 | 1.2301e-09 | 1.9678e-09 | 2.0354e-17 | 1.8331e-09 | -5.5539e-10 | -4.0708e-17 | -1.8331e-09 | 5.5539e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.97142 | 0.89974 | 1.1 | 0.97142 | 0.89974 | -1.3273e-09 | -128.9719 | 122.9242 | -1.3273e-09 | -128.9719 | 122.9242
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0708e-17 | -4.1005e-10 | -6.5593e-10 | -4.0708e-17 | 4.1005e-10 | 6.5593e-10 | -9.4302e-28 | 6.1102e-10 | -1.8513e-10 | 9.4302e-28 | -6.1102e-10 | 1.8513e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.97142 | 0.89974 | 1.1 | 0.97142 | 0.89974 | -1.3273e-09 | -128.9719 | 122.9242 | -1.3273e-09 | -128.9719 | 122.9242
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2212e-16 | -8.2009e-10 | -1.3119e-09 | -1.4248e-16 | 8.2009e-10 | 1.3119e-09 | 2.0354e-17 | 1.222e-09 | -3.7026e-10 | -2.0354e-17 | -1.222e-09 | 3.7026e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.97142 | 0.89974 | 1.1 | 0.97142 | 0.89974 | -1.3273e-09 | -128.9719 | 122.9242 | -1.3273e-09 | -128.9719 | 122.9242
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.0354e-17 | -4.1005e-10 | -6.5593e-10 | 4.0708e-17 | 4.1005e-10 | 6.5593e-10 | -2.0354e-17 | 6.1102e-10 | -1.8513e-10 | 2.0354e-17 | -6.1102e-10 | 1.8513e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.97142 | 0.89974 | 1.1 | 0.97142 | 0.89974 | -1.3273e-09 | -128.9719 | 122.9242 | -1.3273e-09 | -128.9719 | 122.9242
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.715e-28 | -4.1005e-10 | -6.5593e-10 | 0 | 4.1005e-10 | 6.5593e-10 | -2.0354e-17 | 6.1102e-10 | -1.8513e-10 | 0 | -6.1102e-10 | 1.8513e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.97142 | 0.89974 | 1.1 | 0.97142 | 0.89974 | -1.3272e-09 | -128.9719 | 122.9242 | -1.3272e-09 | -128.9719 | 122.9242
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.715e-28 | -4.1005e-10 | -6.5593e-10 | 0 | 4.1005e-10 | 6.5593e-10 | -2.0354e-17 | 6.1102e-10 | -1.8513e-10 | 0 | -6.1102e-10 | 1.8513e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.97142 | 0.89974 | 1.1 | 0.97142 | 0.89974 | -1.3272e-09 | -128.9719 | 122.9242 | -1.3272e-09 | -128.9719 | 122.9242
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.0885e-16 | -3.2804e-09 | -5.2475e-09 | -5.0885e-16 | 3.2804e-09 | 5.2475e-09 | 6.1062e-17 | 4.8882e-09 | -1.481e-09 | -8.1416e-17 | -4.8882e-09 | 1.481e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.97142 | 0.89974 | 1.1 | 0.97142 | 0.89974 | -1.3272e-09 | -128.9719 | 122.9242 | -1.3273e-09 | -128.9719 | 122.9242
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0708e-17 | -8.2009e-10 | -1.3119e-09 | -6.1062e-17 | 8.2009e-10 | 1.3119e-09 | -2.0354e-17 | 1.222e-09 | -3.7026e-10 | 1.4145e-27 | -1.222e-09 | 3.7026e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.97142 | 0.89974 | 1.1 | 0.97142 | 0.89974 | -1.3272e-09 | -128.9719 | 122.9242 | -1.3272e-09 | -128.9719 | 122.9242
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0708e-17 | -8.2009e-10 | -1.3119e-09 | -6.1062e-17 | 8.2009e-10 | 1.3119e-09 | -2.0354e-17 | 1.222e-09 | -3.7026e-10 | 1.4145e-27 | -1.222e-09 | 3.7026e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.97142 | 0.89974 | 1.1 | 0.97142 | 0.89974 | -1.3272e-09 | -128.9719 | 122.9242 | -1.3272e-09 | -128.9719 | 122.9242
Line4_2_6 | 0 | 1.9564 | 1.9564 | 0 | 1.9564 | 1.9564 | 0 | 0.4518 | 0.4518 | 0 | 0.4518 | 0.4518 | 1.0584e-15 | 0.3453 | -0.11566 | -1.0584e-15 | -0.30702 | 0.15393 | -3.6637e-16 | 0.13675 | 0.32252 | 3.6637e-16 | -0.060208 | -0.24598 | 0 | -158.05 | 21.95 | 0 | 21.95 | -158.05 | 1.1 | 0.82203 | 0.75838 | 1.1 | 0.6925 | 0.64226 | -1.3273e-09 | -136.444 | 131.678 | -1.3273e-09 | -146.955 | 143.988
Line5_6_7 | 0 | 1.9564 | 1.9564 | 0 | 1.9564 | 1.9564 | 0 | 0.4518 | 0.4518 | 0 | 0.4518 | 0.4518 | 8.9558e-16 | 0.30702 | -0.15393 | -8.9558e-16 | -0.26875 | 0.1922 | -3.6637e-16 | 0.060208 | 0.24598 | 3.6637e-16 | 0.016339 | -0.16943 | 0 | -158.05 | 21.95 | 0 | 21.95 | -158.05 | 1.1 | 0.6925 | 0.64226 | 1.1 | 0.59594 | 0.56711 | -1.3273e-09 | -146.955 | 143.988 | -1.3273e-09 | -161.529 | 160.5532
Line6_7_8 | 0 | 1.9564 | 1.9564 | 0 | 1.9564 | 1.9564 | 0 | 0.4518 | 0.4518 | 0 | 0.4518 | 0.4518 | 6.5133e-16 | 0.26875 | -0.1922 | -6.5133e-16 | -0.23048 | 0.23048 | -2.4425e-16 | -0.016339 | 0.16943 | 2.4425e-16 | 0.092885 | -0.092885 | 0 | -158.05 | 21.95 | 0 | 21.95 | -158.05 | 1.1 | 0.59594 | 0.56711 | 1.1 | 0.55 | 0.55 | -1.3273e-09 | -161.529 | 160.5532 | -1.3273e-09 | -180 | -180
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2567e-16 | 1.6274e-16 | -6.5125e-16 | -3.2567e-16 | 8.3797e-17 | 2.2031e-18 | -8.1416e-17 | 1.9211e-09 | -1.9211e-09 | 8.1416e-17 | -1.9211e-09 | 1.9211e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.55 | 0.55 | 1.1 | 0.55 | 0.55 | -1.3273e-09 | -180 | -180 | -1.3273e-09 | -180 | 180
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6283e-16 | 2.4416e-16 | -3.2558e-16 | -1.6283e-16 | 2.381e-18 | 2.2031e-18 | -3.7721e-27 | 1.9211e-09 | -1.9211e-09 | 3.7721e-27 | -1.9211e-09 | 1.9211e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.55 | 0.55 | 1.1 | 0.55 | 0.55 | -1.3273e-09 | -180 | -180 | -1.3273e-09 | -180 | 180
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.885e-16 | -2.8703e-09 | -4.5915e-09 | -4.4779e-16 | 2.8703e-09 | 4.5915e-09 | -2.0354e-17 | 4.2771e-09 | -1.2959e-09 | 1.0373e-26 | -4.2771e-09 | 1.2959e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.97142 | 0.89974 | 1.1 | 0.97142 | 0.89974 | -1.3273e-09 | -128.9719 | 122.9242 | -1.3273e-09 | -128.9719 | 122.9242

## LL_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0.057717 | 0.057717 | 0 | 0.057717 | 0.057717 | 0 | 0.013329 | 0.013329 | 0 | 0.013329 | 0.013329 | 1.1536e-17 | 0.013468 | 0.0034547 | -1.0322e-17 | -0.013435 | -0.0034214 | 7.2858e-18 | 0.0037057 | 0.013484 | -9.7145e-18 | -0.0036391 | -0.013417 | 0 | -135.6822 | 44.3178 | 0 | 44.3178 | -135.6822 | 1.05 | 1.048 | 1.0443 | 1.05 | 1.0443 | 1.0388 | 1.715e-11 | -120.2981 | 119.9471 | 1.715e-11 | -120.5262 | 120.0122
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.2858e-18 | -4.627e-11 | -1.3184e-10 | -7.2858e-18 | 4.627e-11 | 1.3184e-10 | 1.2143e-18 | 1.2595e-10 | 2.226e-11 | -1.8215e-18 | -1.2595e-10 | -2.226e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0443 | 1.05 | 1.048 | 1.0443 | 1.715e-11 | -120.2981 | 119.9471 | 1.7149e-11 | -120.2981 | 119.9471
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0715e-18 | -3.8558e-11 | -1.0987e-10 | -5.4644e-18 | 3.8558e-11 | 1.0987e-10 | 1.2143e-18 | 1.0496e-10 | 1.855e-11 | -1.2143e-18 | -1.0496e-10 | -1.855e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0443 | 1.05 | 1.048 | 1.0443 | 1.7149e-11 | -120.2981 | 119.9471 | 1.7149e-11 | -120.2981 | 119.9471
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9465e-18 | -2.3135e-11 | -6.592e-11 | -3.9465e-18 | 2.3135e-11 | 6.592e-11 | 1.2143e-18 | 6.2976e-11 | 1.113e-11 | -1.2143e-18 | -6.2976e-11 | -1.113e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0443 | 1.05 | 1.048 | 1.0443 | 1.7149e-11 | -120.2981 | 119.9471 | 1.7149e-11 | -120.2981 | 119.9471
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8173e-31 | -7.7116e-12 | -2.1973e-11 | 0 | 7.7116e-12 | 2.1973e-11 | -6.0715e-19 | 2.0992e-11 | 3.71e-12 | 0 | -2.0992e-11 | -3.71e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0443 | 1.05 | 1.048 | 1.0443 | 1.7149e-11 | -120.2981 | 119.9471 | 1.7149e-11 | -120.2981 | 119.9471
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4286e-18 | -1.5423e-11 | -4.3946e-11 | -2.4286e-18 | 1.5423e-11 | 4.3946e-11 | 1.8215e-18 | 4.1984e-11 | 7.42e-12 | -1.8215e-18 | -4.1984e-11 | -7.42e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0443 | 1.05 | 1.048 | 1.0443 | 1.7149e-11 | -120.2981 | 119.9471 | 1.7149e-11 | -120.2981 | 119.9471
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0715e-19 | -7.7116e-12 | -2.1973e-11 | -6.0715e-19 | 7.7116e-12 | 2.1973e-11 | -6.0715e-19 | 2.0992e-11 | 3.71e-12 | 6.0715e-19 | -2.0992e-11 | -3.71e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0443 | 1.05 | 1.048 | 1.0443 | 1.7149e-11 | -120.2981 | 119.9471 | 1.7149e-11 | -120.2981 | 119.9471
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.2143e-18 | -7.7116e-12 | -2.1973e-11 | 6.0715e-19 | 7.7116e-12 | 2.1973e-11 | -3.6347e-31 | 2.0992e-11 | 3.71e-12 | 1.8173e-31 | -2.0992e-11 | -3.71e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0443 | 1.05 | 1.048 | 1.0443 | 1.715e-11 | -120.2981 | 119.9471 | 1.715e-11 | -120.2981 | 119.9471
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.2143e-18 | -7.7116e-12 | -2.1973e-11 | 6.0715e-19 | 7.7116e-12 | 2.1973e-11 | -3.6347e-31 | 2.0992e-11 | 3.71e-12 | 1.8173e-31 | -2.0992e-11 | -3.71e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0443 | 1.05 | 1.048 | 1.0443 | 1.715e-11 | -120.2981 | 119.9471 | 1.715e-11 | -120.2981 | 119.9471
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.7145e-18 | -6.1693e-11 | -1.7579e-10 | -9.7145e-18 | 6.1693e-11 | 1.7579e-10 | 6.6787e-18 | 1.6794e-10 | 2.968e-11 | -7.2858e-18 | -1.6794e-10 | -2.968e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0443 | 1.05 | 1.048 | 1.0443 | 1.715e-11 | -120.2981 | 119.9471 | 1.715e-11 | -120.2981 | 119.9471
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2143e-18 | -1.5423e-11 | -4.3946e-11 | -1.8215e-18 | 1.5423e-11 | 4.3946e-11 | 6.0715e-19 | 4.1984e-11 | 7.42e-12 | -1.2143e-18 | -4.1984e-11 | -7.42e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0443 | 1.05 | 1.048 | 1.0443 | 1.715e-11 | -120.2981 | 119.9471 | 1.715e-11 | -120.2981 | 119.9471
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2143e-18 | -1.5423e-11 | -4.3946e-11 | -1.8215e-18 | 1.5423e-11 | 4.3946e-11 | 6.0715e-19 | 4.1984e-11 | 7.42e-12 | -1.2143e-18 | -4.1984e-11 | -7.42e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0443 | 1.05 | 1.048 | 1.0443 | 1.715e-11 | -120.2981 | 119.9471 | 1.715e-11 | -120.2981 | 119.9471
Line4_2_6 | 0 | 0.057717 | 0.057717 | 0 | 0.057717 | 0.057717 | 0 | 0.013329 | 0.013329 | 0 | 0.013329 | 0.013329 | 6.0715e-18 | 0.013435 | 0.0034214 | -9.7145e-18 | -0.013402 | -0.003388 | 1.2143e-17 | 0.0036391 | 0.013417 | -7.2858e-18 | -0.0035725 | -0.01335 | 0 | -135.6822 | 44.3178 | 0 | 44.3178 | -135.6822 | 1.05 | 1.0443 | 1.0388 | 1.05 | 1.0405 | 1.0333 | 1.715e-11 | -120.5262 | 120.0122 | 1.715e-11 | -120.7558 | 120.078
Line5_6_7 | 0 | 0.057717 | 0.057717 | 0 | 0.057717 | 0.057717 | 0 | 0.013329 | 0.013329 | 0 | 0.013329 | 0.013329 | 4.8572e-18 | 0.013402 | 0.003388 | -7.2858e-18 | -0.013368 | -0.0033547 | 7.2858e-18 | 0.0035725 | 0.01335 | -2.4286e-18 | -0.0035059 | -0.013284 | 0 | -135.6822 | 44.3178 | 0 | 44.3178 | -135.6822 | 1.05 | 1.0405 | 1.0333 | 1.05 | 1.0368 | 1.0279 | 1.715e-11 | -120.7558 | 120.078 | 1.715e-11 | -120.9872 | 120.1445
Line6_7_8 | 0 | 0.057717 | 0.057717 | 0 | 0.057717 | 0.057717 | 0 | 0.013329 | 0.013329 | 0 | 0.013329 | 0.013329 | 9.7145e-18 | 0.013368 | 0.0033547 | -7.2858e-18 | -0.013335 | -0.0033214 | -4.8572e-18 | 0.0035059 | 0.013284 | 2.4286e-18 | -0.0034392 | -0.013217 | 0 | -135.6822 | 44.3178 | 0 | 44.3178 | -135.6822 | 1.05 | 1.0368 | 1.0279 | 1.05 | 1.0332 | 1.0224 | 1.715e-11 | -120.9872 | 120.1445 | 1.7149e-11 | -121.2201 | 120.2117
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.2856e-11 | -1.0336e-10 | -2.4286e-18 | 6.2856e-11 | 1.0336e-10 | 0 | 8.4699e-11 | -1.4546e-11 | -7.2691e-31 | -8.4699e-11 | 1.4546e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.0332 | 1.0224 | 1.05 | 1.0332 | 1.0224 | 1.7149e-11 | -121.2201 | 120.2117 | 1.7149e-11 | -121.2201 | 120.2117
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.2858e-18 | -6.2856e-11 | -1.0336e-10 | 4.8572e-18 | 6.2856e-11 | 1.0336e-10 | -2.1807e-30 | 8.4699e-11 | -1.4546e-11 | 1.4538e-30 | -8.4699e-11 | 1.4546e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.0332 | 1.0224 | 1.05 | 1.0332 | 1.0224 | 1.7149e-11 | -121.2201 | 120.2117 | 1.7149e-11 | -121.2201 | 120.2117
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.7145e-18 | -5.3981e-11 | -1.5381e-10 | -1.0322e-17 | 5.3981e-11 | 1.5381e-10 | 4.8572e-18 | 1.4694e-10 | 2.597e-11 | -4.2501e-18 | -1.4694e-10 | -2.597e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0443 | 1.05 | 1.048 | 1.0443 | 1.715e-11 | -120.2981 | 119.9471 | 1.715e-11 | -120.2981 | 119.9471

## LL_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0.060452 | 0.060452 | 0 | 0.060452 | 0.060452 | 0 | 0.013961 | 0.013961 | 0 | 0.013961 | 0.013961 | 2.9259e-17 | 0.014777 | 0.0037874 | -3.0531e-17 | -0.01474 | -0.0037509 | -2.1656e-30 | 0.004065 | 0.014792 | 2.26e-30 | -0.0039919 | -0.014719 | 0 | -135.6932 | 44.3068 | 0 | 44.3068 | -135.6932 | 1.1 | 1.0978 | 1.0937 | 1.1 | 1.0939 | 1.088 | -4.2408e-12 | -120.3121 | 119.9447 | -4.2412e-12 | -120.5402 | 120.0098
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.9508e-18 | -5.3155e-11 | -1.5146e-10 | -8.5869e-18 | 5.3155e-11 | 1.5146e-10 | 4.4525e-18 | 1.4472e-10 | 2.555e-11 | -3.1803e-18 | -1.4472e-10 | -2.555e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0937 | 1.1 | 1.0978 | 1.0937 | -4.2412e-12 | -120.3121 | 119.9447 | -4.2414e-12 | -120.3121 | 119.9447
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.3148e-18 | -4.4296e-11 | -1.2622e-10 | -6.6787e-18 | 4.4296e-11 | 1.2622e-10 | -5.4148e-31 | 1.206e-10 | 2.1292e-11 | -1.9082e-18 | -1.206e-10 | -2.1292e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0937 | 1.1 | 1.0978 | 1.0937 | -4.2414e-12 | -120.3121 | 119.9447 | -4.2415e-12 | -120.3121 | 119.9447
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7705e-18 | -2.6578e-11 | -7.5731e-11 | -4.1344e-18 | 2.6578e-11 | 7.5731e-11 | 3.8164e-18 | 7.2361e-11 | 1.2775e-11 | -2.5443e-18 | -7.2361e-11 | -1.2775e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0937 | 1.1 | 1.0978 | 1.0937 | -4.2415e-12 | -120.3121 | 119.9447 | -4.2416e-12 | -120.3121 | 119.9447
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.1803e-19 | -8.8592e-12 | -2.5244e-11 | 9.541e-19 | 8.8592e-12 | 2.5244e-11 | 6.3607e-19 | 2.412e-11 | 4.2584e-12 | 6.3607e-19 | -2.412e-11 | -4.2584e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0937 | 1.1 | 1.0978 | 1.0937 | -4.2415e-12 | -120.3121 | 119.9447 | -4.2415e-12 | -120.3121 | 119.9447
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8164e-18 | -1.7718e-11 | -5.0487e-11 | -3.8164e-18 | 1.7718e-11 | 5.0487e-11 | 1.2721e-18 | 4.824e-11 | 8.5168e-12 | -6.3607e-19 | -4.824e-11 | -8.5168e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0937 | 1.1 | 1.0978 | 1.0937 | -4.2416e-12 | -120.3121 | 119.9447 | -4.2416e-12 | -120.3121 | 119.9447
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.3607e-19 | -8.8592e-12 | -2.5244e-11 | 6.3607e-19 | 8.8592e-12 | 2.5244e-11 | -6.3607e-19 | 2.412e-11 | 4.2584e-12 | -4.7088e-32 | -2.412e-11 | -4.2584e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0937 | 1.1 | 1.0978 | 1.0937 | -4.2416e-12 | -120.3121 | 119.9447 | -4.2416e-12 | -120.3121 | 119.9447
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1803e-19 | -8.8592e-12 | -2.5244e-11 | 9.541e-19 | 8.8592e-12 | 2.5244e-11 | -6.3607e-19 | 2.412e-11 | 4.2584e-12 | 6.3607e-19 | -2.412e-11 | -4.2584e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0937 | 1.1 | 1.0978 | 1.0937 | -4.2409e-12 | -120.3121 | 119.9447 | -4.2409e-12 | -120.3121 | 119.9447
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1803e-19 | -8.8592e-12 | -2.5244e-11 | 9.541e-19 | 8.8592e-12 | 2.5244e-11 | -6.3607e-19 | 2.412e-11 | 4.2584e-12 | 6.3607e-19 | -2.412e-11 | -4.2584e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0937 | 1.1 | 1.0978 | 1.0937 | -4.2409e-12 | -120.3121 | 119.9447 | -4.2409e-12 | -120.3121 | 119.9447
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2721e-17 | -7.0874e-11 | -2.0195e-10 | -1.2721e-17 | 7.0874e-11 | 2.0195e-10 | 7.6328e-18 | 1.9296e-10 | 3.4067e-11 | -8.2688e-18 | -1.9296e-10 | -3.4067e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0937 | 1.1 | 1.0978 | 1.0937 | -4.2408e-12 | -120.3121 | 119.9447 | -4.241e-12 | -120.3121 | 119.9447
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9082e-18 | -1.7718e-11 | -5.0487e-11 | -2.5443e-18 | 1.7718e-11 | 5.0487e-11 | 6.3607e-19 | 4.824e-11 | 8.5168e-12 | -1.9082e-18 | -4.824e-11 | -8.5168e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0937 | 1.1 | 1.0978 | 1.0937 | -4.2408e-12 | -120.3121 | 119.9447 | -4.2409e-12 | -120.3121 | 119.9447
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9082e-18 | -1.7718e-11 | -5.0487e-11 | -2.5443e-18 | 1.7718e-11 | 5.0487e-11 | 6.3607e-19 | 4.824e-11 | 8.5168e-12 | -1.9082e-18 | -4.824e-11 | -8.5168e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0937 | 1.1 | 1.0978 | 1.0937 | -4.2408e-12 | -120.3121 | 119.9447 | -4.2409e-12 | -120.3121 | 119.9447
Line4_2_6 | 0 | 0.060452 | 0.060452 | 0 | 0.060452 | 0.060452 | 0 | 0.013961 | 0.013961 | 0 | 0.013961 | 0.013961 | 2.2898e-17 | 0.01474 | 0.0037509 | -2.1626e-17 | -0.014704 | -0.0037143 | -2.5443e-18 | 0.0039919 | 0.014719 | 1.601e-30 | -0.0039188 | -0.014646 | 0 | -135.6932 | 44.3068 | 0 | 44.3068 | -135.6932 | 1.1 | 1.0939 | 1.088 | 1.1 | 1.09 | 1.0823 | -4.2412e-12 | -120.5402 | 120.0098 | -4.2416e-12 | -120.7698 | 120.0757
Line5_6_7 | 0 | 0.060452 | 0.060452 | 0 | 0.060452 | 0.060452 | 0 | 0.013961 | 0.013961 | 0 | 0.013961 | 0.013961 | 2.2898e-17 | 0.014704 | 0.0037143 | -2.5443e-17 | -0.014667 | -0.0036778 | -1.2721e-17 | 0.0039188 | 0.014646 | 7.6328e-18 | -0.0038457 | -0.014572 | 0 | -135.6932 | 44.3068 | 0 | 44.3068 | -135.6932 | 1.1 | 1.09 | 1.0823 | 1.1 | 1.0861 | 1.0765 | -4.2416e-12 | -120.7698 | 120.0757 | -4.242e-12 | -121.0011 | 120.1422
Line6_7_8 | 0 | 0.060452 | 0.060452 | 0 | 0.060452 | 0.060452 | 0 | 0.013961 | 0.013961 | 0 | 0.013961 | 0.013961 | 1.5266e-17 | 0.014667 | 0.0036778 | -1.2721e-17 | -0.014631 | -0.0036413 | -1.1302e-30 | 0.0038457 | 0.014572 | 2.5443e-18 | -0.0037726 | -0.014499 | 0 | -135.6932 | 44.3068 | 0 | 44.3068 | -135.6932 | 1.1 | 1.0861 | 1.0765 | 1.1 | 1.0823 | 1.0708 | -4.242e-12 | -121.0011 | 120.1422 | -4.2423e-12 | -121.2341 | 120.2095
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5443e-18 | -6.9334e-11 | -1.1449e-10 | -2.5443e-18 | 6.9334e-11 | 1.1449e-10 | 2.5443e-18 | 9.4011e-11 | -1.5791e-11 | 1.8839e-31 | -9.4011e-11 | 1.5791e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0823 | 1.0708 | 1.1 | 1.0823 | 1.0708 | -4.2423e-12 | -121.2341 | 120.2095 | -4.2424e-12 | -121.2341 | 120.2095
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.0885e-18 | -6.9334e-11 | -1.1449e-10 | 1.8839e-31 | 6.9334e-11 | 1.1449e-10 | -5.0885e-18 | 9.4011e-11 | -1.5791e-11 | 2.5443e-18 | -9.4011e-11 | 1.5791e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0823 | 1.0708 | 1.1 | 1.0823 | 1.0708 | -4.2423e-12 | -121.2341 | 120.2095 | -4.2424e-12 | -121.2341 | 120.2095
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.859e-18 | -6.2015e-11 | -1.7671e-10 | -9.859e-18 | 6.2015e-11 | 1.7671e-10 | 5.0885e-18 | 1.6884e-10 | 2.9809e-11 | -5.7246e-18 | -1.6884e-10 | -2.9809e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0937 | 1.1 | 1.0978 | 1.0937 | -4.241e-12 | -120.3121 | 119.9447 | -4.2412e-12 | -120.3121 | 119.9447

## LL_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 1.455 | 1.455 | 0 | 1.455 | 1.455 | 0 | 0.33601 | 0.33601 | 0 | 0.33601 | 0.33601 | -3.5157e-17 | 0.28984 | 0.03533 | 2.8749e-27 | -0.24919 | 0.005316 | 2.9884e-16 | 0.073022 | 0.26569 | -2.9884e-16 | -0.030682 | -0.22336 | 0 | -142.8727 | 37.1273 | 0 | 37.1273 | -142.8727 | 0.95 | 0.88953 | 0.79769 | 0.95 | 0.74721 | 0.66491 | 5.5121e-10 | -128.7319 | 119.553 | 5.5121e-10 | -135.8534 | 128.4907
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3946e-18 | -9.6789e-10 | -2.6725e-09 | -4.3946e-18 | 9.6789e-10 | 2.6725e-09 | 8.7893e-17 | 2.8224e-09 | 1.3007e-10 | -8.7893e-17 | -2.8224e-09 | -1.3007e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.88953 | 0.79769 | 0.95 | 0.88953 | 0.79769 | 5.5121e-10 | -128.7319 | 119.553 | 5.5121e-10 | -128.7319 | 119.553
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.7893e-18 | -8.0657e-10 | -2.2271e-09 | 8.7893e-18 | 8.0657e-10 | 2.2271e-09 | 3.5157e-17 | 2.352e-09 | 1.0839e-10 | -5.2736e-17 | -2.352e-09 | -1.0839e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.88953 | 0.79769 | 0.95 | 0.88953 | 0.79769 | 5.5121e-10 | -128.7319 | 119.553 | 5.5121e-10 | -128.7319 | 119.553
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.3184e-17 | -4.8394e-10 | -1.3362e-09 | 2.1973e-17 | 4.8394e-10 | 1.3362e-09 | 3.5157e-17 | 1.4112e-09 | 6.5035e-11 | -3.5157e-17 | -1.4112e-09 | -6.5035e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.88953 | 0.79769 | 0.95 | 0.88953 | 0.79769 | 5.5121e-10 | -128.7319 | 119.553 | 5.5122e-10 | -128.7319 | 119.553
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3946e-18 | -1.6131e-10 | -4.4541e-10 | -4.3946e-18 | 1.6131e-10 | 4.4541e-10 | 1.7579e-17 | 4.7039e-10 | 2.1678e-11 | -1.7579e-17 | -4.7039e-10 | -2.1679e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.88953 | 0.79769 | 0.95 | 0.88953 | 0.79769 | 5.5121e-10 | -128.7319 | 119.553 | 5.5121e-10 | -128.7319 | 119.553
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.7893e-18 | -3.2263e-10 | -8.9083e-10 | 8.7893e-18 | 3.2263e-10 | 8.9083e-10 | 1.7579e-17 | 9.4079e-10 | 4.3357e-11 | 8.4558e-29 | -9.4079e-10 | -4.3357e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.88953 | 0.79769 | 0.95 | 0.88953 | 0.79769 | 5.5122e-10 | -128.7319 | 119.553 | 5.5122e-10 | -128.7319 | 119.553
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.6368e-17 | -1.6131e-10 | -4.4541e-10 | 2.6368e-17 | 1.6131e-10 | 4.4541e-10 | 1.7579e-17 | 4.7039e-10 | 2.1678e-11 | -1.7579e-17 | -4.7039e-10 | -2.1678e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.88953 | 0.79769 | 0.95 | 0.88953 | 0.79769 | 5.5122e-10 | -128.7319 | 119.553 | 5.5122e-10 | -128.7319 | 119.553
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.3184e-17 | -1.6131e-10 | -4.4541e-10 | -4.3946e-18 | 1.6131e-10 | 4.4541e-10 | 1.7579e-17 | 4.7039e-10 | 2.1678e-11 | -1.7579e-17 | -4.7039e-10 | -2.1679e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.88953 | 0.79769 | 0.95 | 0.88953 | 0.79769 | 5.5121e-10 | -128.7319 | 119.553 | 5.5121e-10 | -128.7319 | 119.553
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.3184e-17 | -1.6131e-10 | -4.4541e-10 | -4.3946e-18 | 1.6131e-10 | 4.4541e-10 | 1.7579e-17 | 4.7039e-10 | 2.1678e-11 | -1.7579e-17 | -4.7039e-10 | -2.1679e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.88953 | 0.79769 | 0.95 | 0.88953 | 0.79769 | 5.5121e-10 | -128.7319 | 119.553 | 5.5121e-10 | -128.7319 | 119.553
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3184e-17 | -1.2905e-09 | -3.5633e-09 | -2.1973e-17 | 1.2905e-09 | 3.5633e-09 | 8.7893e-17 | 3.7632e-09 | 1.7343e-10 | -7.0314e-17 | -3.7632e-09 | -1.7343e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.88953 | 0.79769 | 0.95 | 0.88953 | 0.79769 | 5.5121e-10 | -128.7319 | 119.553 | 5.5121e-10 | -128.7319 | 119.553
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.7893e-18 | -3.2263e-10 | -8.9083e-10 | -8.7893e-18 | 3.2263e-10 | 8.9083e-10 | 3.5157e-17 | 9.4079e-10 | 4.3357e-11 | -1.7579e-17 | -9.4079e-10 | -4.3357e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.88953 | 0.79769 | 0.95 | 0.88953 | 0.79769 | 5.5121e-10 | -128.7319 | 119.553 | 5.5121e-10 | -128.7319 | 119.553
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.7893e-18 | -3.2263e-10 | -8.9083e-10 | -8.7893e-18 | 3.2263e-10 | 8.9083e-10 | 3.5157e-17 | 9.4079e-10 | 4.3357e-11 | -1.7579e-17 | -9.4079e-10 | -4.3357e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.88953 | 0.79769 | 0.95 | 0.88953 | 0.79769 | 5.5121e-10 | -128.7319 | 119.553 | 5.5121e-10 | -128.7319 | 119.553
Line4_2_6 | 0 | 1.455 | 1.455 | 0 | 1.455 | 1.455 | 0 | 0.33601 | 0.33601 | 0 | 0.33601 | 0.33601 | -3.5157e-17 | 0.24919 | -0.005316 | 3.5157e-17 | -0.20855 | 0.045962 | 2.8126e-16 | 0.030682 | 0.22336 | -2.8126e-16 | 0.011658 | -0.18102 | 0 | -142.8727 | 37.1273 | 0 | 37.1273 | -142.8727 | 0.95 | 0.74721 | 0.66491 | 0.95 | 0.62161 | 0.55581 | 5.5121e-10 | -135.8534 | 128.4907 | 5.5122e-10 | -146.0722 | 141.3743
Line5_6_7 | 0 | 1.455 | 1.455 | 0 | 1.455 | 1.455 | 0 | 0.33601 | 0.33601 | 0 | 0.33601 | 0.33601 | -2.3676e-27 | 0.20855 | -0.045962 | 2.3676e-27 | -0.1679 | 0.086608 | 2.461e-16 | -0.011658 | 0.18102 | -2.461e-16 | 0.053997 | -0.13868 | 0 | -142.8727 | 37.1273 | 0 | 37.1273 | -142.8727 | 0.95 | 0.62161 | 0.55581 | 0.95 | 0.52489 | 0.48658 | 5.5122e-10 | -146.0722 | 141.3743 | 5.5122e-10 | -160.7007 | 159.1134
Line6_7_8 | 0 | 1.455 | 1.455 | 0 | 1.455 | 1.455 | 0 | 0.33601 | 0.33601 | 0 | 0.33601 | 0.33601 | 7.0314e-17 | 0.1679 | -0.086608 | -7.0314e-17 | -0.12725 | 0.12725 | 7.0314e-17 | -0.053997 | 0.13868 | -7.0314e-17 | 0.096337 | -0.096337 | 0 | -142.8727 | 37.1273 | 0 | 37.1273 | -142.8727 | 0.95 | 0.52489 | 0.48658 | 0.95 | 0.475 | 0.475 | 5.5122e-10 | -160.7007 | 159.1134 | 5.5122e-10 | 180 | 180
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.0314e-17 | -1.406e-16 | -1.4065e-16 | -1.4063e-16 | 1.4387e-16 | 4.2518e-16 | 6.7647e-28 | 1.4329e-09 | -1.4329e-09 | -7.0314e-17 | -1.4329e-09 | 1.4329e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.475 | 0.475 | 0.95 | 0.475 | 0.475 | 5.5122e-10 | 180 | 180 | 5.5122e-10 | -180 | 180
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.0314e-17 | -3.5126e-17 | -2.4126e-20 | 6.7647e-28 | 3.8402e-17 | 1.4393e-16 | 1.4063e-16 | 1.4329e-09 | -1.4329e-09 | -7.0314e-17 | -1.4329e-09 | 1.4329e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.475 | 0.475 | 0.95 | 0.475 | 0.475 | 5.5122e-10 | 180 | 180 | 5.5122e-10 | -180 | 180
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3946e-18 | -1.1292e-09 | -3.1179e-09 | -4.3946e-18 | 1.1292e-09 | 3.1179e-09 | 5.2736e-17 | 3.2928e-09 | 1.5175e-10 | -3.5157e-17 | -3.2928e-09 | -1.5175e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.88953 | 0.79769 | 0.95 | 0.88953 | 0.79769 | 5.5121e-10 | -128.7319 | 119.553 | 5.5121e-10 | -128.7319 | 119.553

## LL_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 1.3784 | 1.3784 | 0 | 1.3784 | 1.3784 | 0 | 0.31833 | 0.31833 | 0 | 0.31833 | 0.31833 | -1.6653e-17 | 0.26013 | 0.031709 | 1.6653e-17 | -0.22365 | 0.0047711 | 2.8311e-16 | 0.065537 | 0.23846 | -2.6645e-16 | -0.027537 | -0.20046 | 0 | -142.8727 | 37.1273 | 0 | 37.1273 | -142.8727 | 0.9 | 0.84271 | 0.7557 | 0.9 | 0.70788 | 0.62991 | 4.7387e-10 | -128.7319 | 119.553 | 4.7388e-10 | -135.8534 | 128.4907
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.6653e-17 | -8.6869e-10 | -2.3986e-09 | 1.6653e-17 | 8.6869e-10 | 2.3986e-09 | 6.6613e-17 | 2.5331e-09 | 1.1674e-10 | -4.996e-17 | -2.5331e-09 | -1.1674e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.84271 | 0.7557 | 0.9 | 0.84271 | 0.7557 | 4.7387e-10 | -128.7319 | 119.553 | 4.7388e-10 | -128.7319 | 119.553
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.0817e-17 | -7.2391e-10 | -1.9988e-09 | 2.0817e-17 | 7.2391e-10 | 1.9988e-09 | 6.6613e-17 | 2.1109e-09 | 9.7283e-11 | -4.996e-17 | -2.1109e-09 | -9.7283e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.84271 | 0.7557 | 0.9 | 0.84271 | 0.7557 | 4.7388e-10 | -128.7319 | 119.553 | 4.7388e-10 | -128.7319 | 119.553
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.3267e-18 | -4.3434e-10 | -1.1993e-09 | 8.3267e-18 | 4.3434e-10 | 1.1993e-09 | 1.6653e-17 | 1.2665e-09 | 5.837e-11 | 6.8868e-29 | -1.2665e-09 | -5.837e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.84271 | 0.7557 | 0.9 | 0.84271 | 0.7557 | 4.7388e-10 | -128.7319 | 119.553 | 4.7388e-10 | -128.7319 | 119.553
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.7547e-28 | -1.4478e-10 | -3.9976e-10 | 2.7547e-28 | 1.4478e-10 | 3.9976e-10 | 3.3307e-17 | 4.2218e-10 | 1.9457e-11 | -3.3307e-17 | -4.2218e-10 | -1.9457e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.84271 | 0.7557 | 0.9 | 0.84271 | 0.7557 | 4.7388e-10 | -128.7319 | 119.553 | 4.7388e-10 | -128.7319 | 119.553
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.1321e-28 | -2.8956e-10 | -7.9952e-10 | 4.1321e-28 | 2.8956e-10 | 7.9952e-10 | 4.996e-17 | 8.4436e-10 | 3.8913e-11 | -4.996e-17 | -8.4436e-10 | -3.8913e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.84271 | 0.7557 | 0.9 | 0.84271 | 0.7557 | 4.7388e-10 | -128.7319 | 119.553 | 4.7388e-10 | -128.7319 | 119.553
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.4478e-10 | -3.9976e-10 | -1.3774e-28 | 1.4478e-10 | 3.9976e-10 | 0 | 4.2218e-10 | 1.9457e-11 | 1.6653e-17 | -4.2218e-10 | -1.9457e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.84271 | 0.7557 | 0.9 | 0.84271 | 0.7557 | 4.7388e-10 | -128.7319 | 119.553 | 4.7388e-10 | -128.7319 | 119.553
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.1633e-18 | -1.4478e-10 | -3.9976e-10 | 4.1633e-18 | 1.4478e-10 | 3.9976e-10 | -1.6653e-17 | 4.2218e-10 | 1.9457e-11 | 1.6653e-17 | -4.2218e-10 | -1.9457e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.84271 | 0.7557 | 0.9 | 0.84271 | 0.7557 | 4.7387e-10 | -128.7319 | 119.553 | 4.7387e-10 | -128.7319 | 119.553
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.1633e-18 | -1.4478e-10 | -3.9976e-10 | 4.1633e-18 | 1.4478e-10 | 3.9976e-10 | -1.6653e-17 | 4.2218e-10 | 1.9457e-11 | 1.6653e-17 | -4.2218e-10 | -1.9457e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.84271 | 0.7557 | 0.9 | 0.84271 | 0.7557 | 4.7387e-10 | -128.7319 | 119.553 | 4.7387e-10 | -128.7319 | 119.553
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.1633e-18 | -1.1582e-09 | -3.1981e-09 | 4.1633e-18 | 1.1582e-09 | 3.1981e-09 | 9.992e-17 | 3.3775e-09 | 1.5565e-10 | -8.3267e-17 | -3.3775e-09 | -1.5565e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.84271 | 0.7557 | 0.9 | 0.84271 | 0.7557 | 4.7387e-10 | -128.7319 | 119.553 | 4.7387e-10 | -128.7319 | 119.553
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.3267e-18 | -2.8956e-10 | -7.9952e-10 | 8.3267e-18 | 2.8956e-10 | 7.9952e-10 | 4.996e-17 | 8.4436e-10 | 3.8913e-11 | -4.996e-17 | -8.4436e-10 | -3.8913e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.84271 | 0.7557 | 0.9 | 0.84271 | 0.7557 | 4.7387e-10 | -128.7319 | 119.553 | 4.7387e-10 | -128.7319 | 119.553
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.3267e-18 | -2.8956e-10 | -7.9952e-10 | 8.3267e-18 | 2.8956e-10 | 7.9952e-10 | 4.996e-17 | 8.4436e-10 | 3.8913e-11 | -4.996e-17 | -8.4436e-10 | -3.8913e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.84271 | 0.7557 | 0.9 | 0.84271 | 0.7557 | 4.7387e-10 | -128.7319 | 119.553 | 4.7387e-10 | -128.7319 | 119.553
Line4_2_6 | 0 | 1.3784 | 1.3784 | 0 | 1.3784 | 1.3784 | 0 | 0.31833 | 0.31833 | 0 | 0.31833 | 0.31833 | -2.2038e-27 | 0.22365 | -0.0047711 | -3.3307e-17 | -0.18717 | 0.041251 | 2.6645e-16 | 0.027537 | 0.20046 | -2.6645e-16 | 0.010463 | -0.16246 | 0 | -142.8727 | 37.1273 | 0 | 37.1273 | -142.8727 | 0.9 | 0.70788 | 0.62991 | 0.9 | 0.5889 | 0.52656 | 4.7388e-10 | -135.8534 | 128.4907 | 4.7388e-10 | -146.0722 | 141.3743
Line5_6_7 | 0 | 1.3784 | 1.3784 | 0 | 1.3784 | 1.3784 | 0 | 0.31833 | 0.31833 | 0 | 0.31833 | 0.31833 | 3.3307e-17 | 0.18717 | -0.041251 | -9.992e-17 | -0.15069 | 0.077731 | 1.9984e-16 | -0.010463 | 0.16246 | -1.9984e-16 | 0.048463 | -0.12446 | 0 | -142.8727 | 37.1273 | 0 | 37.1273 | -142.8727 | 0.9 | 0.5889 | 0.52656 | 0.9 | 0.49726 | 0.46097 | 4.7388e-10 | -146.0722 | 141.3743 | 4.7389e-10 | -160.7007 | 159.1134
Line6_7_8 | 0 | 1.3784 | 1.3784 | 0 | 1.3784 | 1.3784 | 0 | 0.31833 | 0.31833 | 0 | 0.31833 | 0.31833 | -6.6613e-17 | 0.15069 | -0.077731 | 1.1019e-27 | -0.11421 | 0.11421 | 1.3323e-16 | -0.048463 | 0.12446 | -1.3323e-16 | 0.086463 | -0.086463 | 0 | -142.8727 | 37.1273 | 0 | 37.1273 | -142.8727 | 0.9 | 0.49726 | 0.46097 | 0.9 | 0.45 | 0.45 | 4.7389e-10 | -160.7007 | 159.1134 | 4.7389e-10 | 180 | 180
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.6613e-17 | 1.9986e-16 | -1.3324e-16 | -6.6613e-17 | -1.9692e-16 | 1.3619e-16 | 6.6613e-17 | 1.286e-09 | -1.286e-09 | -6.6613e-17 | -1.286e-09 | 1.286e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.45 | 0.45 | 0.9 | 0.45 | 0.45 | 4.7389e-10 | 180 | 180 | 4.7389e-10 | -180 | 180
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.6613e-17 | -9.9896e-17 | 1.3321e-16 | -6.6613e-17 | 1.0284e-16 | -1.3027e-16 | 6.6613e-17 | 1.286e-09 | -1.286e-09 | -6.6613e-17 | -1.286e-09 | 1.286e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.45 | 0.45 | 0.9 | 0.45 | 0.45 | 4.7389e-10 | 180 | 180 | 4.7389e-10 | -180 | 180
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.498e-17 | -1.0135e-09 | -2.7983e-09 | -1.6653e-17 | 1.0135e-09 | 2.7983e-09 | 4.996e-17 | 2.9553e-09 | 1.362e-10 | -3.3307e-17 | -2.9553e-09 | -1.362e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.84271 | 0.7557 | 0.9 | 0.84271 | 0.7557 | 4.7387e-10 | -128.7319 | 119.553 | 4.7387e-10 | -128.7319 | 119.553

## LL_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0.051843 | 0.051843 | 0 | 0.051843 | 0.051843 | 0 | 0.011973 | 0.011973 | 0 | 0.011973 | 0.011973 | 2.7466e-18 | 0.010966 | 0.0028847 | -2.7466e-18 | -0.010915 | -0.0028331 | 8.7893e-18 | 0.0029326 | 0.010936 | -8.7893e-18 | -0.0028788 | -0.010882 | 0 | -135.2796 | 44.7204 | 0 | 44.7204 | -135.2796 | 0.95 | 0.94815 | 0.94465 | 0.95 | 0.94283 | 0.93921 | 1.2699e-11 | -120.3084 | 119.9432 | 1.2699e-11 | -120.5043 | 120.1275
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3733e-19 | -3.8309e-11 | -1.1119e-10 | 1.3733e-19 | 3.8309e-11 | 1.1119e-10 | 2.1973e-18 | 1.0665e-10 | 1.9584e-11 | -2.1973e-18 | -1.0665e-10 | -1.9584e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94815 | 0.94465 | 0.95 | 0.94815 | 0.94465 | 1.2699e-11 | -120.3084 | 119.9432 | 1.2699e-11 | -120.3084 | 119.9432
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.9266e-19 | -3.1925e-11 | -9.2658e-11 | -6.18e-19 | 3.1925e-11 | 9.2658e-11 | 2.1973e-18 | 8.8872e-11 | 1.632e-11 | -2.1973e-18 | -8.8872e-11 | -1.632e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94815 | 0.94465 | 0.95 | 0.94815 | 0.94465 | 1.2699e-11 | -120.3084 | 119.9432 | 1.2699e-11 | -120.3084 | 119.9432
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.3733e-19 | -1.9155e-11 | -5.5595e-11 | 1.3733e-19 | 1.9155e-11 | 5.5595e-11 | 1.648e-18 | 5.3323e-11 | 9.7921e-12 | -2.1973e-18 | -5.3323e-11 | -9.7921e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94815 | 0.94465 | 0.95 | 0.94815 | 0.94465 | 1.2699e-11 | -120.3084 | 119.9432 | 1.2699e-11 | -120.3084 | 119.9432
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.06e-19 | -6.3849e-12 | -1.8532e-11 | -2.06e-19 | 6.3849e-12 | 1.8532e-11 | 4.5658e-32 | 1.7774e-11 | 3.264e-12 | -1.0987e-18 | -1.7774e-11 | -3.264e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94815 | 0.94465 | 0.95 | 0.94815 | 0.94465 | 1.2699e-11 | -120.3084 | 119.9432 | 1.2699e-11 | -120.3084 | 119.9432
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.03e-18 | -1.277e-11 | -3.7063e-11 | 1.03e-18 | 1.277e-11 | 3.7063e-11 | 5.4933e-19 | 3.5549e-11 | 6.5281e-12 | -5.4933e-19 | -3.5549e-11 | -6.5281e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94815 | 0.94465 | 0.95 | 0.94815 | 0.94465 | 1.2699e-11 | -120.3084 | 119.9432 | 1.2699e-11 | -120.3084 | 119.9432
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.0987e-18 | -6.3849e-12 | -1.8532e-11 | 1.0987e-18 | 6.3849e-12 | 1.8532e-11 | -2.4351e-31 | 1.7774e-11 | 3.264e-12 | 2.4351e-31 | -1.7775e-11 | -3.264e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94815 | 0.94465 | 0.95 | 0.94815 | 0.94465 | 1.2699e-11 | -120.3084 | 119.9432 | 1.2699e-11 | -120.3084 | 119.9432
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.2399e-19 | -6.3849e-12 | -1.8532e-11 | 8.2399e-19 | 6.3849e-12 | 1.8532e-11 | 1.0987e-18 | 1.7774e-11 | 3.264e-12 | -5.4933e-19 | -1.7774e-11 | -3.264e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94815 | 0.94465 | 0.95 | 0.94815 | 0.94465 | 1.2699e-11 | -120.3084 | 119.9432 | 1.2699e-11 | -120.3084 | 119.9432
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.2399e-19 | -6.3849e-12 | -1.8532e-11 | 8.2399e-19 | 6.3849e-12 | 1.8532e-11 | 1.0987e-18 | 1.7774e-11 | 3.264e-12 | -5.4933e-19 | -1.7774e-11 | -3.264e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94815 | 0.94465 | 0.95 | 0.94815 | 0.94465 | 1.2699e-11 | -120.3084 | 119.9432 | 1.2699e-11 | -120.3084 | 119.9432
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5107e-18 | -5.1079e-11 | -1.4825e-10 | -1.7853e-18 | 5.1079e-11 | 1.4825e-10 | 2.1973e-18 | 1.422e-10 | 2.6112e-11 | -2.7466e-18 | -1.422e-10 | -2.6112e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94815 | 0.94465 | 0.95 | 0.94815 | 0.94465 | 1.2699e-11 | -120.3084 | 119.9432 | 1.2699e-11 | -120.3084 | 119.9432
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4333e-19 | -1.277e-11 | -3.7063e-11 | -6.18e-19 | 1.277e-11 | 3.7063e-11 | 1.648e-18 | 3.5549e-11 | 6.5281e-12 | -1.648e-18 | -3.5549e-11 | -6.5281e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94815 | 0.94465 | 0.95 | 0.94815 | 0.94465 | 1.2699e-11 | -120.3084 | 119.9432 | 1.2699e-11 | -120.3084 | 119.9432
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4333e-19 | -1.277e-11 | -3.7063e-11 | -6.18e-19 | 1.277e-11 | 3.7063e-11 | 1.648e-18 | 3.5549e-11 | 6.5281e-12 | -1.648e-18 | -3.5549e-11 | -6.5281e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94815 | 0.94465 | 0.95 | 0.94815 | 0.94465 | 1.2699e-11 | -120.3084 | 119.9432 | 1.2699e-11 | -120.3084 | 119.9432
Line4_2_6 | 0 | 0.051843 | 0.051843 | 0 | 0.051843 | 0.051843 | 0 | 0.011973 | 0.011973 | 0 | 0.011973 | 0.011973 | 3.296e-18 | 0.010915 | 0.0028331 | -3.296e-18 | -0.010863 | -0.0027815 | 8.7893e-18 | 0.0028788 | 0.010882 | -8.7893e-18 | -0.0028251 | -0.010828 | 0 | -135.2796 | 44.7204 | 0 | 44.7204 | -135.2796 | 0.95 | 0.94283 | 0.93921 | 0.95 | 0.93752 | 0.93379 | 1.2699e-11 | -120.5043 | 120.1275 | 1.2699e-11 | -120.7024 | 120.3141
Line5_6_7 | 0 | 0.051843 | 0.051843 | 0 | 0.051843 | 0.051843 | 0 | 0.011973 | 0.011973 | 0 | 0.011973 | 0.011973 | 3.296e-18 | 0.010863 | 0.0027815 | -3.296e-18 | -0.010812 | -0.0027299 | 1.0987e-17 | 0.0028251 | 0.010828 | -1.0987e-17 | -0.0027713 | -0.010775 | 0 | -135.2796 | 44.7204 | 0 | 44.7204 | -135.2796 | 0.95 | 0.93752 | 0.93379 | 0.95 | 0.93223 | 0.92837 | 1.2699e-11 | -120.7024 | 120.3141 | 1.27e-11 | -120.9028 | 120.5028
Line6_7_8 | 0 | 0.051843 | 0.051843 | 0 | 0.051843 | 0.051843 | 0 | 0.011973 | 0.011973 | 0 | 0.011973 | 0.011973 | 2.1973e-18 | 0.010812 | 0.0027299 | -4.3946e-18 | -0.01076 | -0.0026783 | 4.3946e-18 | 0.0027713 | 0.010775 | -4.3946e-18 | -0.0027175 | -0.010721 | 0 | -135.2796 | 44.7204 | 0 | 44.7204 | -135.2796 | 0.95 | 0.93223 | 0.92837 | 0.95 | 0.92694 | 0.92297 | 1.27e-11 | -120.9028 | 120.5028 | 1.27e-11 | -121.1055 | 120.6937
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.8704e-31 | -7.7759e-11 | -9.1252e-11 | -2.1973e-18 | 7.7759e-11 | 9.1252e-11 | 2.1973e-18 | 6.2294e-11 | -3.8923e-11 | -4.8704e-31 | -6.2294e-11 | 3.8923e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.92694 | 0.92297 | 0.95 | 0.92694 | 0.92297 | 1.27e-11 | -121.1055 | 120.6937 | 1.27e-11 | -121.1055 | 120.6937
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.7759e-11 | -9.1252e-11 | -2.1973e-18 | 7.7759e-11 | 9.1252e-11 | 0 | 6.2294e-11 | -3.8923e-11 | -4.8704e-31 | -6.2294e-11 | 3.8923e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.92694 | 0.92297 | 0.95 | 0.92694 | 0.92297 | 1.27e-11 | -121.1055 | 120.6937 | 1.27e-11 | -121.1055 | 120.6937
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5793e-18 | -4.4694e-11 | -1.2972e-10 | -1.5793e-18 | 4.4694e-11 | 1.2972e-10 | 2.7466e-18 | 1.2442e-10 | 2.2848e-11 | -3.296e-18 | -1.2442e-10 | -2.2848e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94815 | 0.94465 | 0.95 | 0.94815 | 0.94465 | 1.2699e-11 | -120.3084 | 119.9432 | 1.2699e-11 | -120.3084 | 119.9432

## LL_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0.049114 | 0.049114 | 0 | 0.049114 | 0.049114 | 0 | 0.011342 | 0.011342 | 0 | 0.011342 | 0.011342 | 1.5613e-18 | 0.0098425 | 0.002589 | -1.5613e-18 | -0.0097961 | -0.0025427 | 9.3675e-18 | 0.002632 | 0.009815 | -8.3267e-18 | -0.0025837 | -0.0097667 | 0 | -135.2796 | 44.7204 | 0 | 44.7204 | -135.2796 | 0.9 | 0.89825 | 0.89493 | 0.9 | 0.89321 | 0.88978 | 1.6807e-11 | -120.3084 | 119.9432 | 1.6807e-11 | -120.5043 | 120.1275
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.6329e-31 | -3.4383e-11 | -9.9793e-11 | 2.6021e-19 | 3.4383e-11 | 9.9793e-11 | 2.6021e-18 | 9.5716e-11 | 1.7577e-11 | -2.0817e-18 | -9.5716e-11 | -1.7577e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89825 | 0.89493 | 0.9 | 0.89825 | 0.89493 | 1.6807e-11 | -120.3084 | 119.9432 | 1.6807e-11 | -120.3084 | 119.9432
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.6021e-19 | -2.8652e-11 | -8.3161e-11 | 2.6021e-19 | 2.8652e-11 | 8.3161e-11 | 3.1225e-18 | 7.9764e-11 | 1.4648e-11 | -2.6021e-18 | -7.9764e-11 | -1.4648e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89825 | 0.89493 | 0.9 | 0.89825 | 0.89493 | 1.6807e-11 | -120.3084 | 119.9432 | 1.6807e-11 | -120.3084 | 119.9432
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.301e-19 | -1.7191e-11 | -4.9896e-11 | -1.301e-19 | 1.7191e-11 | 4.9896e-11 | 3.8165e-32 | 4.7858e-11 | 8.7885e-12 | -5.2042e-19 | -4.7858e-11 | -8.7885e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89825 | 0.89493 | 0.9 | 0.89825 | 0.89493 | 1.6807e-11 | -120.3084 | 119.9432 | 1.6807e-11 | -120.3084 | 119.9432
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.5052e-20 | -5.7305e-12 | -1.6632e-11 | 6.5052e-20 | 5.7305e-12 | 1.6632e-11 | -5.2042e-19 | 1.5953e-11 | 2.9295e-12 | -5.2042e-19 | -1.5953e-11 | -2.9295e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89825 | 0.89493 | 0.9 | 0.89825 | 0.89493 | 1.6807e-11 | -120.3084 | 119.9432 | 1.6807e-11 | -120.3084 | 119.9432
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.9516e-19 | -1.1461e-11 | -3.3264e-11 | 4.5536e-19 | 1.1461e-11 | 3.3264e-11 | 5.2042e-19 | 3.1905e-11 | 5.859e-12 | -5.2042e-19 | -3.1905e-11 | -5.859e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89825 | 0.89493 | 0.9 | 0.89825 | 0.89493 | 1.6807e-11 | -120.3084 | 119.9432 | 1.6807e-11 | -120.3084 | 119.9432
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.1557e-19 | -5.7305e-12 | -1.6632e-11 | 9.7578e-19 | 5.7305e-12 | 1.6632e-11 | -2.0991e-31 | 1.5953e-11 | 2.9295e-12 | 2.8624e-31 | -1.5953e-11 | -2.9295e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89825 | 0.89493 | 0.9 | 0.89825 | 0.89493 | 1.6807e-11 | -120.3084 | 119.9432 | 1.6807e-11 | -120.3084 | 119.9432
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.2042e-19 | -5.7305e-12 | -1.6632e-11 | 1.9516e-19 | 5.7305e-12 | 1.6632e-11 | -1.5266e-31 | 1.5953e-11 | 2.9295e-12 | 5.7246e-32 | -1.5953e-11 | -2.9295e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89825 | 0.89493 | 0.9 | 0.89825 | 0.89493 | 1.6807e-11 | -120.3084 | 119.9432 | 1.6807e-11 | -120.3084 | 119.9432
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.2042e-19 | -5.7305e-12 | -1.6632e-11 | 1.9516e-19 | 5.7305e-12 | 1.6632e-11 | -1.5266e-31 | 1.5953e-11 | 2.9295e-12 | 5.7246e-32 | -1.5953e-11 | -2.9295e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89825 | 0.89493 | 0.9 | 0.89825 | 0.89493 | 1.6807e-11 | -120.3084 | 119.9432 | 1.6807e-11 | -120.3084 | 119.9432
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.301e-18 | -4.5844e-11 | -1.3306e-10 | -1.301e-18 | 4.5844e-11 | 1.3306e-10 | 1.5613e-18 | 1.2762e-10 | 2.3436e-11 | -1.5613e-18 | -1.2762e-10 | -2.3436e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89825 | 0.89493 | 0.9 | 0.89825 | 0.89493 | 1.6807e-11 | -120.3084 | 119.9432 | 1.6807e-11 | -120.3084 | 119.9432
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.5536e-19 | -1.1461e-11 | -3.3264e-11 | 1.301e-19 | 1.1461e-11 | 3.3264e-11 | 1.0408e-18 | 3.1905e-11 | 5.859e-12 | -1.0408e-18 | -3.1905e-11 | -5.859e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89825 | 0.89493 | 0.9 | 0.89825 | 0.89493 | 1.6807e-11 | -120.3084 | 119.9432 | 1.6807e-11 | -120.3084 | 119.9432
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.5536e-19 | -1.1461e-11 | -3.3264e-11 | 1.301e-19 | 1.1461e-11 | 3.3264e-11 | 1.0408e-18 | 3.1905e-11 | 5.859e-12 | -1.0408e-18 | -3.1905e-11 | -5.859e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89825 | 0.89493 | 0.9 | 0.89825 | 0.89493 | 1.6807e-11 | -120.3084 | 119.9432 | 1.6807e-11 | -120.3084 | 119.9432
Line4_2_6 | 0 | 0.049114 | 0.049114 | 0 | 0.049114 | 0.049114 | 0 | 0.011342 | 0.011342 | 0 | 0.011342 | 0.011342 | -3.0532e-30 | 0.0097961 | 0.0025427 | 1.0408e-18 | -0.0097498 | -0.0024964 | 1.0408e-17 | 0.0025837 | 0.0097667 | -9.3675e-18 | -0.0025355 | -0.0097185 | 0 | -135.2796 | 44.7204 | 0 | 44.7204 | -135.2796 | 0.9 | 0.89321 | 0.88978 | 0.9 | 0.88818 | 0.88464 | 1.6807e-11 | -120.5043 | 120.1275 | 1.6807e-11 | -120.7024 | 120.3141
Line5_6_7 | 0 | 0.049114 | 0.049114 | 0 | 0.049114 | 0.049114 | 0 | 0.011342 | 0.011342 | 0 | 0.011342 | 0.011342 | 4.1633e-18 | 0.0097498 | 0.0024964 | -4.1633e-18 | -0.0097035 | -0.0024501 | 6.245e-18 | 0.0025355 | 0.0097185 | -6.245e-18 | -0.0024873 | -0.0096702 | 0 | -135.2796 | 44.7204 | 0 | 44.7204 | -135.2796 | 0.9 | 0.88818 | 0.88464 | 0.9 | 0.88316 | 0.87951 | 1.6807e-11 | -120.7024 | 120.3141 | 1.6807e-11 | -120.9028 | 120.5028
Line6_7_8 | 0 | 0.049114 | 0.049114 | 0 | 0.049114 | 0.049114 | 0 | 0.011342 | 0.011342 | 0 | 0.011342 | 0.011342 | -2.0817e-18 | 0.0097035 | 0.0024501 | 1.8319e-30 | -0.0096572 | -0.0024038 | 6.245e-18 | 0.0024873 | 0.0096702 | -6.245e-18 | -0.002439 | -0.009622 | 0 | -135.2796 | 44.7204 | 0 | 44.7204 | -135.2796 | 0.9 | 0.88316 | 0.87951 | 0.9 | 0.87816 | 0.87439 | 1.6807e-11 | -120.9028 | 120.5028 | 1.6807e-11 | -121.1055 | 120.6937
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0817e-18 | -6.9789e-11 | -8.1899e-11 | -4.1633e-18 | 6.9789e-11 | 8.1899e-11 | 2.0817e-18 | 5.5909e-11 | -3.4934e-11 | -4.1633e-18 | -5.5909e-11 | 3.4934e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.87816 | 0.87439 | 0.9 | 0.87816 | 0.87439 | 1.6807e-11 | -121.1055 | 120.6937 | 1.6807e-11 | -121.1055 | 120.6937
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.9789e-11 | -8.1899e-11 | 6.1065e-31 | 6.9789e-11 | 8.1899e-11 | 0 | 5.5909e-11 | -3.4934e-11 | -2.0817e-18 | -5.5909e-11 | 3.4934e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.87816 | 0.87439 | 0.9 | 0.87816 | 0.87439 | 1.6807e-11 | -121.1055 | 120.6937 | 1.6808e-11 | -121.1055 | 120.6937
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4568e-19 | -4.0113e-11 | -1.1643e-10 | -5.8547e-19 | 4.0113e-11 | 1.1643e-10 | 2.0817e-18 | 1.1167e-10 | 2.0507e-11 | -2.6021e-18 | -1.1167e-10 | -2.0507e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89825 | 0.89493 | 0.9 | 0.89825 | 0.89493 | 1.6807e-11 | -120.3084 | 119.9432 | 1.6807e-11 | -120.3084 | 119.9432

## LG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.00029361 | 2.2874e-06 | 2.2874e-06 | 0.00029323 | 1.907e-06 | 1.907e-06 | 6.7806e-05 | 5.2825e-07 | 5.2825e-07 | 6.7718e-05 | 4.4039e-07 | 4.4039e-07 | 2.859e-09 | 5.1626e-07 | -4.4352e-07 | -2.1406e-09 | -4.3628e-07 | 3.6354e-07 | 5.7208e-09 | -8.1015e-07 | -8.5212e-07 | -4.2834e-09 | 6.7162e-07 | 7.136e-07 | -89.8316 | -92.504 | -92.504 | 90.1686 | 86.9956 | 86.9956 |  | 9.4319e-05 | 1.8186 | 1.8185 | 7.0712e-05 | 1.8186 | 1.8185 | -26.3853 | -149.997 | 149.9994 | -26.3843 | -149.9969 | 149.9994
Line10_11_12 | 2.2873e-06 | 2.2873e-06 | 2.2873e-06 | 1.9069e-06 | 1.9069e-06 | 1.9069e-06 | 5.2824e-07 | 5.2824e-07 | 5.2824e-07 | 4.4039e-07 | 4.4039e-07 | 4.4039e-07 | 2.0109e-11 | 5.1625e-07 | -4.4352e-07 | -1.6414e-11 | -4.3627e-07 | 3.6354e-07 | 4.5436e-11 | -8.1014e-07 | -8.5211e-07 | -3.7984e-11 | 6.7162e-07 | 7.1359e-07 | -92.5038 | -92.5037 | -92.5037 | 86.9958 | 86.9959 | 86.9959 |  | 9.4061e-05 | 1.8186 | 1.8185 | 9.396e-05 | 1.8186 | 1.8185 | -26.3774 | -149.997 | 149.9994 | -26.3742 | -149.997 | 149.9994
Line11_12_13 | 1.9061e-06 | 1.9061e-06 | 1.9061e-06 | 1.5257e-06 | 1.5257e-06 | 1.5257e-06 | 4.402e-07 | 4.402e-07 | 4.402e-07 | 3.5235e-07 | 3.5235e-07 | 3.5235e-07 | 1.6738e-11 | 4.3021e-07 | -3.696e-07 | -1.3053e-11 | -3.5023e-07 | 2.8962e-07 | 3.7823e-11 | -6.7512e-07 | -7.1009e-07 | -3.0393e-11 | 5.3659e-07 | 5.7157e-07 | -92.5038 | -92.5037 | -92.5037 | 86.8708 | 86.8709 | 86.8709 |  | 9.396e-05 | 1.8186 | 1.8185 | 9.3877e-05 | 1.8186 | 1.8185 | -26.3742 | -149.997 | 149.9994 | -26.3716 | -149.997 | 149.9994
Line12_13_15 | 1.1437e-06 | 1.1437e-06 | 1.1437e-06 | 0 | 0 | 0 | 2.6412e-07 | 2.6412e-07 | 2.6412e-07 | 0 | 0 | 0 | 1.0033e-11 | 2.5812e-07 | -2.2176e-07 | -6.3611e-12 | -1.7815e-07 | 1.4178e-07 | 2.2674e-11 | -4.0507e-07 | -4.2605e-07 | -1.5269e-11 | 2.6655e-07 | 2.8754e-07 | -92.5038 | -92.5037 | -92.5037 | 0 | 0 | 0 |  | 9.3877e-05 | 1.8186 | 1.8185 | 9.3831e-05 | 1.8186 | 1.8185 | -26.3716 | -149.997 | 149.9994 | -26.37 | -149.997 | 149.9994
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3442e-12 | 8.6042e-08 | -7.392e-08 | 3.2375e-13 | -6.0628e-09 | -6.0625e-09 | 7.5581e-12 | -1.3502e-07 | -1.4202e-07 | -1.6052e-13 | -3.5004e-09 | 3.5006e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 9.3877e-05 | 1.8186 | 1.8185 | 9.3868e-05 | 1.8186 | 1.8185 | -26.3716 | -149.997 | 149.9994 | -26.3711 | -149.997 | 149.9994
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.6847e-12 | 1.7208e-07 | -1.4784e-07 | -3.0177e-12 | -9.2104e-08 | 6.7857e-08 | 1.5109e-11 | -2.7005e-07 | -2.8404e-07 | -7.7127e-12 | 1.3152e-07 | 1.4552e-07 | 0 | 0 | 0 | 0 | 0 | 0 |  | 9.3831e-05 | 1.8186 | 1.8185 | 9.3803e-05 | 1.8186 | 1.8185 | -26.37 | -149.997 | 149.9994 | -26.369 | -149.997 | 149.9994
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3412e-12 | 8.6042e-08 | -7.392e-08 | 3.235e-13 | -6.0628e-09 | -6.0625e-09 | 7.5523e-12 | -1.3502e-07 | -1.4202e-07 | -1.6038e-13 | -3.5004e-09 | 3.5006e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 9.3803e-05 | 1.8186 | 1.8185 | 9.3794e-05 | 1.8186 | 1.8185 | -26.369 | -149.997 | 149.9994 | -26.3685 | -149.997 | 149.9994
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3607e-12 | 8.6042e-08 | -7.392e-08 | 3.2514e-13 | -6.0628e-09 | -6.0625e-09 | 7.5908e-12 | -1.3502e-07 | -1.4202e-07 | -1.613e-13 | -3.5004e-09 | 3.5006e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 9.4292e-05 | 1.8186 | 1.8185 | 9.4282e-05 | 1.8186 | 1.8185 | -26.3842 | -149.997 | 149.9994 | -26.3837 | -149.997 | 149.9994
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3607e-12 | 8.6042e-08 | -7.392e-08 | 3.2514e-13 | -6.0628e-09 | -6.0625e-09 | 7.5908e-12 | -1.3502e-07 | -1.4202e-07 | -1.613e-13 | -3.5004e-09 | 3.5006e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 9.4292e-05 | 1.8186 | 1.8185 | 9.4282e-05 | 1.8186 | 1.8185 | -26.3842 | -149.997 | 149.9994 | -26.3837 | -149.997 | 149.9994
Line1_1_3 | 3.0498e-06 | 3.0498e-06 | 3.0498e-06 | 2.6694e-06 | 2.6694e-06 | 2.6694e-06 | 7.0432e-07 | 7.0432e-07 | 7.0432e-07 | 6.1646e-07 | 6.1646e-07 | 6.1646e-07 | 2.6894e-11 | 6.8833e-07 | -5.9136e-07 | -2.3169e-11 | -6.0835e-07 | 5.1138e-07 | 6.0744e-11 | -1.0802e-06 | -1.1361e-06 | -5.3236e-11 | 9.4166e-07 | 9.9763e-07 | -92.5038 | -92.5037 | -92.5037 | 87.1388 | 87.1388 | 87.1388 |  | 9.4319e-05 | 1.8186 | 1.8185 | 9.4181e-05 | 1.8186 | 1.8185 | -26.3853 | -149.997 | 149.9994 | -26.3811 | -149.997 | 149.9994
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7236e-12 | 1.7208e-07 | -1.4784e-07 | -3.0355e-12 | -9.2104e-08 | 6.7857e-08 | 1.5186e-11 | -2.7005e-07 | -2.8404e-07 | -7.7521e-12 | 1.3152e-07 | 1.4552e-07 | 0 | 0 | 0 | 0 | 0 | 0 |  | 9.4319e-05 | 1.8186 | 1.8185 | 9.4292e-05 | 1.8186 | 1.8185 | -26.3853 | -149.997 | 149.9994 | -26.3842 | -149.997 | 149.9994
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7236e-12 | 1.7208e-07 | -1.4784e-07 | -3.0355e-12 | -9.2104e-08 | 6.7857e-08 | 1.5186e-11 | -2.7005e-07 | -2.8404e-07 | -7.7521e-12 | 1.3152e-07 | 1.4552e-07 | 0 | 0 | 0 | 0 | 0 | 0 |  | 9.4319e-05 | 1.8186 | 1.8185 | 9.4292e-05 | 1.8186 | 1.8185 | -26.3853 | -149.997 | 149.9994 | -26.3842 | -149.997 | 149.9994
Line4_2_6 | 0.00029323 | 1.9061e-06 | 1.9061e-06 | 0.00029285 | 1.5257e-06 | 1.5257e-06 | 6.7718e-05 | 4.4021e-07 | 4.4021e-07 | 6.763e-05 | 3.5235e-07 | 3.5235e-07 | 2.1408e-09 | 4.3022e-07 | -3.696e-07 | -1.4247e-09 | -3.5024e-07 | 2.8962e-07 | 4.2833e-09 | -6.7512e-07 | -7.101e-07 | -2.8507e-09 | 5.366e-07 | 5.7158e-07 | -89.8282 | -92.504 | -92.504 | 90.1721 | 86.8706 | 86.8706 |  | 7.0712e-05 | 1.8186 | 1.8185 | 4.7123e-05 | 1.8186 | 1.8185 | -26.3843 | -149.9969 | 149.9994 | -26.3833 | -149.9968 | 149.9994
Line5_6_7 | 0.00029285 | 1.5249e-06 | 1.5249e-06 | 0.00029247 | 1.1445e-06 | 1.1445e-06 | 6.763e-05 | 3.5217e-07 | 3.5217e-07 | 6.7542e-05 | 2.6432e-07 | 2.6432e-07 | 1.4249e-09 | 3.4418e-07 | -2.9568e-07 | -7.1124e-10 | -2.642e-07 | 2.157e-07 | 2.8506e-09 | -5.401e-07 | -5.6808e-07 | -1.4229e-09 | 4.0157e-07 | 4.2956e-07 | -89.8247 | -92.504 | -92.504 | 90.1756 | 86.6623 | 86.6623 |  | 4.7123e-05 | 1.8186 | 1.8185 | 2.3552e-05 | 1.8186 | 1.8185 | -26.3833 | -149.9968 | 149.9994 | -26.3825 | -149.9966 | 149.9994
Line6_7_8 | 0.00029247 | 1.1437e-06 | 1.1437e-06 | 0.00029208 | 0 | 0 | 6.7542e-05 | 2.6412e-07 | 2.6412e-07 | 6.7454e-05 | 0 | 0 | 7.1132e-10 | 2.5813e-07 | -2.2176e-07 | -1.6837e-14 | -1.7815e-07 | 1.4178e-07 | 1.4229e-09 | -4.0507e-07 | -4.2606e-07 | 2.1947e-15 | 2.6655e-07 | 2.8754e-07 | -89.8212 | -92.5041 | -92.5041 | 90.1791 | 0 | 0 |  | 2.3552e-05 | 1.8186 | 1.8185 | 0 | 1.8186 | 1.8185 | -26.3825 | -149.9966 | 149.9994 | 0 | -149.9965 | 149.9994
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2085e-17 | 8.6045e-08 | -7.392e-08 | -3.048e-17 | -6.0627e-09 | -6.0623e-09 | -1.8325e-18 | -1.3502e-07 | -1.4202e-07 | 1.7691e-17 | -3.5004e-09 | 3.5006e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 1.8186 | 1.8185 | 0 | 1.8186 | 1.8185 | 0 | -149.9965 | 149.9994 | 0 | -149.9965 | 149.9994
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2085e-17 | 8.6045e-08 | -7.392e-08 | -3.048e-17 | -6.0627e-09 | -6.0623e-09 | -1.8325e-18 | -1.3502e-07 | -1.4202e-07 | 1.7691e-17 | -3.5004e-09 | 3.5006e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 1.8186 | 1.8185 | 0 | 1.8186 | 1.8185 | 0 | -149.9965 | 149.9994 | 0 | -149.9965 | 149.9994
Line9_3_11 | 2.6686e-06 | 2.6686e-06 | 2.6686e-06 | 2.2881e-06 | 2.2881e-06 | 2.2881e-06 | 6.1628e-07 | 6.1628e-07 | 6.1628e-07 | 5.2842e-07 | 5.2842e-07 | 5.2842e-07 | 2.3494e-11 | 6.0229e-07 | -5.1744e-07 | -1.9785e-11 | -5.2231e-07 | 4.3746e-07 | 5.3074e-11 | -9.4516e-07 | -9.9413e-07 | -4.5597e-11 | 8.0664e-07 | 8.5561e-07 | -92.5038 | -92.5037 | -92.5037 | 87.0792 | 87.0793 | 87.0793 |  | 9.4181e-05 | 1.8186 | 1.8185 | 9.4061e-05 | 1.8186 | 1.8185 | -26.3811 | -149.997 | 149.9994 | -26.3774 | -149.997 | 149.9994

## LG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.00030759 | 2.3963e-06 | 2.3963e-06 | 0.00030719 | 1.9978e-06 | 1.9978e-06 | 7.1035e-05 | 5.534e-07 | 5.534e-07 | 7.0943e-05 | 4.6136e-07 | 4.6136e-07 | 3.1377e-09 | 5.666e-07 | -4.8677e-07 | -2.3493e-09 | -4.7882e-07 | 3.9898e-07 | 6.2786e-09 | -8.8914e-07 | -9.352e-07 | -4.701e-09 | 7.3711e-07 | 7.8318e-07 | -89.8316 | -92.5039 | -92.5039 | 90.1686 | 86.9956 | 86.9956 |  | 9.881e-05 | 1.9052 | 1.9051 | 7.4079e-05 | 1.9052 | 1.9051 | -26.3853 | -149.997 | 149.9994 | -26.3843 | -149.9969 | 149.9994
Line10_11_12 | 2.3963e-06 | 2.3963e-06 | 2.3963e-06 | 1.9977e-06 | 1.9977e-06 | 1.9977e-06 | 5.5339e-07 | 5.5339e-07 | 5.5339e-07 | 4.6136e-07 | 4.6136e-07 | 4.6136e-07 | 2.207e-11 | 5.6659e-07 | -4.8677e-07 | -1.8014e-11 | -4.7881e-07 | 3.9898e-07 | 4.9866e-11 | -8.8913e-07 | -9.3519e-07 | -4.1687e-11 | 7.371e-07 | 7.8317e-07 | -92.5038 | -92.5037 | -92.5037 | 86.9958 | 86.9959 | 86.9959 |  | 9.854e-05 | 1.9052 | 1.9051 | 9.8434e-05 | 1.9052 | 1.9051 | -26.3774 | -149.997 | 149.9994 | -26.3743 | -149.997 | 149.9994
Line11_12_13 | 1.9969e-06 | 1.9969e-06 | 1.9969e-06 | 1.5984e-06 | 1.5984e-06 | 1.5984e-06 | 4.6116e-07 | 4.6116e-07 | 4.6116e-07 | 3.6913e-07 | 3.6913e-07 | 3.6913e-07 | 1.837e-11 | 4.7216e-07 | -4.0564e-07 | -1.4326e-11 | -3.8438e-07 | 3.1786e-07 | 4.1511e-11 | -7.4094e-07 | -7.7933e-07 | -3.3356e-11 | 5.8891e-07 | 6.273e-07 | -92.5038 | -92.5037 | -92.5037 | 86.8708 | 86.8709 | 86.8709 |  | 9.8434e-05 | 1.9052 | 1.9051 | 9.8347e-05 | 1.9052 | 1.9051 | -26.3743 | -149.997 | 149.9994 | -26.3717 | -149.997 | 149.9994
Line12_13_15 | 1.1981e-06 | 1.1981e-06 | 1.1981e-06 | 0 | 0 | 0 | 2.767e-07 | 2.767e-07 | 2.767e-07 | 0 | 0 | 0 | 1.1011e-11 | 2.8329e-07 | -2.4338e-07 | -6.9813e-12 | -1.9552e-07 | 1.556e-07 | 2.4885e-11 | -4.4457e-07 | -4.676e-07 | -1.6758e-11 | 2.9254e-07 | 3.1557e-07 | -92.5038 | -92.5037 | -92.5037 | 0 | 0 | 0 |  | 9.8347e-05 | 1.9052 | 1.9051 | 9.8298e-05 | 1.9052 | 1.9051 | -26.3717 | -149.997 | 149.9994 | -26.3701 | -149.997 | 149.9994
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6703e-12 | 9.4431e-08 | -8.1128e-08 | 3.5532e-13 | -6.6539e-09 | -6.6536e-09 | 8.295e-12 | -1.4819e-07 | -1.5587e-07 | -1.7618e-13 | -3.8418e-09 | 3.8419e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 9.8347e-05 | 1.9052 | 1.9051 | 9.8337e-05 | 1.9052 | 1.9051 | -26.3717 | -149.997 | 149.9994 | -26.3712 | -149.997 | 149.9994
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.3365e-12 | 1.8886e-07 | -1.6226e-07 | -3.312e-12 | -1.0109e-07 | 7.4474e-08 | 1.6582e-11 | -2.9638e-07 | -3.1173e-07 | -8.4647e-12 | 1.4435e-07 | 1.5971e-07 | 0 | 0 | 0 | 0 | 0 | 0 |  | 9.8298e-05 | 1.9052 | 1.9051 | 9.827e-05 | 1.9052 | 1.9051 | -26.3701 | -149.997 | 149.9994 | -26.3691 | -149.997 | 149.9994
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.667e-12 | 9.4431e-08 | -8.1128e-08 | 3.5504e-13 | -6.654e-09 | -6.6536e-09 | 8.2887e-12 | -1.4819e-07 | -1.5587e-07 | -1.7602e-13 | -3.8418e-09 | 3.8419e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 9.827e-05 | 1.9052 | 1.9051 | 9.826e-05 | 1.9052 | 1.9051 | -26.3691 | -149.997 | 149.9994 | -26.3685 | -149.997 | 149.9994
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6883e-12 | 9.4431e-08 | -8.1128e-08 | 3.5685e-13 | -6.6539e-09 | -6.6536e-09 | 8.3309e-12 | -1.4819e-07 | -1.5587e-07 | -1.7703e-13 | -3.8417e-09 | 3.8419e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 9.8781e-05 | 1.9052 | 1.9051 | 9.8772e-05 | 1.9052 | 1.9051 | -26.3843 | -149.997 | 149.9994 | -26.3838 | -149.997 | 149.9994
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6883e-12 | 9.4431e-08 | -8.1128e-08 | 3.5685e-13 | -6.6539e-09 | -6.6536e-09 | 8.3309e-12 | -1.4819e-07 | -1.5587e-07 | -1.7703e-13 | -3.8417e-09 | 3.8419e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 9.8781e-05 | 1.9052 | 1.9051 | 9.8772e-05 | 1.9052 | 1.9051 | -26.3843 | -149.997 | 149.9994 | -26.3838 | -149.997 | 149.9994
Line1_1_3 | 3.195e-06 | 3.195e-06 | 3.195e-06 | 2.7965e-06 | 2.7965e-06 | 2.7965e-06 | 7.3786e-07 | 7.3786e-07 | 7.3786e-07 | 6.4582e-07 | 6.4582e-07 | 6.4582e-07 | 2.9517e-11 | 7.5545e-07 | -6.4902e-07 | -2.5428e-11 | -6.6767e-07 | 5.6124e-07 | 6.6666e-11 | -1.1855e-06 | -1.2469e-06 | -5.8426e-11 | 1.0335e-06 | 1.0949e-06 | -92.5038 | -92.5037 | -92.5037 | 87.1388 | 87.1388 | 87.1388 |  | 9.881e-05 | 1.9052 | 1.9051 | 9.8665e-05 | 1.9052 | 1.9051 | -26.3853 | -149.997 | 149.9994 | -26.3811 | -149.997 | 149.9994
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.3792e-12 | 1.8886e-07 | -1.6226e-07 | -3.3315e-12 | -1.0109e-07 | 7.4474e-08 | 1.6667e-11 | -2.9638e-07 | -3.1173e-07 | -8.5079e-12 | 1.4435e-07 | 1.5971e-07 | 0 | 0 | 0 | 0 | 0 | 0 |  | 9.881e-05 | 1.9052 | 1.9051 | 9.8781e-05 | 1.9052 | 1.9051 | -26.3853 | -149.997 | 149.9994 | -26.3843 | -149.997 | 149.9994
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.3792e-12 | 1.8886e-07 | -1.6226e-07 | -3.3315e-12 | -1.0109e-07 | 7.4474e-08 | 1.6667e-11 | -2.9638e-07 | -3.1173e-07 | -8.5079e-12 | 1.4435e-07 | 1.5971e-07 | 0 | 0 | 0 | 0 | 0 | 0 |  | 9.881e-05 | 1.9052 | 1.9051 | 9.8781e-05 | 1.9052 | 1.9051 | -26.3853 | -149.997 | 149.9994 | -26.3843 | -149.997 | 149.9994
Line4_2_6 | 0.00030719 | 1.9969e-06 | 1.9969e-06 | 0.00030679 | 1.5984e-06 | 1.5984e-06 | 7.0943e-05 | 4.6117e-07 | 4.6117e-07 | 7.085e-05 | 3.6913e-07 | 3.6913e-07 | 2.3495e-09 | 4.7217e-07 | -4.0564e-07 | -1.5637e-09 | -3.8439e-07 | 3.1786e-07 | 4.7009e-09 | -7.4095e-07 | -7.7934e-07 | -3.1286e-09 | 5.8892e-07 | 6.2731e-07 | -89.8281 | -92.504 | -92.504 | 90.1721 | 86.8706 | 86.8706 |  | 7.4079e-05 | 1.9052 | 1.9051 | 4.9366e-05 | 1.9052 | 1.9051 | -26.3843 | -149.9969 | 149.9994 | -26.3834 | -149.9967 | 149.9994
Line5_6_7 | 0.00030679 | 1.5975e-06 | 1.5975e-06 | 0.00030639 | 1.199e-06 | 1.199e-06 | 7.085e-05 | 3.6894e-07 | 3.6894e-07 | 7.0758e-05 | 2.7691e-07 | 2.7691e-07 | 1.5638e-09 | 3.7773e-07 | -3.2451e-07 | -7.8059e-10 | -2.8996e-07 | 2.3673e-07 | 3.1285e-09 | -5.9276e-07 | -6.2347e-07 | -1.5616e-09 | 4.4073e-07 | 4.7144e-07 | -89.8247 | -92.504 | -92.504 | 90.1756 | 86.6623 | 86.6623 |  | 4.9366e-05 | 1.9052 | 1.9051 | 2.4673e-05 | 1.9052 | 1.9051 | -26.3834 | -149.9967 | 149.9994 | -26.3828 | -149.9966 | 149.9994
Line6_7_8 | 0.00030639 | 1.1982e-06 | 1.1982e-06 | 0.00030599 | 0 | 0 | 7.0758e-05 | 2.767e-07 | 2.767e-07 | 7.0666e-05 | 0 | 0 | 7.8068e-10 | 2.833e-07 | -2.4338e-07 | -1.7243e-14 | -1.9552e-07 | 1.556e-07 | 1.5616e-09 | -4.4457e-07 | -4.676e-07 | 2.2136e-14 | 2.9254e-07 | 3.1558e-07 | -89.8212 | -92.5041 | -92.5041 | 90.1791 | 0 | 0 |  | 2.4673e-05 | 1.9052 | 1.9051 | 0 | 1.9052 | 1.9051 | -26.3828 | -149.9966 | 149.9994 | 0 | -149.9965 | 149.9994
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3834e-17 | 9.4434e-08 | -8.1127e-08 | -3.4578e-17 | -6.6538e-09 | -6.6534e-09 | -2.7806e-17 | -1.4819e-07 | -1.5587e-07 | 1.9482e-17 | -3.8417e-09 | 3.8419e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 1.9052 | 1.9051 | 0 | 1.9052 | 1.9051 | 0 | -149.9965 | 149.9994 | 0 | -149.9965 | 149.9994
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3834e-17 | 9.4434e-08 | -8.1127e-08 | -3.4578e-17 | -6.6538e-09 | -6.6534e-09 | -2.7806e-17 | -1.4819e-07 | -1.5587e-07 | 1.9482e-17 | -3.8417e-09 | 3.8419e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 1.9052 | 1.9051 | 0 | 1.9052 | 1.9051 | 0 | -149.9965 | 149.9994 | 0 | -149.9965 | 149.9994
Line9_3_11 | 2.7956e-06 | 2.7956e-06 | 2.7956e-06 | 2.3971e-06 | 2.3971e-06 | 2.3971e-06 | 6.4563e-07 | 6.4563e-07 | 6.4563e-07 | 5.5359e-07 | 5.5359e-07 | 5.5359e-07 | 2.5785e-11 | 6.6102e-07 | -5.6789e-07 | -2.1714e-11 | -5.7324e-07 | 4.8011e-07 | 5.8249e-11 | -1.0373e-06 | -1.0911e-06 | -5.0042e-11 | 8.8529e-07 | 9.3903e-07 | -92.5038 | -92.5037 | -92.5037 | 87.0792 | 87.0793 | 87.0793 |  | 9.8665e-05 | 1.9052 | 1.9051 | 9.854e-05 | 1.9052 | 1.9051 | -26.3811 | -149.997 | 149.9994 | -26.3774 | -149.997 | 149.9994

## LG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.00029184 | 2.2736e-06 | 2.2736e-06 | 0.00029147 | 1.8955e-06 | 1.8955e-06 | 6.7399e-05 | 5.2507e-07 | 5.2507e-07 | 6.7311e-05 | 4.3775e-07 | 4.3775e-07 | 4.2522e-07 | 5.1149e-07 | -4.4276e-07 | -4.2396e-07 | -4.3227e-07 | 3.6298e-07 | 4.2836e-07 | -8.0488e-07 | -8.4092e-07 | -4.2639e-07 | 6.6726e-07 | 7.0426e-07 | -89.4906 | -92.163 | -92.163 | 90.5096 | 87.3366 | 87.3366 |  | 0.0089553 | 1.8162 | 1.8099 | 0.008933 | 1.8162 | 1.8099 | -44.2801 | -149.7275 | 150.0695 | -44.3272 | -149.7274 | 150.0695
Line10_11_12 | 2.2736e-06 | 2.2736e-06 | 2.2736e-06 | 1.8955e-06 | 1.8955e-06 | 1.8955e-06 | 5.2507e-07 | 5.2507e-07 | 5.2507e-07 | 4.3774e-07 | 4.3774e-07 | 4.3774e-07 | 3.1534e-09 | 5.1148e-07 | -4.4275e-07 | -2.6035e-09 | -4.3226e-07 | 3.6298e-07 | 3.4878e-09 | -8.0487e-07 | -8.4091e-07 | -2.9305e-09 | 6.6726e-07 | 7.0425e-07 | -92.1628 | -92.1627 | -92.1627 | 87.3368 | 87.3369 | 87.3369 |  | 0.0089551 | 1.8162 | 1.8099 | 0.008955 | 1.8162 | 1.81 | -44.2805 | -149.7275 | 150.0695 | -44.2807 | -149.7275 | 150.0695
Line11_12_13 | 1.8947e-06 | 1.8947e-06 | 1.8947e-06 | 1.5166e-06 | 1.5166e-06 | 1.5166e-06 | 4.3756e-07 | 4.3756e-07 | 4.3756e-07 | 3.5023e-07 | 3.5023e-07 | 3.5023e-07 | 2.6278e-09 | 4.2623e-07 | -3.6896e-07 | -2.0779e-09 | -3.4701e-07 | 2.8919e-07 | 2.9065e-09 | -6.7072e-07 | -7.0076e-07 | -2.3492e-09 | 5.3311e-07 | 5.641e-07 | -92.1628 | -92.1627 | -92.1627 | 87.2118 | 87.2119 | 87.2119 |  | 0.008955 | 1.8162 | 1.81 | 0.0089549 | 1.8162 | 1.81 | -44.2807 | -149.7275 | 150.0695 | -44.2808 | -149.7275 | 150.0695
Line12_13_15 | 1.1368e-06 | 1.1368e-06 | 1.1368e-06 | 0 | 0 | 0 | 2.6253e-07 | 2.6253e-07 | 2.6253e-07 | 0 | 0 | 0 | 1.5767e-09 | 2.5574e-07 | -2.2138e-07 | -1.0267e-09 | -1.7652e-07 | 1.416e-07 | 1.7439e-09 | -4.0243e-07 | -4.2045e-07 | -1.1866e-09 | 2.6482e-07 | 2.8379e-07 | -92.1628 | -92.1627 | -92.1627 | 0 | 0 | 0 |  | 0.0089549 | 1.8162 | 1.81 | 0.0089549 | 1.8162 | 1.81 | -44.2808 | -149.7275 | 150.0695 | -44.2809 | -149.7275 | 150.0695
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2556e-10 | 8.5247e-08 | -7.3792e-08 | 2.4388e-11 | -6.0229e-09 | -5.9812e-09 | 5.8129e-10 | -1.3414e-07 | -1.4015e-07 | -2.4071e-11 | -3.4674e-09 | 3.4915e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.0089549 | 1.8162 | 1.81 | 0.0089549 | 1.8162 | 1.81 | -44.2808 | -149.7275 | 150.0695 | -44.2808 | -149.7275 | 150.0695
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0511e-09 | 1.7049e-07 | -1.4758e-07 | -5.0117e-10 | -9.127e-08 | 6.7811e-08 | 1.1626e-09 | -2.6829e-07 | -2.803e-07 | -6.0535e-10 | 1.3068e-07 | 1.4364e-07 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.0089549 | 1.8162 | 1.81 | 0.0089548 | 1.8162 | 1.81 | -44.2809 | -149.7275 | 150.0695 | -44.2809 | -149.7276 | 150.0695
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2556e-10 | 8.5247e-08 | -7.3792e-08 | 2.4388e-11 | -6.0229e-09 | -5.9812e-09 | 5.8128e-10 | -1.3415e-07 | -1.4015e-07 | -2.407e-11 | -3.4674e-09 | 3.4915e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.0089548 | 1.8162 | 1.81 | 0.0089548 | 1.8162 | 1.81 | -44.2809 | -149.7276 | 150.0695 | -44.281 | -149.7276 | 150.0695
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2558e-10 | 8.5247e-08 | -7.3792e-08 | 2.439e-11 | -6.0229e-09 | -5.9812e-09 | 5.8132e-10 | -1.3414e-07 | -1.4015e-07 | -2.4071e-11 | -3.4674e-09 | 3.4915e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.0089553 | 1.8162 | 1.8099 | 0.0089553 | 1.8162 | 1.8099 | -44.2801 | -149.7275 | 150.0695 | -44.2801 | -149.7275 | 150.0695
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2558e-10 | 8.5247e-08 | -7.3792e-08 | 2.439e-11 | -6.0229e-09 | -5.9812e-09 | 5.8132e-10 | -1.3414e-07 | -1.4015e-07 | -2.4071e-11 | -3.4674e-09 | 3.4915e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.0089553 | 1.8162 | 1.8099 | 0.0089553 | 1.8162 | 1.8099 | -44.2801 | -149.7275 | 150.0695 | -44.2801 | -149.7275 | 150.0695
Line1_1_3 | 3.0315e-06 | 3.0315e-06 | 3.0315e-06 | 2.6533e-06 | 2.6533e-06 | 2.6533e-06 | 7.0009e-07 | 7.0009e-07 | 7.0009e-07 | 6.1276e-07 | 6.1276e-07 | 6.1276e-07 | 4.2047e-09 | 6.8197e-07 | -5.9034e-07 | -3.6546e-09 | -6.0275e-07 | 5.1057e-07 | 4.6506e-09 | -1.0732e-06 | -1.1212e-06 | -4.0932e-09 | 9.3555e-07 | 9.8455e-07 | -92.1628 | -92.1627 | -92.1627 | 87.4797 | 87.4798 | 87.4798 |  | 0.0089553 | 1.8162 | 1.8099 | 0.0089552 | 1.8162 | 1.8099 | -44.2801 | -149.7275 | 150.0695 | -44.2803 | -149.7275 | 150.0695
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0512e-09 | 1.7049e-07 | -1.4758e-07 | -5.0119e-10 | -9.1269e-08 | 6.7811e-08 | 1.1626e-09 | -2.6829e-07 | -2.803e-07 | -6.0539e-10 | 1.3068e-07 | 1.4364e-07 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.0089553 | 1.8162 | 1.8099 | 0.0089553 | 1.8162 | 1.8099 | -44.2801 | -149.7275 | 150.0695 | -44.2801 | -149.7275 | 150.0695
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0512e-09 | 1.7049e-07 | -1.4758e-07 | -5.0119e-10 | -9.1269e-08 | 6.7811e-08 | 1.1626e-09 | -2.6829e-07 | -2.803e-07 | -6.0539e-10 | 1.3068e-07 | 1.4364e-07 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.0089553 | 1.8162 | 1.8099 | 0.0089553 | 1.8162 | 1.8099 | -44.2801 | -149.7275 | 150.0695 | -44.2801 | -149.7275 | 150.0695
Line4_2_6 | 0.00029147 | 1.8947e-06 | 1.8947e-06 | 0.00029109 | 1.5166e-06 | 1.5166e-06 | 6.7311e-05 | 4.3756e-07 | 4.3756e-07 | 6.7224e-05 | 3.5024e-07 | 3.5024e-07 | 4.2399e-07 | 4.2624e-07 | -3.6896e-07 | -4.2274e-07 | -3.4702e-07 | 2.8919e-07 | 4.2636e-07 | -6.7073e-07 | -7.0076e-07 | -4.244e-07 | 5.3312e-07 | 5.641e-07 | -89.4872 | -92.163 | -92.163 | 90.513 | 87.2116 | 87.2116 |  | 0.008933 | 1.8162 | 1.8099 | 0.0089108 | 1.8162 | 1.8099 | -44.3272 | -149.7274 | 150.0695 | -44.3745 | -149.7273 | 150.0695
Line5_6_7 | 0.00029109 | 1.5158e-06 | 1.5158e-06 | 0.00029071 | 1.1377e-06 | 1.1377e-06 | 6.7224e-05 | 3.5005e-07 | 3.5005e-07 | 6.7136e-05 | 2.6273e-07 | 2.6273e-07 | 4.2276e-07 | 3.41e-07 | -2.9517e-07 | -4.2151e-07 | -2.6177e-07 | 2.154e-07 | 4.2437e-07 | -5.3658e-07 | -5.6061e-07 | -4.2241e-07 | 3.9897e-07 | 4.2395e-07 | -89.4837 | -92.1631 | -92.1631 | 90.5165 | 87.0032 | 87.0032 |  | 0.0089108 | 1.8162 | 1.8099 | 0.0088885 | 1.8162 | 1.8099 | -44.3745 | -149.7273 | 150.0695 | -44.422 | -149.7272 | 150.0695
Line6_7_8 | 0.00029071 | 1.1368e-06 | 1.1368e-06 | 0.00029033 | 0 | 0 | 6.7136e-05 | 2.6254e-07 | 2.6254e-07 | 6.7049e-05 | 0 | 0 | 4.2153e-07 | 2.5575e-07 | -2.2138e-07 | -4.2028e-07 | -1.7652e-07 | 1.416e-07 | 4.2239e-07 | -4.0244e-07 | -4.2046e-07 | -4.2043e-07 | 2.6482e-07 | 2.838e-07 | -89.4802 | -92.1631 | -92.1631 | 90.52 | 0 | 0 |  | 0.0088885 | 1.8162 | 1.8099 | 0.0088663 | 1.8162 | 1.8099 | -44.422 | -149.7272 | 150.0695 | -44.4697 | -149.7271 | 150.0695
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2226e-10 | 8.525e-08 | -7.3792e-08 | 2.4071e-11 | -6.0228e-09 | -5.981e-09 | 5.7383e-10 | -1.3415e-07 | -1.4015e-07 | -2.3913e-11 | -3.4673e-09 | 3.4914e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.0088663 | 1.8162 | 1.8099 | 0.0088663 | 1.8162 | 1.8099 | -44.4697 | -149.7271 | 150.0695 | -44.4697 | -149.7271 | 150.0695
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2226e-10 | 8.525e-08 | -7.3792e-08 | 2.4071e-11 | -6.0228e-09 | -5.981e-09 | 5.7383e-10 | -1.3415e-07 | -1.4015e-07 | -2.3913e-11 | -3.4673e-09 | 3.4914e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.0088663 | 1.8162 | 1.8099 | 0.0088663 | 1.8162 | 1.8099 | -44.4697 | -149.7271 | 150.0695 | -44.4697 | -149.7271 | 150.0695
Line9_3_11 | 2.6525e-06 | 2.6525e-06 | 2.6525e-06 | 2.2744e-06 | 2.2744e-06 | 2.2744e-06 | 6.1258e-07 | 6.1258e-07 | 6.1258e-07 | 5.2525e-07 | 5.2525e-07 | 5.2525e-07 | 3.679e-09 | 5.9673e-07 | -5.1655e-07 | -3.129e-09 | -5.175e-07 | 4.3677e-07 | 4.0692e-09 | -9.3901e-07 | -9.8106e-07 | -3.5119e-09 | 8.014e-07 | 8.444e-07 | -92.1628 | -92.1627 | -92.1627 | 87.4202 | 87.4203 | 87.4203 |  | 0.0089552 | 1.8162 | 1.8099 | 0.0089551 | 1.8162 | 1.8099 | -44.2803 | -149.7275 | 150.0695 | -44.2805 | -149.7275 | 150.0695

## LG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.00030574 | 2.3819e-06 | 2.3819e-06 | 0.00030534 | 1.9858e-06 | 1.9858e-06 | 7.0608e-05 | 5.5008e-07 | 5.5008e-07 | 7.0516e-05 | 4.5859e-07 | 4.5859e-07 | 4.6668e-07 | 5.6136e-07 | -4.8593e-07 | -4.653e-07 | -4.7441e-07 | 3.9837e-07 | 4.7012e-07 | -8.8336e-07 | -9.2291e-07 | -4.6796e-07 | 7.3232e-07 | 7.7292e-07 | -89.4906 | -92.163 | -92.163 | 90.5096 | 87.3366 | 87.3366 |  | 0.0093818 | 1.9027 | 1.8961 | 0.0093584 | 1.9027 | 1.8961 | -44.2801 | -149.7275 | 150.0695 | -44.3272 | -149.7274 | 150.0695
Line10_11_12 | 2.3819e-06 | 2.3819e-06 | 2.3819e-06 | 1.9857e-06 | 1.9857e-06 | 1.9857e-06 | 5.5007e-07 | 5.5007e-07 | 5.5007e-07 | 4.5858e-07 | 4.5858e-07 | 4.5858e-07 | 3.4609e-09 | 5.6135e-07 | -4.8593e-07 | -2.8573e-09 | -4.744e-07 | 3.9837e-07 | 3.8279e-09 | -8.8335e-07 | -9.229e-07 | -3.2163e-09 | 7.3232e-07 | 7.7291e-07 | -92.1628 | -92.1627 | -92.1627 | 87.3368 | 87.3369 | 87.3369 |  | 0.0093815 | 1.9027 | 1.8961 | 0.0093814 | 1.9027 | 1.8961 | -44.2805 | -149.7275 | 150.0695 | -44.2807 | -149.7275 | 150.0695
Line11_12_13 | 1.9849e-06 | 1.9849e-06 | 1.9849e-06 | 1.5888e-06 | 1.5888e-06 | 1.5888e-06 | 4.5839e-07 | 4.5839e-07 | 4.5839e-07 | 3.6691e-07 | 3.6691e-07 | 3.6691e-07 | 2.8841e-09 | 4.6779e-07 | -4.0494e-07 | -2.2805e-09 | -3.8084e-07 | 3.1739e-07 | 3.1899e-09 | -7.3612e-07 | -7.6908e-07 | -2.5783e-09 | 5.8509e-07 | 6.191e-07 | -92.1628 | -92.1627 | -92.1627 | 87.2118 | 87.2119 | 87.2119 |  | 0.0093814 | 1.9027 | 1.8961 | 0.0093813 | 1.9027 | 1.8961 | -44.2807 | -149.7275 | 150.0695 | -44.2808 | -149.7275 | 150.0695
Line12_13_15 | 1.1909e-06 | 1.1909e-06 | 1.1909e-06 | 0 | 0 | 0 | 2.7503e-07 | 2.7503e-07 | 2.7503e-07 | 0 | 0 | 0 | 1.7304e-09 | 2.8068e-07 | -2.4296e-07 | -1.1268e-09 | -1.9373e-07 | 1.5541e-07 | 1.9139e-09 | -4.4167e-07 | -4.6145e-07 | -1.3023e-09 | 2.9064e-07 | 3.1146e-07 | -92.1628 | -92.1627 | -92.1627 | 0 | 0 | 0 |  | 0.0093813 | 1.9027 | 1.8961 | 0.0093813 | 1.9027 | 1.8961 | -44.2808 | -149.7275 | 150.0695 | -44.2809 | -149.7275 | 150.0695
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.7681e-10 | 9.3559e-08 | -8.0988e-08 | 2.6766e-11 | -6.6102e-09 | -6.5644e-09 | 6.3796e-10 | -1.4722e-07 | -1.5382e-07 | -2.6418e-11 | -3.8055e-09 | 3.8319e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.0093813 | 1.9027 | 1.8961 | 0.0093813 | 1.9027 | 1.8961 | -44.2808 | -149.7275 | 150.0695 | -44.2808 | -149.7275 | 150.0695
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1536e-09 | 1.8712e-07 | -1.6198e-07 | -5.5004e-10 | -1.0017e-07 | 7.4423e-08 | 1.2759e-09 | -2.9445e-07 | -3.0763e-07 | -6.6438e-10 | 1.4342e-07 | 1.5765e-07 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.0093813 | 1.9027 | 1.8961 | 0.0093812 | 1.9027 | 1.8961 | -44.2809 | -149.7275 | 150.0695 | -44.2809 | -149.7275 | 150.0695
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.7681e-10 | 9.3559e-08 | -8.0988e-08 | 2.6766e-11 | -6.6102e-09 | -6.5644e-09 | 6.3796e-10 | -1.4722e-07 | -1.5382e-07 | -2.6417e-11 | -3.8055e-09 | 3.8319e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.0093812 | 1.9027 | 1.8961 | 0.0093812 | 1.9027 | 1.8961 | -44.2809 | -149.7275 | 150.0695 | -44.281 | -149.7275 | 150.0695
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.7683e-10 | 9.3559e-08 | -8.0988e-08 | 2.6768e-11 | -6.6102e-09 | -6.5644e-09 | 6.38e-10 | -1.4722e-07 | -1.5382e-07 | -2.6418e-11 | -3.8055e-09 | 3.8319e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.0093817 | 1.9027 | 1.8961 | 0.0093817 | 1.9027 | 1.8961 | -44.2801 | -149.7275 | 150.0695 | -44.2801 | -149.7275 | 150.0695
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.7683e-10 | 9.3559e-08 | -8.0988e-08 | 2.6768e-11 | -6.6102e-09 | -6.5644e-09 | 6.38e-10 | -1.4722e-07 | -1.5382e-07 | -2.6418e-11 | -3.8055e-09 | 3.8319e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.0093817 | 1.9027 | 1.8961 | 0.0093817 | 1.9027 | 1.8961 | -44.2801 | -149.7275 | 150.0695 | -44.2801 | -149.7275 | 150.0695
Line1_1_3 | 3.1758e-06 | 3.1758e-06 | 3.1758e-06 | 2.7797e-06 | 2.7797e-06 | 2.7797e-06 | 7.3343e-07 | 7.3343e-07 | 7.3343e-07 | 6.4194e-07 | 6.4194e-07 | 6.4194e-07 | 4.6146e-09 | 7.4847e-07 | -6.479e-07 | -4.011e-09 | -6.6152e-07 | 5.6035e-07 | 5.104e-09 | -1.1778e-06 | -1.2305e-06 | -4.4923e-09 | 1.0268e-06 | 1.0805e-06 | -92.1628 | -92.1627 | -92.1627 | 87.4797 | 87.4798 | 87.4798 |  | 0.0093818 | 1.9027 | 1.8961 | 0.0093816 | 1.9027 | 1.8961 | -44.2801 | -149.7275 | 150.0695 | -44.2803 | -149.7275 | 150.0695
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1537e-09 | 1.8712e-07 | -1.6198e-07 | -5.5006e-10 | -1.0017e-07 | 7.4423e-08 | 1.276e-09 | -2.9445e-07 | -3.0763e-07 | -6.6442e-10 | 1.4342e-07 | 1.5765e-07 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.0093818 | 1.9027 | 1.8961 | 0.0093817 | 1.9027 | 1.8961 | -44.2801 | -149.7275 | 150.0695 | -44.2801 | -149.7275 | 150.0695
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1537e-09 | 1.8712e-07 | -1.6198e-07 | -5.5006e-10 | -1.0017e-07 | 7.4423e-08 | 1.276e-09 | -2.9445e-07 | -3.0763e-07 | -6.6442e-10 | 1.4342e-07 | 1.5765e-07 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.0093818 | 1.9027 | 1.8961 | 0.0093817 | 1.9027 | 1.8961 | -44.2801 | -149.7275 | 150.0695 | -44.2801 | -149.7275 | 150.0695
Line4_2_6 | 0.00030534 | 1.9849e-06 | 1.9849e-06 | 0.00030495 | 1.5888e-06 | 1.5888e-06 | 7.0516e-05 | 4.584e-07 | 4.584e-07 | 7.0425e-05 | 3.6692e-07 | 3.6692e-07 | 4.6533e-07 | 4.678e-07 | -4.0494e-07 | -4.6395e-07 | -3.8085e-07 | 3.1739e-07 | 4.6794e-07 | -7.3613e-07 | -7.6909e-07 | -4.6578e-07 | 5.851e-07 | 6.191e-07 | -89.4872 | -92.163 | -92.163 | 90.5131 | 87.2116 | 87.2116 |  | 0.0093584 | 1.9027 | 1.8961 | 0.0093351 | 1.9027 | 1.8961 | -44.3272 | -149.7274 | 150.0695 | -44.3745 | -149.7273 | 150.0695
Line5_6_7 | 0.00030495 | 1.5879e-06 | 1.5879e-06 | 0.00030455 | 1.1918e-06 | 1.1918e-06 | 7.0425e-05 | 3.6672e-07 | 3.6672e-07 | 7.0333e-05 | 2.7524e-07 | 2.7524e-07 | 4.6398e-07 | 3.7424e-07 | -3.2395e-07 | -4.6261e-07 | -2.8729e-07 | 2.364e-07 | 4.6575e-07 | -5.889e-07 | -6.1527e-07 | -4.636e-07 | 4.3787e-07 | 4.6529e-07 | -89.4837 | -92.1631 | -92.1631 | 90.5165 | 87.0032 | 87.0032 |  | 0.0093351 | 1.9027 | 1.8961 | 0.0093118 | 1.9027 | 1.8961 | -44.3745 | -149.7273 | 150.0695 | -44.422 | -149.7272 | 150.0695
Line6_7_8 | 0.00030455 | 1.191e-06 | 1.191e-06 | 0.00030415 | 0 | 0 | 7.0333e-05 | 2.7504e-07 | 2.7504e-07 | 7.0242e-05 | 0 | 0 | 4.6263e-07 | 2.8068e-07 | -2.4296e-07 | -4.6126e-07 | -1.9373e-07 | 1.5541e-07 | 4.6357e-07 | -4.4168e-07 | -4.6145e-07 | -4.6143e-07 | 2.9064e-07 | 3.1147e-07 | -89.4802 | -92.1631 | -92.1631 | 90.52 | 0 | 0 |  | 0.0093118 | 1.9027 | 1.8961 | 0.0092885 | 1.9027 | 1.8961 | -44.422 | -149.7272 | 150.0695 | -44.4697 | -149.727 | 150.0695
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.7318e-10 | 9.3562e-08 | -8.0987e-08 | 2.6419e-11 | -6.61e-09 | -6.5642e-09 | 6.2978e-10 | -1.4722e-07 | -1.5382e-07 | -2.6244e-11 | -3.8054e-09 | 3.8319e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.0092885 | 1.9027 | 1.8961 | 0.0092885 | 1.9027 | 1.8961 | -44.4697 | -149.727 | 150.0695 | -44.4697 | -149.727 | 150.0695
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.7318e-10 | 9.3562e-08 | -8.0987e-08 | 2.6419e-11 | -6.61e-09 | -6.5642e-09 | 6.2978e-10 | -1.4722e-07 | -1.5382e-07 | -2.6244e-11 | -3.8054e-09 | 3.8319e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.0092885 | 1.9027 | 1.8961 | 0.0092885 | 1.9027 | 1.8961 | -44.4697 | -149.727 | 150.0695 | -44.4697 | -149.727 | 150.0695
Line9_3_11 | 2.7788e-06 | 2.7788e-06 | 2.7788e-06 | 2.3827e-06 | 2.3827e-06 | 2.3827e-06 | 6.4175e-07 | 6.4175e-07 | 6.4175e-07 | 5.5026e-07 | 5.5026e-07 | 5.5026e-07 | 4.0378e-09 | 6.5491e-07 | -5.6691e-07 | -3.4341e-09 | -5.6796e-07 | 4.7936e-07 | 4.4659e-09 | -1.0306e-06 | -1.0767e-06 | -3.8543e-09 | 8.7954e-07 | 9.2673e-07 | -92.1628 | -92.1627 | -92.1627 | 87.4202 | 87.4203 | 87.4203 |  | 0.0093816 | 1.9027 | 1.8961 | 0.0093815 | 1.9027 | 1.8961 | -44.2803 | -149.7275 | 150.0695 | -44.2805 | -149.7275 | 150.0695

## LG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.00026565 | 2.0695e-06 | 2.0695e-06 | 0.0002653 | 1.7253e-06 | 1.7253e-06 | 6.1348e-05 | 4.7794e-07 | 4.7794e-07 | 6.1269e-05 | 3.9845e-07 | 3.9845e-07 | 4.4943e-09 | 4.226e-07 | -3.6307e-07 | -3.365e-09 | -3.5713e-07 | 2.9759e-07 | 4.6834e-09 | -6.6319e-07 | -6.9753e-07 | -3.5067e-09 | 5.498e-07 | 5.8414e-07 | -89.8295 | -92.5021 | -92.5021 | 90.1707 | 86.9974 | 86.9974 |  | 0.00010581 | 1.6454 | 1.6453 | 7.9323e-05 | 1.6454 | 1.6453 | -43.6487 | -149.9959 | 150.0005 | -43.6477 | -149.9957 | 150.0005
Line10_11_12 | 2.0695e-06 | 2.0695e-06 | 2.0695e-06 | 1.7253e-06 | 1.7253e-06 | 1.7253e-06 | 4.7793e-07 | 4.7793e-07 | 4.7793e-07 | 3.9844e-07 | 3.9844e-07 | 3.9844e-07 | 3.3177e-11 | 4.2259e-07 | -3.6307e-07 | -2.735e-11 | -3.5712e-07 | 2.976e-07 | 3.7979e-11 | -6.6319e-07 | -6.9751e-07 | -3.187e-11 | 5.4979e-07 | 5.8413e-07 | -92.5017 | -92.5016 | -92.5016 | 86.9979 | 86.998 | 86.998 |  | 0.00010552 | 1.6454 | 1.6453 | 0.0001054 | 1.6454 | 1.6453 | -43.6409 | -149.9959 | 150.0005 | -43.6377 | -149.9959 | 150.0005
Line11_12_13 | 1.7246e-06 | 1.7246e-06 | 1.7246e-06 | 1.3804e-06 | 1.3804e-06 | 1.3804e-06 | 3.9828e-07 | 3.9828e-07 | 3.9828e-07 | 3.1879e-07 | 3.1879e-07 | 3.1879e-07 | 2.7616e-11 | 3.5216e-07 | -3.0256e-07 | -2.1807e-11 | -2.8669e-07 | 2.3709e-07 | 3.1617e-11 | -5.5266e-07 | -5.8126e-07 | -2.5525e-11 | 4.3926e-07 | 4.6788e-07 | -92.5017 | -92.5016 | -92.5016 | 86.8729 | 86.873 | 86.873 |  | 0.0001054 | 1.6454 | 1.6453 | 0.00010531 | 1.6454 | 1.6453 | -43.6377 | -149.9959 | 150.0005 | -43.6351 | -149.9959 | 150.0005
Line12_13_15 | 1.0348e-06 | 1.0348e-06 | 1.0348e-06 | 0 | 0 | 0 | 2.3897e-07 | 2.3897e-07 | 2.3897e-07 | 0 | 0 | 0 | 1.6554e-11 | 2.113e-07 | -1.8154e-07 | -1.0765e-11 | -1.4583e-07 | 1.1606e-07 | 1.8954e-11 | -3.316e-07 | -3.4876e-07 | -1.2883e-11 | 2.182e-07 | 2.3537e-07 | -92.5017 | -92.5016 | -92.5016 | 0 | 0 | 0 |  | 0.00010531 | 1.6454 | 1.6453 | 0.00010526 | 1.6454 | 1.6453 | -43.6351 | -149.9959 | 150.0005 | -43.6335 | -149.9959 | 150.0005
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.518e-12 | 7.0432e-08 | -6.0512e-08 | 2.6543e-13 | -4.9631e-09 | -4.9626e-09 | 6.318e-12 | -1.1053e-07 | -1.1625e-07 | -2.5311e-13 | -2.8654e-09 | 2.8656e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.00010531 | 1.6454 | 1.6453 | 0.0001053 | 1.6454 | 1.6453 | -43.6351 | -149.9959 | 150.0005 | -43.6346 | -149.9959 | 150.0005
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.103e-11 | 1.4086e-07 | -1.2102e-07 | -5.2482e-12 | -7.5395e-08 | 5.5549e-08 | 1.263e-11 | -2.2106e-07 | -2.325e-07 | -6.5662e-12 | 1.0767e-07 | 1.1912e-07 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.00010526 | 1.6454 | 1.6453 | 0.00010523 | 1.6454 | 1.6453 | -43.6335 | -149.9959 | 150.0005 | -43.6325 | -149.9959 | 150.0005
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5134e-12 | 7.0432e-08 | -6.0512e-08 | 2.6523e-13 | -4.9631e-09 | -4.9626e-09 | 6.3133e-12 | -1.1053e-07 | -1.1625e-07 | -2.529e-13 | -2.8654e-09 | 2.8656e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.00010523 | 1.6454 | 1.6453 | 0.00010522 | 1.6454 | 1.6453 | -43.6325 | -149.9959 | 150.0005 | -43.632 | -149.9959 | 150.0005
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5438e-12 | 7.0432e-08 | -6.0512e-08 | 2.6654e-13 | -4.9631e-09 | -4.9626e-09 | 6.3447e-12 | -1.1053e-07 | -1.1625e-07 | -2.5428e-13 | -2.8654e-09 | 2.8656e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.00010577 | 1.6454 | 1.6453 | 0.00010576 | 1.6454 | 1.6453 | -43.6477 | -149.9959 | 150.0005 | -43.6472 | -149.9959 | 150.0005
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5438e-12 | 7.0432e-08 | -6.0512e-08 | 2.6654e-13 | -4.9631e-09 | -4.9626e-09 | 6.3447e-12 | -1.1053e-07 | -1.1625e-07 | -2.5428e-13 | -2.8654e-09 | 2.8656e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.00010577 | 1.6454 | 1.6453 | 0.00010576 | 1.6454 | 1.6453 | -43.6477 | -149.9959 | 150.0005 | -43.6472 | -149.9959 | 150.0005
Line1_1_3 | 2.7593e-06 | 2.7593e-06 | 2.7593e-06 | 2.4151e-06 | 2.4151e-06 | 2.4151e-06 | 6.3724e-07 | 6.3724e-07 | 6.3724e-07 | 5.5775e-07 | 5.5775e-07 | 5.5775e-07 | 4.4365e-11 | 5.6345e-07 | -4.841e-07 | -3.8493e-11 | -4.9799e-07 | 4.1862e-07 | 5.0772e-11 | -8.8425e-07 | -9.3002e-07 | -4.4617e-11 | 7.7086e-07 | 8.1663e-07 | -92.5017 | -92.5016 | -92.5016 | 87.1409 | 87.1409 | 87.1409 |  | 0.00010581 | 1.6454 | 1.6453 | 0.00010565 | 1.6454 | 1.6453 | -43.6487 | -149.9959 | 150.0005 | -43.6445 | -149.9959 | 150.0005
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1091e-11 | 1.4086e-07 | -1.2102e-07 | -5.2773e-12 | -7.5395e-08 | 5.5549e-08 | 1.2693e-11 | -2.2106e-07 | -2.325e-07 | -6.599e-12 | 1.0767e-07 | 1.1912e-07 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.00010581 | 1.6454 | 1.6453 | 0.00010577 | 1.6454 | 1.6453 | -43.6487 | -149.9959 | 150.0005 | -43.6477 | -149.9959 | 150.0005
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1091e-11 | 1.4086e-07 | -1.2102e-07 | -5.2773e-12 | -7.5395e-08 | 5.5549e-08 | 1.2693e-11 | -2.2106e-07 | -2.325e-07 | -6.599e-12 | 1.0767e-07 | 1.1912e-07 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.00010581 | 1.6454 | 1.6453 | 0.00010577 | 1.6454 | 1.6453 | -43.6487 | -149.9959 | 150.0005 | -43.6477 | -149.9959 | 150.0005
Line4_2_6 | 0.0002653 | 1.7246e-06 | 1.7246e-06 | 0.00026496 | 1.3804e-06 | 1.3804e-06 | 6.1269e-05 | 3.9828e-07 | 3.9828e-07 | 6.1189e-05 | 3.188e-07 | 3.188e-07 | 3.3652e-09 | 3.5217e-07 | -3.0256e-07 | -2.2396e-09 | -2.867e-07 | 2.3708e-07 | 3.5065e-09 | -5.5266e-07 | -5.8127e-07 | -2.3338e-09 | 4.3926e-07 | 4.6788e-07 | -89.826 | -92.5022 | -92.5022 | 90.1742 | 86.8723 | 86.8723 |  | 7.9323e-05 | 1.6454 | 1.6453 | 5.2861e-05 | 1.6454 | 1.6453 | -43.6477 | -149.9957 | 150.0005 | -43.6466 | -149.9956 | 150.0005
Line5_6_7 | 0.00026496 | 1.3797e-06 | 1.3797e-06 | 0.00026461 | 1.0355e-06 | 1.0355e-06 | 6.1189e-05 | 3.1863e-07 | 3.1863e-07 | 6.1109e-05 | 2.3915e-07 | 2.3915e-07 | 2.2397e-09 | 2.8174e-07 | -2.4204e-07 | -1.118e-09 | -2.1627e-07 | 1.7657e-07 | 2.3336e-09 | -4.4213e-07 | -4.6502e-07 | -1.1649e-09 | 3.2873e-07 | 3.5163e-07 | -89.8225 | -92.5023 | -92.5023 | 90.1777 | 86.664 | 86.664 |  | 5.2861e-05 | 1.6454 | 1.6453 | 2.642e-05 | 1.6454 | 1.6453 | -43.6466 | -149.9956 | 150.0005 | -43.6454 | -149.9954 | 150.0006
Line6_7_8 | 0.00026461 | 1.0348e-06 | 1.0348e-06 | 0.00026427 | 0 | 0 | 6.1109e-05 | 2.3897e-07 | 2.3897e-07 | 6.103e-05 | 0 | 0 | 1.118e-09 | 2.1131e-07 | -1.8153e-07 | 1.1472e-14 | -1.4583e-07 | 1.1606e-07 | 1.1648e-09 | -3.3159e-07 | -3.4876e-07 | 1.5934e-15 | 2.182e-07 | 2.3537e-07 | -89.819 | -92.5024 | -92.5024 | 90.1812 | 0 | 0 |  | 2.642e-05 | 1.6454 | 1.6453 | 0 | 1.6454 | 1.6453 | -43.6454 | -149.9954 | 150.0006 | 0 | -149.9952 | 150.0006
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.486e-17 | 7.0436e-08 | -6.051e-08 | -2.3898e-17 | -4.963e-09 | -4.9624e-09 | -2.7786e-18 | -1.1053e-07 | -1.1625e-07 | 2.7876e-17 | -2.8653e-09 | 2.8656e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 1.6454 | 1.6453 | 0 | 1.6454 | 1.6453 | 0 | -149.9952 | 150.0006 | 0 | -149.9952 | 150.0006
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.486e-17 | 7.0436e-08 | -6.051e-08 | -2.3898e-17 | -4.963e-09 | -4.9624e-09 | -2.7786e-18 | -1.1053e-07 | -1.1625e-07 | 2.7876e-17 | -2.8653e-09 | 2.8656e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 1.6454 | 1.6453 | 0 | 1.6454 | 1.6453 | 0 | -149.9952 | 150.0006 | 0 | -149.9952 | 150.0006
Line9_3_11 | 2.4144e-06 | 2.4144e-06 | 2.4144e-06 | 2.0702e-06 | 2.0702e-06 | 2.0702e-06 | 5.5759e-07 | 5.5759e-07 | 5.5759e-07 | 4.781e-07 | 4.781e-07 | 4.781e-07 | 3.8759e-11 | 4.9302e-07 | -4.2358e-07 | -3.2911e-11 | -4.2755e-07 | 3.5811e-07 | 4.4363e-11 | -7.7372e-07 | -8.1377e-07 | -3.8233e-11 | 6.6032e-07 | 7.0038e-07 | -92.5017 | -92.5016 | -92.5016 | 87.0813 | 87.0814 | 87.0814 |  | 0.00010565 | 1.6454 | 1.6453 | 0.00010552 | 1.6454 | 1.6453 | -43.6445 | -149.9959 | 150.0005 | -43.6409 | -149.9959 | 150.0005

## LG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.00025166 | 1.9606e-06 | 1.9606e-06 | 0.00025134 | 1.6345e-06 | 1.6345e-06 | 5.8119e-05 | 4.5278e-07 | 4.5278e-07 | 5.8044e-05 | 3.7748e-07 | 3.7748e-07 | 4.0336e-09 | 3.7929e-07 | -3.2586e-07 | -3.0201e-09 | -3.2053e-07 | 2.6709e-07 | 4.2034e-09 | -5.9522e-07 | -6.2603e-07 | -3.1473e-09 | 4.9344e-07 | 5.2427e-07 | -89.8295 | -92.5021 | -92.5021 | 90.1707 | 86.9974 | 86.9974 |  | 0.00010024 | 1.5588 | 1.5587 | 7.5148e-05 | 1.5588 | 1.5587 | -43.6487 | -149.9959 | 150.0005 | -43.6477 | -149.9957 | 150.0005
Line10_11_12 | 1.9606e-06 | 1.9606e-06 | 1.9606e-06 | 1.6345e-06 | 1.6345e-06 | 1.6345e-06 | 4.5278e-07 | 4.5278e-07 | 4.5278e-07 | 3.7747e-07 | 3.7747e-07 | 3.7747e-07 | 2.9777e-11 | 3.7928e-07 | -3.2586e-07 | -2.4547e-11 | -3.2052e-07 | 2.671e-07 | 3.4087e-11 | -5.9522e-07 | -6.2602e-07 | -2.8604e-11 | 4.9344e-07 | 5.2426e-07 | -92.5017 | -92.5016 | -92.5016 | 86.9979 | 86.998 | 86.998 |  | 9.9963e-05 | 1.5588 | 1.5587 | 9.9855e-05 | 1.5588 | 1.5587 | -43.6409 | -149.9959 | 150.0005 | -43.6377 | -149.9959 | 150.0005
Line11_12_13 | 1.6338e-06 | 1.6338e-06 | 1.6338e-06 | 1.3078e-06 | 1.3078e-06 | 1.3078e-06 | 3.7731e-07 | 3.7731e-07 | 3.7731e-07 | 3.0201e-07 | 3.0201e-07 | 3.0201e-07 | 2.4786e-11 | 3.1607e-07 | -2.7155e-07 | -1.9572e-11 | -2.5731e-07 | 2.1279e-07 | 2.8376e-11 | -4.9601e-07 | -5.2169e-07 | -2.2909e-11 | 3.9424e-07 | 4.1992e-07 | -92.5017 | -92.5016 | -92.5016 | 86.8729 | 86.873 | 86.873 |  | 9.9855e-05 | 1.5588 | 1.5587 | 9.9767e-05 | 1.5588 | 1.5587 | -43.6377 | -149.9959 | 150.0005 | -43.6351 | -149.9959 | 150.0005
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4857e-11 | 1.8964e-07 | -1.6293e-07 | -9.6617e-12 | -1.3088e-07 | 1.0417e-07 | 1.7011e-11 | -2.9761e-07 | -3.1301e-07 | -1.1563e-11 | 1.9583e-07 | 2.1125e-07 | 0 | 0 | 0 | 0 | 0 | 0 |  | 9.9767e-05 | 1.5588 | 1.5587 | 9.9718e-05 | 1.5588 | 1.5587 | -43.6351 | -149.9959 | 150.0005 | -43.6335 | -149.9959 | 150.0005
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.9525e-12 | 6.3213e-08 | -5.431e-08 | 2.3822e-13 | -4.4544e-09 | -4.454e-09 | 5.6705e-12 | -9.9203e-08 | -1.0434e-07 | -2.2717e-13 | -2.5717e-09 | 2.5719e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 9.9767e-05 | 1.5588 | 1.5587 | 9.9757e-05 | 1.5588 | 1.5587 | -43.6351 | -149.9959 | 150.0005 | -43.6346 | -149.9959 | 150.0005
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.8998e-12 | 1.2643e-07 | -1.0862e-07 | -4.7103e-12 | -6.7667e-08 | 4.9856e-08 | 1.1336e-11 | -1.9841e-07 | -2.0867e-07 | -5.8932e-12 | 9.6631e-08 | 1.0691e-07 | 0 | 0 | 0 | 0 | 0 | 0 |  | 9.9718e-05 | 1.5588 | 1.5587 | 9.9689e-05 | 1.5588 | 1.5587 | -43.6335 | -149.9959 | 150.0005 | -43.6325 | -149.9959 | 150.0005
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.9483e-12 | 6.3213e-08 | -5.431e-08 | 2.3805e-13 | -4.4544e-09 | -4.454e-09 | 5.6662e-12 | -9.9203e-08 | -1.0434e-07 | -2.2698e-13 | -2.5717e-09 | 2.5719e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 9.9689e-05 | 1.5588 | 1.5587 | 9.9679e-05 | 1.5588 | 1.5587 | -43.6325 | -149.9959 | 150.0005 | -43.632 | -149.9959 | 150.0005
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.9756e-12 | 6.3213e-08 | -5.431e-08 | 2.3923e-13 | -4.4544e-09 | -4.454e-09 | 5.6944e-12 | -9.9203e-08 | -1.0434e-07 | -2.2822e-13 | -2.5717e-09 | 2.5719e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.00010021 | 1.5588 | 1.5587 | 0.0001002 | 1.5588 | 1.5587 | -43.6477 | -149.9959 | 150.0005 | -43.6472 | -149.9959 | 150.0005
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.9756e-12 | 6.3213e-08 | -5.431e-08 | 2.3923e-13 | -4.4544e-09 | -4.454e-09 | 5.6944e-12 | -9.9203e-08 | -1.0434e-07 | -2.2822e-13 | -2.5717e-09 | 2.5719e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.00010021 | 1.5588 | 1.5587 | 0.0001002 | 1.5588 | 1.5587 | -43.6477 | -149.9959 | 150.0005 | -43.6472 | -149.9959 | 150.0005
Line1_1_3 | 2.6141e-06 | 2.6141e-06 | 2.6141e-06 | 2.288e-06 | 2.288e-06 | 2.288e-06 | 6.037e-07 | 6.037e-07 | 6.037e-07 | 5.2839e-07 | 5.2839e-07 | 5.2839e-07 | 3.9817e-11 | 5.057e-07 | -4.3448e-07 | -3.4547e-11 | -4.4695e-07 | 3.7571e-07 | 4.5568e-11 | -7.9362e-07 | -8.347e-07 | -4.0044e-11 | 6.9185e-07 | 7.3293e-07 | -92.5017 | -92.5016 | -92.5016 | 87.1409 | 87.1409 | 87.1409 |  | 0.00010024 | 1.5588 | 1.5587 | 0.00010009 | 1.5588 | 1.5587 | -43.6487 | -149.9959 | 150.0005 | -43.6445 | -149.9959 | 150.0005
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.9544e-12 | 1.2643e-07 | -1.0862e-07 | -4.7364e-12 | -6.7667e-08 | 4.9856e-08 | 1.1392e-11 | -1.9841e-07 | -2.0867e-07 | -5.9227e-12 | 9.6631e-08 | 1.0691e-07 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.00010024 | 1.5588 | 1.5587 | 0.00010021 | 1.5588 | 1.5587 | -43.6487 | -149.9959 | 150.0005 | -43.6477 | -149.9959 | 150.0005
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.9544e-12 | 1.2643e-07 | -1.0862e-07 | -4.7364e-12 | -6.7667e-08 | 4.9856e-08 | 1.1392e-11 | -1.9841e-07 | -2.0867e-07 | -5.9227e-12 | 9.6631e-08 | 1.0691e-07 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.00010024 | 1.5588 | 1.5587 | 0.00010021 | 1.5588 | 1.5587 | -43.6487 | -149.9959 | 150.0005 | -43.6477 | -149.9959 | 150.0005
Line4_2_6 | 0.00025134 | 1.6338e-06 | 1.6338e-06 | 0.00025101 | 1.3078e-06 | 1.3078e-06 | 5.8044e-05 | 3.7732e-07 | 3.7732e-07 | 5.7969e-05 | 3.0202e-07 | 3.0202e-07 | 3.0203e-09 | 3.1608e-07 | -2.7155e-07 | -2.0101e-09 | -2.5732e-07 | 2.1278e-07 | 3.1471e-09 | -4.9602e-07 | -5.217e-07 | -2.0946e-09 | 3.9424e-07 | 4.1993e-07 | -89.826 | -92.5022 | -92.5022 | 90.1742 | 86.8723 | 86.8723 |  | 7.5148e-05 | 1.5588 | 1.5587 | 5.0079e-05 | 1.5588 | 1.5587 | -43.6477 | -149.9957 | 150.0005 | -43.6466 | -149.9956 | 150.0005
Line5_6_7 | 0.00025101 | 1.3071e-06 | 1.3071e-06 | 0.00025068 | 0 | 0 | 5.7969e-05 | 3.0186e-07 | 3.0186e-07 | 5.7893e-05 | 0 | 0 | 2.0102e-09 | 2.5286e-07 | -2.1724e-07 | -1.0034e-09 | -1.941e-07 | 1.5847e-07 | 2.0944e-09 | -3.9681e-07 | -4.1736e-07 | -1.0455e-09 | 2.9504e-07 | 3.1559e-07 | -89.8225 | -92.5023 | -92.5023 | 90.1777 | 0 | 0 |  | 5.0079e-05 | 1.5588 | 1.5587 | 2.503e-05 | 1.5588 | 1.5587 | -43.6466 | -149.9956 | 150.0005 | -43.6454 | -149.9954 | 150.0006
Line6_7_8 | 0.00025068 | 0 | 0 | 0.00025036 | 0 | 0 | 5.7893e-05 | 0 | 0 | 5.7818e-05 | 0 | 0 | 1.0034e-09 | 1.8965e-07 | -1.6293e-07 | 1.0296e-14 | -1.3089e-07 | 1.0416e-07 | 1.0454e-09 | -2.9761e-07 | -3.1302e-07 | 1.4301e-15 | 1.9583e-07 | 2.1125e-07 | -89.819 | 0 | 0 | 90.1812 | 0 | 0 |  | 2.503e-05 | 1.5588 | 1.5587 | 0 | 1.5588 | 1.5587 | -43.6454 | -149.9954 | 150.0006 | 0 | -149.9952 | 150.0006
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.3337e-17 | 6.3217e-08 | -5.4308e-08 | -2.1449e-17 | -4.4543e-09 | -4.4538e-09 | -2.4938e-18 | -9.9203e-08 | -1.0434e-07 | 2.5019e-17 | -2.5716e-09 | 2.5719e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 1.5588 | 1.5587 | 0 | 1.5588 | 1.5587 | 0 | -149.9952 | 150.0006 | 0 | -149.9952 | 150.0006
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.3337e-17 | 6.3217e-08 | -5.4308e-08 | -2.1449e-17 | -4.4543e-09 | -4.4538e-09 | -2.4938e-18 | -9.9203e-08 | -1.0434e-07 | 2.5019e-17 | -2.5716e-09 | 2.5719e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 1.5588 | 1.5587 | 0 | 1.5588 | 1.5587 | 0 | -149.9952 | 150.0006 | 0 | -149.9952 | 150.0006
Line9_3_11 | 2.2873e-06 | 2.2873e-06 | 2.2873e-06 | 1.9613e-06 | 1.9613e-06 | 1.9613e-06 | 5.2824e-07 | 5.2824e-07 | 5.2824e-07 | 4.5293e-07 | 4.5293e-07 | 4.5293e-07 | 3.4786e-11 | 4.4249e-07 | -3.8017e-07 | -2.9538e-11 | -3.8373e-07 | 3.2141e-07 | 3.9816e-11 | -6.9442e-07 | -7.3036e-07 | -3.4314e-11 | 5.9265e-07 | 6.286e-07 | -92.5017 | -92.5016 | -92.5016 | 87.0813 | 87.0814 | 87.0814 |  | 0.00010009 | 1.5588 | 1.5587 | 9.9963e-05 | 1.5588 | 1.5587 | -43.6445 | -149.9959 | 150.0005 | -43.6409 | -149.9959 | 150.0005

## LG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.00026405 | 2.0571e-06 | 2.0571e-06 | 0.00026371 | 1.715e-06 | 1.715e-06 | 6.098e-05 | 4.7507e-07 | 4.7507e-07 | 6.09e-05 | 3.9606e-07 | 3.9606e-07 | 3.5021e-07 | 4.187e-07 | -3.6244e-07 | -3.4865e-07 | -3.5385e-07 | 2.9714e-07 | 3.5065e-07 | -6.5888e-07 | -6.8836e-07 | -3.4904e-07 | 5.4623e-07 | 5.7649e-07 | -89.4885 | -92.1612 | -92.1612 | 90.5117 | 87.3384 | 87.3384 |  | 0.0081271 | 1.6433 | 1.6376 | 0.0081007 | 1.6433 | 1.6375 | -44.4525 | -149.7265 | 150.0706 | -44.4563 | -149.7263 | 150.0706
Line10_11_12 | 2.0571e-06 | 2.0571e-06 | 2.0571e-06 | 1.7149e-06 | 1.7149e-06 | 1.7149e-06 | 4.7506e-07 | 4.7506e-07 | 4.7506e-07 | 3.9605e-07 | 3.9605e-07 | 3.9605e-07 | 2.5979e-09 | 4.1869e-07 | -3.6244e-07 | -2.1449e-09 | -3.5384e-07 | 2.9714e-07 | 2.8559e-09 | -6.5888e-07 | -6.8835e-07 | -2.3997e-09 | 5.4622e-07 | 5.7648e-07 | -92.1607 | -92.1606 | -92.1606 | 87.3389 | 87.339 | 87.339 |  | 0.0081268 | 1.6433 | 1.6376 | 0.0081267 | 1.6433 | 1.6376 | -44.4525 | -149.7265 | 150.0705 | -44.4525 | -149.7265 | 150.0705
Line11_12_13 | 1.7142e-06 | 1.7142e-06 | 1.7142e-06 | 1.3721e-06 | 1.3721e-06 | 1.3721e-06 | 3.9588e-07 | 3.9588e-07 | 3.9588e-07 | 3.1688e-07 | 3.1688e-07 | 3.1688e-07 | 2.1649e-09 | 3.4891e-07 | -3.0204e-07 | -1.7119e-09 | -2.8405e-07 | 2.3673e-07 | 2.3799e-09 | -5.4906e-07 | -5.7362e-07 | -1.9237e-09 | 4.3641e-07 | 4.6176e-07 | -92.1607 | -92.1606 | -92.1606 | 87.2139 | 87.214 | 87.214 |  | 0.0081267 | 1.6433 | 1.6376 | 0.0081266 | 1.6433 | 1.6376 | -44.4525 | -149.7265 | 150.0705 | -44.4524 | -149.7265 | 150.0705
Line12_13_15 | 1.0285e-06 | 1.0285e-06 | 1.0285e-06 | 0 | 0 | 0 | 2.3753e-07 | 2.3753e-07 | 2.3753e-07 | 0 | 0 | 0 | 1.2989e-09 | 2.0934e-07 | -1.8122e-07 | -8.4597e-10 | -1.4449e-07 | 1.1592e-07 | 1.4279e-09 | -3.2944e-07 | -3.4417e-07 | -9.7175e-10 | 2.1679e-07 | 2.3231e-07 | -92.1607 | -92.1606 | -92.1606 | 0 | 0 | 0 |  | 0.0081266 | 1.6433 | 1.6376 | 0.0081265 | 1.6433 | 1.6376 | -44.4524 | -149.7265 | 150.0705 | -44.4524 | -149.7265 | 150.0705
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3297e-10 | 6.9781e-08 | -6.0407e-08 | 1.9965e-11 | -4.9304e-09 | -4.8961e-09 | 4.7597e-10 | -1.0981e-07 | -1.1472e-07 | -1.9824e-11 | -2.8383e-09 | 2.8582e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.0081266 | 1.6433 | 1.6376 | 0.0081265 | 1.6433 | 1.6376 | -44.4524 | -149.7265 | 150.0705 | -44.4524 | -149.7265 | 150.0705
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.6593e-10 | 1.3956e-07 | -1.2081e-07 | -4.13e-10 | -7.4711e-08 | 5.5511e-08 | 9.5193e-10 | -2.1963e-07 | -2.2945e-07 | -4.9579e-10 | 1.0697e-07 | 1.1758e-07 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.0081265 | 1.6433 | 1.6376 | 0.0081265 | 1.6433 | 1.6376 | -44.4524 | -149.7265 | 150.0705 | -44.4524 | -149.7265 | 150.0705
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3297e-10 | 6.9781e-08 | -6.0407e-08 | 1.9964e-11 | -4.9304e-09 | -4.8961e-09 | 4.7596e-10 | -1.0981e-07 | -1.1472e-07 | -1.9824e-11 | -2.8383e-09 | 2.8582e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.0081265 | 1.6433 | 1.6376 | 0.0081265 | 1.6433 | 1.6376 | -44.4524 | -149.7265 | 150.0705 | -44.4524 | -149.7265 | 150.0705
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.33e-10 | 6.9781e-08 | -6.0407e-08 | 1.9966e-11 | -4.9304e-09 | -4.8961e-09 | 4.7599e-10 | -1.0981e-07 | -1.1472e-07 | -1.9825e-11 | -2.8383e-09 | 2.8582e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.008127 | 1.6433 | 1.6376 | 0.008127 | 1.6433 | 1.6376 | -44.4525 | -149.7265 | 150.0706 | -44.4525 | -149.7265 | 150.0706
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.33e-10 | 6.9781e-08 | -6.0407e-08 | 1.9966e-11 | -4.9304e-09 | -4.8961e-09 | 4.7599e-10 | -1.0981e-07 | -1.1472e-07 | -1.9825e-11 | -2.8383e-09 | 2.8582e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.008127 | 1.6433 | 1.6376 | 0.008127 | 1.6433 | 1.6376 | -44.4525 | -149.7265 | 150.0706 | -44.4525 | -149.7265 | 150.0706
Line1_1_3 | 2.7428e-06 | 2.7428e-06 | 2.7428e-06 | 2.4006e-06 | 2.4006e-06 | 2.4006e-06 | 6.3341e-07 | 6.3341e-07 | 6.3341e-07 | 5.544e-07 | 5.544e-07 | 5.544e-07 | 3.464e-09 | 5.5825e-07 | -4.8326e-07 | -3.011e-09 | -4.934e-07 | 4.1796e-07 | 3.808e-09 | -8.785e-07 | -9.1779e-07 | -3.3517e-09 | 7.6585e-07 | 8.0593e-07 | -92.1607 | -92.1606 | -92.1606 | 87.4818 | 87.4819 | 87.4819 |  | 0.0081271 | 1.6433 | 1.6376 | 0.0081269 | 1.6433 | 1.6376 | -44.4525 | -149.7265 | 150.0706 | -44.4525 | -149.7265 | 150.0705
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.6599e-10 | 1.3956e-07 | -1.2081e-07 | -4.1303e-10 | -7.4711e-08 | 5.5511e-08 | 9.5199e-10 | -2.1962e-07 | -2.2945e-07 | -4.9582e-10 | 1.0697e-07 | 1.1758e-07 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.0081271 | 1.6433 | 1.6376 | 0.008127 | 1.6433 | 1.6376 | -44.4525 | -149.7265 | 150.0706 | -44.4525 | -149.7265 | 150.0706
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.6599e-10 | 1.3956e-07 | -1.2081e-07 | -4.1303e-10 | -7.4711e-08 | 5.5511e-08 | 9.5199e-10 | -2.1962e-07 | -2.2945e-07 | -4.9582e-10 | 1.0697e-07 | 1.1758e-07 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.0081271 | 1.6433 | 1.6376 | 0.008127 | 1.6433 | 1.6376 | -44.4525 | -149.7265 | 150.0706 | -44.4525 | -149.7265 | 150.0706
Line4_2_6 | 0.00026371 | 1.7142e-06 | 1.7142e-06 | 0.00026336 | 1.3721e-06 | 1.3721e-06 | 6.09e-05 | 3.9589e-07 | 3.9589e-07 | 6.0821e-05 | 3.1688e-07 | 3.1688e-07 | 3.4867e-07 | 3.4892e-07 | -3.0203e-07 | -3.4711e-07 | -2.8407e-07 | 2.3673e-07 | 3.4902e-07 | -5.4906e-07 | -5.7363e-07 | -3.4741e-07 | 4.3641e-07 | 4.6176e-07 | -89.4851 | -92.1612 | -92.1612 | 90.5152 | 87.2133 | 87.2133 |  | 0.0081007 | 1.6433 | 1.6375 | 0.0080744 | 1.6433 | 1.6375 | -44.4563 | -149.7263 | 150.0706 | -44.46 | -149.7261 | 150.0706
Line5_6_7 | 0.00026336 | 1.3714e-06 | 1.3714e-06 | 0.00026302 | 1.0293e-06 | 1.0293e-06 | 6.0821e-05 | 3.1671e-07 | 3.1671e-07 | 6.0742e-05 | 2.3771e-07 | 2.3771e-07 | 3.4713e-07 | 2.7914e-07 | -2.4163e-07 | -3.4557e-07 | -2.1428e-07 | 1.7632e-07 | 3.4739e-07 | -4.3925e-07 | -4.589e-07 | -3.4578e-07 | 3.266e-07 | 3.4704e-07 | -89.4816 | -92.1613 | -92.1613 | 90.5187 | 87.0049 | 87.0049 |  | 0.0080744 | 1.6433 | 1.6375 | 0.0080482 | 1.6433 | 1.6375 | -44.46 | -149.7261 | 150.0706 | -44.4638 | -149.7259 | 150.0707
Line6_7_8 | 0.00026302 | 1.0286e-06 | 1.0286e-06 | 0.00026268 | 0 | 0 | 6.0742e-05 | 2.3753e-07 | 2.3753e-07 | 6.0663e-05 | 0 | 0 | 3.4559e-07 | 2.0935e-07 | -1.8122e-07 | -3.4404e-07 | -1.445e-07 | 1.1592e-07 | 3.4577e-07 | -3.2944e-07 | -3.4418e-07 | -3.4416e-07 | 2.1679e-07 | 2.3231e-07 | -89.4781 | -92.1614 | -92.1614 | 90.5221 | 0 | 0 |  | 0.0080482 | 1.6433 | 1.6375 | 0.0080219 | 1.6433 | 1.6375 | -44.4638 | -149.7259 | 150.0707 | -44.4676 | -149.7258 | 150.0707
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2752e-10 | 6.9785e-08 | -6.0406e-08 | 1.9705e-11 | -4.9303e-09 | -4.8959e-09 | 4.6974e-10 | -1.0981e-07 | -1.1473e-07 | -1.9574e-11 | -2.8383e-09 | 2.8581e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.0080219 | 1.6433 | 1.6375 | 0.0080219 | 1.6433 | 1.6375 | -44.4676 | -149.7258 | 150.0707 | -44.4675 | -149.7258 | 150.0707
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2752e-10 | 6.9785e-08 | -6.0406e-08 | 1.9705e-11 | -4.9303e-09 | -4.8959e-09 | 4.6974e-10 | -1.0981e-07 | -1.1473e-07 | -1.9574e-11 | -2.8383e-09 | 2.8581e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.0080219 | 1.6433 | 1.6375 | 0.0080219 | 1.6433 | 1.6375 | -44.4676 | -149.7258 | 150.0707 | -44.4675 | -149.7258 | 150.0707
Line9_3_11 | 2.3999e-06 | 2.3999e-06 | 2.3999e-06 | 2.0578e-06 | 2.0578e-06 | 2.0578e-06 | 5.5424e-07 | 5.5424e-07 | 5.5424e-07 | 4.7522e-07 | 4.7522e-07 | 4.7522e-07 | 3.0309e-09 | 4.8847e-07 | -4.2285e-07 | -2.5779e-09 | -4.2362e-07 | 3.5755e-07 | 3.3319e-09 | -7.6869e-07 | -8.0307e-07 | -2.8757e-09 | 6.5604e-07 | 6.912e-07 | -92.1607 | -92.1606 | -92.1606 | 87.4223 | 87.4224 | 87.4224 |  | 0.0081269 | 1.6433 | 1.6376 | 0.0081268 | 1.6433 | 1.6376 | -44.4525 | -149.7265 | 150.0705 | -44.4525 | -149.7265 | 150.0705

## LG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.00025015 | 1.9488e-06 | 1.9488e-06 | 0.00024983 | 1.6247e-06 | 1.6247e-06 | 5.777e-05 | 4.5006e-07 | 4.5006e-07 | 5.7695e-05 | 3.7521e-07 | 3.7521e-07 | 3.1432e-07 | 3.7578e-07 | -3.2529e-07 | -3.1291e-07 | -3.1758e-07 | 2.6668e-07 | 3.1471e-07 | -5.9135e-07 | -6.178e-07 | -3.1326e-07 | 4.9024e-07 | 5.174e-07 | -89.4885 | -92.1612 | -92.1612 | 90.5117 | 87.3384 | 87.3384 |  | 0.0076993 | 1.5568 | 1.5514 | 0.0076744 | 1.5568 | 1.5514 | -44.4525 | -149.7265 | 150.0706 | -44.4563 | -149.7263 | 150.0706
Line10_11_12 | 1.9488e-06 | 1.9488e-06 | 1.9488e-06 | 1.6247e-06 | 1.6247e-06 | 1.6247e-06 | 4.5006e-07 | 4.5006e-07 | 4.5006e-07 | 3.7521e-07 | 3.7521e-07 | 3.7521e-07 | 2.3316e-09 | 3.7577e-07 | -3.253e-07 | -1.9251e-09 | -3.1757e-07 | 2.6669e-07 | 2.5632e-09 | -5.9134e-07 | -6.178e-07 | -2.1537e-09 | 4.9024e-07 | 5.1739e-07 | -92.1607 | -92.1606 | -92.1606 | 87.3389 | 87.339 | 87.339 |  | 0.007699 | 1.5568 | 1.5514 | 0.0076989 | 1.5568 | 1.5514 | -44.4525 | -149.7265 | 150.0705 | -44.4525 | -149.7265 | 150.0705
Line11_12_13 | 1.624e-06 | 1.624e-06 | 1.624e-06 | 1.2999e-06 | 1.2999e-06 | 1.2999e-06 | 3.7505e-07 | 3.7505e-07 | 3.7505e-07 | 3.002e-07 | 3.002e-07 | 3.002e-07 | 1.943e-09 | 3.1314e-07 | -2.7108e-07 | -1.5365e-09 | -2.5494e-07 | 2.1247e-07 | 2.1359e-09 | -4.9279e-07 | -5.1483e-07 | -1.7265e-09 | 3.9168e-07 | 4.1443e-07 | -92.1607 | -92.1606 | -92.1606 | 87.2139 | 87.214 | 87.214 |  | 0.0076989 | 1.5568 | 1.5514 | 0.0076988 | 1.5568 | 1.5514 | -44.4525 | -149.7265 | 150.0705 | -44.4524 | -149.7265 | 150.0705
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1658e-09 | 1.8789e-07 | -1.6265e-07 | -7.5926e-10 | -1.2968e-07 | 1.0404e-07 | 1.2815e-09 | -2.9567e-07 | -3.089e-07 | -8.7215e-10 | 1.9457e-07 | 2.085e-07 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.0076988 | 1.5568 | 1.5514 | 0.0076988 | 1.5568 | 1.5514 | -44.4524 | -149.7265 | 150.0705 | -44.4524 | -149.7265 | 150.0705
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8859e-10 | 6.2629e-08 | -5.4216e-08 | 1.7918e-11 | -4.4251e-09 | -4.3943e-09 | 4.2718e-10 | -9.8557e-08 | -1.0297e-07 | -1.7792e-11 | -2.5474e-09 | 2.5652e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.0076988 | 1.5568 | 1.5514 | 0.0076988 | 1.5568 | 1.5514 | -44.4524 | -149.7265 | 150.0705 | -44.4524 | -149.7265 | 150.0705
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7718e-10 | 1.2526e-07 | -1.0843e-07 | -3.7067e-10 | -6.7054e-08 | 4.9822e-08 | 8.5436e-10 | -1.9711e-07 | -2.0593e-07 | -4.4497e-10 | 9.601e-08 | 1.0553e-07 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.0076988 | 1.5568 | 1.5514 | 0.0076988 | 1.5568 | 1.5514 | -44.4524 | -149.7265 | 150.0705 | -44.4524 | -149.7265 | 150.0705
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8859e-10 | 6.2629e-08 | -5.4216e-08 | 1.7918e-11 | -4.4251e-09 | -4.3943e-09 | 4.2718e-10 | -9.8558e-08 | -1.0297e-07 | -1.7792e-11 | -2.5474e-09 | 2.5652e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.0076988 | 1.5568 | 1.5514 | 0.0076988 | 1.5568 | 1.5514 | -44.4524 | -149.7265 | 150.0705 | -44.4524 | -149.7265 | 150.0705
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8862e-10 | 6.2629e-08 | -5.4216e-08 | 1.7919e-11 | -4.4251e-09 | -4.3942e-09 | 4.2721e-10 | -9.8557e-08 | -1.0297e-07 | -1.7793e-11 | -2.5474e-09 | 2.5652e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.0076993 | 1.5568 | 1.5514 | 0.0076993 | 1.5568 | 1.5514 | -44.4525 | -149.7265 | 150.0706 | -44.4525 | -149.7265 | 150.0706
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8862e-10 | 6.2629e-08 | -5.4216e-08 | 1.7919e-11 | -4.4251e-09 | -4.3942e-09 | 4.2721e-10 | -9.8557e-08 | -1.0297e-07 | -1.7793e-11 | -2.5474e-09 | 2.5652e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.0076993 | 1.5568 | 1.5514 | 0.0076993 | 1.5568 | 1.5514 | -44.4525 | -149.7265 | 150.0706 | -44.4525 | -149.7265 | 150.0706
Line1_1_3 | 2.5984e-06 | 2.5984e-06 | 2.5984e-06 | 2.2743e-06 | 2.2743e-06 | 2.2743e-06 | 6.0008e-07 | 6.0008e-07 | 6.0008e-07 | 5.2522e-07 | 5.2522e-07 | 5.2522e-07 | 3.1089e-09 | 5.0103e-07 | -4.3373e-07 | -2.7024e-09 | -4.4283e-07 | 3.7512e-07 | 3.4177e-09 | -7.8846e-07 | -8.2373e-07 | -3.0082e-09 | 6.8735e-07 | 7.2333e-07 | -92.1607 | -92.1606 | -92.1606 | 87.4818 | 87.4819 | 87.4819 |  | 0.0076993 | 1.5568 | 1.5514 | 0.0076992 | 1.5568 | 1.5514 | -44.4525 | -149.7265 | 150.0706 | -44.4525 | -149.7265 | 150.0705
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7724e-10 | 1.2526e-07 | -1.0843e-07 | -3.707e-10 | -6.7054e-08 | 4.9822e-08 | 8.5442e-10 | -1.9711e-07 | -2.0593e-07 | -4.45e-10 | 9.601e-08 | 1.0553e-07 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.0076993 | 1.5568 | 1.5514 | 0.0076993 | 1.5568 | 1.5514 | -44.4525 | -149.7265 | 150.0706 | -44.4525 | -149.7265 | 150.0706
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7724e-10 | 1.2526e-07 | -1.0843e-07 | -3.707e-10 | -6.7054e-08 | 4.9822e-08 | 8.5442e-10 | -1.9711e-07 | -2.0593e-07 | -4.45e-10 | 9.601e-08 | 1.0553e-07 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.0076993 | 1.5568 | 1.5514 | 0.0076993 | 1.5568 | 1.5514 | -44.4525 | -149.7265 | 150.0706 | -44.4525 | -149.7265 | 150.0706
Line4_2_6 | 0.00024983 | 1.624e-06 | 1.624e-06 | 0.0002495 | 1.2999e-06 | 1.2999e-06 | 5.7695e-05 | 3.7505e-07 | 3.7505e-07 | 5.762e-05 | 3.002e-07 | 3.002e-07 | 3.1293e-07 | 3.1316e-07 | -2.7108e-07 | -3.1153e-07 | -2.5495e-07 | 2.1247e-07 | 3.1325e-07 | -4.9279e-07 | -5.1484e-07 | -3.118e-07 | 3.9168e-07 | 4.1444e-07 | -89.4851 | -92.1612 | -92.1612 | 90.5152 | 87.2133 | 87.2133 |  | 0.0076744 | 1.5568 | 1.5514 | 0.0076495 | 1.5568 | 1.5514 | -44.4563 | -149.7263 | 150.0706 | -44.46 | -149.7261 | 150.0706
Line5_6_7 | 0.0002495 | 1.2992e-06 | 1.2992e-06 | 0.00024918 | 0 | 0 | 5.762e-05 | 3.0004e-07 | 3.0004e-07 | 5.7545e-05 | 0 | 0 | 3.1155e-07 | 2.5053e-07 | -2.1686e-07 | -3.1015e-07 | -1.9232e-07 | 1.5825e-07 | 3.1178e-07 | -3.9423e-07 | -4.1187e-07 | -3.1034e-07 | 2.9312e-07 | 3.1147e-07 | -89.4816 | -92.1613 | -92.1613 | 90.5187 | 0 | 0 |  | 0.0076495 | 1.5568 | 1.5514 | 0.0076246 | 1.5568 | 1.5514 | -44.46 | -149.7261 | 150.0706 | -44.4638 | -149.7259 | 150.0707
Line6_7_8 | 0.00024918 | 0 | 0 | 0.00024885 | 0 | 0 | 5.7545e-05 | 0 | 0 | 5.747e-05 | 0 | 0 | 3.1017e-07 | 1.879e-07 | -1.6264e-07 | -3.0878e-07 | -1.2969e-07 | 1.0404e-07 | 3.1033e-07 | -2.9567e-07 | -3.089e-07 | -3.0889e-07 | 1.9457e-07 | 2.085e-07 | -89.4781 | 0 | 0 | 90.5221 | 0 | 0 |  | 0.0076246 | 1.5568 | 1.5514 | 0.0075997 | 1.5568 | 1.5513 | -44.4638 | -149.7259 | 150.0707 | -44.4676 | -149.7258 | 150.0707
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.837e-10 | 6.2632e-08 | -5.4215e-08 | 1.7686e-11 | -4.425e-09 | -4.3941e-09 | 4.2159e-10 | -9.8557e-08 | -1.0297e-07 | -1.7568e-11 | -2.5474e-09 | 2.5652e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.0075997 | 1.5568 | 1.5513 | 0.0075997 | 1.5568 | 1.5513 | -44.4676 | -149.7258 | 150.0707 | -44.4675 | -149.7258 | 150.0707
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.837e-10 | 6.2632e-08 | -5.4215e-08 | 1.7686e-11 | -4.425e-09 | -4.3941e-09 | 4.2159e-10 | -9.8557e-08 | -1.0297e-07 | -1.7568e-11 | -2.5474e-09 | 2.5652e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.0075997 | 1.5568 | 1.5513 | 0.0075997 | 1.5568 | 1.5513 | -44.4676 | -149.7258 | 150.0707 | -44.4675 | -149.7258 | 150.0707
Line9_3_11 | 2.2736e-06 | 2.2736e-06 | 2.2736e-06 | 1.9495e-06 | 1.9495e-06 | 1.9495e-06 | 5.2507e-07 | 5.2507e-07 | 5.2507e-07 | 4.5021e-07 | 4.5021e-07 | 4.5021e-07 | 2.7203e-09 | 4.384e-07 | -3.7951e-07 | -2.3137e-09 | -3.802e-07 | 3.209e-07 | 2.9904e-09 | -6.899e-07 | -7.2076e-07 | -2.581e-09 | 5.888e-07 | 6.2036e-07 | -92.1607 | -92.1606 | -92.1606 | 87.4223 | 87.4224 | 87.4224 |  | 0.0076992 | 1.5568 | 1.5514 | 0.007699 | 1.5568 | 1.5514 | -44.4525 | -149.7265 | 150.0705 | -44.4525 | -149.7265 | 150.0705

## LLG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 1.1438e-06 | 1.885 | 1.8851 | 0 | 1.885 | 1.8851 | 2.6414e-07 | 0.43533 | 0.43534 | 0 | 0.43533 | 0.43534 | 1.8188e-08 | 0.14213 | 0.14214 | -1.8189e-08 | -0.1066 | -0.10661 | -4.1562e-07 | 0.28427 | 0.28428 | 3.4635e-07 | -0.2132 | -0.21321 | 87.4946 | -157.885 | 22.1192 | 0 | 22.1151 | -157.8808 |  | 1.575 | 0.73007 | 0.73008 | 1.575 | 0.54755 | 0.54756 | 0.00032801 | -94.4493 | 85.5535 | 0.0003651 | -94.4493 | 85.5535
Line10_11_12 | 1.1437e-06 | 1.1608e-06 | 1.1267e-06 | 0 | 0 | 0 | 2.6414e-07 | 2.6807e-07 | 2.6021e-07 | 0 | 0 | 0 | 1.8186e-08 | -1.9556e-07 | 1.899e-07 | -1.8186e-08 | 1.6355e-07 | -1.5788e-07 | -4.1561e-07 | 7.6747e-09 | -5.4002e-09 | 3.4634e-07 | -5.1832e-09 | 2.9103e-09 | 87.4949 | 87.7981 | 87.1824 | 0 | 0 | 0 |  | 1.575 | 0.73007 | 0.73008 | 1.575 | 0.73007 | 0.73008 | 0.00032572 | -94.4493 | 85.5535 | 0.00032481 | -94.4493 | 85.5535
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5155e-08 | -1.6297e-07 | 1.5825e-07 | -1.5156e-08 | 1.3096e-07 | -1.2623e-07 | -3.4634e-07 | 6.3955e-09 | -4.5002e-09 | 2.7707e-07 | -3.9041e-09 | 2.0103e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.575 | 0.73007 | 0.73008 | 1.575 | 0.73007 | 0.73008 | 0.00032481 | -94.4493 | 85.5535 | 0.00032407 | -94.4493 | 85.5534
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0929e-09 | -9.7781e-08 | 9.4948e-08 | -9.0936e-09 | 6.5769e-08 | -6.2935e-08 | -2.0781e-07 | 3.8373e-09 | -2.7001e-09 | 1.3854e-07 | -1.3459e-09 | 2.1018e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.575 | 0.73007 | 0.73008 | 1.575 | 0.73007 | 0.73008 | 0.00032407 | -94.4493 | 85.5534 | 0.00032366 | -94.4493 | 85.5534
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.031e-09 | -3.2594e-08 | 3.1649e-08 | -3.0317e-09 | 5.8155e-10 | 3.6355e-10 | -6.9269e-08 | 1.2791e-09 | -9.0004e-10 | 3.4498e-14 | 1.2123e-09 | -1.5899e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.575 | 0.73007 | 0.73008 | 1.575 | 0.73007 | 0.73008 | 0.00032407 | -94.4493 | 85.5534 | 0.00032398 | -94.4493 | 85.5534
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0619e-09 | -6.5187e-08 | 6.3299e-08 | -6.0626e-09 | 3.3175e-08 | -3.1286e-08 | -1.3854e-07 | 2.5582e-09 | -1.8001e-09 | 6.9269e-08 | -6.6796e-11 | -6.8986e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.575 | 0.73007 | 0.73008 | 1.575 | 0.73007 | 0.73008 | 0.00032366 | -94.4493 | 85.5534 | 0.00032341 | -94.4493 | 85.5534
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.031e-09 | -3.2594e-08 | 3.1649e-08 | -3.0317e-09 | 5.8155e-10 | 3.6354e-10 | -6.9269e-08 | 1.2791e-09 | -9.0004e-10 | 3.4534e-14 | 1.2123e-09 | -1.5899e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.575 | 0.73007 | 0.73008 | 1.575 | 0.73007 | 0.73008 | 0.00032341 | -94.4493 | 85.5534 | 0.00032332 | -94.4493 | 85.5534
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0309e-09 | -3.2594e-08 | 3.1649e-08 | -3.0317e-09 | 5.8155e-10 | 3.6355e-10 | -6.9269e-08 | 1.2791e-09 | -9.0004e-10 | 3.5585e-14 | 1.2123e-09 | -1.5899e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.575 | 0.73007 | 0.73008 | 1.575 | 0.73007 | 0.73008 | 0.00032776 | -94.4493 | 85.5535 | 0.00032767 | -94.4493 | 85.5535
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0309e-09 | -3.2594e-08 | 3.1649e-08 | -3.0317e-09 | 5.8155e-10 | 3.6355e-10 | -6.9269e-08 | 1.2791e-09 | -9.0004e-10 | 3.5585e-14 | 1.2123e-09 | -1.5899e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.575 | 0.73007 | 0.73008 | 1.575 | 0.73007 | 0.73008 | 0.00032776 | -94.4493 | 85.5535 | 0.00032767 | -94.4493 | 85.5535
Line1_1_3 | 1.525e-06 | 1.5477e-06 | 1.5023e-06 | 1.3348e-06 | 1.3574e-06 | 1.3121e-06 | 3.5218e-07 | 3.5743e-07 | 3.4694e-07 | 3.0825e-07 | 3.1349e-07 | 3.0302e-07 | 2.4248e-08 | -2.6075e-07 | 2.5319e-07 | -2.4248e-08 | 2.2874e-07 | -2.2118e-07 | -5.5415e-07 | 1.0233e-08 | -7.2003e-09 | 4.8488e-07 | -7.7415e-09 | 4.7103e-09 | 87.4949 | 87.7981 | 87.1824 | -92.8626 | -92.5109 | -93.2265 |  | 1.575 | 0.73007 | 0.73008 | 1.575 | 0.73007 | 0.73008 | 0.00032801 | -94.4493 | 85.5535 | 0.00032678 | -94.4493 | 85.5535
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0619e-09 | -6.5187e-08 | 6.3299e-08 | -6.0626e-09 | 3.3175e-08 | -3.1286e-08 | -1.3854e-07 | 2.5582e-09 | -1.8001e-09 | 6.9269e-08 | -6.6814e-11 | -6.8987e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.575 | 0.73007 | 0.73008 | 1.575 | 0.73007 | 0.73008 | 0.00032801 | -94.4493 | 85.5535 | 0.00032776 | -94.4493 | 85.5535
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0619e-09 | -6.5187e-08 | 6.3299e-08 | -6.0626e-09 | 3.3175e-08 | -3.1286e-08 | -1.3854e-07 | 2.5582e-09 | -1.8001e-09 | 6.9269e-08 | -6.6814e-11 | -6.8987e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.575 | 0.73007 | 0.73008 | 1.575 | 0.73007 | 0.73008 | 0.00032801 | -94.4493 | 85.5535 | 0.00032776 | -94.4493 | 85.5535
Line4_2_6 | 0 | 1.885 | 1.8851 | 0 | 1.885 | 1.8851 | 0 | 0.43533 | 0.43534 | 0 | 0.43533 | 0.43534 | 1.5157e-08 | 0.1066 | 0.10661 | -1.5158e-08 | -0.071065 | -0.071071 | -3.4635e-07 | 0.2132 | 0.21321 | 2.7708e-07 | -0.14213 | -0.14214 | 0 | -157.8849 | 22.1192 | 0 | 22.1151 | -157.8808 |  | 1.575 | 0.54755 | 0.54756 | 1.575 | 0.36503 | 0.36504 | 0.0003651 | -94.4493 | 85.5535 | 0.00040236 | -94.4493 | 85.5535
Line5_6_7 | 0 | 1.885 | 1.8851 | 0 | 1.885 | 1.8851 | 0 | 0.43533 | 0.43534 | 0 | 0.43533 | 0.43534 | 1.2126e-08 | 0.071065 | 0.071071 | -1.2126e-08 | -0.035532 | -0.035536 | -2.7708e-07 | 0.14213 | 0.14214 | 2.0781e-07 | -0.071067 | -0.071069 | 0 | -157.8849 | 22.1192 | 0 | 22.1151 | -157.8808 |  | 1.575 | 0.36503 | 0.36504 | 1.575 | 0.18252 | 0.18252 | 0.00040236 | -94.4493 | 85.5535 | 0.00043977 | -94.4493 | 85.5535
Line6_7_8 | 0 | 1.885 | 1.8851 | 0 | 1.885 | 1.8851 | 0 | 0.43533 | 0.43534 | 0 | 0.43533 | 0.43534 | 9.0947e-09 | 0.035532 | 0.035536 | -9.0949e-09 | 1.1498e-11 | -1.1432e-11 | -2.0781e-07 | 0.071067 | 0.071069 | 1.3854e-07 | 4.5255e-11 | -4.4976e-11 | 0 | -157.8849 | 22.1192 | 0 | 22.1151 | -157.8808 |  | 1.575 | 0.18252 | 0.18252 | 1.575 | 0 | 0 | 0.00043977 | -94.4493 | 85.5535 | 0.00047735 | 0 | 0
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0316e-09 | 4.9992e-18 | 4.2642e-18 | -3.0316e-09 | -1.6116e-19 | -1.0796e-17 | -6.9269e-08 | 8.9853e-19 | 7.9566e-19 | 5.1451e-14 | 2.2928e-17 | -5.672e-18 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.575 | 0 | 0 | 1.575 | 0 | 0 | 0.00047735 | 0 | 0 | 0.00047727 | 0 | 0
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0316e-09 | 4.9992e-18 | 4.2642e-18 | -3.0316e-09 | -1.6116e-19 | -1.0796e-17 | -6.9269e-08 | 8.9853e-19 | 7.9566e-19 | 5.1684e-14 | 2.2928e-17 | -5.672e-18 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.575 | 0 | 0 | 1.575 | 0 | 0 | 0.00047735 | 0 | 0 | 0.00047727 | 0 | 0
Line9_3_11 | 1.3344e-06 | 1.3543e-06 | 1.3145e-06 | 1.1441e-06 | 1.164e-06 | 1.1243e-06 | 3.0816e-07 | 3.1275e-07 | 3.0357e-07 | 2.6423e-07 | 2.6881e-07 | 2.5966e-07 | 2.1217e-08 | -2.2816e-07 | 2.2154e-07 | -2.1217e-08 | 1.9614e-07 | -1.8953e-07 | -4.8488e-07 | 8.9538e-09 | -6.3002e-09 | 4.1561e-07 | -6.4624e-09 | 3.8103e-09 | 87.4949 | 87.7981 | 87.1824 | -92.9222 | -92.5622 | -93.2948 |  | 1.575 | 0.73007 | 0.73008 | 1.575 | 0.73007 | 0.73008 | 0.00032678 | -94.4493 | 85.5535 | 0.00032572 | -94.4493 | 85.5535

## LLG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 1.1982e-06 | 1.9563 | 1.9564 | 0 | 1.9563 | 1.9564 | 2.7672e-07 | 0.45179 | 0.45181 | 0 | 0.45179 | 0.45181 | 1.9961e-08 | 0.15309 | 0.1531 | -1.9962e-08 | -0.11481 | -0.11483 | -4.5614e-07 | 0.30618 | 0.30619 | 3.8012e-07 | -0.22963 | -0.22964 | 87.4946 | -158.0521 | 21.9522 | 0 | 21.9479 | -158.0479 |  | 1.65 | 0.75769 | 0.7577 | 1.65 | 0.56826 | 0.56827 | 0.00032902 | -94.6164 | 85.3864 | 0.00036611 | -94.6164 | 85.3864
Line10_11_12 | 1.1982e-06 | 1.2168e-06 | 1.1797e-06 | 0 | 1.0174e-06 | 0 | 2.7671e-07 | 2.81e-07 | 2.7244e-07 | 0 | 2.3496e-07 | 0 | 1.9959e-08 | -2.1272e-07 | 2.0633e-07 | -1.996e-08 | 1.7792e-07 | -1.7153e-07 | -4.5614e-07 | 9.0015e-09 | -6.4362e-09 | 3.8011e-07 | -6.1912e-09 | 3.6276e-09 | 87.4949 | 87.8067 | 87.1731 | 0 | -92.6234 | 0 |  | 1.65 | 0.75769 | 0.7577 | 1.65 | 0.75769 | 0.7577 | 0.00032673 | -94.6164 | 85.3864 | 0.00032582 | -94.6164 | 85.3864
Line11_12_13 | 0 | 1.014e-06 | 0 | 0 | 0 | 0 | 0 | 2.3417e-07 | 0 | 0 | 0 | 0 | 1.6632e-08 | -1.7727e-07 | 1.7194e-07 | -1.6633e-08 | 1.4247e-07 | -1.3714e-07 | -3.8011e-07 | 7.5013e-09 | -5.3635e-09 | 3.0409e-07 | -4.691e-09 | 2.5549e-09 | 0 | 87.8067 | 0 | 0 | 0 | 0 |  | 1.65 | 0.75769 | 0.7577 | 1.65 | 0.75769 | 0.7577 | 0.00032582 | -94.6164 | 85.3864 | 0.00032508 | -94.6164 | 85.3864
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.9795e-09 | -1.0636e-07 | 1.0316e-07 | -9.9803e-09 | 7.1562e-08 | -6.8365e-08 | -2.2807e-07 | 4.5008e-09 | -3.2181e-09 | 1.5205e-07 | -1.6905e-09 | 4.0945e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.65 | 0.75769 | 0.7577 | 1.65 | 0.75769 | 0.7577 | 0.00032508 | -94.6164 | 85.3864 | 0.00032467 | -94.6164 | 85.3864
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3265e-09 | -3.5453e-08 | 3.4388e-08 | -3.3273e-09 | 6.5598e-10 | 4.1007e-10 | -7.6023e-08 | 1.5003e-09 | -1.0727e-09 | 3.8402e-14 | 1.31e-09 | -1.736e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.65 | 0.75769 | 0.7577 | 1.65 | 0.75769 | 0.7577 | 0.00032508 | -94.6164 | 85.3864 | 0.00032499 | -94.6164 | 85.3864
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.653e-09 | -7.0906e-08 | 6.8776e-08 | -6.6538e-09 | 3.6109e-08 | -3.3978e-08 | -1.5205e-07 | 3.0005e-09 | -2.1454e-09 | 7.6023e-08 | -1.9022e-10 | -6.6325e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.65 | 0.75769 | 0.7577 | 1.65 | 0.75769 | 0.7577 | 0.00032467 | -94.6164 | 85.3864 | 0.00032442 | -94.6164 | 85.3864
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3265e-09 | -3.5453e-08 | 3.4388e-08 | -3.3273e-09 | 6.5598e-10 | 4.1007e-10 | -7.6023e-08 | 1.5002e-09 | -1.0727e-09 | 3.8685e-14 | 1.31e-09 | -1.736e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.65 | 0.75769 | 0.7577 | 1.65 | 0.75769 | 0.7577 | 0.00032442 | -94.6164 | 85.3864 | 0.00032433 | -94.6164 | 85.3864
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3265e-09 | -3.5453e-08 | 3.4388e-08 | -3.3273e-09 | 6.5598e-10 | 4.1007e-10 | -7.6023e-08 | 1.5003e-09 | -1.0727e-09 | 3.8799e-14 | 1.31e-09 | -1.736e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.65 | 0.75769 | 0.7577 | 1.65 | 0.75769 | 0.7577 | 0.00032877 | -94.6164 | 85.3864 | 0.00032868 | -94.6164 | 85.3864
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3265e-09 | -3.5453e-08 | 3.4388e-08 | -3.3273e-09 | 6.5598e-10 | 4.1007e-10 | -7.6023e-08 | 1.5003e-09 | -1.0727e-09 | 3.8799e-14 | 1.31e-09 | -1.736e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.65 | 0.75769 | 0.7577 | 1.65 | 0.75769 | 0.7577 | 0.00032877 | -94.6164 | 85.3864 | 0.00032868 | -94.6164 | 85.3864
Line1_1_3 | 1.5976e-06 | 1.6223e-06 | 1.5729e-06 | 1.3983e-06 | 1.423e-06 | 1.3737e-06 | 3.6895e-07 | 3.7466e-07 | 3.6325e-07 | 3.2293e-07 | 3.2863e-07 | 3.1724e-07 | 2.6612e-08 | -2.8362e-07 | 2.751e-07 | -2.6613e-08 | 2.4883e-07 | -2.403e-07 | -6.0818e-07 | 1.2002e-08 | -8.5816e-09 | 5.3216e-07 | -9.1918e-09 | 5.7729e-09 | 87.4949 | 87.8067 | 87.1731 | -92.8626 | -92.5008 | -93.2374 |  | 1.65 | 0.75769 | 0.7577 | 1.65 | 0.75769 | 0.7577 | 0.00032902 | -94.6164 | 85.3864 | 0.00032779 | -94.6164 | 85.3864
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.653e-09 | -7.0906e-08 | 6.8776e-08 | -6.6538e-09 | 3.6109e-08 | -3.3978e-08 | -1.5205e-07 | 3.0005e-09 | -2.1454e-09 | 7.6023e-08 | -1.9023e-10 | -6.6326e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.65 | 0.75769 | 0.7577 | 1.65 | 0.75769 | 0.7577 | 0.00032902 | -94.6164 | 85.3864 | 0.00032877 | -94.6164 | 85.3864
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.653e-09 | -7.0906e-08 | 6.8776e-08 | -6.6538e-09 | 3.6109e-08 | -3.3978e-08 | -1.5205e-07 | 3.0005e-09 | -2.1454e-09 | 7.6023e-08 | -1.9023e-10 | -6.6326e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.65 | 0.75769 | 0.7577 | 1.65 | 0.75769 | 0.7577 | 0.00032902 | -94.6164 | 85.3864 | 0.00032877 | -94.6164 | 85.3864
Line4_2_6 | 0 | 1.9563 | 1.9564 | 0 | 1.9563 | 1.9564 | 0 | 0.45179 | 0.45181 | 0 | 0.45179 | 0.45181 | 1.6635e-08 | 0.11481 | 0.11483 | -1.6635e-08 | -0.076543 | -0.07655 | -3.8012e-07 | 0.22963 | 0.22964 | 3.0409e-07 | -0.15309 | -0.1531 | 0 | -158.0521 | 21.9521 | 0 | 21.9479 | -158.0479 |  | 1.65 | 0.56826 | 0.56827 | 1.65 | 0.37884 | 0.37885 | 0.00036611 | -94.6164 | 85.3864 | 0.00040337 | -94.6164 | 85.3864
Line5_6_7 | 0 | 1.9563 | 1.9564 | 0 | 1.9563 | 1.9564 | 0 | 0.45179 | 0.45181 | 0 | 0.45179 | 0.45181 | 1.3308e-08 | 0.076543 | 0.07655 | -1.3309e-08 | -0.038271 | -0.038275 | -3.0409e-07 | 0.15309 | 0.1531 | 2.2807e-07 | -0.076545 | -0.076548 | 0 | -158.0521 | 21.9521 | 0 | 21.948 | -158.0479 |  | 1.65 | 0.37884 | 0.37885 | 1.65 | 0.18942 | 0.18942 | 0.00040337 | -94.6164 | 85.3864 | 0.00044078 | -94.6164 | 85.3864
Line6_7_8 | 0 | 1.9563 | 1.9564 | 0 | 1.9563 | 1.9564 | 0 | 0.45179 | 0.45181 | 0 | 0.45179 | 0.45181 | 9.9815e-09 | 0.038271 | 0.038275 | -9.9817e-09 | 6.9512e-11 | -6.9425e-11 | -2.2807e-07 | 0.076545 | 0.076548 | 1.5205e-07 | 2.7545e-11 | -2.8682e-11 | 0 | -158.052 | 21.9521 | 0 | 21.948 | -158.0479 |  | 1.65 | 0.18942 | 0.18942 | 1.65 | 0 | 0 | 0.00044078 | -94.6164 | 85.3864 | 0.00047836 | 0 | 0
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3272e-09 | 5.8954e-18 | 5.1929e-18 | -3.3272e-09 | -4.5929e-19 | -1.2099e-17 | -7.6023e-08 | -5.7143e-18 | -4.8238e-18 | 5.6246e-14 | 2.5631e-17 | -6.7048e-18 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.65 | 0 | 0 | 1.65 | 0 | 0 | 0.00047836 | 0 | 0 | 0.00047828 | 0 | 0
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3272e-09 | 5.8954e-18 | 5.1929e-18 | -3.3272e-09 | -4.5928e-19 | -1.2099e-17 | -7.6023e-08 | -5.7143e-18 | -4.8238e-18 | 5.649e-14 | 2.5631e-17 | -6.7048e-18 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.65 | 0 | 0 | 1.65 | 0 | 0 | 0.00047836 | 0 | 0 | 0.00047828 | 0 | 0
Line9_3_11 | 1.3979e-06 | 1.4196e-06 | 1.3763e-06 | 1.1986e-06 | 1.2202e-06 | 1.1771e-06 | 3.2283e-07 | 3.2783e-07 | 3.1785e-07 | 2.7681e-07 | 2.818e-07 | 2.7184e-07 | 2.3285e-08 | -2.4817e-07 | 2.4071e-07 | -2.3286e-08 | 2.1337e-07 | -2.0592e-07 | -5.3216e-07 | 1.0502e-08 | -7.5089e-09 | 4.5614e-07 | -7.6915e-09 | 4.7003e-09 | 87.4949 | 87.8067 | 87.1731 | -92.9222 | -92.5519 | -93.306 |  | 1.65 | 0.75769 | 0.7577 | 1.65 | 0.75769 | 0.7577 | 0.00032779 | -94.6164 | 85.3864 | 0.00032673 | -94.6164 | 85.3864

## LLG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 1.1403e-06 | 0.029222 | 0.029325 | 0 | 0.029222 | 0.029325 | 2.6334e-07 | 0.0067484 | 0.0067722 | 0 | 0.0067485 | 0.0067722 | 1.729e-08 | 0.0043036 | 0.0043341 | -1.7428e-08 | -0.0042951 | -0.0043254 | -4.1398e-07 | 0.0043381 | 0.0043682 | 3.4499e-07 | -0.004321 | -0.004351 | 87.6656 | -135.4494 | 44.7571 | 0 | 44.5508 | -135.2432 |  | 1.5734 | 0.9055 | 0.90863 | 1.5734 | 0.90281 | 0.90594 | 0.057217 | -90.2209 | 89.9815 | 0.057254 | -90.2771 | 89.9255
Line10_11_12 | 1.1403e-06 | 1.1405e-06 | 1.1401e-06 | 0 | 0 | 0 | 2.6334e-07 | 2.6339e-07 | 2.6329e-07 | 0 | 0 | 0 | 1.7288e-08 | -2.3834e-07 | 2.3904e-07 | -1.7426e-08 | 1.9863e-07 | -1.992e-07 | -4.1398e-07 | -8.7552e-09 | 9.706e-09 | 3.4499e-07 | 9.0275e-09 | -9.8384e-09 | 87.6659 | 87.6753 | 87.6563 | 0 | 0 | 0 |  | 1.5734 | 0.9055 | 0.90863 | 1.5734 | 0.9055 | 0.90863 | 0.057214 | -90.2209 | 89.9815 | 0.057214 | -90.2209 | 89.9815
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4407e-08 | -1.9862e-07 | 1.992e-07 | -1.4545e-08 | 1.5891e-07 | -1.5936e-07 | -3.4498e-07 | -7.296e-09 | 8.0883e-09 | 2.7599e-07 | 7.5683e-09 | -8.2208e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.5734 | 0.9055 | 0.90863 | 1.5734 | 0.9055 | 0.90863 | 0.057214 | -90.2209 | 89.9815 | 0.057213 | -90.2209 | 89.9815
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.6441e-09 | -1.1917e-07 | 1.1952e-07 | -8.7823e-09 | 7.9466e-08 | -7.9678e-08 | -2.0699e-07 | -4.3776e-09 | 4.853e-09 | 1.38e-07 | 4.6499e-09 | -4.9854e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.5734 | 0.9055 | 0.90863 | 1.5734 | 0.9055 | 0.90863 | 0.057213 | -90.2209 | 89.9815 | 0.057212 | -90.2209 | 89.9815
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8814e-09 | -3.9723e-08 | 3.984e-08 | -3.0195e-09 | 1.9412e-11 | 1.7504e-12 | -6.8997e-08 | -1.4592e-09 | 1.6177e-09 | 6.049e-12 | 1.7314e-09 | -1.7501e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.5734 | 0.9055 | 0.90863 | 1.5734 | 0.9055 | 0.90863 | 0.057213 | -90.2209 | 89.9815 | 0.057213 | -90.2209 | 89.9815
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.7628e-09 | -7.9446e-08 | 7.968e-08 | -5.9009e-09 | 3.9742e-08 | -3.9838e-08 | -1.3799e-07 | -2.9184e-09 | 3.2353e-09 | 6.9003e-08 | 3.1906e-09 | -3.3678e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.5734 | 0.9055 | 0.90863 | 1.5734 | 0.9055 | 0.90863 | 0.057212 | -90.2209 | 89.9815 | 0.057212 | -90.2209 | 89.9815
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8814e-09 | -3.9723e-08 | 3.984e-08 | -3.0195e-09 | 1.9411e-11 | 1.7503e-12 | -6.8997e-08 | -1.4592e-09 | 1.6177e-09 | 6.0489e-12 | 1.7314e-09 | -1.7501e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.5734 | 0.9055 | 0.90863 | 1.5734 | 0.9055 | 0.90863 | 0.057212 | -90.2209 | 89.9815 | 0.057212 | -90.2209 | 89.9815
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8814e-09 | -3.9723e-08 | 3.984e-08 | -3.0195e-09 | 1.9413e-11 | 1.7502e-12 | -6.8997e-08 | -1.4592e-09 | 1.6177e-09 | 6.0504e-12 | 1.7314e-09 | -1.7501e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.5734 | 0.9055 | 0.90863 | 1.5734 | 0.9055 | 0.90863 | 0.057216 | -90.2209 | 89.9815 | 0.057216 | -90.2209 | 89.9815
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8814e-09 | -3.9723e-08 | 3.984e-08 | -3.0195e-09 | 1.9413e-11 | 1.7502e-12 | -6.8997e-08 | -1.4592e-09 | 1.6177e-09 | 6.0504e-12 | 1.7314e-09 | -1.7501e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.5734 | 0.9055 | 0.90863 | 1.5734 | 0.9055 | 0.90863 | 0.057216 | -90.2209 | 89.9815 | 0.057216 | -90.2209 | 89.9815
Line1_1_3 | 1.5204e-06 | 1.5207e-06 | 1.5201e-06 | 1.3307e-06 | 1.331e-06 | 1.3305e-06 | 3.5112e-07 | 3.5119e-07 | 3.5106e-07 | 3.0732e-07 | 3.0739e-07 | 3.0726e-07 | 2.3051e-08 | -3.1778e-07 | 3.1872e-07 | -2.3189e-08 | 2.7808e-07 | -2.7888e-07 | -5.5197e-07 | -1.1674e-08 | 1.2941e-08 | 4.8298e-07 | 1.1946e-08 | -1.3074e-08 | 87.6659 | 87.6753 | 87.6563 | -92.6916 | -92.6807 | -92.7025 |  | 1.5734 | 0.9055 | 0.90863 | 1.5734 | 0.9055 | 0.90863 | 0.057217 | -90.2209 | 89.9815 | 0.057216 | -90.2209 | 89.9815
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.7627e-09 | -7.9446e-08 | 7.968e-08 | -5.9009e-09 | 3.9742e-08 | -3.9838e-08 | -1.3799e-07 | -2.9184e-09 | 3.2353e-09 | 6.9003e-08 | 3.1906e-09 | -3.3678e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.5734 | 0.9055 | 0.90863 | 1.5734 | 0.9055 | 0.90863 | 0.057217 | -90.2209 | 89.9815 | 0.057216 | -90.2209 | 89.9815
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.7627e-09 | -7.9446e-08 | 7.968e-08 | -5.9009e-09 | 3.9742e-08 | -3.9838e-08 | -1.3799e-07 | -2.9184e-09 | 3.2353e-09 | 6.9003e-08 | 3.1906e-09 | -3.3678e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.5734 | 0.9055 | 0.90863 | 1.5734 | 0.9055 | 0.90863 | 0.057217 | -90.2209 | 89.9815 | 0.057216 | -90.2209 | 89.9815
Line4_2_6 | 0 | 0.029222 | 0.029325 | 0 | 0.029222 | 0.029324 | 0 | 0.0067485 | 0.0067722 | 0 | 0.0067485 | 0.0067722 | 1.4409e-08 | 0.0042951 | 0.0043254 | -1.4547e-08 | -0.0042866 | -0.0043168 | -3.4499e-07 | 0.004321 | 0.004351 | 2.76e-07 | -0.0043039 | -0.0043338 | 0 | -135.4492 | 44.7568 | 0 | 44.5511 | -135.2434 |  | 1.5734 | 0.90281 | 0.90594 | 1.5734 | 0.90012 | 0.90324 | 0.057254 | -90.2771 | 89.9255 | 0.057291 | -90.3337 | 89.8692
Line5_6_7 | 0 | 0.029222 | 0.029324 | 0 | 0.029222 | 0.029324 | 0 | 0.0067485 | 0.0067722 | 0 | 0.0067485 | 0.0067721 | 1.1528e-08 | 0.0042866 | 0.0043168 | -1.1665e-08 | -0.0042782 | -0.0043081 | -2.7599e-07 | 0.0043039 | 0.0043338 | 2.07e-07 | -0.0042868 | -0.0043166 | 0 | -135.4489 | 44.7566 | 0 | 44.5514 | -135.2437 |  | 1.5734 | 0.90012 | 0.90324 | 1.5734 | 0.89743 | 0.90055 | 0.057291 | -90.3337 | 89.8692 | 0.057328 | -90.3906 | 89.8126
Line6_7_8 | 0 | 0.029222 | 0.029324 | 0 | 0.029222 | 0.029324 | 0 | 0.0067485 | 0.0067721 | 0 | 0.0067486 | 0.0067721 | 8.6459e-09 | 0.0042782 | 0.0043081 | -8.7835e-09 | -0.0042697 | -0.0042995 | -2.0699e-07 | 0.0042868 | 0.0043166 | 1.38e-07 | -0.0042697 | -0.0042994 | 0 | -135.4487 | 44.7563 | 0 | 44.5516 | -135.2439 |  | 1.5734 | 0.89743 | 0.90055 | 1.5734 | 0.89475 | 0.89785 | 0.057328 | -90.3906 | 89.8126 | 0.057365 | -90.4479 | 89.7556
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.882e-09 | -3.9293e-08 | 3.9339e-08 | -3.0195e-09 | 6.1198e-11 | 3.0367e-11 | -6.8997e-08 | -1.2749e-09 | 1.4553e-09 | 6.0653e-12 | 1.699e-09 | -1.7411e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.5734 | 0.89475 | 0.89785 | 1.5734 | 0.89475 | 0.89785 | 0.057365 | -90.4479 | 89.7556 | 0.057365 | -90.4479 | 89.7556
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.882e-09 | -3.9293e-08 | 3.9339e-08 | -3.0195e-09 | 6.1198e-11 | 3.0367e-11 | -6.8997e-08 | -1.2749e-09 | 1.4553e-09 | 6.0658e-12 | 1.699e-09 | -1.7411e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.5734 | 0.89475 | 0.89785 | 1.5734 | 0.89475 | 0.89785 | 0.057365 | -90.4479 | 89.7556 | 0.057365 | -90.4479 | 89.7556
Line9_3_11 | 1.3304e-06 | 1.3306e-06 | 1.3301e-06 | 1.1407e-06 | 1.1409e-06 | 1.1405e-06 | 3.0723e-07 | 3.0729e-07 | 3.0718e-07 | 2.6343e-07 | 2.6349e-07 | 2.6338e-07 | 2.017e-08 | -2.7806e-07 | 2.7888e-07 | -2.0308e-08 | 2.3836e-07 | -2.3904e-07 | -4.8298e-07 | -1.0214e-08 | 1.1324e-08 | 4.1399e-07 | 1.0487e-08 | -1.1456e-08 | 87.6659 | 87.6753 | 87.6563 | -92.7511 | -92.74 | -92.7623 |  | 1.5734 | 0.9055 | 0.90863 | 1.5734 | 0.9055 | 0.90863 | 0.057216 | -90.2209 | 89.9815 | 0.057214 | -90.2209 | 89.9815

## LLG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 1.1946e-06 | 0.030609 | 0.030717 | 0 | 0.03061 | 0.030717 | 2.7589e-07 | 0.0070689 | 0.0070939 | 0 | 0.007069 | 0.0070939 | 1.8976e-08 | 0.0047222 | 0.0047556 | -1.9128e-08 | -0.0047128 | -0.0047461 | -4.5435e-07 | 0.00476 | 0.004793 | 3.7863e-07 | -0.0047412 | -0.0047741 | 87.6656 | -135.4551 | 44.7515 | 0 | 44.5452 | -135.2488 |  | 1.6483 | 0.9485 | 0.95179 | 1.6483 | 0.94569 | 0.94896 | 0.057218 | -90.2266 | 89.9759 | 0.057255 | -90.2828 | 89.9199
Line10_11_12 | 1.1946e-06 | 1.1948e-06 | 1.1944e-06 | 0 | 0 | 0 | 2.7588e-07 | 2.7593e-07 | 2.7583e-07 | 0 | 0 | 0 | 1.8974e-08 | -2.6155e-07 | 2.6232e-07 | -1.9126e-08 | 2.1798e-07 | -2.1859e-07 | -4.5435e-07 | -9.58e-09 | 1.0627e-08 | 3.7863e-07 | 9.8831e-09 | -1.0777e-08 | 87.6659 | 87.6758 | 87.6559 | 0 | 0 | 0 |  | 1.6483 | 0.9485 | 0.95179 | 1.6483 | 0.9485 | 0.95179 | 0.057215 | -90.2265 | 89.9759 | 0.057215 | -90.2265 | 89.9759
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5812e-08 | -2.1796e-07 | 2.186e-07 | -1.5963e-08 | 1.7439e-07 | -1.7488e-07 | -3.7862e-07 | -7.9834e-09 | 8.8562e-09 | 3.029e-07 | 8.2864e-09 | -9.0058e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.6483 | 0.9485 | 0.95179 | 1.6483 | 0.9485 | 0.95179 | 0.057215 | -90.2265 | 89.9759 | 0.057214 | -90.2265 | 89.9759
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.487e-09 | -1.3078e-07 | 1.3116e-07 | -9.6386e-09 | 8.7205e-08 | -8.7436e-08 | -2.2717e-07 | -4.79e-09 | 5.3137e-09 | 1.5146e-07 | 5.0931e-09 | -5.4633e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.6483 | 0.9485 | 0.95179 | 1.6483 | 0.9485 | 0.95179 | 0.057214 | -90.2265 | 89.9759 | 0.057213 | -90.2265 | 89.9759
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1623e-09 | -4.3592e-08 | 4.3719e-08 | -3.3139e-09 | 2.1878e-11 | 2.1234e-12 | -7.5724e-08 | -1.5967e-09 | 1.7712e-09 | 6.6398e-12 | 1.8997e-09 | -1.9208e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.6483 | 0.9485 | 0.95179 | 1.6483 | 0.9485 | 0.95179 | 0.057214 | -90.2265 | 89.9759 | 0.057214 | -90.2265 | 89.9759
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.3246e-09 | -8.7183e-08 | 8.7439e-08 | -6.4763e-09 | 4.3614e-08 | -4.3717e-08 | -1.5145e-07 | -3.1933e-09 | 3.5425e-09 | 7.5731e-08 | 3.4964e-09 | -3.6921e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.6483 | 0.9485 | 0.95179 | 1.6483 | 0.9485 | 0.95179 | 0.057213 | -90.2265 | 89.9759 | 0.057213 | -90.2265 | 89.9759
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1623e-09 | -4.3592e-08 | 4.3719e-08 | -3.3139e-09 | 2.1878e-11 | 2.1237e-12 | -7.5724e-08 | -1.5967e-09 | 1.7712e-09 | 6.6393e-12 | 1.8997e-09 | -1.9208e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.6483 | 0.9485 | 0.95179 | 1.6483 | 0.9485 | 0.95179 | 0.057213 | -90.2265 | 89.9759 | 0.057213 | -90.2265 | 89.9759
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1623e-09 | -4.3592e-08 | 4.3719e-08 | -3.3139e-09 | 2.1879e-11 | 2.123e-12 | -7.5724e-08 | -1.5967e-09 | 1.7712e-09 | 6.6403e-12 | 1.8997e-09 | -1.9208e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.6483 | 0.9485 | 0.95179 | 1.6483 | 0.9485 | 0.95179 | 0.057217 | -90.2266 | 89.9759 | 0.057217 | -90.2266 | 89.9759
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1623e-09 | -4.3592e-08 | 4.3719e-08 | -3.3139e-09 | 2.1879e-11 | 2.123e-12 | -7.5724e-08 | -1.5967e-09 | 1.7712e-09 | 6.6403e-12 | 1.8997e-09 | -1.9208e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.6483 | 0.9485 | 0.95179 | 1.6483 | 0.9485 | 0.95179 | 0.057217 | -90.2266 | 89.9759 | 0.057217 | -90.2266 | 89.9759
Line1_1_3 | 1.5928e-06 | 1.5931e-06 | 1.5925e-06 | 1.3941e-06 | 1.3944e-06 | 1.3938e-06 | 3.6784e-07 | 3.6791e-07 | 3.6777e-07 | 3.2196e-07 | 3.2203e-07 | 3.2189e-07 | 2.5299e-08 | -3.4873e-07 | 3.4975e-07 | -2.545e-08 | 3.0516e-07 | -3.0603e-07 | -6.0579e-07 | -1.2773e-08 | 1.417e-08 | 5.3008e-07 | 1.3076e-08 | -1.4319e-08 | 87.6659 | 87.6758 | 87.6559 | -92.6916 | -92.6802 | -92.7031 |  | 1.6483 | 0.9485 | 0.95179 | 1.6483 | 0.9485 | 0.95179 | 0.057218 | -90.2266 | 89.9759 | 0.057216 | -90.2266 | 89.9759
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.3246e-09 | -8.7183e-08 | 8.7439e-08 | -6.4763e-09 | 4.3614e-08 | -4.3717e-08 | -1.5145e-07 | -3.1933e-09 | 3.5425e-09 | 7.5731e-08 | 3.4964e-09 | -3.6921e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.6483 | 0.9485 | 0.95179 | 1.6483 | 0.9485 | 0.95179 | 0.057218 | -90.2266 | 89.9759 | 0.057217 | -90.2266 | 89.9759
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.3246e-09 | -8.7183e-08 | 8.7439e-08 | -6.4763e-09 | 4.3614e-08 | -4.3717e-08 | -1.5145e-07 | -3.1933e-09 | 3.5425e-09 | 7.5731e-08 | 3.4964e-09 | -3.6921e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.6483 | 0.9485 | 0.95179 | 1.6483 | 0.9485 | 0.95179 | 0.057218 | -90.2266 | 89.9759 | 0.057217 | -90.2266 | 89.9759
Line4_2_6 | 0 | 0.03061 | 0.030717 | 0 | 0.03061 | 0.030717 | 0 | 0.007069 | 0.0070939 | 0 | 0.007069 | 0.0070938 | 1.5814e-08 | 0.0047128 | 0.0047461 | -1.5965e-08 | -0.0047035 | -0.0047366 | -3.7863e-07 | 0.0047412 | 0.0047741 | 3.0291e-07 | -0.0047225 | -0.0047553 | 0 | -135.4548 | 44.7512 | 0 | 44.5454 | -135.249 |  | 1.6483 | 0.94569 | 0.94896 | 1.6483 | 0.94287 | 0.94614 | 0.057255 | -90.2828 | 89.9199 | 0.057292 | -90.3394 | 89.8636
Line5_6_7 | 0 | 0.03061 | 0.030717 | 0 | 0.03061 | 0.030717 | 0 | 0.007069 | 0.0070938 | 0 | 0.007069 | 0.0070938 | 1.2652e-08 | 0.0047035 | 0.0047366 | -1.2803e-08 | -0.0046942 | -0.0047271 | -3.029e-07 | 0.0047225 | 0.0047553 | 2.2718e-07 | -0.0047037 | -0.0047364 | 0 | -135.4546 | 44.751 | 0 | 44.5457 | -135.2493 |  | 1.6483 | 0.94287 | 0.94614 | 1.6483 | 0.94006 | 0.94332 | 0.057292 | -90.3394 | 89.8636 | 0.057329 | -90.3963 | 89.807
Line6_7_8 | 0 | 0.03061 | 0.030717 | 0 | 0.03061 | 0.030717 | 0 | 0.0070691 | 0.0070938 | 0 | 0.0070691 | 0.0070938 | 9.4889e-09 | 0.0046942 | 0.0047271 | -9.64e-09 | -0.0046849 | -0.0047176 | -2.2718e-07 | 0.0047037 | 0.0047364 | 1.5146e-07 | -0.004685 | -0.0047175 | 0 | -135.4543 | 44.7507 | 0 | 44.546 | -135.2495 |  | 1.6483 | 0.94006 | 0.94332 | 1.6483 | 0.93725 | 0.9405 | 0.057329 | -90.3963 | 89.807 | 0.057366 | -90.4535 | 89.75
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.163e-09 | -4.312e-08 | 4.3169e-08 | -3.3139e-09 | 6.7721e-11 | 3.3519e-11 | -7.5725e-08 | -1.3945e-09 | 1.5931e-09 | 6.6567e-12 | 1.8641e-09 | -1.911e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.6483 | 0.93725 | 0.9405 | 1.6483 | 0.93725 | 0.9405 | 0.057366 | -90.4535 | 89.75 | 0.057366 | -90.4535 | 89.75
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.163e-09 | -4.312e-08 | 4.3169e-08 | -3.3139e-09 | 6.7721e-11 | 3.3519e-11 | -7.5725e-08 | -1.3945e-09 | 1.5931e-09 | 6.6567e-12 | 1.8641e-09 | -1.911e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.6483 | 0.93725 | 0.9405 | 1.6483 | 0.93725 | 0.9405 | 0.057366 | -90.4535 | 89.75 | 0.057366 | -90.4535 | 89.75
Line9_3_11 | 1.3937e-06 | 1.394e-06 | 1.3934e-06 | 1.195e-06 | 1.1953e-06 | 1.1948e-06 | 3.2186e-07 | 3.2192e-07 | 3.218e-07 | 2.7598e-07 | 2.7604e-07 | 2.7592e-07 | 2.2136e-08 | -3.0514e-07 | 3.0604e-07 | -2.2288e-08 | 2.6157e-07 | -2.6231e-07 | -5.3007e-07 | -1.1177e-08 | 1.2399e-08 | 4.5435e-07 | 1.148e-08 | -1.2548e-08 | 87.6659 | 87.6758 | 87.6559 | -92.7511 | -92.7395 | -92.7629 |  | 1.6483 | 0.9485 | 0.95179 | 1.6483 | 0.9485 | 0.95179 | 0.057216 | -90.2266 | 89.9759 | 0.057215 | -90.2265 | 89.9759

## LLG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 1.0348e-06 | 1.4549 | 1.455 | 0 | 1.4549 | 1.455 | 2.3898e-07 | 0.336 | 0.33602 | 0 | 0.336 | 0.33602 | 1.4887e-08 | 0.16257 | 0.16259 | -1.4888e-08 | -0.12193 | -0.12195 | -3.4022e-07 | 0.16935 | 0.16936 | 2.8352e-07 | -0.12701 | -0.12702 | 87.4952 | -142.8748 | 37.1294 | 0 | 37.1252 | -142.8706 |  | 1.425 | 0.69867 | 0.6987 | 1.425 | 0.524 | 0.52402 | 0.00061252 | -96.705 | 83.2978 | 0.00068404 | -96.705 | 83.2978
Line10_11_12 | 1.0348e-06 | 1.0468e-06 | 1.0229e-06 | 0 | 0 | 0 | 2.3898e-07 | 2.4174e-07 | 2.3624e-07 | 0 | 0 | 0 | 1.4883e-08 | -1.6834e-07 | 1.6471e-07 | -1.4885e-08 | 1.4073e-07 | -1.3709e-07 | -3.4022e-07 | 1.3707e-08 | -1.0747e-08 | 2.8351e-07 | -1.046e-08 | 7.5009e-09 | 87.4957 | 87.9499 | 87.0309 | 0 | 0 | 0 |  | 1.425 | 0.69867 | 0.6987 | 1.425 | 0.69867 | 0.6987 | 0.00060829 | -96.705 | 83.2978 | 0.00060663 | -96.705 | 83.2978
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2403e-08 | -1.4028e-07 | 1.3726e-07 | -1.2404e-08 | 1.1267e-07 | -1.0964e-07 | -2.8351e-07 | 1.1422e-08 | -8.9554e-09 | 2.2681e-07 | -8.1752e-09 | 5.7098e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.425 | 0.69867 | 0.6987 | 1.425 | 0.69867 | 0.6987 | 0.00060663 | -96.705 | 83.2978 | 0.00060527 | -96.705 | 83.2978
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4417e-09 | -8.417e-08 | 8.2353e-08 | -7.4429e-09 | 5.6559e-08 | -5.4741e-08 | -1.7011e-07 | 6.8533e-09 | -5.3733e-09 | 1.1341e-07 | -3.6064e-09 | 2.1276e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.425 | 0.69867 | 0.6987 | 1.425 | 0.69867 | 0.6987 | 0.00060527 | -96.705 | 83.2978 | 0.00060451 | -96.705 | 83.2978
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4806e-09 | -2.8057e-08 | 2.7451e-08 | -2.4817e-09 | 4.4546e-10 | 1.6132e-10 | -5.6703e-08 | 2.2844e-09 | -1.7911e-09 | 5.247e-14 | 9.6245e-10 | -1.4546e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.425 | 0.69867 | 0.6987 | 1.425 | 0.69867 | 0.6987 | 0.00060527 | -96.705 | 83.2978 | 0.00060511 | -96.705 | 83.2978
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.9611e-09 | -5.6113e-08 | 5.4902e-08 | -4.9623e-09 | 2.8502e-08 | -2.729e-08 | -1.1341e-07 | 4.5688e-09 | -3.5822e-09 | 5.6703e-08 | -1.322e-09 | 3.3652e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.425 | 0.69867 | 0.6987 | 1.425 | 0.69867 | 0.6987 | 0.00060451 | -96.705 | 83.2978 | 0.00060405 | -96.705 | 83.2978
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4806e-09 | -2.8057e-08 | 2.7451e-08 | -2.4817e-09 | 4.4546e-10 | 1.6132e-10 | -5.6703e-08 | 2.2844e-09 | -1.7911e-09 | 5.2734e-14 | 9.6245e-10 | -1.4546e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.425 | 0.69867 | 0.6987 | 1.425 | 0.69867 | 0.6987 | 0.00060405 | -96.705 | 83.2978 | 0.00060389 | -96.705 | 83.2978
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4806e-09 | -2.8057e-08 | 2.7451e-08 | -2.4817e-09 | 4.4546e-10 | 1.6132e-10 | -5.6703e-08 | 2.2844e-09 | -1.7911e-09 | 5.3178e-14 | 9.6245e-10 | -1.4546e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.425 | 0.69867 | 0.6987 | 1.425 | 0.69867 | 0.6987 | 0.00061206 | -96.705 | 83.2978 | 0.00061191 | -96.705 | 83.2978
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4806e-09 | -2.8057e-08 | 2.7451e-08 | -2.4817e-09 | 4.4546e-10 | 1.6132e-10 | -5.6703e-08 | 2.2844e-09 | -1.7911e-09 | 5.3178e-14 | 9.6245e-10 | -1.4546e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.425 | 0.69867 | 0.6987 | 1.425 | 0.69867 | 0.6987 | 0.00061206 | -96.705 | 83.2978 | 0.00061191 | -96.705 | 83.2978
Line1_1_3 | 1.3798e-06 | 1.3957e-06 | 1.3639e-06 | 1.2076e-06 | 1.2235e-06 | 1.1919e-06 | 3.1864e-07 | 3.2232e-07 | 3.1498e-07 | 2.7889e-07 | 2.8256e-07 | 2.7525e-07 | 1.9845e-08 | -2.2445e-07 | 2.1961e-07 | -1.9846e-08 | 1.9684e-07 | -1.92e-07 | -4.5362e-07 | 1.8275e-08 | -1.4329e-08 | 3.9692e-07 | -1.5029e-08 | 1.1083e-08 | 87.4957 | 87.9499 | 87.0309 | -92.8618 | -92.339 | -93.3985 |  | 1.425 | 0.69867 | 0.6987 | 1.425 | 0.69867 | 0.6987 | 0.00061252 | -96.705 | 83.2978 | 0.00061026 | -96.705 | 83.2978
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.9611e-09 | -5.6113e-08 | 5.4902e-08 | -4.9623e-09 | 2.8502e-08 | -2.729e-08 | -1.1341e-07 | 4.5689e-09 | -3.5822e-09 | 5.6703e-08 | -1.322e-09 | 3.3652e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.425 | 0.69867 | 0.6987 | 1.425 | 0.69867 | 0.6987 | 0.00061252 | -96.705 | 83.2978 | 0.00061206 | -96.705 | 83.2978
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.9611e-09 | -5.6113e-08 | 5.4902e-08 | -4.9623e-09 | 2.8502e-08 | -2.729e-08 | -1.1341e-07 | 4.5689e-09 | -3.5822e-09 | 5.6703e-08 | -1.322e-09 | 3.3652e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.425 | 0.69867 | 0.6987 | 1.425 | 0.69867 | 0.6987 | 0.00061252 | -96.705 | 83.2978 | 0.00061206 | -96.705 | 83.2978
Line4_2_6 | 0 | 1.4549 | 1.455 | 0 | 1.4549 | 1.455 | 0 | 0.336 | 0.33602 | 0 | 0.336 | 0.33602 | 1.2406e-08 | 0.12193 | 0.12195 | -1.2407e-08 | -0.081287 | -0.081297 | -2.8352e-07 | 0.12701 | 0.12702 | 2.2681e-07 | -0.084676 | -0.084682 | 0 | -142.8748 | 37.1294 | 0 | 37.1252 | -142.8706 |  | 1.425 | 0.524 | 0.52402 | 1.425 | 0.34934 | 0.34935 | 0.00068404 | -96.705 | 83.2978 | 0.00075585 | -96.705 | 83.2978
Line5_6_7 | 0 | 1.4549 | 1.455 | 0 | 1.4549 | 1.455 | 0 | 0.336 | 0.33602 | 0 | 0.336 | 0.33602 | 9.9257e-09 | 0.081287 | 0.081297 | -9.9264e-09 | -0.040644 | -0.040648 | -2.2681e-07 | 0.084676 | 0.084682 | 1.7011e-07 | -0.042338 | -0.042341 | 0 | -142.8748 | 37.1294 | 0 | 37.1252 | -142.8706 |  | 1.425 | 0.34934 | 0.34935 | 1.425 | 0.17467 | 0.17467 | 0.00075585 | -96.705 | 83.2978 | 0.00082797 | -96.705 | 83.2978
Line6_7_8 | 0 | 1.4549 | 1.455 | 0 | 1.4549 | 1.455 | 0 | 0.336 | 0.33602 | 0 | 0.336 | 0.33602 | 7.4447e-09 | 0.040644 | 0.040648 | -7.445e-09 | -1.0384e-11 | 1.0385e-11 | -1.7011e-07 | 0.042338 | 0.042341 | 1.1341e-07 | -3.2183e-11 | 3.3264e-11 | 0 | -142.8748 | 37.1294 | 0 | 37.1252 | -142.8706 |  | 1.425 | 0.17467 | 0.17467 | 1.425 | 0 | 0 | 0.00082797 | -96.705 | 83.2978 | 0.00090039 | 0 | 0
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4817e-09 | -4.01e-18 | -3.5275e-18 | -2.4817e-09 | 7.3719e-18 | -1.2849e-17 | -5.6703e-08 | -1.5854e-18 | -1.4613e-18 | 7.7868e-14 | 2.2684e-17 | -1.9169e-18 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.425 | 0 | 0 | 1.425 | 0 | 0 | 0.00090039 | 0 | 0 | 0.00090023 | 0 | 0
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4817e-09 | -4.01e-18 | -3.5275e-18 | -2.4817e-09 | 7.3719e-18 | -1.2849e-17 | -5.6703e-08 | -1.5854e-18 | -1.4613e-18 | 7.8078e-14 | 2.2684e-17 | -1.9169e-18 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.425 | 0 | 0 | 1.425 | 0 | 0 | 0.00090039 | 0 | 0 | 0.00090023 | 0 | 0
Line9_3_11 | 1.2073e-06 | 1.2212e-06 | 1.1934e-06 | 1.0352e-06 | 1.0491e-06 | 1.0214e-06 | 2.7881e-07 | 2.8203e-07 | 2.7561e-07 | 2.3906e-07 | 2.4227e-07 | 2.3588e-07 | 1.7364e-08 | -1.964e-07 | 1.9216e-07 | -1.7365e-08 | 1.6879e-07 | -1.6455e-07 | -3.9692e-07 | 1.5991e-08 | -1.2538e-08 | 3.4022e-07 | -1.2744e-08 | 9.2919e-09 | 87.4957 | 87.9499 | 87.0309 | -92.9213 | -92.3871 | -93.4701 |  | 1.425 | 0.69867 | 0.6987 | 1.425 | 0.69867 | 0.6987 | 0.00061026 | -96.705 | 83.2978 | 0.00060829 | -96.705 | 83.2978

## LLG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 1.3784 | 1.3784 | 0 | 1.3784 | 1.3784 | 0 | 0.31832 | 0.31834 | 0 | 0.31832 | 0.31834 | 1.3361e-08 | 0.14591 | 0.14593 | -1.3362e-08 | -0.10943 | -0.10945 | -3.0535e-07 | 0.15199 | 0.15201 | 2.5446e-07 | -0.114 | -0.114 | 0 | -142.8748 | 37.1294 | 0 | 37.1252 | -142.8706 |  | 1.35 | 0.6619 | 0.66192 | 1.35 | 0.49642 | 0.49644 | 0.00061252 | -96.705 | 83.2978 | 0.00068404 | -96.705 | 83.2978
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3358e-08 | -1.5109e-07 | 1.4783e-07 | -1.3359e-08 | 1.2631e-07 | -1.2304e-07 | -3.0535e-07 | 1.2302e-08 | -9.6451e-09 | 2.5446e-07 | -9.3876e-09 | 6.7321e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.35 | 0.6619 | 0.66192 | 1.35 | 0.6619 | 0.66192 | 0.00060829 | -96.705 | 83.2978 | 0.00060663 | -96.705 | 83.2978
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1132e-08 | -1.2591e-07 | 1.2319e-07 | -1.1133e-08 | 1.0112e-07 | -9.8405e-08 | -2.5446e-07 | 1.0251e-08 | -8.0376e-09 | 2.0356e-07 | -7.3373e-09 | 5.1246e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.35 | 0.6619 | 0.66192 | 1.35 | 0.6619 | 0.66192 | 0.00060663 | -96.705 | 83.2978 | 0.00060527 | -96.705 | 83.2978
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.679e-09 | -7.5543e-08 | 7.3913e-08 | -6.68e-09 | 5.0762e-08 | -4.913e-08 | -1.5267e-07 | 6.1508e-09 | -4.8225e-09 | 1.0178e-07 | -3.2368e-09 | 1.9095e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.35 | 0.6619 | 0.66192 | 1.35 | 0.6619 | 0.66192 | 0.00060527 | -96.705 | 83.2978 | 0.00060451 | -96.705 | 83.2978
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2263e-09 | -2.5181e-08 | 2.4638e-08 | -2.2274e-09 | 3.998e-10 | 1.4479e-10 | -5.0891e-08 | 2.0503e-09 | -1.6075e-09 | 4.7369e-14 | 8.638e-10 | -1.3055e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.35 | 0.6619 | 0.66192 | 1.35 | 0.6619 | 0.66192 | 0.00060527 | -96.705 | 83.2978 | 0.00060511 | -96.705 | 83.2978
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4527e-09 | -5.0362e-08 | 4.9275e-08 | -4.4537e-09 | 2.5581e-08 | -2.4493e-08 | -1.0178e-07 | 4.1006e-09 | -3.215e-09 | 5.0891e-08 | -1.1865e-09 | 3.0203e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.35 | 0.6619 | 0.66192 | 1.35 | 0.6619 | 0.66192 | 0.00060451 | -96.705 | 83.2978 | 0.00060405 | -96.705 | 83.2978
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2263e-09 | -2.5181e-08 | 2.4638e-08 | -2.2274e-09 | 3.998e-10 | 1.4479e-10 | -5.0891e-08 | 2.0503e-09 | -1.6075e-09 | 4.7016e-14 | 8.638e-10 | -1.3055e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.35 | 0.6619 | 0.66192 | 1.35 | 0.6619 | 0.66192 | 0.00060405 | -96.705 | 83.2978 | 0.00060389 | -96.705 | 83.2978
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2263e-09 | -2.5181e-08 | 2.4638e-08 | -2.2274e-09 | 3.998e-10 | 1.4479e-10 | -5.0891e-08 | 2.0503e-09 | -1.6075e-09 | 4.7604e-14 | 8.638e-10 | -1.3055e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.35 | 0.6619 | 0.66192 | 1.35 | 0.6619 | 0.66192 | 0.00061206 | -96.705 | 83.2978 | 0.00061191 | -96.705 | 83.2978
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2263e-09 | -2.5181e-08 | 2.4638e-08 | -2.2274e-09 | 3.998e-10 | 1.4479e-10 | -5.0891e-08 | 2.0503e-09 | -1.6075e-09 | 4.7604e-14 | 8.638e-10 | -1.3055e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.35 | 0.6619 | 0.66192 | 1.35 | 0.6619 | 0.66192 | 0.00061206 | -96.705 | 83.2978 | 0.00061191 | -96.705 | 83.2978
Line1_1_3 | 1.3071e-06 | 1.3222e-06 | 1.2921e-06 | 1.1441e-06 | 1.1591e-06 | 1.1291e-06 | 3.0187e-07 | 3.0536e-07 | 2.984e-07 | 2.6421e-07 | 2.6769e-07 | 2.6076e-07 | 1.7811e-08 | -2.0145e-07 | 1.971e-07 | -1.7812e-08 | 1.7667e-07 | -1.7232e-07 | -4.0713e-07 | 1.6402e-08 | -1.286e-08 | 3.5624e-07 | -1.3488e-08 | 9.9471e-09 | 87.4957 | 87.9499 | 87.0309 | -92.8618 | -92.339 | -93.3985 |  | 1.35 | 0.6619 | 0.66192 | 1.35 | 0.6619 | 0.66192 | 0.00061252 | -96.705 | 83.2978 | 0.00061026 | -96.705 | 83.2978
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4526e-09 | -5.0362e-08 | 4.9275e-08 | -4.4537e-09 | 2.5581e-08 | -2.4493e-08 | -1.0178e-07 | 4.1006e-09 | -3.215e-09 | 5.0891e-08 | -1.1865e-09 | 3.0203e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.35 | 0.6619 | 0.66192 | 1.35 | 0.6619 | 0.66192 | 0.00061252 | -96.705 | 83.2978 | 0.00061206 | -96.705 | 83.2978
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4526e-09 | -5.0362e-08 | 4.9275e-08 | -4.4537e-09 | 2.5581e-08 | -2.4493e-08 | -1.0178e-07 | 4.1006e-09 | -3.215e-09 | 5.0891e-08 | -1.1865e-09 | 3.0203e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.35 | 0.6619 | 0.66192 | 1.35 | 0.6619 | 0.66192 | 0.00061252 | -96.705 | 83.2978 | 0.00061206 | -96.705 | 83.2978
Line4_2_6 | 0 | 1.3784 | 1.3784 | 0 | 1.3784 | 1.3784 | 0 | 0.31832 | 0.31834 | 0 | 0.31832 | 0.31834 | 1.1135e-08 | 0.10943 | 0.10945 | -1.1136e-08 | -0.072956 | -0.072964 | -2.5446e-07 | 0.114 | 0.114 | 2.0357e-07 | -0.075997 | -0.076003 | 0 | -142.8748 | 37.1294 | 0 | 37.1252 | -142.8706 |  | 1.35 | 0.49642 | 0.49644 | 1.35 | 0.33095 | 0.33096 | 0.00068404 | -96.705 | 83.2978 | 0.00075585 | -96.705 | 83.2978
Line5_6_7 | 0 | 1.3784 | 1.3784 | 0 | 1.3784 | 1.3784 | 0 | 0.31832 | 0.31834 | 0 | 0.31832 | 0.31834 | 8.9084e-09 | 0.072956 | 0.072964 | -8.909e-09 | -0.036478 | -0.036482 | -2.0357e-07 | 0.075997 | 0.076003 | 1.5268e-07 | -0.037999 | -0.038001 | 0 | -142.8748 | 37.1294 | 0 | 37.1252 | -142.8706 |  | 1.35 | 0.33095 | 0.33096 | 1.35 | 0.16547 | 0.16548 | 0.00075585 | -96.705 | 83.2978 | 0.00082797 | -96.705 | 83.2978
Line6_7_8 | 0 | 1.3784 | 1.3784 | 0 | 1.3784 | 1.3784 | 0 | 0.31832 | 0.31834 | 0 | 0.31832 | 0.31834 | 6.6817e-09 | 0.036478 | 0.036482 | -6.6819e-09 | -9.672e-12 | 9.6732e-12 | -1.5268e-07 | 0.037999 | 0.038001 | 1.0178e-07 | -2.8621e-11 | 2.9592e-11 | 0 | -142.8748 | 37.1294 | 0 | 37.1252 | -142.8706 |  | 1.35 | 0.16547 | 0.16548 | 1.35 | 0 | 0 | 0.00082797 | -96.705 | 83.2978 | 0.00090039 | 0 | 0
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2273e-09 | -3.6017e-18 | -3.1686e-18 | -2.2273e-09 | 6.6186e-18 | -1.153e-17 | -5.0892e-08 | -1.3669e-18 | -1.2633e-18 | 7.0518e-14 | 2.0355e-17 | -1.7165e-18 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.35 | 0 | 0 | 1.35 | 0 | 0 | 0.00090039 | 0 | 0 | 0.00090023 | 0 | 0
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2273e-09 | -3.6017e-18 | -3.1686e-18 | -2.2273e-09 | 6.6186e-18 | -1.153e-17 | -5.0892e-08 | -1.3669e-18 | -1.2633e-18 | 7.0018e-14 | 2.0355e-17 | -1.7165e-18 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.35 | 0 | 0 | 1.35 | 0 | 0 | 0.00090039 | 0 | 0 | 0.00090023 | 0 | 0
Line9_3_11 | 1.1437e-06 | 1.157e-06 | 1.1306e-06 | 0 | 0 | 0 | 2.6414e-07 | 2.6719e-07 | 2.611e-07 | 0 | 0 | 0 | 1.5584e-08 | -1.7627e-07 | 1.7246e-07 | -1.5585e-08 | 1.5149e-07 | -1.4768e-07 | -3.5624e-07 | 1.4352e-08 | -1.1253e-08 | 3.0535e-07 | -1.1438e-08 | 8.3396e-09 | 87.4957 | 87.9499 | 87.0309 | 0 | 0 | 0 |  | 1.35 | 0.6619 | 0.66192 | 1.35 | 0.6619 | 0.66192 | 0.00061026 | -96.705 | 83.2978 | 0.00060829 | -96.705 | 83.2978

## LLG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 1.0317e-06 | 0.02634 | 0.026434 | 0 | 0.026341 | 0.026434 | 2.3826e-07 | 0.0060831 | 0.0061047 | 0 | 0.0060831 | 0.0061047 | 1.4152e-08 | 0.0035224 | 0.0035475 | -1.4266e-08 | -0.0035091 | -0.003534 | -3.3889e-07 | 0.0035249 | 0.0035495 | 2.8241e-07 | -0.003511 | -0.0035355 | 87.6662 | -135.2458 | 44.9608 | 0 | 44.7545 | -135.0395 |  | 1.4235 | 0.81919 | 0.82204 | 1.4235 | 0.81602 | 0.81887 | 0.0575 | -90.2257 | 89.9768 | 0.057571 | -90.2303 | 89.9724
Line10_11_12 | 1.0317e-06 | 1.0319e-06 | 1.0315e-06 | 0 | 0 | 0 | 2.3826e-07 | 2.3831e-07 | 2.3822e-07 | 0 | 0 | 0 | 1.4149e-08 | -1.9509e-07 | 1.9566e-07 | -1.4262e-08 | 1.6259e-07 | -1.6305e-07 | -3.3888e-07 | -7.146e-09 | 7.9269e-09 | 2.8241e-07 | 7.372e-09 | -8.0385e-09 | 87.6667 | 87.6765 | 87.6568 | 0 | 0 | 0 |  | 1.4235 | 0.81919 | 0.82204 | 1.4235 | 0.81919 | 0.82204 | 0.057496 | -90.2257 | 89.9768 | 0.057494 | -90.2257 | 89.9768
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1791e-08 | -1.6257e-07 | 1.6305e-07 | -1.1904e-08 | 1.3007e-07 | -1.3044e-07 | -2.824e-07 | -5.955e-09 | 6.6057e-09 | 2.2593e-07 | 6.181e-09 | -6.7173e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.4235 | 0.81919 | 0.82204 | 1.4235 | 0.81919 | 0.82204 | 0.057494 | -90.2257 | 89.9768 | 0.057493 | -90.2257 | 89.9768
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.0744e-09 | -9.7543e-08 | 9.7831e-08 | -7.188e-09 | 6.5045e-08 | -6.5219e-08 | -1.6944e-07 | -3.573e-09 | 3.9634e-09 | 1.1297e-07 | 3.799e-09 | -4.075e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.4235 | 0.81919 | 0.82204 | 1.4235 | 0.81919 | 0.82204 | 0.057493 | -90.2257 | 89.9768 | 0.057492 | -90.2257 | 89.9768
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3581e-09 | -3.2514e-08 | 3.261e-08 | -2.4718e-09 | 1.6226e-11 | 1.493e-12 | -5.648e-08 | -1.191e-09 | 1.3211e-09 | 4.9763e-12 | 1.417e-09 | -1.4327e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.4235 | 0.81919 | 0.82204 | 1.4235 | 0.81919 | 0.82204 | 0.057493 | -90.2257 | 89.9768 | 0.057492 | -90.2257 | 89.9768
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7163e-09 | -6.5029e-08 | 6.5221e-08 | -4.8299e-09 | 3.2531e-08 | -3.2609e-08 | -1.1296e-07 | -2.382e-09 | 2.6423e-09 | 5.6485e-08 | 2.608e-09 | -2.7539e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.4235 | 0.81919 | 0.82204 | 1.4235 | 0.81919 | 0.82204 | 0.057492 | -90.2257 | 89.9768 | 0.057491 | -90.2257 | 89.9768
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3581e-09 | -3.2514e-08 | 3.261e-08 | -2.4718e-09 | 1.6226e-11 | 1.4932e-12 | -5.648e-08 | -1.191e-09 | 1.3211e-09 | 4.9758e-12 | 1.417e-09 | -1.4327e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.4235 | 0.81919 | 0.82204 | 1.4235 | 0.81919 | 0.82204 | 0.057491 | -90.2257 | 89.9768 | 0.057491 | -90.2257 | 89.9768
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3581e-09 | -3.2514e-08 | 3.261e-08 | -2.4718e-09 | 1.6227e-11 | 1.4928e-12 | -5.648e-08 | -1.191e-09 | 1.3211e-09 | 4.9764e-12 | 1.417e-09 | -1.4327e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.4235 | 0.81919 | 0.82204 | 1.4235 | 0.81919 | 0.82204 | 0.057499 | -90.2257 | 89.9768 | 0.057499 | -90.2257 | 89.9768
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3581e-09 | -3.2514e-08 | 3.261e-08 | -2.4718e-09 | 1.6227e-11 | 1.4928e-12 | -5.648e-08 | -1.191e-09 | 1.3211e-09 | 4.9764e-12 | 1.417e-09 | -1.4327e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.4235 | 0.81919 | 0.82204 | 1.4235 | 0.81919 | 0.82204 | 0.057499 | -90.2257 | 89.9768 | 0.057499 | -90.2257 | 89.9768
Line1_1_3 | 1.3756e-06 | 1.3759e-06 | 1.3753e-06 | 1.204e-06 | 1.2043e-06 | 1.2037e-06 | 3.1768e-07 | 3.1774e-07 | 3.1762e-07 | 2.7805e-07 | 2.7811e-07 | 2.7799e-07 | 1.8865e-08 | -2.6012e-07 | 2.6088e-07 | -1.8979e-08 | 2.2762e-07 | -2.2827e-07 | -4.5184e-07 | -9.5279e-09 | 1.0569e-08 | 3.9537e-07 | 9.7539e-09 | -1.0681e-08 | 87.6667 | 87.6765 | 87.6568 | -92.6907 | -92.6794 | -92.7021 |  | 1.4235 | 0.81919 | 0.82204 | 1.4235 | 0.81919 | 0.82204 | 0.0575 | -90.2257 | 89.9768 | 0.057498 | -90.2257 | 89.9768
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7162e-09 | -6.5029e-08 | 6.5221e-08 | -4.8299e-09 | 3.2531e-08 | -3.2609e-08 | -1.1296e-07 | -2.382e-09 | 2.6423e-09 | 5.6485e-08 | 2.608e-09 | -2.7539e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.4235 | 0.81919 | 0.82204 | 1.4235 | 0.81919 | 0.82204 | 0.0575 | -90.2257 | 89.9768 | 0.057499 | -90.2257 | 89.9768
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7162e-09 | -6.5029e-08 | 6.5221e-08 | -4.8299e-09 | 3.2531e-08 | -3.2609e-08 | -1.1296e-07 | -2.382e-09 | 2.6423e-09 | 5.6485e-08 | 2.608e-09 | -2.7539e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.4235 | 0.81919 | 0.82204 | 1.4235 | 0.81919 | 0.82204 | 0.0575 | -90.2257 | 89.9768 | 0.057499 | -90.2257 | 89.9768
Line4_2_6 | 0 | 0.026341 | 0.026434 | 0 | 0.026341 | 0.026434 | 0 | 0.0060831 | 0.0061047 | 0 | 0.0060831 | 0.0061046 | 1.1794e-08 | 0.0035091 | 0.003534 | -1.1908e-08 | -0.0034958 | -0.0035206 | -2.824e-07 | 0.003511 | 0.0035355 | 2.2593e-07 | -0.0034971 | -0.0035215 | 0 | -135.2455 | 44.9605 | 0 | 44.7547 | -135.0398 |  | 1.4235 | 0.81602 | 0.81887 | 1.4235 | 0.81286 | 0.81569 | 0.057571 | -90.2303 | 89.9724 | 0.057643 | -90.2349 | 89.9681
Line5_6_7 | 0 | 0.026341 | 0.026434 | 0 | 0.026341 | 0.026434 | 0 | 0.0060831 | 0.0061046 | 0 | 0.0060832 | 0.0061046 | 9.4359e-09 | 0.0034958 | 0.0035206 | -9.5491e-09 | -0.0034825 | -0.0035071 | -2.2592e-07 | 0.0034971 | 0.0035215 | 1.6945e-07 | -0.0034832 | -0.0035076 | 0 | -135.2453 | 44.9603 | 0 | 44.755 | -135.04 |  | 1.4235 | 0.81286 | 0.81569 | 1.4235 | 0.8097 | 0.81252 | 0.057643 | -90.2349 | 89.9681 | 0.057714 | -90.2396 | 89.9637
Line6_7_8 | 0 | 0.026341 | 0.026434 | 0 | 0.026341 | 0.026434 | 0 | 0.0060832 | 0.0061046 | 0 | 0.0060832 | 0.0061046 | 7.0773e-09 | 0.0034825 | 0.0035071 | -7.1901e-09 | -0.0034692 | -0.0034937 | -1.6944e-07 | 0.0034832 | 0.0035076 | 1.1297e-07 | -0.0034693 | -0.0034936 | 0 | -135.245 | 44.96 | 0 | 44.7552 | -135.0403 |  | 1.4235 | 0.8097 | 0.81252 | 1.4235 | 0.80653 | 0.80935 | 0.057714 | -90.2396 | 89.9637 | 0.057786 | -90.2443 | 89.9592
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3592e-09 | -3.2051e-08 | 3.2071e-08 | -2.4717e-09 | 5.3849e-11 | 3.8678e-11 | -5.6481e-08 | -1.1619e-09 | 1.2922e-09 | 5.0011e-12 | 1.3943e-09 | -1.4114e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.4235 | 0.80653 | 0.80935 | 1.4235 | 0.80653 | 0.80935 | 0.057786 | -90.2443 | 89.9592 | 0.057786 | -90.2443 | 89.9592
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3592e-09 | -3.2051e-08 | 3.2071e-08 | -2.4717e-09 | 5.3849e-11 | 3.8678e-11 | -5.6481e-08 | -1.1619e-09 | 1.2922e-09 | 5.0011e-12 | 1.3943e-09 | -1.4114e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.4235 | 0.80653 | 0.80935 | 1.4235 | 0.80653 | 0.80935 | 0.057786 | -90.2443 | 89.9592 | 0.057786 | -90.2443 | 89.9592
Line9_3_11 | 1.2037e-06 | 1.2039e-06 | 1.2034e-06 | 1.0321e-06 | 1.0323e-06 | 1.0318e-06 | 2.7797e-07 | 2.7802e-07 | 2.7792e-07 | 2.3834e-07 | 2.384e-07 | 2.3829e-07 | 1.6507e-08 | -2.276e-07 | 2.2827e-07 | -1.6621e-08 | 1.951e-07 | -1.9566e-07 | -3.9536e-07 | -8.3369e-09 | 9.248e-09 | 3.3889e-07 | 8.563e-09 | -9.3596e-09 | 87.6667 | 87.6765 | 87.6568 | -92.7503 | -92.7387 | -92.7619 |  | 1.4235 | 0.81919 | 0.82204 | 1.4235 | 0.81919 | 0.82204 | 0.057498 | -90.2257 | 89.9768 | 0.057496 | -90.2257 | 89.9768

## LLG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0.024954 | 0.025043 | 0 | 0.024954 | 0.025043 | 0 | 0.0057629 | 0.0057834 | 0 | 0.0057629 | 0.0057834 | 1.2702e-08 | 0.0031614 | 0.0031839 | -1.2804e-08 | -0.0031495 | -0.0031718 | -3.0415e-07 | 0.0031636 | 0.0031857 | 2.5346e-07 | -0.0031511 | -0.0031731 | 0 | -135.2458 | 44.9608 | 0 | 44.7545 | -135.0395 |  | 1.3486 | 0.77607 | 0.77877 | 1.3486 | 0.77307 | 0.77577 | 0.0575 | -90.2257 | 89.9768 | 0.057571 | -90.2303 | 89.9724
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2699e-08 | -1.7509e-07 | 1.7561e-07 | -1.2801e-08 | 1.4592e-07 | -1.4634e-07 | -3.0415e-07 | -6.4136e-09 | 7.1144e-09 | 2.5346e-07 | 6.6164e-09 | -7.2146e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3486 | 0.77607 | 0.77877 | 1.3486 | 0.77607 | 0.77877 | 0.057496 | -90.2257 | 89.9768 | 0.057494 | -90.2257 | 89.9768
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0582e-08 | -1.4591e-07 | 1.4634e-07 | -1.0684e-08 | 1.1674e-07 | -1.1707e-07 | -2.5346e-07 | -5.3446e-09 | 5.9287e-09 | 2.0277e-07 | 5.5475e-09 | -6.0288e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3486 | 0.77607 | 0.77877 | 1.3486 | 0.77607 | 0.77877 | 0.057494 | -90.2257 | 89.9768 | 0.057493 | -90.2257 | 89.9768
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.3493e-09 | -8.7546e-08 | 8.7804e-08 | -6.4513e-09 | 5.8378e-08 | -5.8535e-08 | -1.5207e-07 | -3.2068e-09 | 3.5572e-09 | 1.0139e-07 | 3.4096e-09 | -3.6574e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3486 | 0.77607 | 0.77877 | 1.3486 | 0.77607 | 0.77877 | 0.057493 | -90.2257 | 89.9768 | 0.057492 | -90.2257 | 89.9768
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1164e-09 | -2.9182e-08 | 2.9268e-08 | -2.2184e-09 | 1.4563e-11 | 1.3398e-12 | -5.0691e-08 | -1.0689e-09 | 1.1857e-09 | 4.466e-12 | 1.2718e-09 | -1.2859e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3486 | 0.77607 | 0.77877 | 1.3486 | 0.77607 | 0.77877 | 0.057493 | -90.2257 | 89.9768 | 0.057492 | -90.2257 | 89.9768
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2329e-09 | -5.8364e-08 | 5.8536e-08 | -4.3349e-09 | 2.9197e-08 | -2.9267e-08 | -1.0138e-07 | -2.1379e-09 | 2.3715e-09 | 5.0696e-08 | 2.3407e-09 | -2.4716e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3486 | 0.77607 | 0.77877 | 1.3486 | 0.77607 | 0.77877 | 0.057492 | -90.2257 | 89.9768 | 0.057491 | -90.2257 | 89.9768
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1164e-09 | -2.9182e-08 | 2.9268e-08 | -2.2184e-09 | 1.4563e-11 | 1.3399e-12 | -5.0691e-08 | -1.0689e-09 | 1.1857e-09 | 4.466e-12 | 1.2718e-09 | -1.2859e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3486 | 0.77607 | 0.77877 | 1.3486 | 0.77607 | 0.77877 | 0.057491 | -90.2257 | 89.9768 | 0.057491 | -90.2257 | 89.9768
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1164e-09 | -2.9182e-08 | 2.9268e-08 | -2.2184e-09 | 1.4564e-11 | 1.3399e-12 | -5.0691e-08 | -1.0689e-09 | 1.1857e-09 | 4.4662e-12 | 1.2718e-09 | -1.2859e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3486 | 0.77607 | 0.77877 | 1.3486 | 0.77607 | 0.77877 | 0.057499 | -90.2257 | 89.9768 | 0.057499 | -90.2257 | 89.9768
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1164e-09 | -2.9182e-08 | 2.9268e-08 | -2.2184e-09 | 1.4564e-11 | 1.3399e-12 | -5.0691e-08 | -1.0689e-09 | 1.1857e-09 | 4.4662e-12 | 1.2718e-09 | -1.2859e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3486 | 0.77607 | 0.77877 | 1.3486 | 0.77607 | 0.77877 | 0.057499 | -90.2257 | 89.9768 | 0.057499 | -90.2257 | 89.9768
Line1_1_3 | 1.3032e-06 | 1.3035e-06 | 1.303e-06 | 1.1406e-06 | 1.1409e-06 | 1.1404e-06 | 3.0096e-07 | 3.0102e-07 | 3.0091e-07 | 2.6342e-07 | 2.6348e-07 | 2.6336e-07 | 1.6931e-08 | -2.3346e-07 | 2.3414e-07 | -1.7033e-08 | 2.0429e-07 | -2.0488e-07 | -4.0553e-07 | -8.5514e-09 | 9.4859e-09 | 3.5484e-07 | 8.7542e-09 | -9.5861e-09 | 87.6667 | 87.6765 | 87.6568 | -92.6907 | -92.6794 | -92.7021 |  | 1.3486 | 0.77607 | 0.77877 | 1.3486 | 0.77607 | 0.77877 | 0.0575 | -90.2257 | 89.9768 | 0.057498 | -90.2257 | 89.9768
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2328e-09 | -5.8364e-08 | 5.8536e-08 | -4.3348e-09 | 2.9197e-08 | -2.9267e-08 | -1.0138e-07 | -2.1378e-09 | 2.3715e-09 | 5.0696e-08 | 2.3407e-09 | -2.4716e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3486 | 0.77607 | 0.77877 | 1.3486 | 0.77607 | 0.77877 | 0.0575 | -90.2257 | 89.9768 | 0.057499 | -90.2257 | 89.9768
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2328e-09 | -5.8364e-08 | 5.8536e-08 | -4.3348e-09 | 2.9197e-08 | -2.9267e-08 | -1.0138e-07 | -2.1378e-09 | 2.3715e-09 | 5.0696e-08 | 2.3407e-09 | -2.4716e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3486 | 0.77607 | 0.77877 | 1.3486 | 0.77607 | 0.77877 | 0.0575 | -90.2257 | 89.9768 | 0.057499 | -90.2257 | 89.9768
Line4_2_6 | 0 | 0.024954 | 0.025043 | 0 | 0.024954 | 0.025043 | 0 | 0.0057629 | 0.0057834 | 0 | 0.005763 | 0.0057833 | 1.0585e-08 | 0.0031495 | 0.0031718 | -1.0687e-08 | -0.0031375 | -0.0031597 | -2.5346e-07 | 0.0031511 | 0.0031731 | 2.0277e-07 | -0.0031387 | -0.0031606 | 0 | -135.2455 | 44.9605 | 0 | 44.7547 | -135.0398 |  | 1.3486 | 0.77307 | 0.77577 | 1.3486 | 0.77008 | 0.77276 | 0.057571 | -90.2303 | 89.9724 | 0.057643 | -90.2349 | 89.9681
Line5_6_7 | 0 | 0.024954 | 0.025043 | 0 | 0.024955 | 0.025042 | 0 | 0.005763 | 0.0057833 | 0 | 0.005763 | 0.0057833 | 8.4688e-09 | 0.0031375 | 0.0031597 | -8.5703e-09 | -0.0031256 | -0.0031477 | -2.0277e-07 | 0.0031387 | 0.0031606 | 1.5208e-07 | -0.0031262 | -0.0031481 | 0 | -135.2453 | 44.9603 | 0 | 44.755 | -135.04 |  | 1.3486 | 0.77008 | 0.77276 | 1.3486 | 0.76708 | 0.76976 | 0.057643 | -90.2349 | 89.9681 | 0.057714 | -90.2396 | 89.9637
Line6_7_8 | 0 | 0.024955 | 0.025042 | 0 | 0.024955 | 0.025042 | 0 | 0.005763 | 0.0057833 | 0 | 0.005763 | 0.0057833 | 6.352e-09 | 0.0031256 | 0.0031477 | -6.4532e-09 | -0.0031137 | -0.0031356 | -1.5208e-07 | 0.0031262 | 0.0031481 | 1.0139e-07 | -0.0031137 | -0.0031355 | 0 | -135.245 | 44.96 | 0 | 44.7552 | -135.0403 |  | 1.3486 | 0.76708 | 0.76976 | 1.3486 | 0.76408 | 0.76676 | 0.057714 | -90.2396 | 89.9637 | 0.057786 | -90.2443 | 89.9592
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1174e-09 | -2.8766e-08 | 2.8783e-08 | -2.2184e-09 | 4.8329e-11 | 3.4714e-11 | -5.0692e-08 | -1.0428e-09 | 1.1597e-09 | 4.4888e-12 | 1.2514e-09 | -1.2667e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3486 | 0.76408 | 0.76676 | 1.3486 | 0.76408 | 0.76676 | 0.057786 | -90.2443 | 89.9592 | 0.057786 | -90.2443 | 89.9592
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1174e-09 | -2.8766e-08 | 2.8783e-08 | -2.2184e-09 | 4.8329e-11 | 3.4714e-11 | -5.0692e-08 | -1.0428e-09 | 1.1597e-09 | 4.4886e-12 | 1.2514e-09 | -1.2667e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3486 | 0.76408 | 0.76676 | 1.3486 | 0.76408 | 0.76676 | 0.057786 | -90.2443 | 89.9592 | 0.057786 | -90.2443 | 89.9592
Line9_3_11 | 1.1403e-06 | 1.1405e-06 | 1.1401e-06 | 0 | 0 | 0 | 2.6334e-07 | 2.6339e-07 | 2.6329e-07 | 0 | 0 | 0 | 1.4815e-08 | -2.0427e-07 | 2.0488e-07 | -1.4917e-08 | 1.7511e-07 | -1.7561e-07 | -3.5484e-07 | -7.4825e-09 | 8.3002e-09 | 3.0415e-07 | 7.6853e-09 | -8.4003e-09 | 87.6667 | 87.6765 | 87.6568 | 0 | 0 | 0 |  | 1.3486 | 0.77607 | 0.77877 | 1.3486 | 0.77607 | 0.77877 | 0.057498 | -90.2257 | 89.9768 | 0.057496 | -90.2257 | 89.9768