## LLL_max_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 10.7672 | 10.7672 | 21.4845 | 0 | 372.9852 | 372.9852 | -1e-07 | 180.8533 | -1e-07 | 205.199 | 131.3915 | -48.6085 | 0 | 0.73333 | 0 | -6.1578e-09
Line_1 | 5.3836 | 5.3836 | 0 | 0 | 186.4926 | 186.4926 | 135.64 | -90.4267 | 153.8992 | -102.5995 | -48.6085 | 131.3915 | 1.1 | 0.73333 | -6.4228e-09 | -6.1578e-09
Line_2 | 5.3836 | 5.3836 | 0 | 0 | 186.4926 | 186.4926 | 135.64 | -90.4267 | 153.8992 | -102.5995 | -48.6085 | 131.3915 | 1.1 | 0.73333 | -6.4228e-09 | -6.1578e-09

## LLL_max_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 10.7672 | 10.7672 | 21.4845 | 0 | 372.9852 | 372.9852 | -1e-07 | 180.8533 | -1e-07 | 205.199 | 131.3915 | -48.6085 | 0 | 0.73333 | 0 | -6.1578e-09
Line_1 | 5.3836 | 5.3836 | 0 | 0 | 186.4926 | 186.4926 | 135.64 | -90.4267 | 153.8992 | -102.5995 | -48.6085 | 131.3915 | 1.1 | 0.73333 | -6.4228e-09 | -6.1578e-09
Line_2 | 5.3836 | 5.3836 | 0 | 0 | 186.4926 | 186.4926 | 135.64 | -90.4267 | 153.8992 | -102.5995 | -48.6085 | 131.3915 | 1.1 | 0.73333 | -6.4228e-09 | -6.1578e-09

## LLL_max_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 1.1262 | 1.1262 | 2.2473 | 0 | 39.0138 | 39.0138 | -32.6787 | 34.6574 | -20.5285 | 22.7736 | 146.1637 | -33.8363 | 0.98918 | 1.063 | -1.6995 | -0.52712
Line_1 | 0.56312 | 0.56312 | 0 | 0 | 19.5069 | 19.5069 | 17.8234 | -17.3287 | 11.9481 | -11.3868 | -33.8363 | 146.1637 | 1.1 | 1.063 | -8.4397e-10 | -0.52712
Line_2 | 0.56312 | 0.56312 | 0 | 0 | 19.5069 | 19.5069 | 17.8234 | -17.3287 | 11.9481 | -11.3868 | -33.8363 | 146.1637 | 1.1 | 1.063 | -8.4397e-10 | -0.52712

## LLL_max_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 1.1262 | 1.1262 | 2.2473 | 0 | 39.0138 | 39.0138 | -32.6787 | 34.6574 | -20.5285 | 22.7736 | 146.1637 | -33.8363 | 0.98918 | 1.063 | -1.6995 | -0.52712
Line_1 | 0.56312 | 0.56312 | 0 | 0 | 19.5069 | 19.5069 | 17.8234 | -17.3287 | 11.9481 | -11.3868 | -33.8363 | 146.1637 | 1.1 | 1.063 | -8.4397e-10 | -0.52712
Line_2 | 0.56312 | 0.56312 | 0 | 0 | 19.5069 | 19.5069 | 17.8234 | -17.3287 | 11.9481 | -11.3868 | -33.8363 | 146.1637 | 1.1 | 1.063 | -8.4397e-10 | -0.52712

## LLL_min_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 6.6379 | 6.6379 | 13.8188 | 0 | 229.9447 | 229.9447 | -1e-07 | 131.9749 | -1e-07 | 77.99 | 149.4192 | -30.5808 | 0 | 0.66667 | 0 | -5.6057e-09
Line_1 | 3.319 | 3.319 | 0 | 0 | 114.9723 | 114.9723 | 98.9811 | -65.9874 | 58.4925 | -38.995 | -30.5808 | 149.4192 | 1 | 0.66667 | -5.6712e-09 | -5.6057e-09
Line_2 | 3.319 | 3.319 | 0 | 0 | 114.9723 | 114.9723 | 98.9811 | -65.9874 | 58.4925 | -38.995 | -30.5808 | 149.4192 | 1 | 0.66667 | -5.6712e-09 | -5.6057e-09

## LLL_min_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 6.6379 | 6.6379 | 13.8188 | 0 | 229.9447 | 229.9447 | -1e-07 | 131.9749 | -1e-07 | 77.99 | 149.4192 | -30.5808 | 0 | 0.66667 | 0 | -5.6057e-09
Line_1 | 3.319 | 3.319 | 0 | 0 | 114.9723 | 114.9723 | 98.9811 | -65.9874 | 58.4925 | -38.995 | -30.5808 | 149.4192 | 1 | 0.66667 | -5.6712e-09 | -5.6057e-09
Line_2 | 3.319 | 3.319 | 0 | 0 | 114.9723 | 114.9723 | 98.9811 | -65.9874 | 58.4925 | -38.995 | -30.5808 | 149.4192 | 1 | 0.66667 | -5.6712e-09 | -5.6057e-09

## LLL_min_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.92661 | 0.92661 | 1.929 | 0 | 32.0988 | 32.0988 | -25.7048 | 28.2765 | -10.2263 | 11.7461 | 157.0699 | -22.9301 | 0.86185 | 0.9539 | -1.2356 | -0.37209
Line_1 | 0.46331 | 0.46331 | 0 | 0 | 16.0494 | 16.0494 | 14.7812 | -14.1383 | 6.253 | -5.873 | -22.9301 | 157.0699 | 1 | 0.9539 | -8.469e-10 | -0.37209
Line_2 | 0.46331 | 0.46331 | 0 | 0 | 16.0494 | 16.0494 | 14.7812 | -14.1383 | 6.253 | -5.873 | -22.9301 | 157.0699 | 1 | 0.9539 | -8.469e-10 | -0.37209

## LLL_min_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.92661 | 0.92661 | 1.929 | 0 | 32.0988 | 32.0988 | -25.7048 | 28.2765 | -10.2263 | 11.7461 | 157.0699 | -22.9301 | 0.86185 | 0.9539 | -1.2356 | -0.37209
Line_1 | 0.46331 | 0.46331 | 0 | 0 | 16.0494 | 16.0494 | 14.7812 | -14.1383 | 6.253 | -5.873 | -22.9301 | 157.0699 | 1 | 0.9539 | -8.469e-10 | -0.37209
Line_2 | 0.46331 | 0.46331 | 0 | 0 | 16.0494 | 16.0494 | 14.7812 | -14.1383 | 6.253 | -5.873 | -22.9301 | 157.0699 | 1 | 0.9539 | -8.469e-10 | -0.37209

## LL_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 9.3246 | 9.3246 | 0 | 9.3246 | 9.3246 | 0 | 107.6715 | 107.6715 | 0 | 107.6715 | 107.6715 | -1.4516e-10 | -44.4269 | 44.4269 | 1.4516e-10 | 89.6402 | 0.78645 | -5.2019e-10 | 39.1559 | -39.1559 | 5.2019e-10 | 12.1438 | 90.4556 | 0 | 41.3915 | -138.6085 | 0 | -138.6085 | 41.3915 | 1.1 | 0.55 | 0.55 | 1.1 | 0.84014 | 0.84014 | 9.8458e-11 | -180 | -180 | 3.2819e-11 | -130.8934 | 130.8934
Line_1 | 0 | 4.6623 | 4.6623 | 0 | 4.6623 | 4.6623 | 0 | 53.8358 | 53.8358 | 0 | 53.8358 | 53.8358 | 7.2579e-11 | 56.1234 | 11.6966 | -7.2582e-11 | -44.8201 | -0.39323 | 2.6009e-10 | 18.8969 | 58.0528 | -2.6009e-10 | -6.0719 | -45.2278 | 0 | -138.6085 | 41.3915 | 0 | 41.3915 | -138.6085 | 1.1 | 1.1 | 1.1 | 1.1 | 0.84014 | 0.84014 | -1.0222e-20 | -120 | 120 | 3.2819e-11 | -130.8934 | 130.8934
Line_2 | 0 | 4.6623 | 4.6623 | 0 | 4.6623 | 4.6623 | 0 | 53.8358 | 53.8358 | 0 | 53.8358 | 53.8358 | 7.2579e-11 | 56.1234 | 11.6966 | -7.2582e-11 | -44.8201 | -0.39323 | 2.6009e-10 | 18.8969 | 58.0528 | -2.6009e-10 | -6.0719 | -45.2278 | 0 | -138.6085 | 41.3915 | 0 | 41.3915 | -138.6085 | 1.1 | 1.1 | 1.1 | 1.1 | 0.84014 | 0.84014 | -1.0222e-20 | -120 | 120 | 3.2819e-11 | -130.8934 | 130.8934

## LL_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 9.3246 | 9.3246 | 0 | 9.3246 | 9.3246 | 0 | 107.6715 | 107.6715 | 0 | 107.6715 | 107.6715 | -1.4516e-10 | -44.4269 | 44.4269 | 1.4516e-10 | 89.6402 | 0.78645 | -5.2019e-10 | 39.1559 | -39.1559 | 5.2019e-10 | 12.1438 | 90.4556 | 0 | 41.3915 | -138.6085 | 0 | -138.6085 | 41.3915 | 1.1 | 0.55 | 0.55 | 1.1 | 0.84014 | 0.84014 | 9.8458e-11 | -180 | -180 | 3.2819e-11 | -130.8934 | 130.8934
Line_1 | 0 | 4.6623 | 4.6623 | 0 | 4.6623 | 4.6623 | 0 | 53.8358 | 53.8358 | 0 | 53.8358 | 53.8358 | 7.2579e-11 | 56.1234 | 11.6966 | -7.2582e-11 | -44.8201 | -0.39323 | 2.6009e-10 | 18.8969 | 58.0528 | -2.6009e-10 | -6.0719 | -45.2278 | 0 | -138.6085 | 41.3915 | 0 | 41.3915 | -138.6085 | 1.1 | 1.1 | 1.1 | 1.1 | 0.84014 | 0.84014 | -1.0222e-20 | -120 | 120 | 3.2819e-11 | -130.8934 | 130.8934
Line_2 | 0 | 4.6623 | 4.6623 | 0 | 4.6623 | 4.6623 | 0 | 53.8358 | 53.8358 | 0 | 53.8358 | 53.8358 | 7.2579e-11 | 56.1234 | 11.6966 | -7.2582e-11 | -44.8201 | -0.39323 | 2.6009e-10 | 18.8969 | 58.0528 | -2.6009e-10 | -6.0719 | -45.2278 | 0 | -138.6085 | 41.3915 | 0 | 41.3915 | -138.6085 | 1.1 | 1.1 | 1.1 | 1.1 | 0.84014 | 0.84014 | -1.0222e-20 | -120 | 120 | 3.2819e-11 | -130.8934 | 130.8934

## LL_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 1.771 | 1.771 | 0 | 1.771 | 1.771 | 0 | 20.4497 | 20.4497 | 0 | 20.4497 | 20.4497 | -2.6634e-11 | -19.9549 | -6.9806 | 2.6632e-11 | 21.5858 | 8.6115 | -9.5438e-11 | 0.72769 | -17.6484 | 9.544e-11 | 1.1228 | 19.4988 | 0 | 54.7762 | -125.2238 | 0 | -125.2238 | 54.7762 | 1.1 | 0.97645 | 0.92807 | 1.1 | 1.057 | 1.0424 | 1.8063e-11 | -127.3123 | 123.1957 | 6.0211e-12 | -122.2462 | 120.948
Line_1 | 0 | 0.8855 | 0.8855 | 0 | 0.8855 | 0.8855 | 0 | 10.2249 | 10.2249 | 0 | 10.2249 | 10.2249 | 1.3316e-11 | 11.2006 | 4.7135 | -1.3317e-11 | -10.7929 | -4.3057 | 4.7719e-11 | 1.024 | 10.212 | -4.7719e-11 | -0.5614 | -9.7494 | 0 | -125.2238 | 54.7762 | 0 | 54.7762 | -125.2238 | 1.1 | 1.1 | 1.1 | 1.1 | 1.057 | 1.0424 | -1.8786e-21 | -120 | 120 | 6.0211e-12 | -122.2462 | 120.948
Line_2 | 0 | 0.8855 | 0.8855 | 0 | 0.8855 | 0.8855 | 0 | 10.2249 | 10.2249 | 0 | 10.2249 | 10.2249 | 1.3316e-11 | 11.2006 | 4.7135 | -1.3317e-11 | -10.7929 | -4.3057 | 4.7719e-11 | 1.024 | 10.212 | -4.7719e-11 | -0.5614 | -9.7494 | 0 | -125.2238 | 54.7762 | 0 | 54.7762 | -125.2238 | 1.1 | 1.1 | 1.1 | 1.1 | 1.057 | 1.0424 | -1.8786e-21 | -120 | 120 | 6.0211e-12 | -122.2462 | 120.948

## LL_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 1.771 | 1.771 | 0 | 1.771 | 1.771 | 0 | 20.4497 | 20.4497 | 0 | 20.4497 | 20.4497 | -2.6634e-11 | -19.9549 | -6.9806 | 2.6632e-11 | 21.5858 | 8.6115 | -9.5438e-11 | 0.72769 | -17.6484 | 9.544e-11 | 1.1228 | 19.4988 | 0 | 54.7762 | -125.2238 | 0 | -125.2238 | 54.7762 | 1.1 | 0.97645 | 0.92807 | 1.1 | 1.057 | 1.0424 | 1.8063e-11 | -127.3123 | 123.1957 | 6.0211e-12 | -122.2462 | 120.948
Line_1 | 0 | 0.8855 | 0.8855 | 0 | 0.8855 | 0.8855 | 0 | 10.2249 | 10.2249 | 0 | 10.2249 | 10.2249 | 1.3316e-11 | 11.2006 | 4.7135 | -1.3317e-11 | -10.7929 | -4.3057 | 4.7719e-11 | 1.024 | 10.212 | -4.7719e-11 | -0.5614 | -9.7494 | 0 | -125.2238 | 54.7762 | 0 | 54.7762 | -125.2238 | 1.1 | 1.1 | 1.1 | 1.1 | 1.057 | 1.0424 | -1.8786e-21 | -120 | 120 | 6.0211e-12 | -122.2462 | 120.948
Line_2 | 0 | 0.8855 | 0.8855 | 0 | 0.8855 | 0.8855 | 0 | 10.2249 | 10.2249 | 0 | 10.2249 | 10.2249 | 1.3316e-11 | 11.2006 | 4.7135 | -1.3317e-11 | -10.7929 | -4.3057 | 4.7719e-11 | 1.024 | 10.212 | -4.7719e-11 | -0.5614 | -9.7494 | 0 | -125.2238 | 54.7762 | 0 | 54.7762 | -125.2238 | 1.1 | 1.1 | 1.1 | 1.1 | 1.057 | 1.0424 | -1.8786e-21 | -120 | 120 | 6.0211e-12 | -122.2462 | 120.948

## LL_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 5.7486 | 5.7486 | 0 | 5.7486 | 5.7486 | 0 | 66.3793 | 66.3793 | 0 | 66.3793 | 66.3793 | -2.3585e-11 | -16.8853 | 16.8853 | 2.3583e-11 | 49.879 | 16.1084 | -4.7332e-11 | 28.5734 | -28.5734 | 4.7332e-11 | -9.0759 | 48.0709 | 0 | 59.4192 | -120.5808 | 0 | -120.5808 | 59.4192 | 1 | 0.5 | 0.5 | 1 | 0.76376 | 0.76376 | 2.1493e-11 | -180 | 180 | 7.1645e-12 | -130.8934 | 130.8934
Line_1 | 0 | 2.8743 | 2.8743 | 0 | 2.8743 | 2.8743 | 0 | 33.1897 | 33.1897 | 0 | 33.1897 | 33.1897 | 1.1794e-11 | 33.1879 | 16.3026 | -1.1794e-11 | -24.9395 | -8.0542 | 2.3663e-11 | 0.33642 | 28.9098 | -2.3663e-11 | 4.538 | -24.0354 | 0 | -120.5808 | 59.4192 | 0 | 59.4192 | -120.5808 | 1 | 1 | 1 | 1 | 0.76376 | 0.76376 | -1.9872e-21 | -120 | 120 | 7.1645e-12 | -130.8934 | 130.8934
Line_2 | 0 | 2.8743 | 2.8743 | 0 | 2.8743 | 2.8743 | 0 | 33.1897 | 33.1897 | 0 | 33.1897 | 33.1897 | 1.1794e-11 | 33.1879 | 16.3026 | -1.1794e-11 | -24.9395 | -8.0542 | 2.3663e-11 | 0.33642 | 28.9098 | -2.3663e-11 | 4.538 | -24.0354 | 0 | -120.5808 | 59.4192 | 0 | 59.4192 | -120.5808 | 1 | 1 | 1 | 1 | 0.76376 | 0.76376 | -1.9872e-21 | -120 | 120 | 7.1645e-12 | -130.8934 | 130.8934

## LL_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 5.7486 | 5.7486 | 0 | 5.7486 | 5.7486 | 0 | 66.3793 | 66.3793 | 0 | 66.3793 | 66.3793 | -2.3585e-11 | -16.8853 | 16.8853 | 2.3583e-11 | 49.879 | 16.1084 | -4.7332e-11 | 28.5734 | -28.5734 | 4.7332e-11 | -9.0759 | 48.0709 | 0 | 59.4192 | -120.5808 | 0 | -120.5808 | 59.4192 | 1 | 0.5 | 0.5 | 1 | 0.76376 | 0.76376 | 2.1493e-11 | -180 | 180 | 7.1645e-12 | -130.8934 | 130.8934
Line_1 | 0 | 2.8743 | 2.8743 | 0 | 2.8743 | 2.8743 | 0 | 33.1897 | 33.1897 | 0 | 33.1897 | 33.1897 | 1.1794e-11 | 33.1879 | 16.3026 | -1.1794e-11 | -24.9395 | -8.0542 | 2.3663e-11 | 0.33642 | 28.9098 | -2.3663e-11 | 4.538 | -24.0354 | 0 | -120.5808 | 59.4192 | 0 | 59.4192 | -120.5808 | 1 | 1 | 1 | 1 | 0.76376 | 0.76376 | -1.9872e-21 | -120 | 120 | 7.1645e-12 | -130.8934 | 130.8934
Line_2 | 0 | 2.8743 | 2.8743 | 0 | 2.8743 | 2.8743 | 0 | 33.1897 | 33.1897 | 0 | 33.1897 | 33.1897 | 1.1794e-11 | 33.1879 | 16.3026 | -1.1794e-11 | -24.9395 | -8.0542 | 2.3663e-11 | 0.33642 | 28.9098 | -2.3663e-11 | 4.538 | -24.0354 | 0 | -120.5808 | 59.4192 | 0 | 59.4192 | -120.5808 | 1 | 1 | 1 | 1 | 0.76376 | 0.76376 | -1.9872e-21 | -120 | 120 | 7.1645e-12 | -130.8934 | 130.8934

## LL_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 1.4097 | 1.4097 | 0 | 1.4097 | 1.4097 | 0 | 16.2777 | 16.2777 | 0 | 16.2777 | 16.2777 | 4.2335e-12 | -13.2084 | -6.6226 | -4.2339e-12 | 15.1925 | 8.6067 | 8.8904e-12 | 3.4982 | -11.3877 | -8.8913e-12 | -2.3257 | 12.5602 | 0 | 66.1346 | -113.8654 | 0 | -113.8654 | 66.1346 | 1 | 0.83942 | 0.80929 | 1 | 0.9442 | 0.93539 | -4.1123e-12 | -128.6994 | 125.9541 | -1.3708e-12 | -122.569 | 121.7143
Line_1 | 0 | 0.70485 | 0.70485 | 0 | 0.70485 | 0.70485 | 0 | 8.1389 | 8.1389 | 0 | 8.1389 | 8.1389 | -2.1168e-12 | 8.0923 | 4.7994 | 2.1168e-12 | -7.5962 | -4.3033 | -4.4453e-12 | -0.86976 | 6.5732 | 4.4456e-12 | 1.1629 | -6.2801 | 0 | -113.8654 | 66.1346 | 0 | 66.1346 | -113.8654 | 1 | 1 | 1 | 1 | 0.9442 | 0.93539 | 3.7162e-22 | -120 | 120 | -1.3708e-12 | -122.569 | 121.7143
Line_2 | 0 | 0.70485 | 0.70485 | 0 | 0.70485 | 0.70485 | 0 | 8.1389 | 8.1389 | 0 | 8.1389 | 8.1389 | -2.1168e-12 | 8.0923 | 4.7994 | 2.1168e-12 | -7.5962 | -4.3033 | -4.4453e-12 | -0.86976 | 6.5732 | 4.4456e-12 | 1.1629 | -6.2801 | 0 | -113.8654 | 66.1346 | 0 | 66.1346 | -113.8654 | 1 | 1 | 1 | 1 | 0.9442 | 0.93539 | 3.7162e-22 | -120 | 120 | -1.3708e-12 | -122.569 | 121.7143

## LL_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 1.4097 | 1.4097 | 0 | 1.4097 | 1.4097 | 0 | 16.2777 | 16.2777 | 0 | 16.2777 | 16.2777 | 4.2335e-12 | -13.2084 | -6.6226 | -4.2339e-12 | 15.1925 | 8.6067 | 8.8904e-12 | 3.4982 | -11.3877 | -8.8913e-12 | -2.3257 | 12.5602 | 0 | 66.1346 | -113.8654 | 0 | -113.8654 | 66.1346 | 1 | 0.83942 | 0.80929 | 1 | 0.9442 | 0.93539 | -4.1123e-12 | -128.6994 | 125.9541 | -1.3708e-12 | -122.569 | 121.7143
Line_1 | 0 | 0.70485 | 0.70485 | 0 | 0.70485 | 0.70485 | 0 | 8.1389 | 8.1389 | 0 | 8.1389 | 8.1389 | -2.1168e-12 | 8.0923 | 4.7994 | 2.1168e-12 | -7.5962 | -4.3033 | -4.4453e-12 | -0.86976 | 6.5732 | 4.4456e-12 | 1.1629 | -6.2801 | 0 | -113.8654 | 66.1346 | 0 | 66.1346 | -113.8654 | 1 | 1 | 1 | 1 | 0.9442 | 0.93539 | 3.7162e-22 | -120 | 120 | -1.3708e-12 | -122.569 | 121.7143
Line_2 | 0 | 0.70485 | 0.70485 | 0 | 0.70485 | 0.70485 | 0 | 8.1389 | 8.1389 | 0 | 8.1389 | 8.1389 | -2.1168e-12 | 8.0923 | 4.7994 | 2.1168e-12 | -7.5962 | -4.3033 | -4.4453e-12 | -0.86976 | 6.5732 | 4.4456e-12 | 1.1629 | -6.2801 | 0 | -113.8654 | 66.1346 | 0 | 66.1346 | -113.8654 | 1 | 1 | 1 | 1 | 0.9442 | 0.93539 | 3.7162e-22 | -120 | 120 | -1.3708e-12 | -122.569 | 121.7143

## LG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 4.1363 | 0.61861 | 0.61861 | 4.137 | 0.62079 | 0.62079 | 47.7619 | 7.1431 | 7.1431 | 47.7702 | 7.1683 | 7.1683 | 5.2143e-11 | 0.8834 | 12.1336 | 32.3708 | 2.0142 | -9.3006 | -3.0456e-11 | 10.9219 | 3.2637 | 13.3844 | -8.3809 | -0.73215 | 157.5955 | 124.2437 | 124.2437 | -22.4443 | -55.9413 | -55.9413 |  | 0 | 1.534 | 1.759 | 0.73327 | 1.2024 | 1.3015 | 0 | -150.3805 | 139.2989 | 0.019412 | -132.4279 | 128.5597
Line_1 | 2.0687 | 0.31095 | 0.31095 | 2.0685 | 0.3104 | 0.3104 | 23.8872 | 3.5905 | 3.5905 | 23.8851 | 3.5842 | 3.5842 | 24.2821 | 1.7334 | -3.9401 | -16.1854 | -1.0071 | 4.6503 | 10.0402 | -3.5488 | 0.27321 | -6.6922 | 4.1905 | 0.36607 | -22.4642 | -56.0335 | -56.0335 | 157.5557 | 124.0587 | 124.0587 |  | 1.1 | 1.1 | 1.1 | 0.73327 | 1.2024 | 1.3015 | -3.4494e-09 | -120 | 120 | 0.019412 | -132.4279 | 128.5597
Line_2 | 2.0687 | 0.31095 | 0.31095 | 2.0685 | 0.3104 | 0.3104 | 23.8872 | 3.5905 | 3.5905 | 23.8851 | 3.5842 | 3.5842 | 24.2821 | 1.7334 | -3.9401 | -16.1854 | -1.0071 | 4.6503 | 10.0402 | -3.5488 | 0.27321 | -6.6922 | 4.1905 | 0.36607 | -22.4642 | -56.0335 | -56.0335 | 157.5557 | 124.0587 | 124.0587 |  | 1.1 | 1.1 | 1.1 | 0.73327 | 1.2024 | 1.3015 | -3.4494e-09 | -120 | 120 | 0.019412 | -132.4279 | 128.5597

## LG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 4.1363 | 0.61861 | 0.61861 | 4.137 | 0.62079 | 0.62079 | 47.7619 | 7.1431 | 7.1431 | 47.7702 | 7.1683 | 7.1683 | 5.2143e-11 | 0.8834 | 12.1336 | 32.3708 | 2.0142 | -9.3006 | -3.0456e-11 | 10.9219 | 3.2637 | 13.3844 | -8.3809 | -0.73215 | 157.5955 | 124.2437 | 124.2437 | -22.4443 | -55.9413 | -55.9413 |  | 0 | 1.534 | 1.759 | 0.73327 | 1.2024 | 1.3015 | 0 | -150.3805 | 139.2989 | 0.019412 | -132.4279 | 128.5597
Line_1 | 2.0687 | 0.31095 | 0.31095 | 2.0685 | 0.3104 | 0.3104 | 23.8872 | 3.5905 | 3.5905 | 23.8851 | 3.5842 | 3.5842 | 24.2821 | 1.7334 | -3.9401 | -16.1854 | -1.0071 | 4.6503 | 10.0402 | -3.5488 | 0.27321 | -6.6922 | 4.1905 | 0.36607 | -22.4642 | -56.0335 | -56.0335 | 157.5557 | 124.0587 | 124.0587 |  | 1.1 | 1.1 | 1.1 | 0.73327 | 1.2024 | 1.3015 | -3.4494e-09 | -120 | 120 | 0.019412 | -132.4279 | 128.5597
Line_2 | 2.0687 | 0.31095 | 0.31095 | 2.0685 | 0.3104 | 0.3104 | 23.8872 | 3.5905 | 3.5905 | 23.8851 | 3.5842 | 3.5842 | 24.2821 | 1.7334 | -3.9401 | -16.1854 | -1.0071 | 4.6503 | 10.0402 | -3.5488 | 0.27321 | -6.6922 | 4.1905 | 0.36607 | -22.4642 | -56.0335 | -56.0335 | 157.5557 | 124.0587 | 124.0587 |  | 1.1 | 1.1 | 1.1 | 0.73327 | 1.2024 | 1.3015 | -3.4494e-09 | -120 | 120 | 0.019412 | -132.4279 | 128.5597

## LG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.0669 | 0.15956 | 0.15956 | 1.0671 | 0.16012 | 0.16012 | 12.3191 | 1.8424 | 1.8424 | 12.3213 | 1.8489 | 1.8489 | -8.0488 | -0.93384 | 2.2974 | 10.1994 | 1.1338 | -2.1133 | -6.1771 | 1.8743 | 0.50292 | 7.0742 | -1.7061 | -0.34034 | 146.3481 | 112.9964 | 112.9964 | -33.6917 | -67.1887 | -67.1887 |  | 0.82359 | 1.1366 | 1.2765 | 1.0074 | 1.1079 | 1.1577 | 3.8527 | -130.5191 | 125.3439 | 1.0529 | -123.581 | 121.9601
Line_1 | 0.53357 | 0.080201 | 0.080201 | 0.53353 | 0.08006 | 0.08006 | 6.1612 | 0.92609 | 0.92609 | 6.1606 | 0.92445 | 0.92445 | 5.6376 | 0.61705 | -1.0105 | -5.0997 | -0.56692 | 1.0566 | 3.7615 | -0.81055 | -0.1291 | -3.5371 | 0.85303 | 0.17017 | -33.7116 | -67.2808 | -67.2808 | 146.3083 | 112.8113 | 112.8113 |  | 1.1 | 1.1 | 1.1 | 1.0074 | 1.1079 | 1.1577 | -8.0086e-10 | -120 | 120 | 1.0529 | -123.581 | 121.9601
Line_2 | 0.53357 | 0.080201 | 0.080201 | 0.53353 | 0.08006 | 0.08006 | 6.1612 | 0.92609 | 0.92609 | 6.1606 | 0.92445 | 0.92445 | 5.6376 | 0.61705 | -1.0105 | -5.0997 | -0.56692 | 1.0566 | 3.7615 | -0.81055 | -0.1291 | -3.5371 | 0.85303 | 0.17017 | -33.7116 | -67.2808 | -67.2808 | 146.3083 | 112.8113 | 112.8113 |  | 1.1 | 1.1 | 1.1 | 1.0074 | 1.1079 | 1.1577 | -8.0086e-10 | -120 | 120 | 1.0529 | -123.581 | 121.9601

## LG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.0669 | 0.15956 | 0.15956 | 1.0671 | 0.16012 | 0.16012 | 12.3191 | 1.8424 | 1.8424 | 12.3213 | 1.8489 | 1.8489 | -8.0488 | -0.93384 | 2.2974 | 10.1994 | 1.1338 | -2.1133 | -6.1771 | 1.8743 | 0.50292 | 7.0742 | -1.7061 | -0.34034 | 146.3481 | 112.9964 | 112.9964 | -33.6917 | -67.1887 | -67.1887 |  | 0.82359 | 1.1366 | 1.2765 | 1.0074 | 1.1079 | 1.1577 | 3.8527 | -130.5191 | 125.3439 | 1.0529 | -123.581 | 121.9601
Line_1 | 0.53357 | 0.080201 | 0.080201 | 0.53353 | 0.08006 | 0.08006 | 6.1612 | 0.92609 | 0.92609 | 6.1606 | 0.92445 | 0.92445 | 5.6376 | 0.61705 | -1.0105 | -5.0997 | -0.56692 | 1.0566 | 3.7615 | -0.81055 | -0.1291 | -3.5371 | 0.85303 | 0.17017 | -33.7116 | -67.2808 | -67.2808 | 146.3083 | 112.8113 | 112.8113 |  | 1.1 | 1.1 | 1.1 | 1.0074 | 1.1079 | 1.1577 | -8.0086e-10 | -120 | 120 | 1.0529 | -123.581 | 121.9601
Line_2 | 0.53357 | 0.080201 | 0.080201 | 0.53353 | 0.08006 | 0.08006 | 6.1612 | 0.92609 | 0.92609 | 6.1606 | 0.92445 | 0.92445 | 5.6376 | 0.61705 | -1.0105 | -5.0997 | -0.56692 | 1.0566 | 3.7615 | -0.81055 | -0.1291 | -3.5371 | 0.85303 | 0.17017 | -33.7116 | -67.2808 | -67.2808 | 146.3083 | 112.8113 | 112.8113 |  | 1.1 | 1.1 | 1.1 | 1.0074 | 1.1079 | 1.1577 | -8.0086e-10 | -120 | 120 | 1.0529 | -123.581 | 121.9601

## LG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 2.0701 | 0.43176 | 0.43176 | 2.07 | 0.43376 | 0.43376 | 23.9036 | 4.9855 | 4.9855 | 23.9026 | 5.0086 | 5.0086 | 1.7495e-12 | 1.1502 | 7.9467 | 15.864 | 0.8846 | -5.9682 | 4.499e-12 | 7.1979 | 1.8713 | 1.4943 | -5.503 | -0.18335 | 174.7353 | 128.0867 | 128.0867 | -5.3431 | -52.1785 | -52.1785 |  | 0 | 1.4621 | 1.6376 | 0.66663 | 1.1128 | 1.1921 | 0 | -150.9922 | 141.3374 | 0.038098 | -133.0464 | 129.5811
Line_1 | 1.035 | 0.21738 | 0.21738 | 1.035 | 0.21688 | 0.21688 | 11.9511 | 2.5101 | 2.5101 | 11.9513 | 2.5043 | 2.5043 | 11.8984 | 0.9529 | -2.4876 | -7.932 | -0.4423 | 2.9841 | 1.121 | -2.3222 | 0.33587 | -0.74717 | 2.7515 | 0.091677 | -5.3823 | -52.3104 | -52.3104 | 174.6569 | 127.8215 | 127.8215 |  | 1 | 1 | 1 | 0.66663 | 1.1128 | 1.1921 | -2.0452e-09 | -120 | 120 | 0.038098 | -133.0464 | 129.5811
Line_2 | 1.035 | 0.21738 | 0.21738 | 1.035 | 0.21688 | 0.21688 | 11.9511 | 2.5101 | 2.5101 | 11.9513 | 2.5043 | 2.5043 | 11.8984 | 0.9529 | -2.4876 | -7.932 | -0.4423 | 2.9841 | 1.121 | -2.3222 | 0.33587 | -0.74717 | 2.7515 | 0.091677 | -5.3823 | -52.3104 | -52.3104 | 174.6569 | 127.8215 | 127.8215 |  | 1 | 1 | 1 | 0.66663 | 1.1128 | 1.1921 | -2.0452e-09 | -120 | 120 | 0.038098 | -133.0464 | 129.5811

## LG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 2.0701 | 0.43176 | 0.43176 | 2.07 | 0.43376 | 0.43376 | 23.9036 | 4.9855 | 4.9855 | 23.9026 | 5.0086 | 5.0086 | 1.7495e-12 | 1.1502 | 7.9467 | 15.864 | 0.8846 | -5.9682 | 4.499e-12 | 7.1979 | 1.8713 | 1.4943 | -5.503 | -0.18335 | 174.7353 | 128.0867 | 128.0867 | -5.3431 | -52.1785 | -52.1785 |  | 0 | 1.4621 | 1.6376 | 0.66663 | 1.1128 | 1.1921 | 0 | -150.9922 | 141.3374 | 0.038098 | -133.0464 | 129.5811
Line_1 | 1.035 | 0.21738 | 0.21738 | 1.035 | 0.21688 | 0.21688 | 11.9511 | 2.5101 | 2.5101 | 11.9513 | 2.5043 | 2.5043 | 11.8984 | 0.9529 | -2.4876 | -7.932 | -0.4423 | 2.9841 | 1.121 | -2.3222 | 0.33587 | -0.74717 | 2.7515 | 0.091677 | -5.3823 | -52.3104 | -52.3104 | 174.6569 | 127.8215 | 127.8215 |  | 1 | 1 | 1 | 0.66663 | 1.1128 | 1.1921 | -2.0452e-09 | -120 | 120 | 0.038098 | -133.0464 | 129.5811
Line_2 | 1.035 | 0.21738 | 0.21738 | 1.035 | 0.21688 | 0.21688 | 11.9511 | 2.5101 | 2.5101 | 11.9513 | 2.5043 | 2.5043 | 11.8984 | 0.9529 | -2.4876 | -7.932 | -0.4423 | 2.9841 | 1.121 | -2.3222 | 0.33587 | -0.74717 | 2.7515 | 0.091677 | -5.3823 | -52.3104 | -52.3104 | 174.6569 | 127.8215 | 127.8215 |  | 1 | 1 | 1 | 0.66663 | 1.1128 | 1.1921 | -2.0452e-09 | -120 | 120 | 0.038098 | -133.0464 | 129.5811

## LG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.79347 | 0.16549 | 0.16549 | 0.79344 | 0.16626 | 0.16626 | 9.1622 | 1.9109 | 1.9109 | 9.1618 | 1.9198 | 1.9198 | -5.0042 | -0.7484 | 2.3321 | 7.3305 | 1.0554 | -2.045 | -3.0945 | 1.8725 | 0.66188 | 3.3208 | -1.623 | -0.4211 | 158.1041 | 111.4555 | 111.4555 | -21.9743 | -68.8098 | -68.8098 |  | 0.64218 | 1.0553 | 1.2686 | 0.87838 | 1.0084 | 1.0875 | 9.8361 | -136.7593 | 127.3005 | 2.3969 | -125.7757 | 122.826
Line_1 | 0.39671 | 0.083322 | 0.083322 | 0.39672 | 0.08313 | 0.08313 | 4.5808 | 0.96212 | 0.96212 | 4.5809 | 0.9599 | 0.9599 | 4.2469 | 0.60472 | -0.95043 | -3.6652 | -0.5277 | 1.0225 | 1.717 | -0.74833 | -0.14954 | -1.6604 | 0.81152 | 0.21055 | -22.0135 | -68.9416 | -68.9416 | 158.0257 | 111.1902 | 111.1902 |  | 1 | 1 | 1 | 0.87838 | 1.0084 | 1.0875 | -7.2998e-10 | -120 | 120 | 2.3969 | -125.7757 | 122.826
Line_2 | 0.39671 | 0.083322 | 0.083322 | 0.39672 | 0.08313 | 0.08313 | 4.5808 | 0.96212 | 0.96212 | 4.5809 | 0.9599 | 0.9599 | 4.2469 | 0.60472 | -0.95043 | -3.6652 | -0.5277 | 1.0225 | 1.717 | -0.74833 | -0.14954 | -1.6604 | 0.81152 | 0.21055 | -22.0135 | -68.9416 | -68.9416 | 158.0257 | 111.1902 | 111.1902 |  | 1 | 1 | 1 | 0.87838 | 1.0084 | 1.0875 | -7.2998e-10 | -120 | 120 | 2.3969 | -125.7757 | 122.826

## LG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.79347 | 0.16549 | 0.16549 | 0.79344 | 0.16626 | 0.16626 | 9.1622 | 1.9109 | 1.9109 | 9.1618 | 1.9198 | 1.9198 | -5.0042 | -0.7484 | 2.3321 | 7.3305 | 1.0554 | -2.045 | -3.0945 | 1.8725 | 0.66188 | 3.3208 | -1.623 | -0.4211 | 158.1041 | 111.4555 | 111.4555 | -21.9743 | -68.8098 | -68.8098 |  | 0.64218 | 1.0553 | 1.2686 | 0.87838 | 1.0084 | 1.0875 | 9.8361 | -136.7593 | 127.3005 | 2.3969 | -125.7757 | 122.826
Line_1 | 0.39671 | 0.083322 | 0.083322 | 0.39672 | 0.08313 | 0.08313 | 4.5808 | 0.96212 | 0.96212 | 4.5809 | 0.9599 | 0.9599 | 4.2469 | 0.60472 | -0.95043 | -3.6652 | -0.5277 | 1.0225 | 1.717 | -0.74833 | -0.14954 | -1.6604 | 0.81152 | 0.21055 | -22.0135 | -68.9416 | -68.9416 | 158.0257 | 111.1902 | 111.1902 |  | 1 | 1 | 1 | 0.87838 | 1.0084 | 1.0875 | -7.2998e-10 | -120 | 120 | 2.3969 | -125.7757 | 122.826
Line_2 | 0.39671 | 0.083322 | 0.083322 | 0.39672 | 0.08313 | 0.08313 | 4.5808 | 0.96212 | 0.96212 | 4.5809 | 0.9599 | 0.9599 | 4.2469 | 0.60472 | -0.95043 | -3.6652 | -0.5277 | 1.0225 | 1.717 | -0.74833 | -0.14954 | -1.6604 | 0.81152 | 0.21055 | -22.0135 | -68.9416 | -68.9416 | 158.0257 | 111.1902 | 111.1902 |  | 1 | 1 | 1 | 0.87838 | 1.0084 | 1.0875 | -7.2998e-10 | -120 | 120 | 2.3969 | -125.7757 | 122.826

## LLG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.35936 | 10.0308 | 8.7723 | 0.36063 | 10.0298 | 8.7736 | 4.1495 | 115.826 | 101.2934 | 4.1642 | 115.814 | 101.309 | 4.3927 | 1.335e-10 | 8.5258e-11 | -3.4258 | 76.6791 | 24.4787 | 4.7871 | -8.826e-12 | 7.7417e-11 | -3.9467 | 36.5428 | 70.1291 | -49.8619 | 34.5357 | -130.7632 | 129.953 | -145.4722 | 49.2438 |  | 1.5658 | 0 | 0 | 1.255 | 0.73343 | 0.73319 | -2.402 | 0 | 0 | -1.0051 | -119.9912 | 120.0022
Line_1 | 0.18063 | 5.0146 | 4.3871 | 0.18031 | 5.0149 | 4.3868 | 2.0858 | 57.904 | 50.6584 | 2.0821 | 57.907 | 50.6545 | -1.4705 | 57.5011 | 18.3692 | 1.7129 | -38.3395 | -12.2393 | -1.7611 | 27.3972 | 52.6095 | 1.9734 | -18.2714 | -35.0646 | 129.8609 | -145.4761 | 49.2473 | -50.047 | 34.5278 | -130.7562 |  | 1.1 | 1.1 | 1.1 | 1.255 | 0.73343 | 0.73319 | 2.0889e-10 | -120 | 120 | -1.0051 | -119.9912 | 120.0022
Line_2 | 0.18063 | 5.0146 | 4.3871 | 0.18031 | 5.0149 | 4.3868 | 2.0858 | 57.904 | 50.6584 | 2.0821 | 57.907 | 50.6545 | -1.4705 | 57.5011 | 18.3692 | 1.7129 | -38.3395 | -12.2393 | -1.7611 | 27.3972 | 52.6095 | 1.9734 | -18.2714 | -35.0646 | 129.8609 | -145.4761 | 49.2473 | -50.047 | 34.5278 | -130.7562 |  | 1.1 | 1.1 | 1.1 | 1.255 | 0.73343 | 0.73319 | 2.0889e-10 | -120 | 120 | -1.0051 | -119.9912 | 120.0022

## LLG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.35936 | 10.0308 | 8.7723 | 0.36063 | 10.0298 | 8.7736 | 4.1495 | 115.826 | 101.2934 | 4.1642 | 115.814 | 101.309 | 4.3927 | 1.335e-10 | 8.5258e-11 | -3.4258 | 76.6791 | 24.4787 | 4.7871 | -8.826e-12 | 7.7417e-11 | -3.9467 | 36.5428 | 70.1291 | -49.8619 | 34.5357 | -130.7632 | 129.953 | -145.4722 | 49.2438 |  | 1.5658 | 0 | 0 | 1.255 | 0.73343 | 0.73319 | -2.402 | 0 | 0 | -1.0051 | -119.9912 | 120.0022
Line_1 | 0.18063 | 5.0146 | 4.3871 | 0.18031 | 5.0149 | 4.3868 | 2.0858 | 57.904 | 50.6584 | 2.0821 | 57.907 | 50.6545 | -1.4705 | 57.5011 | 18.3692 | 1.7129 | -38.3395 | -12.2393 | -1.7611 | 27.3972 | 52.6095 | 1.9734 | -18.2714 | -35.0646 | 129.8609 | -145.4761 | 49.2473 | -50.047 | 34.5278 | -130.7562 |  | 1.1 | 1.1 | 1.1 | 1.255 | 0.73343 | 0.73319 | 2.0889e-10 | -120 | 120 | -1.0051 | -119.9912 | 120.0022
Line_2 | 0.18063 | 5.0146 | 4.3871 | 0.18031 | 5.0149 | 4.3868 | 2.0858 | 57.904 | 50.6584 | 2.0821 | 57.907 | 50.6545 | -1.4705 | 57.5011 | 18.3692 | 1.7129 | -38.3395 | -12.2393 | -1.7611 | 27.3972 | 52.6095 | 1.9734 | -18.2714 | -35.0646 | 129.8609 | -145.4761 | 49.2473 | -50.047 | 34.5278 | -130.7562 |  | 1.1 | 1.1 | 1.1 | 1.255 | 0.73343 | 0.73319 | 2.0889e-10 | -120 | 120 | -1.0051 | -119.9912 | 120.0022

## LLG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.1359 | 1.1013 | 1.1023 | 0.13638 | 1.1008 | 1.1029 | 1.5692 | 12.7166 | 12.7279 | 1.5748 | 12.7114 | 12.7353 | 0.98922 | -9.6423 | -9.797 | -0.84883 | 11.1521 | 10.8092 | 1.7245 | -7.8492 | -5.1756 | -1.6092 | 7.5007 | 7.2339 | -63.0693 | 28.432 | -96.1313 | 116.7456 | -151.5923 | 83.8631 |  | 1.2669 | 0.97771 | 0.87054 | 1.1553 | 1.0573 | 1.0213 | -2.9084 | -112.4213 | 111.7157 | -1.0655 | -117.6683 | 117.655
Line_1 | 0.06831 | 0.55031 | 0.55162 | 0.06819 | 0.55042 | 0.55146 | 0.78878 | 6.3544 | 6.3695 | 0.78739 | 6.3557 | 6.3677 | -0.38923 | 5.9531 | 5.6583 | 0.42442 | -5.5761 | -5.4046 | -0.77546 | 3.663 | 4.1321 | 0.8046 | -3.7504 | -3.6169 | 116.6535 | -151.6045 | 83.8603 | -63.2544 | 28.4077 | -96.1369 |  | 1.1 | 1.1 | 1.1 | 1.1553 | 1.0573 | 1.0213 | 5.5292e-11 | -120 | 120 | -1.0655 | -117.6683 | 117.655
Line_2 | 0.06831 | 0.55031 | 0.55162 | 0.06819 | 0.55042 | 0.55146 | 0.78878 | 6.3544 | 6.3695 | 0.78739 | 6.3557 | 6.3677 | -0.38923 | 5.9531 | 5.6583 | 0.42442 | -5.5761 | -5.4046 | -0.77546 | 3.663 | 4.1321 | 0.8046 | -3.7504 | -3.6169 | 116.6535 | -151.6045 | 83.8603 | -63.2544 | 28.4077 | -96.1369 |  | 1.1 | 1.1 | 1.1 | 1.1553 | 1.0573 | 1.0213 | 5.5292e-11 | -120 | 120 | -1.0655 | -117.6683 | 117.655

## LLG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.1359 | 1.1013 | 1.1023 | 0.13638 | 1.1008 | 1.1029 | 1.5692 | 12.7166 | 12.7279 | 1.5748 | 12.7114 | 12.7353 | 0.98922 | -9.6423 | -9.797 | -0.84883 | 11.1521 | 10.8092 | 1.7245 | -7.8492 | -5.1756 | -1.6092 | 7.5007 | 7.2339 | -63.0693 | 28.432 | -96.1313 | 116.7456 | -151.5923 | 83.8631 |  | 1.2669 | 0.97771 | 0.87054 | 1.1553 | 1.0573 | 1.0213 | -2.9084 | -112.4213 | 111.7157 | -1.0655 | -117.6683 | 117.655
Line_1 | 0.06831 | 0.55031 | 0.55162 | 0.06819 | 0.55042 | 0.55146 | 0.78878 | 6.3544 | 6.3695 | 0.78739 | 6.3557 | 6.3677 | -0.38923 | 5.9531 | 5.6583 | 0.42442 | -5.5761 | -5.4046 | -0.77546 | 3.663 | 4.1321 | 0.8046 | -3.7504 | -3.6169 | 116.6535 | -151.6045 | 83.8603 | -63.2544 | 28.4077 | -96.1369 |  | 1.1 | 1.1 | 1.1 | 1.1553 | 1.0573 | 1.0213 | 5.5292e-11 | -120 | 120 | -1.0655 | -117.6683 | 117.655
Line_2 | 0.06831 | 0.55031 | 0.55162 | 0.06819 | 0.55042 | 0.55146 | 0.78878 | 6.3544 | 6.3695 | 0.78739 | 6.3557 | 6.3677 | -0.38923 | 5.9531 | 5.6583 | 0.42442 | -5.5761 | -5.4046 | -0.77546 | 3.663 | 4.1321 | 0.8046 | -3.7504 | -3.6169 | 116.6535 | -151.6045 | 83.8603 | -63.2544 | 28.4077 | -96.1369 |  | 1.1 | 1.1 | 1.1 | 1.1553 | 1.0573 | 1.0213 | 5.5292e-11 | -120 | 120 | -1.0655 | -117.6683 | 117.655

## LLG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.2418 | 6.0392 | 5.524 | 0.24292 | 6.0379 | 5.5255 | 2.7921 | 69.7349 | 63.7858 | 2.805 | 69.7198 | 63.8027 | 2.8532 | -3.8047e-10 | -2.3366e-10 | -2.2238 | 46.1981 | 24.8863 | 2.8445 | -2.706e-12 | -2.5863e-10 | -2.3272 | 5.2305 | 34.4767 | -46.8684 | 53.5628 | -114.1759 | 132.8663 | -126.4458 | 65.8303 |  | 1.443 | 0 | 0 | 1.1475 | 0.66686 | 0.66643 | -1.9558 | 0 | 0 | -0.83191 | -119.9863 | 120.0074
Line_1 | 0.12174 | 3.0186 | 2.7631 | 0.12146 | 3.019 | 2.7627 | 1.4058 | 34.8561 | 31.9056 | 1.4025 | 34.8599 | 31.9014 | -0.95395 | 34.6355 | 18.6785 | 1.1119 | -23.099 | -12.4432 | -1.0325 | 3.9156 | 25.8666 | 1.1636 | -2.6152 | -17.2384 | 132.7344 | -126.45 | 65.8334 | -47.1337 | 53.5542 | -114.1697 |  | 1 | 1 | 1 | 1.1475 | 0.66686 | 0.66643 | 1.6397e-10 | -120 | 120 | -0.83191 | -119.9863 | 120.0074
Line_2 | 0.12174 | 3.0186 | 2.7631 | 0.12146 | 3.019 | 2.7627 | 1.4058 | 34.8561 | 31.9056 | 1.4025 | 34.8599 | 31.9014 | -0.95395 | 34.6355 | 18.6785 | 1.1119 | -23.099 | -12.4432 | -1.0325 | 3.9156 | 25.8666 | 1.1636 | -2.6152 | -17.2384 | 132.7344 | -126.45 | 65.8334 | -47.1337 | 53.5542 | -114.1697 |  | 1 | 1 | 1 | 1.1475 | 0.66686 | 0.66643 | 1.6397e-10 | -120 | 120 | -0.83191 | -119.9863 | 120.0074

## LLG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.2418 | 6.0392 | 5.524 | 0.24292 | 6.0379 | 5.5255 | 2.7921 | 69.7349 | 63.7858 | 2.805 | 69.7198 | 63.8027 | 2.8532 | -3.8047e-10 | -2.3366e-10 | -2.2238 | 46.1981 | 24.8863 | 2.8445 | -2.706e-12 | -2.5863e-10 | -2.3272 | 5.2305 | 34.4767 | -46.8684 | 53.5628 | -114.1759 | 132.8663 | -126.4458 | 65.8303 |  | 1.443 | 0 | 0 | 1.1475 | 0.66686 | 0.66643 | -1.9558 | 0 | 0 | -0.83191 | -119.9863 | 120.0074
Line_1 | 0.12174 | 3.0186 | 2.7631 | 0.12146 | 3.019 | 2.7627 | 1.4058 | 34.8561 | 31.9056 | 1.4025 | 34.8599 | 31.9014 | -0.95395 | 34.6355 | 18.6785 | 1.1119 | -23.099 | -12.4432 | -1.0325 | 3.9156 | 25.8666 | 1.1636 | -2.6152 | -17.2384 | 132.7344 | -126.45 | 65.8334 | -47.1337 | 53.5542 | -114.1697 |  | 1 | 1 | 1 | 1.1475 | 0.66686 | 0.66643 | 1.6397e-10 | -120 | 120 | -0.83191 | -119.9863 | 120.0074
Line_2 | 0.12174 | 3.0186 | 2.7631 | 0.12146 | 3.019 | 2.7627 | 1.4058 | 34.8561 | 31.9056 | 1.4025 | 34.8599 | 31.9014 | -0.95395 | 34.6355 | 18.6785 | 1.1119 | -23.099 | -12.4432 | -1.0325 | 3.9156 | 25.8666 | 1.1636 | -2.6152 | -17.2384 | 132.7344 | -126.45 | 65.8334 | -47.1337 | 53.5542 | -114.1697 |  | 1 | 1 | 1 | 1.1475 | 0.66686 | 0.66643 | 1.6397e-10 | -120 | 120 | -0.83191 | -119.9863 | 120.0074

## LLG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.12961 | 0.87833 | 0.87934 | 0.13022 | 0.8776 | 0.88015 | 1.4967 | 10.1421 | 10.1538 | 1.5036 | 10.1336 | 10.1631 | 0.97144 | -7.5583 | -6.9047 | -0.78787 | 8.977 | 8.2337 | 1.5547 | -4.2774 | -2.1535 | -1.4101 | 3.4058 | 3.9938 | -62.1099 | 42.9931 | -88.8826 | 117.6249 | -137.0345 | 91.1 |  | 1.2249 | 0.8563 | 0.71232 | 1.0743 | 0.94748 | 0.90044 | -4.1093 | -107.5005 | 108.4397 | -1.5677 | -116.2582 | 116.9758
Line_1 | 0.065259 | 0.43861 | 0.44028 | 0.065108 | 0.4388 | 0.44007 | 0.75354 | 5.0647 | 5.0839 | 0.7518 | 5.0668 | 5.0815 | -0.34787 | 4.8421 | 4.4504 | 0.39393 | -4.4885 | -4.1169 | -0.66844 | 1.4849 | 2.4576 | 0.70507 | -1.7029 | -1.9969 | 117.493 | -137.0483 | 91.0913 | -62.3751 | 42.9655 | -88.9 |  | 1 | 1 | 1 | 1.0743 | 0.94748 | 0.90044 | 5.9794e-11 | -120 | 120 | -1.5677 | -116.2582 | 116.9758
Line_2 | 0.065259 | 0.43861 | 0.44028 | 0.065108 | 0.4388 | 0.44007 | 0.75354 | 5.0647 | 5.0839 | 0.7518 | 5.0668 | 5.0815 | -0.34787 | 4.8421 | 4.4504 | 0.39393 | -4.4885 | -4.1169 | -0.66844 | 1.4849 | 2.4576 | 0.70507 | -1.7029 | -1.9969 | 117.493 | -137.0483 | 91.0913 | -62.3751 | 42.9655 | -88.9 |  | 1 | 1 | 1 | 1.0743 | 0.94748 | 0.90044 | 5.9794e-11 | -120 | 120 | -1.5677 | -116.2582 | 116.9758

## LLG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.12961 | 0.87833 | 0.87934 | 0.13022 | 0.8776 | 0.88015 | 1.4967 | 10.1421 | 10.1538 | 1.5036 | 10.1336 | 10.1631 | 0.97144 | -7.5583 | -6.9047 | -0.78787 | 8.977 | 8.2337 | 1.5547 | -4.2774 | -2.1535 | -1.4101 | 3.4058 | 3.9938 | -62.1099 | 42.9931 | -88.8826 | 117.6249 | -137.0345 | 91.1 |  | 1.2249 | 0.8563 | 0.71232 | 1.0743 | 0.94748 | 0.90044 | -4.1093 | -107.5005 | 108.4397 | -1.5677 | -116.2582 | 116.9758
Line_1 | 0.065259 | 0.43861 | 0.44028 | 0.065108 | 0.4388 | 0.44007 | 0.75354 | 5.0647 | 5.0839 | 0.7518 | 5.0668 | 5.0815 | -0.34787 | 4.8421 | 4.4504 | 0.39393 | -4.4885 | -4.1169 | -0.66844 | 1.4849 | 2.4576 | 0.70507 | -1.7029 | -1.9969 | 117.493 | -137.0483 | 91.0913 | -62.3751 | 42.9655 | -88.9 |  | 1 | 1 | 1 | 1.0743 | 0.94748 | 0.90044 | 5.9794e-11 | -120 | 120 | -1.5677 | -116.2582 | 116.9758
Line_2 | 0.065259 | 0.43861 | 0.44028 | 0.065108 | 0.4388 | 0.44007 | 0.75354 | 5.0647 | 5.0839 | 0.7518 | 5.0668 | 5.0815 | -0.34787 | 4.8421 | 4.4504 | 0.39393 | -4.4885 | -4.1169 | -0.66844 | 1.4849 | 2.4576 | 0.70507 | -1.7029 | -1.9969 | 117.493 | -137.0483 | 91.0913 | -62.3751 | 42.9655 | -88.9 |  | 1 | 1 | 1 | 1.0743 | 0.94748 | 0.90044 | 5.9794e-11 | -120 | 120 | -1.5677 | -116.2582 | 116.9758