## LLL_max_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 4.283 | 4.283 | 0 | 6.9696 | 148.3662 | 148.3662 | 28.6163 | -1e-07 | 32.4685 | -1e-07 | -77.7798 | 102.2202 | 0.29171 | 0 | -29.1714 | 0
Line_1 | 16.1507 | 16.1507 | 0 | 26.2818 | 559.4778 | 559.4778 | 406.92 | -1e-07 | 461.6977 | -1e-07 | -48.6085 | 131.3915 | 1.1 | 0 | -1.9268e-08 | 0
Line_2 | 16.1507 | 16.1507 | 0 | 26.2818 | 559.4778 | 559.4778 | 406.92 | -1e-07 | 461.6977 | -1e-07 | -48.6085 | 131.3915 | 1.1 | 0 | -1.9268e-08 | 0
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.1 | -1.9268e-08 | -1.9268e-08

## LLL_max_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 4.283 | 4.283 | 0 | 6.9696 | 148.3662 | 148.3662 | 28.6163 | -1e-07 | 32.4685 | -1e-07 | -77.7798 | 102.2202 | 0.29171 | 0 | -29.1714 | 0
Line_1 | 16.1507 | 16.1507 | 0 | 26.2818 | 559.4778 | 559.4778 | 406.92 | -1e-07 | 461.6977 | -1e-07 | -48.6085 | 131.3915 | 1.1 | 0 | -1.9268e-08 | 0
Line_2 | 16.1507 | 16.1507 | 0 | 26.2818 | 559.4778 | 559.4778 | 406.92 | -1e-07 | 461.6977 | -1e-07 | -48.6085 | 131.3915 | 1.1 | 0 | -1.9268e-08 | 0
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.1 | -1.9268e-08 | -1.9268e-08

## LLL_max_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.20307 | 0.20307 | 0 | 0.33045 | 7.0346 | 7.0346 | 2.4825 | -2.4181 | 7.0389 | -6.966 | -71.1838 | 108.8162 | 1.061 | 1.0482 | -0.61025 | -0.32747
Line_1 | 0.76577 | 0.76577 | 0 | 1.2461 | 26.527 | 26.527 | 21.6805 | -20.7657 | 19.5297 | -18.4918 | -42.0124 | 137.9876 | 1.1 | 1.0482 | -1.0266e-09 | -0.32747
Line_2 | 0.76577 | 0.76577 | 0 | 1.2461 | 26.527 | 26.527 | 21.6805 | -20.7657 | 19.5297 | -18.4918 | -42.0124 | 137.9876 | 1.1 | 1.0482 | -1.0266e-09 | -0.32747
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.1 | -1.0266e-09 | -1.0266e-09

## LLL_max_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.20307 | 0.20307 | 0 | 0.33045 | 7.0346 | 7.0346 | 2.4825 | -2.4181 | 7.0389 | -6.966 | -71.1838 | 108.8162 | 1.061 | 1.0482 | -0.61025 | -0.32747
Line_1 | 0.76577 | 0.76577 | 0 | 1.2461 | 26.527 | 26.527 | 21.6805 | -20.7657 | 19.5297 | -18.4918 | -42.0124 | 137.9876 | 1.1 | 1.0482 | -1.0266e-09 | -0.32747
Line_2 | 0.76577 | 0.76577 | 0 | 1.2461 | 26.527 | 26.527 | 21.6805 | -20.7657 | 19.5297 | -18.4918 | -42.0124 | 137.9876 | 1.1 | 1.0482 | -1.0266e-09 | -0.32747
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.1 | -1.0266e-09 | -1.0266e-09

## LLL_min_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 3.6016 | 3.6016 | 0 | 5.4211 | 124.7634 | 124.7634 | 38.8525 | -1e-07 | 22.9597 | -1e-07 | -69.6723 | 110.3277 | 0.36172 | 0 | -39.0915 | 0
Line_1 | 9.9569 | 9.9569 | 0 | 14.987 | 344.917 | 344.917 | 296.9434 | -1e-07 | 175.4774 | -1e-07 | -30.5808 | 149.4192 | 1 | 0 | -1.7014e-08 | 0
Line_2 | 9.9569 | 9.9569 | 0 | 14.987 | 344.917 | 344.917 | 296.9434 | -1e-07 | 175.4774 | -1e-07 | -30.5808 | 149.4192 | 1 | 0 | -1.7014e-08 | 0
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | -1.7014e-08 | -1.7014e-08

## LLL_min_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 3.6016 | 3.6016 | 0 | 5.4211 | 124.7634 | 124.7634 | 38.8525 | -1e-07 | 22.9597 | -1e-07 | -69.6723 | 110.3277 | 0.36172 | 0 | -39.0915 | 0
Line_1 | 9.9569 | 9.9569 | 0 | 14.987 | 344.917 | 344.917 | 296.9434 | -1e-07 | 175.4774 | -1e-07 | -30.5808 | 149.4192 | 1 | 0 | -1.7014e-08 | 0
Line_2 | 9.9569 | 9.9569 | 0 | 14.987 | 344.917 | 344.917 | 296.9434 | -1e-07 | 175.4774 | -1e-07 | -30.5808 | 149.4192 | 1 | 0 | -1.7014e-08 | 0
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | -1.7014e-08 | -1.7014e-08

## LLL_min_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.24067 | 0.24067 | 0 | 0.36225 | 8.337 | 8.337 | 1.7416 | -1.5681 | 7.7288 | -7.6263 | -77.801 | 102.199 | 0.9503 | 0.9339 | -0.49997 | 0.57968
Line_1 | 0.66534 | 0.66534 | 0 | 1.0015 | 23.0482 | 23.0482 | 17.9851 | -16.6592 | 14.4136 | -13.6301 | -38.7094 | 141.2906 | 1 | 0.9339 | -1.0305e-09 | 0.57968
Line_2 | 0.66534 | 0.66534 | 0 | 1.0015 | 23.0482 | 23.0482 | 17.9851 | -16.6592 | 14.4136 | -13.6301 | -38.7094 | 141.2906 | 1 | 0.9339 | -1.0305e-09 | 0.57968
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | -1.0305e-09 | -1.0305e-09

## LLL_min_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.24067 | 0.24067 | 0 | 0.36225 | 8.337 | 8.337 | 1.7416 | -1.5681 | 7.7288 | -7.6263 | -77.801 | 102.199 | 0.9503 | 0.9339 | -0.49997 | 0.57968
Line_1 | 0.66534 | 0.66534 | 0 | 1.0015 | 23.0482 | 23.0482 | 17.9851 | -16.6592 | 14.4136 | -13.6301 | -38.7094 | 141.2906 | 1 | 0.9339 | -1.0305e-09 | 0.57968
Line_2 | 0.66534 | 0.66534 | 0 | 1.0015 | 23.0482 | 23.0482 | 17.9851 | -16.6592 | 14.4136 | -13.6301 | -38.7094 | 141.2906 | 1 | 0.9339 | -1.0305e-09 | 0.57968
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | -1.0305e-09 | -1.0305e-09

## LL_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 3.7092 | 3.7092 | 0 | 3.7092 | 3.7092 | 0 | 42.8296 | 42.8296 | 0 | 42.8296 | 42.8296 | -1.8592e-10 | 30.1766 | -15.8685 | 1.8591e-10 | -23.0225 | 23.0225 | -6.672e-10 | 3.131 | 13.1032 | 6.672e-10 | 4.9861 | -4.9861 | 0 | -167.7798 | 12.2202 | 0 | 12.2202 | -167.7798 | 1.1 | 0.70836 | 0.48049 | 1.1 | 0.55 | 0.55 | 1.2639e-10 | -161.8563 | 152.6723 | 4.2142e-11 | -180 | -180
Line_1 | 0 | 13.9869 | 13.9869 | 0 | 13.9869 | 13.9869 | 0 | 161.5073 | 161.5073 | 0 | 161.5073 | 161.5073 | 9.2953e-11 | 168.3703 | 35.0897 | -9.2958e-11 | -66.6403 | 66.6403 | 3.3359e-10 | 56.6906 | 174.1583 | -3.3359e-10 | 58.7338 | -58.7338 | 0 | -138.6085 | 41.3915 | 0 | 41.3915 | -138.6085 | 1.1 | 1.1 | 1.1 | 1.1 | 0.55 | 0.55 | -1.2943e-20 | -120 | 120 | 4.2142e-11 | -180 | -180
Line_2 | 0 | 13.9869 | 13.9869 | 0 | 13.9869 | 13.9869 | 0 | 161.5073 | 161.5073 | 0 | 161.5073 | 161.5073 | 9.2953e-11 | 168.3703 | 35.0897 | -9.2958e-11 | -66.6403 | 66.6403 | 3.3359e-10 | 56.6906 | 174.1583 | -3.3359e-10 | 58.7338 | -58.7338 | 0 | -138.6085 | 41.3915 | 0 | 41.3915 | -138.6085 | 1.1 | 1.1 | 1.1 | 1.1 | 0.55 | 0.55 | -1.2938e-20 | -120 | 120 | 4.2142e-11 | -180 | -180
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4264e-24 | 1.8717e-23 | 1.1958e-23 | -4.8528e-24 | 4.7221e-24 | -3.5525e-24 | 2.4264e-23 | 1.3008e-23 | 1.8111e-23 | -1.9411e-23 | -2.0938e-23 | -1.3258e-23 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | -1.2943e-20 | -120 | 120 | -1.2938e-20 | -120 | 120

## LL_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 3.7092 | 3.7092 | 0 | 3.7092 | 3.7092 | 0 | 42.8296 | 42.8296 | 0 | 42.8296 | 42.8296 | -1.8592e-10 | 30.1766 | -15.8685 | 1.8591e-10 | -23.0225 | 23.0225 | -6.672e-10 | 3.131 | 13.1032 | 6.672e-10 | 4.9861 | -4.9861 | 0 | -167.7798 | 12.2202 | 0 | 12.2202 | -167.7798 | 1.1 | 0.70836 | 0.48049 | 1.1 | 0.55 | 0.55 | 1.2639e-10 | -161.8563 | 152.6723 | 4.2142e-11 | -180 | -180
Line_1 | 0 | 13.9869 | 13.9869 | 0 | 13.9869 | 13.9869 | 0 | 161.5073 | 161.5073 | 0 | 161.5073 | 161.5073 | 9.2953e-11 | 168.3703 | 35.0897 | -9.2958e-11 | -66.6403 | 66.6403 | 3.3359e-10 | 56.6906 | 174.1583 | -3.3359e-10 | 58.7338 | -58.7338 | 0 | -138.6085 | 41.3915 | 0 | 41.3915 | -138.6085 | 1.1 | 1.1 | 1.1 | 1.1 | 0.55 | 0.55 | -1.2943e-20 | -120 | 120 | 4.2142e-11 | -180 | -180
Line_2 | 0 | 13.9869 | 13.9869 | 0 | 13.9869 | 13.9869 | 0 | 161.5073 | 161.5073 | 0 | 161.5073 | 161.5073 | 9.2953e-11 | 168.3703 | 35.0897 | -9.2958e-11 | -66.6403 | 66.6403 | 3.3359e-10 | 56.6906 | 174.1583 | -3.3359e-10 | 58.7338 | -58.7338 | 0 | -138.6085 | 41.3915 | 0 | 41.3915 | -138.6085 | 1.1 | 1.1 | 1.1 | 1.1 | 0.55 | 0.55 | -1.2938e-20 | -120 | 120 | 4.2142e-11 | -180 | -180
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4264e-24 | 1.8717e-23 | 1.1958e-23 | -4.8528e-24 | 4.7221e-24 | -3.5525e-24 | 2.4264e-23 | 1.3008e-23 | 1.8111e-23 | -1.9411e-23 | -2.0938e-23 | -1.3258e-23 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | -1.2943e-20 | -120 | 120 | -1.2938e-20 | -120 | 120

## LL_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 0.3359 | 0.3359 | 0 | 0.3359 | 0.3359 | 0 | 3.8787 | 3.8787 | 0 | 3.8787 | 3.8787 | -1.5933e-11 | 3.1842 | -0.86144 | 1.5932e-11 | -3.1255 | 0.92012 | -5.7174e-11 | 2.5656 | 3.9207 | 5.7174e-11 | -2.4991 | -3.8541 | 0 | -161.4818 | 18.5182 | 0 | 18.5182 | -161.4818 | 1.1 | 1.0543 | 1.0349 | 1.1 | 1.0317 | 1.0216 | 1.0828e-11 | -122.6222 | 120.9101 | 3.6094e-12 | -122.8373 | 121.9453
Line_1 | 0 | 1.2667 | 1.2667 | 0 | 1.2667 | 1.2667 | 0 | 14.6263 | 14.6263 | 0 | 14.6263 | 14.6263 | 7.9671e-12 | 15.7189 | 4.8888 | -7.9671e-12 | -14.8846 | -4.0544 | 2.8587e-11 | 3.4303 | 15.3281 | -2.8587e-11 | -2.4837 | -14.3815 | 0 | -132.3104 | 47.6896 | 0 | 47.6896 | -132.3104 | 1.1 | 1.1 | 1.1 | 1.1 | 1.0317 | 1.0216 | -1.1104e-21 | -120 | 120 | 3.6094e-12 | -122.8373 | 121.9453
Line_2 | 0 | 1.2667 | 1.2667 | 0 | 1.2667 | 1.2667 | 0 | 14.6263 | 14.6263 | 0 | 14.6263 | 14.6263 | 7.9671e-12 | 15.7189 | 4.8888 | -7.9671e-12 | -14.8846 | -4.0544 | 2.8587e-11 | 3.4303 | 15.3281 | -2.8587e-11 | -2.4837 | -14.3815 | 0 | -132.3104 | 47.6896 | 0 | 47.6896 | -132.3104 | 1.1 | 1.1 | 1.1 | 1.1 | 1.0317 | 1.0216 | -1.1099e-21 | -120 | 120 | 3.6094e-12 | -122.8373 | 121.9453
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.3077e-25 | -2.1338e-24 | 4.6302e-25 | 7.5825e-26 | 2.0065e-24 | 5.1182e-25 | 3.3363e-24 | 2.3702e-24 | 1.6244e-24 | -2.7297e-24 | -1.3774e-24 | -8.8649e-25 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | -1.1104e-21 | -120 | 120 | -1.1099e-21 | -120 | 120

## LL_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 0.3359 | 0.3359 | 0 | 0.3359 | 0.3359 | 0 | 3.8787 | 3.8787 | 0 | 3.8787 | 3.8787 | -1.5933e-11 | 3.1842 | -0.86144 | 1.5932e-11 | -3.1255 | 0.92012 | -5.7174e-11 | 2.5656 | 3.9207 | 5.7174e-11 | -2.4991 | -3.8541 | 0 | -161.4818 | 18.5182 | 0 | 18.5182 | -161.4818 | 1.1 | 1.0543 | 1.0349 | 1.1 | 1.0317 | 1.0216 | 1.0828e-11 | -122.6222 | 120.9101 | 3.6094e-12 | -122.8373 | 121.9453
Line_1 | 0 | 1.2667 | 1.2667 | 0 | 1.2667 | 1.2667 | 0 | 14.6263 | 14.6263 | 0 | 14.6263 | 14.6263 | 7.9671e-12 | 15.7189 | 4.8888 | -7.9671e-12 | -14.8846 | -4.0544 | 2.8587e-11 | 3.4303 | 15.3281 | -2.8587e-11 | -2.4837 | -14.3815 | 0 | -132.3104 | 47.6896 | 0 | 47.6896 | -132.3104 | 1.1 | 1.1 | 1.1 | 1.1 | 1.0317 | 1.0216 | -1.1104e-21 | -120 | 120 | 3.6094e-12 | -122.8373 | 121.9453
Line_2 | 0 | 1.2667 | 1.2667 | 0 | 1.2667 | 1.2667 | 0 | 14.6263 | 14.6263 | 0 | 14.6263 | 14.6263 | 7.9671e-12 | 15.7189 | 4.8888 | -7.9671e-12 | -14.8846 | -4.0544 | 2.8587e-11 | 3.4303 | 15.3281 | -2.8587e-11 | -2.4837 | -14.3815 | 0 | -132.3104 | 47.6896 | 0 | 47.6896 | -132.3104 | 1.1 | 1.1 | 1.1 | 1.1 | 1.0317 | 1.0216 | -1.1099e-21 | -120 | 120 | 3.6094e-12 | -122.8373 | 121.9453
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.3077e-25 | -2.1338e-24 | 4.6302e-25 | 7.5825e-26 | 2.0065e-24 | 5.1182e-25 | 3.3363e-24 | 2.3702e-24 | 1.6244e-24 | -2.7297e-24 | -1.3774e-24 | -8.8649e-25 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | -1.1104e-21 | -120 | 120 | -1.1099e-21 | -120 | 120

## LL_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 3.1191 | 3.1191 | 0 | 3.1191 | 3.1191 | 0 | 36.0161 | 36.0161 | 0 | 36.0161 | 36.0161 | 1.4526e-11 | 26.5997 | -7.1734 | -1.4528e-11 | -16.8865 | 16.8865 | 3.0406e-11 | -0.51586 | 11.9957 | -3.0411e-11 | 6.2558 | -6.2558 | 0 | -159.6723 | 20.3277 | 0 | 20.3277 | -159.6723 | 1 | 0.73869 | 0.38808 | 1 | 0.5 | 0.5 | -1.4076e-11 | -160.7833 | 141.207 | -4.7022e-12 | -180 | 180
Line_1 | 0 | 8.6229 | 8.6229 | 0 | 8.6229 | 8.6229 | 0 | 99.569 | 99.569 | 0 | 99.569 | 99.569 | -7.2807e-12 | 99.5638 | 48.9079 | 7.2807e-12 | -25.328 | 25.328 | -1.521e-11 | 1.0093 | 86.7294 | 1.5206e-11 | 42.8601 | -42.8601 | 0 | -120.5808 | 59.4192 | 0 | 59.4192 | -120.5808 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 1.3742e-21 | -120 | 120 | -4.7022e-12 | -180 | 180
Line_2 | 0 | 8.6229 | 8.6229 | 0 | 8.6229 | 8.6229 | 0 | 99.569 | 99.569 | 0 | 99.569 | 99.569 | -7.2807e-12 | 99.5638 | 48.9079 | 7.2807e-12 | -25.328 | 25.328 | -1.521e-11 | 1.0093 | 86.7294 | 1.5206e-11 | 42.8601 | -42.8601 | 0 | -120.5808 | 59.4192 | 0 | 59.4192 | -120.5808 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 1.3728e-21 | -120 | 120 | -4.7022e-12 | -180 | 180
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2058e-24 | 1.4475e-23 | 1.5282e-23 | -2.2058e-24 | -1.2693e-23 | -1.6385e-23 | 2.2058e-24 | -5.8101e-24 | 8.8233e-24 | -2.2058e-24 | 6.6913e-24 | -6.913e-24 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1.3742e-21 | -120 | 120 | 1.3728e-21 | -120 | 120

## LL_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 3.1191 | 3.1191 | 0 | 3.1191 | 3.1191 | 0 | 36.0161 | 36.0161 | 0 | 36.0161 | 36.0161 | 1.4526e-11 | 26.5997 | -7.1734 | -1.4528e-11 | -16.8865 | 16.8865 | 3.0406e-11 | -0.51586 | 11.9957 | -3.0411e-11 | 6.2558 | -6.2558 | 0 | -159.6723 | 20.3277 | 0 | 20.3277 | -159.6723 | 1 | 0.73869 | 0.38808 | 1 | 0.5 | 0.5 | -1.4076e-11 | -160.7833 | 141.207 | -4.7022e-12 | -180 | 180
Line_1 | 0 | 8.6229 | 8.6229 | 0 | 8.6229 | 8.6229 | 0 | 99.569 | 99.569 | 0 | 99.569 | 99.569 | -7.2807e-12 | 99.5638 | 48.9079 | 7.2807e-12 | -25.328 | 25.328 | -1.521e-11 | 1.0093 | 86.7294 | 1.5206e-11 | 42.8601 | -42.8601 | 0 | -120.5808 | 59.4192 | 0 | 59.4192 | -120.5808 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 1.3742e-21 | -120 | 120 | -4.7022e-12 | -180 | 180
Line_2 | 0 | 8.6229 | 8.6229 | 0 | 8.6229 | 8.6229 | 0 | 99.569 | 99.569 | 0 | 99.569 | 99.569 | -7.2807e-12 | 99.5638 | 48.9079 | 7.2807e-12 | -25.328 | 25.328 | -1.521e-11 | 1.0093 | 86.7294 | 1.5206e-11 | 42.8601 | -42.8601 | 0 | -120.5808 | 59.4192 | 0 | 59.4192 | -120.5808 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 1.3728e-21 | -120 | 120 | -4.7022e-12 | -180 | 180
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2058e-24 | 1.4475e-23 | 1.5282e-23 | -2.2058e-24 | -1.2693e-23 | -1.6385e-23 | 2.2058e-24 | -5.8101e-24 | 8.8233e-24 | -2.2058e-24 | 6.6913e-24 | -6.913e-24 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1.3742e-21 | -120 | 120 | 1.3728e-21 | -120 | 120

## LL_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 0.39097 | 0.39097 | 0 | 0.39097 | 0.39097 | 0 | 4.5145 | 4.5145 | 0 | 4.5145 | 4.5145 | -3.5261e-12 | 3.0443 | -1.3596 | 3.5261e-12 | -2.8917 | 1.5122 | -7.1338e-12 | 2.9481 | 3.9411 | 7.1338e-12 | -2.8579 | -3.8509 | 0 | -167.2932 | 12.7068 | 0 | 12.7068 | -167.2932 | 1 | 0.93871 | 0.92347 | 1 | 0.90057 | 0.91642 | 3.246e-12 | -123.2136 | 121.7406 | 1.0819e-12 | -122.6304 | 124.1466
Line_1 | 0 | 1.0809 | 1.0809 | 0 | 1.0809 | 1.0809 | 0 | 12.4807 | 12.4807 | 0 | 12.4807 | 12.4807 | 1.7624e-12 | 12.3531 | 4.6346 | -1.7624e-12 | -11.1867 | -3.4682 | 3.5649e-12 | 1.7805 | 11.5883 | -3.5646e-12 | -1.0912 | -10.899 | 0 | -128.2017 | 51.7983 | 0 | 51.7983 | -128.2017 | 1 | 1 | 1 | 1 | 0.90057 | 0.91642 | -2.8418e-22 | -120 | 120 | 1.0819e-12 | -122.6304 | 124.1466
Line_2 | 0 | 1.0809 | 1.0809 | 0 | 1.0809 | 1.0809 | 0 | 12.4807 | 12.4807 | 0 | 12.4807 | 12.4807 | 1.7624e-12 | 12.3531 | 4.6346 | -1.7624e-12 | -11.1867 | -3.4682 | 3.5649e-12 | 1.7805 | 11.5883 | -3.5646e-12 | -1.0912 | -10.899 | 0 | -128.2017 | 51.7983 | 0 | 51.7983 | -128.2017 | 1 | 1 | 1 | 1 | 0.90057 | 0.91642 | -2.8447e-22 | -120 | 120 | 1.0819e-12 | -122.6304 | 124.1466
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8252e-25 | 2.9667e-25 | -2.068e-25 | -5.5145e-25 | -2.0927e-25 | 2.7573e-25 | -4.1359e-25 | 1.341e-24 | 3.5818e-25 | 1.3786e-25 | -9.1392e-25 | -4.7757e-25 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | -2.8418e-22 | -120 | 120 | -2.8447e-22 | -120 | 120

## LL_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 0.39097 | 0.39097 | 0 | 0.39097 | 0.39097 | 0 | 4.5145 | 4.5145 | 0 | 4.5145 | 4.5145 | -3.5261e-12 | 3.0443 | -1.3596 | 3.5261e-12 | -2.8917 | 1.5122 | -7.1338e-12 | 2.9481 | 3.9411 | 7.1338e-12 | -2.8579 | -3.8509 | 0 | -167.2932 | 12.7068 | 0 | 12.7068 | -167.2932 | 1 | 0.93871 | 0.92347 | 1 | 0.90057 | 0.91642 | 3.246e-12 | -123.2136 | 121.7406 | 1.0819e-12 | -122.6304 | 124.1466
Line_1 | 0 | 1.0809 | 1.0809 | 0 | 1.0809 | 1.0809 | 0 | 12.4807 | 12.4807 | 0 | 12.4807 | 12.4807 | 1.7624e-12 | 12.3531 | 4.6346 | -1.7624e-12 | -11.1867 | -3.4682 | 3.5649e-12 | 1.7805 | 11.5883 | -3.5646e-12 | -1.0912 | -10.899 | 0 | -128.2017 | 51.7983 | 0 | 51.7983 | -128.2017 | 1 | 1 | 1 | 1 | 0.90057 | 0.91642 | -2.8418e-22 | -120 | 120 | 1.0819e-12 | -122.6304 | 124.1466
Line_2 | 0 | 1.0809 | 1.0809 | 0 | 1.0809 | 1.0809 | 0 | 12.4807 | 12.4807 | 0 | 12.4807 | 12.4807 | 1.7624e-12 | 12.3531 | 4.6346 | -1.7624e-12 | -11.1867 | -3.4682 | 3.5649e-12 | 1.7805 | 11.5883 | -3.5646e-12 | -1.0912 | -10.899 | 0 | -128.2017 | 51.7983 | 0 | 51.7983 | -128.2017 | 1 | 1 | 1 | 1 | 0.90057 | 0.91642 | -2.8447e-22 | -120 | 120 | 1.0819e-12 | -122.6304 | 124.1466
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8252e-25 | 2.9667e-25 | -2.068e-25 | -5.5145e-25 | -2.0927e-25 | 2.7573e-25 | -4.1359e-25 | 1.341e-24 | 3.5818e-25 | 1.3786e-25 | -9.1392e-25 | -4.7757e-25 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | -2.8418e-22 | -120 | 120 | -2.8447e-22 | -120 | 120

## LG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.1498 | 0.57489 | 0.57489 | 1.1467 | 0.57794 | 0.57794 | 13.2764 | 6.6382 | 6.6382 | 13.2413 | 6.6734 | 6.6734 | 0.6786 | 0.60148 | 10.9931 | 4.3235e-11 | -0.38014 | -10.8619 | 0.78334 | 9.9236 | 2.7143 | 5.3415e-11 | -9.7839 | -2.587 | -55.2487 | 124.7513 | 124.7513 | 124.891 | -55.5259 | -55.5259 |  | 0.078063 | 1.4977 | 1.7058 | 0 | 1.4672 | 1.6731 | -6.1508 | -148.7173 | 138.6209 | 0 | -147.7509 | 137.8707
Line_1 | 6.7574 | 0.2905 | 0.2905 | 6.7567 | 0.28897 | 0.28897 | 78.0275 | 3.3544 | 3.3544 | 78.0195 | 3.3367 | 3.3367 | 76.2711 | 1.6059 | -3.68 | 3.722e-10 | 0.19007 | 5.4309 | 39.3642 | -3.3221 | 0.27024 | 1.5942e-10 | 4.8919 | 1.2935 | -27.2987 | -55.8 | -55.8 | 152.7178 | 124.4741 | 124.4741 |  | 1.1 | 1.1 | 1.1 | 0 | 1.4672 | 1.6731 | -1.0835e-08 | -120 | 120 | 0 | -147.7509 | 137.8707
Line_2 | 6.7574 | 0.2905 | 0.2905 | 6.7567 | 0.28897 | 0.28897 | 78.0275 | 3.3544 | 3.3544 | 78.0195 | 3.3367 | 3.3367 | 76.2711 | 1.6059 | -3.68 | 3.722e-10 | 0.19007 | 5.4309 | 39.3642 | -3.3221 | 0.27024 | 1.5942e-10 | 4.8919 | 1.2935 | -27.2987 | -55.8 | -55.8 | 152.7178 | 124.4741 | 124.4741 |  | 1.1 | 1.1 | 1.1 | 0 | 1.4672 | 1.6731 | -1.0835e-08 | -120 | 120 | 0 | -147.7509 | 137.8707
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2982e-12 | -2.3812e-14 | -2.2744e-12 | 2.2982e-12 | -2.3812e-14 | -2.2744e-12 | 1.2994e-12 | -2.64e-12 | 1.3406e-12 | 1.2994e-12 | -2.64e-12 | 1.3406e-12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | -1.0835e-08 | -120 | 120 | -1.0835e-08 | -120 | 120

## LG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.1498 | 0.57489 | 0.57489 | 1.1467 | 0.57794 | 0.57794 | 13.2764 | 6.6382 | 6.6382 | 13.2413 | 6.6734 | 6.6734 | 0.6786 | 0.60148 | 10.9931 | 4.3235e-11 | -0.38014 | -10.8619 | 0.78334 | 9.9236 | 2.7143 | 5.3415e-11 | -9.7839 | -2.587 | -55.2487 | 124.7513 | 124.7513 | 124.891 | -55.5259 | -55.5259 |  | 0.078063 | 1.4977 | 1.7058 | 0 | 1.4672 | 1.6731 | -6.1508 | -148.7173 | 138.6209 | 0 | -147.7509 | 137.8707
Line_1 | 6.7574 | 0.2905 | 0.2905 | 6.7567 | 0.28897 | 0.28897 | 78.0275 | 3.3544 | 3.3544 | 78.0195 | 3.3367 | 3.3367 | 76.2711 | 1.6059 | -3.68 | 3.722e-10 | 0.19007 | 5.4309 | 39.3642 | -3.3221 | 0.27024 | 1.5942e-10 | 4.8919 | 1.2935 | -27.2987 | -55.8 | -55.8 | 152.7178 | 124.4741 | 124.4741 |  | 1.1 | 1.1 | 1.1 | 0 | 1.4672 | 1.6731 | -1.0835e-08 | -120 | 120 | 0 | -147.7509 | 137.8707
Line_2 | 6.7574 | 0.2905 | 0.2905 | 6.7567 | 0.28897 | 0.28897 | 78.0275 | 3.3544 | 3.3544 | 78.0195 | 3.3367 | 3.3367 | 76.2711 | 1.6059 | -3.68 | 3.722e-10 | 0.19007 | 5.4309 | 39.3642 | -3.3221 | 0.27024 | 1.5942e-10 | 4.8919 | 1.2935 | -27.2987 | -55.8 | -55.8 | 152.7178 | 124.4741 | 124.4741 |  | 1.1 | 1.1 | 1.1 | 0 | 1.4672 | 1.6731 | -1.0835e-08 | -120 | 120 | 0 | -147.7509 | 137.8707
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2982e-12 | -2.3812e-14 | -2.2744e-12 | 2.2982e-12 | -2.3812e-14 | -2.2744e-12 | 1.2994e-12 | -2.64e-12 | 1.3406e-12 | 1.2994e-12 | -2.64e-12 | 1.3406e-12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | -1.0835e-08 | -120 | 120 | -1.0835e-08 | -120 | 120

## LG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.12691 | 0.063453 | 0.063453 | 0.12657 | 0.063789 | 0.063789 | 1.4654 | 0.73269 | 0.73269 | 1.4615 | 0.73658 | 0.73658 | 0.48045 | -0.46362 | 0.84096 | -0.47424 | 0.47146 | -0.84245 | 1.3698 | 0.66541 | 0.16866 | -1.3555 | -0.6643 | -0.17127 | -69.1546 | 110.8454 | 110.8454 | 110.9851 | -69.4318 | -69.4318 |  | 0.99059 | 1.1069 | 1.1706 | 0.98258 | 1.1059 | 1.1671 | 1.517 | -124.288 | 122.1861 | 1.7017 | -124.0682 | 122.0597
Line_1 | 0.74584 | 0.032064 | 0.032064 | 0.74576 | 0.031895 | 0.031895 | 8.6122 | 0.37024 | 0.37024 | 8.6113 | 0.36829 | 0.36829 | 7.1274 | 0.26018 | -0.40144 | -6.1993 | -0.23573 | 0.42122 | 6.2406 | -0.31332 | -0.068661 | -5.7587 | 0.33215 | 0.085634 | -41.2046 | -69.7059 | -69.7059 | 138.8119 | 110.5682 | 110.5682 |  | 1.1 | 1.1 | 1.1 | 0.98258 | 1.1059 | 1.1671 | -1.0125e-09 | -120 | 120 | 1.7017 | -124.0682 | 122.0597
Line_2 | 0.74584 | 0.032064 | 0.032064 | 0.74576 | 0.031895 | 0.031895 | 8.6122 | 0.37024 | 0.37024 | 8.6113 | 0.36829 | 0.36829 | 7.1274 | 0.26018 | -0.40144 | -6.1993 | -0.23573 | 0.42122 | 6.2406 | -0.31332 | -0.068661 | -5.7587 | 0.33215 | 0.085634 | -41.2046 | -69.7059 | -69.7059 | 138.8119 | 110.5682 | 110.5682 |  | 1.1 | 1.1 | 1.1 | 0.98258 | 1.1059 | 1.1671 | -1.0125e-09 | -120 | 120 | 1.7017 | -124.0682 | 122.0597
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1176e-13 | 6.7478e-14 | -2.7924e-13 | 2.1176e-13 | 6.7478e-14 | -2.7924e-13 | 2.0018e-13 | -2.8348e-13 | 8.3303e-14 | 2.0018e-13 | -2.8348e-13 | 8.3303e-14 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | -1.0125e-09 | -120 | 120 | -1.0125e-09 | -120 | 120

## LG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.12691 | 0.063453 | 0.063453 | 0.12657 | 0.063789 | 0.063789 | 1.4654 | 0.73269 | 0.73269 | 1.4615 | 0.73658 | 0.73658 | 0.48045 | -0.46362 | 0.84096 | -0.47424 | 0.47146 | -0.84245 | 1.3698 | 0.66541 | 0.16866 | -1.3555 | -0.6643 | -0.17127 | -69.1546 | 110.8454 | 110.8454 | 110.9851 | -69.4318 | -69.4318 |  | 0.99059 | 1.1069 | 1.1706 | 0.98258 | 1.1059 | 1.1671 | 1.517 | -124.288 | 122.1861 | 1.7017 | -124.0682 | 122.0597
Line_1 | 0.74584 | 0.032064 | 0.032064 | 0.74576 | 0.031895 | 0.031895 | 8.6122 | 0.37024 | 0.37024 | 8.6113 | 0.36829 | 0.36829 | 7.1274 | 0.26018 | -0.40144 | -6.1993 | -0.23573 | 0.42122 | 6.2406 | -0.31332 | -0.068661 | -5.7587 | 0.33215 | 0.085634 | -41.2046 | -69.7059 | -69.7059 | 138.8119 | 110.5682 | 110.5682 |  | 1.1 | 1.1 | 1.1 | 0.98258 | 1.1059 | 1.1671 | -1.0125e-09 | -120 | 120 | 1.7017 | -124.0682 | 122.0597
Line_2 | 0.74584 | 0.032064 | 0.032064 | 0.74576 | 0.031895 | 0.031895 | 8.6122 | 0.37024 | 0.37024 | 8.6113 | 0.36829 | 0.36829 | 7.1274 | 0.26018 | -0.40144 | -6.1993 | -0.23573 | 0.42122 | 6.2406 | -0.31332 | -0.068661 | -5.7587 | 0.33215 | 0.085634 | -41.2046 | -69.7059 | -69.7059 | 138.8119 | 110.5682 | 110.5682 |  | 1.1 | 1.1 | 1.1 | 0.98258 | 1.1059 | 1.1671 | -1.0125e-09 | -120 | 120 | 1.7017 | -124.0682 | 122.0597
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1176e-13 | 6.7478e-14 | -2.7924e-13 | 2.1176e-13 | 6.7478e-14 | -2.7924e-13 | 2.0018e-13 | -2.8348e-13 | 8.3303e-14 | 2.0018e-13 | -2.8348e-13 | 8.3303e-14 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | -1.0125e-09 | -120 | 120 | -1.0125e-09 | -120 | 120

## LG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.79863 | 0.39931 | 0.39931 | 0.79586 | 0.4021 | 0.4021 | 9.2218 | 4.6109 | 4.6109 | 9.1898 | 4.643 | 4.643 | 0.6273 | 0.98485 | 7.1243 | 8.5367e-12 | -0.78171 | -6.9994 | 0.38258 | 6.5235 | 1.4159 | 1.0455e-11 | -6.483 | -1.3827 | -50.2413 | 129.7587 | 129.7587 | 129.9594 | -50.6384 | -50.6384 |  | 0.079676 | 1.4308 | 1.5753 | 0 | 1.4064 | 1.5366 | -18.8627 | -148.8263 | 140.9991 | 0 | -147.5138 | 140.5362
Line_1 | 3.4696 | 0.20245 | 0.20245 | 3.4693 | 0.20105 | 0.20105 | 40.0633 | 2.3377 | 2.3377 | 40.0601 | 2.3215 | 2.3215 | 38.9897 | 0.83889 | -2.3091 | 5.7092e-11 | 0.39086 | 3.4997 | 9.2124 | -2.182 | 0.3645 | 1.4222e-11 | 3.2415 | 0.69135 | -13.2938 | -51.0297 | -51.0297 | 166.7383 | 129.3616 | 129.3616 |  | 1 | 1 | 1 | 0 | 1.4064 | 1.5366 | -6.7018e-09 | -120 | 120 | 0 | -147.5138 | 140.5362
Line_2 | 3.4696 | 0.20245 | 0.20245 | 3.4693 | 0.20105 | 0.20105 | 40.0633 | 2.3377 | 2.3377 | 40.0601 | 2.3215 | 2.3215 | 38.9897 | 0.83889 | -2.3091 | 5.7092e-11 | 0.39086 | 3.4997 | 9.2124 | -2.182 | 0.3645 | 1.4222e-11 | 3.2415 | 0.69135 | -13.2938 | -51.0297 | -51.0297 | 166.7383 | 129.3616 | 129.3616 |  | 1 | 1 | 1 | 0 | 1.4064 | 1.5366 | -6.7018e-09 | -120 | 120 | 0 | -147.5138 | 140.5362
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1983e-12 | -2.8118e-13 | -9.171e-13 | 1.1983e-12 | -2.8118e-13 | -9.171e-13 | 3.6715e-13 | -1.2213e-12 | 8.5417e-13 | 3.6715e-13 | -1.2213e-12 | 8.5417e-13 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 1 | 1 | 1 | -6.7018e-09 | -120 | 120 | -6.7018e-09 | -120 | 120

## LG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.79863 | 0.39931 | 0.39931 | 0.79586 | 0.4021 | 0.4021 | 9.2218 | 4.6109 | 4.6109 | 9.1898 | 4.643 | 4.643 | 0.6273 | 0.98485 | 7.1243 | 8.5367e-12 | -0.78171 | -6.9994 | 0.38258 | 6.5235 | 1.4159 | 1.0455e-11 | -6.483 | -1.3827 | -50.2413 | 129.7587 | 129.7587 | 129.9594 | -50.6384 | -50.6384 |  | 0.079676 | 1.4308 | 1.5753 | 0 | 1.4064 | 1.5366 | -18.8627 | -148.8263 | 140.9991 | 0 | -147.5138 | 140.5362
Line_1 | 3.4696 | 0.20245 | 0.20245 | 3.4693 | 0.20105 | 0.20105 | 40.0633 | 2.3377 | 2.3377 | 40.0601 | 2.3215 | 2.3215 | 38.9897 | 0.83889 | -2.3091 | 5.7092e-11 | 0.39086 | 3.4997 | 9.2124 | -2.182 | 0.3645 | 1.4222e-11 | 3.2415 | 0.69135 | -13.2938 | -51.0297 | -51.0297 | 166.7383 | 129.3616 | 129.3616 |  | 1 | 1 | 1 | 0 | 1.4064 | 1.5366 | -6.7018e-09 | -120 | 120 | 0 | -147.5138 | 140.5362
Line_2 | 3.4696 | 0.20245 | 0.20245 | 3.4693 | 0.20105 | 0.20105 | 40.0633 | 2.3377 | 2.3377 | 40.0601 | 2.3215 | 2.3215 | 38.9897 | 0.83889 | -2.3091 | 5.7092e-11 | 0.39086 | 3.4997 | 9.2124 | -2.182 | 0.3645 | 1.4222e-11 | 3.2415 | 0.69135 | -13.2938 | -51.0297 | -51.0297 | 166.7383 | 129.3616 | 129.3616 |  | 1 | 1 | 1 | 0 | 1.4064 | 1.5366 | -6.7018e-09 | -120 | 120 | 0 | -147.5138 | 140.5362
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1983e-12 | -2.8118e-13 | -9.171e-13 | 1.1983e-12 | -2.8118e-13 | -9.171e-13 | 3.6715e-13 | -1.2213e-12 | 8.5417e-13 | 3.6715e-13 | -1.2213e-12 | 8.5417e-13 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 1 | 1 | 1 | -6.7018e-09 | -120 | 120 | -6.7018e-09 | -120 | 120

## LG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.14389 | 0.071943 | 0.071943 | 0.14339 | 0.072445 | 0.072445 | 1.6615 | 0.83073 | 0.83073 | 1.6557 | 0.83652 | 0.83652 | 0.30062 | -0.48815 | 0.8915 | -0.28404 | 0.50158 | -0.89051 | 1.3754 | 0.67385 | 0.26535 | -1.3573 | -0.67212 | -0.2704 | -73.5064 | 106.4936 | 106.4936 | 106.6943 | -73.9035 | -73.9035 |  | 0.84737 | 1.0016 | 1.1197 | 0.83751 | 1.0025 | 1.1125 | 4.1644 | -127.5861 | 123.0688 | 4.8743 | -127.1704 | 122.9875
Line_1 | 0.6251 | 0.036475 | 0.036475 | 0.62505 | 0.036222 | 0.036222 | 7.2181 | 0.42118 | 0.42118 | 7.2175 | 0.41826 | 0.41826 | 5.7979 | 0.29413 | -0.40814 | -4.5342 | -0.25079 | 0.44525 | 4.2994 | -0.30146 | -0.10399 | -3.9975 | 0.33606 | 0.1352 | -36.5589 | -74.2948 | -74.2948 | 143.4732 | 106.0965 | 106.0965 |  | 1 | 1 | 1 | 0.83751 | 1.0025 | 1.1125 | -9.9658e-10 | -120 | 120 | 4.8743 | -127.1704 | 122.9875
Line_2 | 0.6251 | 0.036475 | 0.036475 | 0.62505 | 0.036222 | 0.036222 | 7.2181 | 0.42118 | 0.42118 | 7.2175 | 0.41826 | 0.41826 | 5.7979 | 0.29413 | -0.40814 | -4.5342 | -0.25079 | 0.44525 | 4.2994 | -0.30146 | -0.10399 | -3.9975 | 0.33606 | 0.1352 | -36.5589 | -74.2948 | -74.2948 | 143.4732 | 106.0965 | 106.0965 |  | 1 | 1 | 1 | 0.83751 | 1.0025 | 1.1125 | -9.9658e-10 | -120 | 120 | 4.8743 | -127.1704 | 122.9875
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7221e-13 | 4.0373e-14 | -2.1258e-13 | 1.7221e-13 | 4.0373e-14 | -2.1258e-13 | 1.4604e-13 | -2.2216e-13 | 7.6115e-14 | 1.4604e-13 | -2.2216e-13 | 7.6115e-14 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 1 | 1 | 1 | -9.9658e-10 | -120 | 120 | -9.9658e-10 | -120 | 120

## LG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.14389 | 0.071943 | 0.071943 | 0.14339 | 0.072445 | 0.072445 | 1.6615 | 0.83073 | 0.83073 | 1.6557 | 0.83652 | 0.83652 | 0.30062 | -0.48815 | 0.8915 | -0.28404 | 0.50158 | -0.89051 | 1.3754 | 0.67385 | 0.26535 | -1.3573 | -0.67212 | -0.2704 | -73.5064 | 106.4936 | 106.4936 | 106.6943 | -73.9035 | -73.9035 |  | 0.84737 | 1.0016 | 1.1197 | 0.83751 | 1.0025 | 1.1125 | 4.1644 | -127.5861 | 123.0688 | 4.8743 | -127.1704 | 122.9875
Line_1 | 0.6251 | 0.036475 | 0.036475 | 0.62505 | 0.036222 | 0.036222 | 7.2181 | 0.42118 | 0.42118 | 7.2175 | 0.41826 | 0.41826 | 5.7979 | 0.29413 | -0.40814 | -4.5342 | -0.25079 | 0.44525 | 4.2994 | -0.30146 | -0.10399 | -3.9975 | 0.33606 | 0.1352 | -36.5589 | -74.2948 | -74.2948 | 143.4732 | 106.0965 | 106.0965 |  | 1 | 1 | 1 | 0.83751 | 1.0025 | 1.1125 | -9.9658e-10 | -120 | 120 | 4.8743 | -127.1704 | 122.9875
Line_2 | 0.6251 | 0.036475 | 0.036475 | 0.62505 | 0.036222 | 0.036222 | 7.2181 | 0.42118 | 0.42118 | 7.2175 | 0.41826 | 0.41826 | 5.7979 | 0.29413 | -0.40814 | -4.5342 | -0.25079 | 0.44525 | 4.2994 | -0.30146 | -0.10399 | -3.9975 | 0.33606 | 0.1352 | -36.5589 | -74.2948 | -74.2948 | 143.4732 | 106.0965 | 106.0965 |  | 1 | 1 | 1 | 0.83751 | 1.0025 | 1.1125 | -9.9658e-10 | -120 | 120 | 4.8743 | -127.1704 | 122.9875
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7221e-13 | 4.0373e-14 | -2.1258e-13 | 1.7221e-13 | 4.0373e-14 | -2.1258e-13 | 1.4604e-13 | -2.2216e-13 | 7.6115e-14 | 1.4604e-13 | -2.2216e-13 | 7.6115e-14 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 1 | 1 | 1 | -9.9658e-10 | -120 | 120 | -9.9658e-10 | -120 | 120

## LLG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.35154 | 3.7947 | 3.6301 | 0.3534 | 3.7952 | 3.6294 | 4.0592 | 43.8174 | 41.9169 | 4.0807 | 43.8237 | 41.9083 | 4.2695 | 7.4848 | 6.8539 | -4.2036 | -9.7034e-11 | -2.5231e-10 | 4.6533 | 8.5147 | 7.7566 | -4.6257 | 2.5274e-10 | 6.0792e-11 | -49.8346 | -170.125 | 14.6717 | 129.8882 | 9.9123 | -165.3665 |  | 1.5558 | 0.25873 | 0.24694 | 1.5317 | 0 | 0 | -2.372 | -121.4418 | 63.2075 | -2.3747 | 0 | 0
Line_1 | 0.17764 | 15.0382 | 13.2031 | 0.1767 | 15.0389 | 13.2021 | 2.0512 | 173.6457 | 152.4558 | 2.0404 | 173.6544 | 152.4442 | -1.4387 | 171.6819 | 56.8485 | 2.1018 | 5.7826e-11 | -6.2277e-10 | -1.7382 | 83.7274 | 157.772 | 2.3128 | 1.0712e-09 | 7.0951e-10 | 129.6141 | -145.998 | 49.8151 | -50.1118 | 34.0059 | -130.1882 |  | 1.1 | 1.1 | 1.1 | 1.5317 | 0 | 0 | 2.0437e-10 | -120 | 120 | -2.3747 | 0 | 0
Line_2 | 0.17764 | 15.0382 | 13.2031 | 0.1767 | 15.0389 | 13.2021 | 2.0512 | 173.6457 | 152.4558 | 2.0404 | 173.6544 | 152.4442 | -1.4387 | 171.6819 | 56.8485 | 2.1018 | 5.7826e-11 | -6.2277e-10 | -1.7382 | 83.7274 | 157.772 | 2.3128 | 1.0712e-09 | 7.0951e-10 | 129.6141 | -145.998 | 49.8151 | -50.1118 | 34.0059 | -130.1882 |  | 1.1 | 1.1 | 1.1 | 1.5317 | 0 | 0 | 2.0437e-10 | -120 | 120 | -2.3747 | 0 | 0
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.474e-12 | 1.6681e-13 | 1.3072e-12 | -1.474e-12 | 1.6681e-13 | 1.3072e-12 | -6.5841e-13 | 1.6058e-12 | -9.4734e-13 | -6.5841e-13 | 1.6058e-12 | -9.4734e-13 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 2.0437e-10 | -120 | 120 | 2.0437e-10 | -120 | 120

## LLG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.35154 | 3.7947 | 3.6301 | 0.3534 | 3.7952 | 3.6294 | 4.0592 | 43.8174 | 41.9169 | 4.0807 | 43.8237 | 41.9083 | 4.2695 | 7.4848 | 6.8539 | -4.2036 | -9.7034e-11 | -2.5231e-10 | 4.6533 | 8.5147 | 7.7566 | -4.6257 | 2.5274e-10 | 6.0792e-11 | -49.8346 | -170.125 | 14.6717 | 129.8882 | 9.9123 | -165.3665 |  | 1.5558 | 0.25873 | 0.24694 | 1.5317 | 0 | 0 | -2.372 | -121.4418 | 63.2075 | -2.3747 | 0 | 0
Line_1 | 0.17764 | 15.0382 | 13.2031 | 0.1767 | 15.0389 | 13.2021 | 2.0512 | 173.6457 | 152.4558 | 2.0404 | 173.6544 | 152.4442 | -1.4387 | 171.6819 | 56.8485 | 2.1018 | 5.7826e-11 | -6.2277e-10 | -1.7382 | 83.7274 | 157.772 | 2.3128 | 1.0712e-09 | 7.0951e-10 | 129.6141 | -145.998 | 49.8151 | -50.1118 | 34.0059 | -130.1882 |  | 1.1 | 1.1 | 1.1 | 1.5317 | 0 | 0 | 2.0437e-10 | -120 | 120 | -2.3747 | 0 | 0
Line_2 | 0.17764 | 15.0382 | 13.2031 | 0.1767 | 15.0389 | 13.2021 | 2.0512 | 173.6457 | 152.4558 | 2.0404 | 173.6544 | 152.4442 | -1.4387 | 171.6819 | 56.8485 | 2.1018 | 5.7826e-11 | -6.2277e-10 | -1.7382 | 83.7274 | 157.772 | 2.3128 | 1.0712e-09 | 7.0951e-10 | 129.6141 | -145.998 | 49.8151 | -50.1118 | 34.0059 | -130.1882 |  | 1.1 | 1.1 | 1.1 | 1.5317 | 0 | 0 | 2.0437e-10 | -120 | 120 | -2.3747 | 0 | 0
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.474e-12 | 1.6681e-13 | 1.3072e-12 | -1.474e-12 | 1.6681e-13 | 1.3072e-12 | -6.5841e-13 | 1.6058e-12 | -9.4734e-13 | -6.5841e-13 | 1.6058e-12 | -9.4734e-13 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 2.0437e-10 | -120 | 120 | 2.0437e-10 | -120 | 120

## LLG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.059652 | 0.18032 | 0.17641 | 0.059968 | 0.18053 | 0.17609 | 0.6888 | 2.0822 | 2.037 | 0.69246 | 2.0846 | 2.0333 | 0.33159 | 1.2903 | 0.056121 | -0.32788 | -1.2785 | -0.03668 | 0.73506 | 1.7851 | 2.0359 | -0.73847 | -1.7652 | -2.0141 | -67.3665 | -170.6831 | 28.5283 | 112.3563 | 9.4357 | -151.5642 |  | 1.1707 | 1.0578 | 0.99986 | 1.1668 | 1.0456 | 0.99073 | -1.647 | -116.5426 | 116.9494 | -1.5847 | -116.4797 | 117.3925
Line_1 | 0.030143 | 0.76456 | 0.74826 | 0.029984 | 0.76469 | 0.74805 | 0.34806 | 8.8284 | 8.6402 | 0.34623 | 8.8299 | 8.6377 | -0.14393 | 7.3928 | 6.9596 | 0.16394 | -6.6487 | -6.5253 | -0.35479 | 6.2971 | 6.4726 | 0.36923 | -6.4054 | -5.5366 | 112.0822 | -160.4241 | 77.0765 | -67.6437 | 19.5883 | -102.9215 |  | 1.1 | 1.1 | 1.1 | 1.1668 | 1.0456 | 0.99073 | 2.0447e-11 | -120 | 120 | -1.5847 | -116.4797 | 117.3925
Line_2 | 0.030143 | 0.76456 | 0.74826 | 0.029984 | 0.76469 | 0.74805 | 0.34806 | 8.8284 | 8.6402 | 0.34623 | 8.8299 | 8.6377 | -0.14393 | 7.3928 | 6.9596 | 0.16394 | -6.6487 | -6.5253 | -0.35479 | 6.2971 | 6.4726 | 0.36923 | -6.4054 | -5.5366 | 112.0822 | -160.4241 | 77.0765 | -67.6437 | 19.5883 | -102.9215 |  | 1.1 | 1.1 | 1.1 | 1.1668 | 1.0456 | 0.99073 | 2.0447e-11 | -120 | 120 | -1.5847 | -116.4797 | 117.3925
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.0485e-13 | -5.5089e-14 | 2.5994e-13 | -2.0485e-13 | -5.5089e-14 | 2.5994e-13 | -1.8188e-13 | 2.6835e-13 | -8.6466e-14 | -1.8188e-13 | 2.6835e-13 | -8.6466e-14 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 2.0447e-11 | -120 | 120 | 2.0447e-11 | -120 | 120

## LLG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.059652 | 0.18032 | 0.17641 | 0.059968 | 0.18053 | 0.17609 | 0.6888 | 2.0822 | 2.037 | 0.69246 | 2.0846 | 2.0333 | 0.33159 | 1.2903 | 0.056121 | -0.32788 | -1.2785 | -0.03668 | 0.73506 | 1.7851 | 2.0359 | -0.73847 | -1.7652 | -2.0141 | -67.3665 | -170.6831 | 28.5283 | 112.3563 | 9.4357 | -151.5642 |  | 1.1707 | 1.0578 | 0.99986 | 1.1668 | 1.0456 | 0.99073 | -1.647 | -116.5426 | 116.9494 | -1.5847 | -116.4797 | 117.3925
Line_1 | 0.030143 | 0.76456 | 0.74826 | 0.029984 | 0.76469 | 0.74805 | 0.34806 | 8.8284 | 8.6402 | 0.34623 | 8.8299 | 8.6377 | -0.14393 | 7.3928 | 6.9596 | 0.16394 | -6.6487 | -6.5253 | -0.35479 | 6.2971 | 6.4726 | 0.36923 | -6.4054 | -5.5366 | 112.0822 | -160.4241 | 77.0765 | -67.6437 | 19.5883 | -102.9215 |  | 1.1 | 1.1 | 1.1 | 1.1668 | 1.0456 | 0.99073 | 2.0447e-11 | -120 | 120 | -1.5847 | -116.4797 | 117.3925
Line_2 | 0.030143 | 0.76456 | 0.74826 | 0.029984 | 0.76469 | 0.74805 | 0.34806 | 8.8284 | 8.6402 | 0.34623 | 8.8299 | 8.6377 | -0.14393 | 7.3928 | 6.9596 | 0.16394 | -6.6487 | -6.5253 | -0.35479 | 6.2971 | 6.4726 | 0.36923 | -6.4054 | -5.5366 | 112.0822 | -160.4241 | 77.0765 | -67.6437 | 19.5883 | -102.9215 |  | 1.1 | 1.1 | 1.1 | 1.1668 | 1.0456 | 0.99073 | 2.0447e-11 | -120 | 120 | -1.5847 | -116.4797 | 117.3925
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.0485e-13 | -5.5089e-14 | 2.5994e-13 | -2.0485e-13 | -5.5089e-14 | 2.5994e-13 | -1.8188e-13 | 2.6835e-13 | -8.6466e-14 | -1.8188e-13 | 2.6835e-13 | -8.6466e-14 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 2.0447e-11 | -120 | 120 | 2.0447e-11 | -120 | 120

## LLG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.23629 | 3.1675 | 3.0745 | 0.23793 | 3.1683 | 3.0735 | 2.7284 | 36.5747 | 35.5012 | 2.7474 | 36.5839 | 35.4903 | 2.782 | 10.0206 | 9.4318 | -2.7245 | -1.428e-10 | -1.5681e-10 | 2.7481 | 5.9458 | 5.5516 | -2.7541 | 9.7818e-11 | -6.2523e-11 | -46.4871 | -161.6372 | 22.352 | 133.1158 | 18.4024 | -157.6876 |  | 1.4332 | 0.31858 | 0.30828 | 1.4101 | 0 | 0 | -1.8379 | -130.9542 | 52.8333 | -1.5745 | 0 | 0
Line_1 | 0.1198 | 9.0315 | 8.3337 | 0.11897 | 9.0325 | 8.3326 | 1.3833 | 104.2873 | 96.2289 | 1.3737 | 104.2983 | 96.2164 | -0.93853 | 103.5019 | 57.1285 | 1.3623 | -1.7703e-10 | -4.2324e-10 | -1.0162 | 12.7753 | 77.436 | 1.3771 | 4.6062e-10 | 1.7414e-10 | 132.7245 | -127.0364 | 66.4181 | -46.8842 | 52.9678 | -113.5849 |  | 1 | 1 | 1 | 1.4101 | 0 | 0 | 1.6132e-10 | -120 | 120 | -1.5745 | 0 | 0
Line_2 | 0.1198 | 9.0315 | 8.3337 | 0.11897 | 9.0325 | 8.3326 | 1.3833 | 104.2873 | 96.2289 | 1.3737 | 104.2983 | 96.2164 | -0.93853 | 103.5019 | 57.1285 | 1.3623 | -1.7703e-10 | -4.2324e-10 | -1.0162 | 12.7753 | 77.436 | 1.3771 | 4.6062e-10 | 1.7414e-10 | 132.7245 | -127.0364 | 66.4181 | -46.8842 | 52.9678 | -113.5849 |  | 1 | 1 | 1 | 1.4101 | 0 | 0 | 1.6132e-10 | -120 | 120 | -1.5745 | 0 | 0
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.2176e-13 | 2.1334e-13 | 5.0842e-13 | -7.2176e-13 | 2.1334e-13 | 5.0842e-13 | -1.7036e-13 | 7.1025e-13 | -5.3988e-13 | -1.7036e-13 | 7.1025e-13 | -5.3988e-13 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 1 | 1 | 1 | 1.6132e-10 | -120 | 120 | 1.6132e-10 | -120 | 120

## LLG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.23629 | 3.1675 | 3.0745 | 0.23793 | 3.1683 | 3.0735 | 2.7284 | 36.5747 | 35.5012 | 2.7474 | 36.5839 | 35.4903 | 2.782 | 10.0206 | 9.4318 | -2.7245 | -1.428e-10 | -1.5681e-10 | 2.7481 | 5.9458 | 5.5516 | -2.7541 | 9.7818e-11 | -6.2523e-11 | -46.4871 | -161.6372 | 22.352 | 133.1158 | 18.4024 | -157.6876 |  | 1.4332 | 0.31858 | 0.30828 | 1.4101 | 0 | 0 | -1.8379 | -130.9542 | 52.8333 | -1.5745 | 0 | 0
Line_1 | 0.1198 | 9.0315 | 8.3337 | 0.11897 | 9.0325 | 8.3326 | 1.3833 | 104.2873 | 96.2289 | 1.3737 | 104.2983 | 96.2164 | -0.93853 | 103.5019 | 57.1285 | 1.3623 | -1.7703e-10 | -4.2324e-10 | -1.0162 | 12.7753 | 77.436 | 1.3771 | 4.6062e-10 | 1.7414e-10 | 132.7245 | -127.0364 | 66.4181 | -46.8842 | 52.9678 | -113.5849 |  | 1 | 1 | 1 | 1.4101 | 0 | 0 | 1.6132e-10 | -120 | 120 | -1.5745 | 0 | 0
Line_2 | 0.1198 | 9.0315 | 8.3337 | 0.11897 | 9.0325 | 8.3326 | 1.3833 | 104.2873 | 96.2289 | 1.3737 | 104.2983 | 96.2164 | -0.93853 | 103.5019 | 57.1285 | 1.3623 | -1.7703e-10 | -4.2324e-10 | -1.0162 | 12.7753 | 77.436 | 1.3771 | 4.6062e-10 | 1.7414e-10 | 132.7245 | -127.0364 | 66.4181 | -46.8842 | 52.9678 | -113.5849 |  | 1 | 1 | 1 | 1.4101 | 0 | 0 | 1.6132e-10 | -120 | 120 | -1.5745 | 0 | 0
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.2176e-13 | 2.1334e-13 | 5.0842e-13 | -7.2176e-13 | 2.1334e-13 | 5.0842e-13 | -1.7036e-13 | 7.1025e-13 | -5.3988e-13 | -1.7036e-13 | 7.1025e-13 | -5.3988e-13 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 1 | 1 | 1 | 1.6132e-10 | -120 | 120 | 1.6132e-10 | -120 | 120

## LLG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.064945 | 0.21523 | 0.20656 | 0.065397 | 0.21554 | 0.20609 | 0.74991 | 2.4853 | 2.3851 | 0.75514 | 2.4889 | 2.3798 | 0.32436 | 1.0886 | -0.15875 | -0.31693 | -1.0492 | 0.20492 | 0.76295 | 2.1128 | 2.0306 | -0.76806 | -2.0853 | -2.0009 | -70.0308 | -176.398 | 21.1602 | 109.5721 | 3.751 | -158.9626 |  | 1.1055 | 0.95635 | 0.85396 | 1.1003 | 0.93792 | 0.84519 | -3.0627 | -113.658 | 115.6305 | -2.8509 | -112.9573 | 116.8848
Line_1 | 0.032927 | 0.6641 | 0.63043 | 0.032699 | 0.66434 | 0.63012 | 0.3802 | 7.6684 | 7.2796 | 0.37757 | 7.6712 | 7.276 | -0.12492 | 6.2772 | 5.5076 | 0.15847 | -5.34 | -4.8648 | -0.3591 | 4.4046 | 4.7602 | 0.38403 | -4.822 | -3.7619 | 109.1808 | -155.0565 | 79.1633 | -70.4279 | 24.9612 | -100.8295 |  | 1 | 1 | 1 | 1.1003 | 0.93792 | 0.84519 | 2.1472e-11 | -120 | 120 | -2.8509 | -112.9573 | 116.8848
Line_2 | 0.032927 | 0.6641 | 0.63043 | 0.032699 | 0.66434 | 0.63012 | 0.3802 | 7.6684 | 7.2796 | 0.37757 | 7.6712 | 7.276 | -0.12492 | 6.2772 | 5.5076 | 0.15847 | -5.34 | -4.8648 | -0.3591 | 4.4046 | 4.7602 | 0.38403 | -4.822 | -3.7619 | 109.1808 | -155.0565 | 79.1633 | -70.4279 | 24.9612 | -100.8295 |  | 1 | 1 | 1 | 1.1003 | 0.93792 | 0.84519 | 2.1472e-11 | -120 | 120 | -2.8509 | -112.9573 | 116.8848
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.6316e-13 | -2.4221e-14 | 1.8738e-13 | -1.6316e-13 | -2.4221e-14 | 1.8738e-13 | -1.2217e-13 | 2.0239e-13 | -8.0218e-14 | -1.2217e-13 | 2.0239e-13 | -8.0218e-14 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 1 | 1 | 1 | 2.1472e-11 | -120 | 120 | 2.1472e-11 | -120 | 120

## LLG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.064945 | 0.21523 | 0.20656 | 0.065397 | 0.21554 | 0.20609 | 0.74991 | 2.4853 | 2.3851 | 0.75514 | 2.4889 | 2.3798 | 0.32436 | 1.0886 | -0.15875 | -0.31693 | -1.0492 | 0.20492 | 0.76295 | 2.1128 | 2.0306 | -0.76806 | -2.0853 | -2.0009 | -70.0308 | -176.398 | 21.1602 | 109.5721 | 3.751 | -158.9626 |  | 1.1055 | 0.95635 | 0.85396 | 1.1003 | 0.93792 | 0.84519 | -3.0627 | -113.658 | 115.6305 | -2.8509 | -112.9573 | 116.8848
Line_1 | 0.032927 | 0.6641 | 0.63043 | 0.032699 | 0.66434 | 0.63012 | 0.3802 | 7.6684 | 7.2796 | 0.37757 | 7.6712 | 7.276 | -0.12492 | 6.2772 | 5.5076 | 0.15847 | -5.34 | -4.8648 | -0.3591 | 4.4046 | 4.7602 | 0.38403 | -4.822 | -3.7619 | 109.1808 | -155.0565 | 79.1633 | -70.4279 | 24.9612 | -100.8295 |  | 1 | 1 | 1 | 1.1003 | 0.93792 | 0.84519 | 2.1472e-11 | -120 | 120 | -2.8509 | -112.9573 | 116.8848
Line_2 | 0.032927 | 0.6641 | 0.63043 | 0.032699 | 0.66434 | 0.63012 | 0.3802 | 7.6684 | 7.2796 | 0.37757 | 7.6712 | 7.276 | -0.12492 | 6.2772 | 5.5076 | 0.15847 | -5.34 | -4.8648 | -0.3591 | 4.4046 | 4.7602 | 0.38403 | -4.822 | -3.7619 | 109.1808 | -155.0565 | 79.1633 | -70.4279 | 24.9612 | -100.8295 |  | 1 | 1 | 1 | 1.1003 | 0.93792 | 0.84519 | 2.1472e-11 | -120 | 120 | -2.8509 | -112.9573 | 116.8848
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.6316e-13 | -2.4221e-14 | 1.8738e-13 | -1.6316e-13 | -2.4221e-14 | 1.8738e-13 | -1.2217e-13 | 2.0239e-13 | -8.0218e-14 | -1.2217e-13 | 2.0239e-13 | -8.0218e-14 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 1 | 1 | 1 | 2.1472e-11 | -120 | 120 | 2.1472e-11 | -120 | 120