## LLL_max_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 4.4073 | 4.4073 | 0 | 0 | 152.6738 | 152.6738 | -3.7266 | 34.0286 | -109.0071 | 143.3883 | 107.028 | -72.972 | 0.7144 | 0.96527 | 15.07 | 3.6776
Line_1 | 2.2037 | 2.2037 | 0 | 0 | 76.3369 | 76.3369 | 24.5898 | -17.0143 | 80.2895 | -71.6942 | -72.972 | 107.028 | 1.1 | 0.96527 | -1.1644e-09 | 3.6776
Line_2 | 2.2037 | 2.2037 | 0 | 0 | 76.3369 | 76.3369 | 24.5898 | -17.0143 | 80.2895 | -71.6942 | -72.972 | 107.028 | 1.1 | 0.96527 | -1.1644e-09 | 3.6776
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.1 | -1.1644e-09 | -1.1644e-09

## LLL_max_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 4.4073 | 4.4073 | 0 | 0 | 152.6738 | 152.6738 | -3.7266 | 34.0286 | -109.0071 | 143.3883 | 107.028 | -72.972 | 0.7144 | 0.96527 | 15.07 | 3.6776
Line_1 | 2.2037 | 2.2037 | 0 | 0 | 76.3369 | 76.3369 | 24.5898 | -17.0143 | 80.2895 | -71.6942 | -72.972 | 107.028 | 1.1 | 0.96527 | -1.1644e-09 | 3.6776
Line_2 | 2.2037 | 2.2037 | 0 | 0 | 76.3369 | 76.3369 | 24.5898 | -17.0143 | 80.2895 | -71.6942 | -72.972 | 107.028 | 1.1 | 0.96527 | -1.1644e-09 | 3.6776
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.1 | -1.1644e-09 | -1.1644e-09

## LLL_max_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 2.8818 | 2.8818 | 0 | 0 | 99.8287 | 99.8287 | -37.4533 | 50.4088 | -71.8789 | 86.5784 | 121.2007 | -58.7993 | 0.8119 | 1.0036 | 3.6785 | 0.99136
Line_1 | 1.4409 | 1.4409 | 0 | 0 | 49.9144 | 49.9144 | 28.4433 | -25.2044 | 46.9641 | -43.2892 | -58.7993 | 121.2007 | 1.1 | 1.0036 | -1.3468e-09 | 0.99136
Line_2 | 1.4409 | 1.4409 | 0 | 0 | 49.9144 | 49.9144 | 28.4433 | -25.2044 | 46.9641 | -43.2892 | -58.7993 | 121.2007 | 1.1 | 1.0036 | -1.3468e-09 | 0.99136
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.1 | -1.3468e-09 | -1.3468e-09

## LLL_max_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 2.8818 | 2.8818 | 0 | 0 | 99.8287 | 99.8287 | -37.4533 | 50.4088 | -71.8789 | 86.5784 | 121.2007 | -58.7993 | 0.8119 | 1.0036 | 3.6785 | 0.99136
Line_1 | 1.4409 | 1.4409 | 0 | 0 | 49.9144 | 49.9144 | 28.4433 | -25.2044 | 46.9641 | -43.2892 | -58.7993 | 121.2007 | 1.1 | 1.0036 | -1.3468e-09 | 0.99136
Line_2 | 1.4409 | 1.4409 | 0 | 0 | 49.9144 | 49.9144 | 28.4433 | -25.2044 | 46.9641 | -43.2892 | -58.7993 | 121.2007 | 1.1 | 1.0036 | -1.3468e-09 | 0.99136
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.1 | -1.3468e-09 | -1.3468e-09

## LLL_min_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 3.597 | 3.597 | 0 | 0 | 124.6031 | 124.6031 | -2.5463 | 41.299 | -74.481 | 97.3818 | 119.1403 | -60.8597 | 0.5981 | 0.84891 | 27.1823 | 6.1588
Line_1 | 1.7985 | 1.7985 | 0 | 0 | 62.3016 | 62.3016 | 30.3377 | -20.6495 | 54.4161 | -48.6909 | -60.8597 | 119.1403 | 1 | 0.84891 | -1.7382e-09 | 6.1588
Line_2 | 1.7985 | 1.7985 | 0 | 0 | 62.3016 | 62.3016 | 30.3377 | -20.6495 | 54.4161 | -48.6909 | -60.8597 | 119.1403 | 1 | 0.84891 | -1.7382e-09 | 6.1588
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | -1.7382e-09 | -1.7382e-09

## LLL_min_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 3.597 | 3.597 | 0 | 0 | 124.6031 | 124.6031 | -2.5463 | 41.299 | -74.481 | 97.3818 | 119.1403 | -60.8597 | 0.5981 | 0.84891 | 27.1823 | 6.1588
Line_1 | 1.7985 | 1.7985 | 0 | 0 | 62.3016 | 62.3016 | 30.3377 | -20.6495 | 54.4161 | -48.6909 | -60.8597 | 119.1403 | 1 | 0.84891 | -1.7382e-09 | 6.1588
Line_2 | 1.7985 | 1.7985 | 0 | 0 | 62.3016 | 62.3016 | 30.3377 | -20.6495 | 54.4161 | -48.6909 | -60.8597 | 119.1403 | 1 | 0.84891 | -1.7382e-09 | 6.1588
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | -1.7382e-09 | -1.7382e-09

## LLL_min_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 2.4531 | 2.4531 | 0 | 0 | 84.9769 | 84.9769 | -29.364 | 47.3878 | -47.5855 | 58.2365 | 131.5832 | -48.4168 | 0.65802 | 0.88354 | 9.9053 | 2.4475
Line_1 | 1.2265 | 1.2265 | 0 | 0 | 42.4884 | 42.4884 | 28.1999 | -23.6939 | 31.781 | -29.1183 | -48.4168 | 131.5832 | 1 | 0.88354 | -1.6157e-09 | 2.4475
Line_2 | 1.2265 | 1.2265 | 0 | 0 | 42.4884 | 42.4884 | 28.1999 | -23.6939 | 31.781 | -29.1183 | -48.4168 | 131.5832 | 1 | 0.88354 | -1.6157e-09 | 2.4475
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | -1.6157e-09 | -1.6157e-09

## LLL_min_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 2.4531 | 2.4531 | 0 | 0 | 84.9769 | 84.9769 | -29.364 | 47.3878 | -47.5855 | 58.2365 | 131.5832 | -48.4168 | 0.65802 | 0.88354 | 9.9053 | 2.4475
Line_1 | 1.2265 | 1.2265 | 0 | 0 | 42.4884 | 42.4884 | 28.1999 | -23.6939 | 31.781 | -29.1183 | -48.4168 | 131.5832 | 1 | 0.88354 | -1.6157e-09 | 2.4475
Line_2 | 1.2265 | 1.2265 | 0 | 0 | 42.4884 | 42.4884 | 28.1999 | -23.6939 | 31.781 | -29.1183 | -48.4168 | 131.5832 | 1 | 0.88354 | -1.6157e-09 | 2.4475
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | -1.6157e-09 | -1.6157e-09

## LL_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 2.05 | 2.05 | 2.05 | 2.05 | 2.05 | 2.05 | 23.6713 | 23.6713 | 23.6713 | 23.6713 | 23.6713 | 23.6713 | -7.7301 | -13.7565 | 9.4883 | 9.9154 | 15.9417 | -7.303 | -34.702 | -11.3406 | -17.8023 | 37.1814 | 13.82 | 20.2817 | 106.2295 | -13.7705 | -133.7705 | -73.7705 | 166.2295 | 46.2295 | 1.5019 | 0.75316 | 0.85221 | 1.6256 | 0.8913 | 0.91066 | 3.6715 | -154.269 | 164.2863 | 1.2976 | -152.8482 | 156.0323
Line_1 | 1.025 | 1.025 | 1.025 | 1.025 | 1.025 | 1.025 | 11.8356 | 11.8356 | 11.8356 | 11.8356 | 11.8356 | 11.8356 | 5.504 | 8.5172 | -3.1052 | -4.9577 | -7.9709 | 3.6515 | 19.2106 | 7.5299 | 10.7607 | -18.5907 | -6.91 | -10.1409 | -73.7705 | 166.2295 | 46.2295 | 106.2295 | -13.7705 | -133.7705 | 1.6884 | 0.96053 | 0.94628 | 1.6256 | 0.8913 | 0.91066 | 0.24197 | -152.2913 | 152.3258 | 1.2976 | -152.8482 | 156.0323
Line_2 | 1.025 | 1.025 | 1.025 | 1.025 | 1.025 | 1.025 | 11.8356 | 11.8356 | 11.8356 | 11.8356 | 11.8356 | 11.8356 | 5.504 | 8.5172 | -3.1052 | -4.9577 | -7.9709 | 3.6515 | 19.2106 | 7.5299 | 10.7607 | -18.5907 | -6.91 | -10.1409 | -73.7705 | 166.2295 | 46.2295 | 106.2295 | -13.7705 | -133.7705 | 1.6884 | 0.96053 | 0.94628 | 1.6256 | 0.8913 | 0.91066 | 0.24197 | -152.2913 | 152.3258 | 1.2976 | -152.8482 | 156.0323
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.0823e-15 | 2.9864e-14 | -3.3876e-15 | -7.8628e-15 | -1.3752e-14 | 9.2451e-15 | 1.9961e-14 | -1.7721e-14 | 3.2146e-14 | -3.2025e-14 | 2.6183e-14 | -4.0279e-14 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6884 | 0.96053 | 0.94628 | 1.6884 | 0.96053 | 0.94628 | 0.24197 | -152.2913 | 152.3258 | 0.24197 | -152.2913 | 152.3258

## LL_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 2.05 | 2.05 | 2.05 | 2.05 | 2.05 | 2.05 | 23.6713 | 23.6713 | 23.6713 | 23.6713 | 23.6713 | 23.6713 | -7.7301 | -13.7565 | 9.4883 | 9.9154 | 15.9417 | -7.303 | -34.702 | -11.3406 | -17.8023 | 37.1814 | 13.82 | 20.2817 | 106.2295 | -13.7705 | -133.7705 | -73.7705 | 166.2295 | 46.2295 | 1.5019 | 0.75316 | 0.85221 | 1.6256 | 0.8913 | 0.91066 | 3.6715 | -154.269 | 164.2863 | 1.2976 | -152.8482 | 156.0323
Line_1 | 1.025 | 1.025 | 1.025 | 1.025 | 1.025 | 1.025 | 11.8356 | 11.8356 | 11.8356 | 11.8356 | 11.8356 | 11.8356 | 5.504 | 8.5172 | -3.1052 | -4.9577 | -7.9709 | 3.6515 | 19.2106 | 7.5299 | 10.7607 | -18.5907 | -6.91 | -10.1409 | -73.7705 | 166.2295 | 46.2295 | 106.2295 | -13.7705 | -133.7705 | 1.6884 | 0.96053 | 0.94628 | 1.6256 | 0.8913 | 0.91066 | 0.24197 | -152.2913 | 152.3258 | 1.2976 | -152.8482 | 156.0323
Line_2 | 1.025 | 1.025 | 1.025 | 1.025 | 1.025 | 1.025 | 11.8356 | 11.8356 | 11.8356 | 11.8356 | 11.8356 | 11.8356 | 5.504 | 8.5172 | -3.1052 | -4.9577 | -7.9709 | 3.6515 | 19.2106 | 7.5299 | 10.7607 | -18.5907 | -6.91 | -10.1409 | -73.7705 | 166.2295 | 46.2295 | 106.2295 | -13.7705 | -133.7705 | 1.6884 | 0.96053 | 0.94628 | 1.6256 | 0.8913 | 0.91066 | 0.24197 | -152.2913 | 152.3258 | 1.2976 | -152.8482 | 156.0323
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.0823e-15 | 2.9864e-14 | -3.3876e-15 | -7.8628e-15 | -1.3752e-14 | 9.2451e-15 | 1.9961e-14 | -1.7721e-14 | 3.2146e-14 | -3.2025e-14 | 2.6183e-14 | -4.0279e-14 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6884 | 0.96053 | 0.94628 | 1.6884 | 0.96053 | 0.94628 | 0.24197 | -152.2913 | 152.3258 | 0.24197 | -152.2913 | 152.3258

## LL_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.66 | 1.66 | 1.66 | 1.66 | 1.66 | 1.66 | 19.1684 | 19.1684 | 19.1684 | 19.1684 | 19.1684 | 19.1684 | -9.0352 | -12.9869 | 2.2554 | 10.4682 | 14.4199 | -0.82245 | -25.5506 | -10.2318 | -14.469 | 27.1765 | 11.8577 | 16.0948 | 114.4835 | -5.5165 | -125.5165 | -65.5165 | 174.4835 | 54.4835 | 1.4138 | 0.86253 | 0.76395 | 1.5193 | 0.97396 | 0.84075 | 5.0088 | -147.2836 | 153.3434 | 3.4171 | -146.0856 | 147.4088
Line_1 | 0.83002 | 0.83002 | 0.83002 | 0.83002 | 0.83002 | 0.83002 | 9.5842 | 9.5842 | 9.5842 | 9.5842 | 9.5842 | 9.5842 | 5.5923 | 7.5682 | -0.052985 | -5.2341 | -7.2099 | 0.41123 | 13.9947 | 6.3353 | 8.4539 | -13.5883 | -5.9288 | -8.0474 | -65.5165 | 174.4835 | 54.4835 | 114.4835 | -5.5165 | -125.5165 | 1.5725 | 1.0298 | 0.88208 | 1.5193 | 0.97396 | 0.84075 | 2.7016 | -145.584 | 144.8426 | 3.4171 | -146.0856 | 147.4088
Line_2 | 0.83002 | 0.83002 | 0.83002 | 0.83002 | 0.83002 | 0.83002 | 9.5842 | 9.5842 | 9.5842 | 9.5842 | 9.5842 | 9.5842 | 5.5923 | 7.5682 | -0.052985 | -5.2341 | -7.2099 | 0.41123 | 13.9947 | 6.3353 | 8.4539 | -13.5883 | -5.9288 | -8.0474 | -65.5165 | 174.4835 | 54.4835 | 114.4835 | -5.5165 | -125.5165 | 1.5725 | 1.0298 | 0.88208 | 1.5193 | 0.97396 | 0.84075 | 2.7016 | -145.584 | 144.8426 | 3.4171 | -146.0856 | 147.4088
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.3852e-14 | 1.0339e-14 | -1.1259e-14 | 1.4881e-14 | 3.5501e-16 | -2.406e-15 | -1.8847e-14 | -1.5091e-14 | 1.304e-14 | 7.0218e-16 | 2.5374e-14 | -3.4161e-15 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5725 | 1.0298 | 0.88208 | 1.5725 | 1.0298 | 0.88208 | 2.7016 | -145.584 | 144.8426 | 2.7016 | -145.584 | 144.8426

## LL_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.66 | 1.66 | 1.66 | 1.66 | 1.66 | 1.66 | 19.1684 | 19.1684 | 19.1684 | 19.1684 | 19.1684 | 19.1684 | -9.0352 | -12.9869 | 2.2554 | 10.4682 | 14.4199 | -0.82245 | -25.5506 | -10.2318 | -14.469 | 27.1765 | 11.8577 | 16.0948 | 114.4835 | -5.5165 | -125.5165 | -65.5165 | 174.4835 | 54.4835 | 1.4138 | 0.86253 | 0.76395 | 1.5193 | 0.97396 | 0.84075 | 5.0088 | -147.2836 | 153.3434 | 3.4171 | -146.0856 | 147.4088
Line_1 | 0.83002 | 0.83002 | 0.83002 | 0.83002 | 0.83002 | 0.83002 | 9.5842 | 9.5842 | 9.5842 | 9.5842 | 9.5842 | 9.5842 | 5.5923 | 7.5682 | -0.052985 | -5.2341 | -7.2099 | 0.41123 | 13.9947 | 6.3353 | 8.4539 | -13.5883 | -5.9288 | -8.0474 | -65.5165 | 174.4835 | 54.4835 | 114.4835 | -5.5165 | -125.5165 | 1.5725 | 1.0298 | 0.88208 | 1.5193 | 0.97396 | 0.84075 | 2.7016 | -145.584 | 144.8426 | 3.4171 | -146.0856 | 147.4088
Line_2 | 0.83002 | 0.83002 | 0.83002 | 0.83002 | 0.83002 | 0.83002 | 9.5842 | 9.5842 | 9.5842 | 9.5842 | 9.5842 | 9.5842 | 5.5923 | 7.5682 | -0.052985 | -5.2341 | -7.2099 | 0.41123 | 13.9947 | 6.3353 | 8.4539 | -13.5883 | -5.9288 | -8.0474 | -65.5165 | 174.4835 | 54.4835 | 114.4835 | -5.5165 | -125.5165 | 1.5725 | 1.0298 | 0.88208 | 1.5193 | 0.97396 | 0.84075 | 2.7016 | -145.584 | 144.8426 | 3.4171 | -146.0856 | 147.4088
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.3852e-14 | 1.0339e-14 | -1.1259e-14 | 1.4881e-14 | 3.5501e-16 | -2.406e-15 | -1.8847e-14 | -1.5091e-14 | 1.304e-14 | 7.0218e-16 | 2.5374e-14 | -3.4161e-15 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5725 | 1.0298 | 0.88208 | 1.5725 | 1.0298 | 0.88208 | 2.7016 | -145.584 | 144.8426 | 2.7016 | -145.584 | 144.8426

## LL_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.6778 | 1.6778 | 1.6778 | 1.6778 | 1.6778 | 1.6778 | 19.3741 | 19.3741 | 19.3741 | 19.3741 | 19.3741 | 19.3741 | -9.2662 | -10.5039 | 5.5938 | 12.0768 | 13.3146 | -2.7831 | -23.99 | -6.1166 | -13.9814 | 25.651 | 7.7775 | 15.6423 | 117.4848 | -2.5152 | -122.5152 | -62.5152 | 177.4848 | 57.4848 | 1.3274 | 0.62738 | 0.77727 | 1.4634 | 0.79589 | 0.82006 | 6.3657 | -152.3022 | 169.2907 | 2.2731 | -152.2244 | 157.5735
Line_1 | 0.83892 | 0.83892 | 0.83892 | 0.83892 | 0.83892 | 0.83892 | 9.6871 | 9.6871 | 9.6871 | 9.6871 | 9.6871 | 9.6871 | 6.7411 | 7.36 | -0.6889 | -6.0384 | -6.6573 | 1.3916 | 13.2407 | 4.304 | 8.2364 | -12.8255 | -3.8888 | -7.8212 | -62.5152 | 177.4848 | 57.4848 | 117.4848 | -2.5152 | -122.5152 | 1.5338 | 0.88015 | 0.85322 | 1.4634 | 0.79589 | 0.82006 | 0.50339 | -152.1966 | 152.266 | 2.2731 | -152.2244 | 157.5735
Line_2 | 0.83892 | 0.83892 | 0.83892 | 0.83892 | 0.83892 | 0.83892 | 9.6871 | 9.6871 | 9.6871 | 9.6871 | 9.6871 | 9.6871 | 6.7411 | 7.36 | -0.6889 | -6.0384 | -6.6573 | 1.3916 | 13.2407 | 4.304 | 8.2364 | -12.8255 | -3.8888 | -7.8212 | -62.5152 | 177.4848 | 57.4848 | 117.4848 | -2.5152 | -122.5152 | 1.5338 | 0.88015 | 0.85322 | 1.4634 | 0.79589 | 0.82006 | 0.50339 | -152.1966 | 152.266 | 2.2731 | -152.2244 | 157.5735
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.1854e-15 | 2.8163e-15 | -1.2613e-14 | 7.1854e-15 | -1.0074e-16 | 1.0732e-14 | -9.1454e-15 | -8.716e-16 | 2.0652e-15 | 9.1454e-15 | 4.6602e-15 | -5.6426e-15 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5338 | 0.88015 | 0.85322 | 1.5338 | 0.88015 | 0.85322 | 0.50339 | -152.1966 | 152.266 | 0.50339 | -152.1966 | 152.266

## LL_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.6778 | 1.6778 | 1.6778 | 1.6778 | 1.6778 | 1.6778 | 19.3741 | 19.3741 | 19.3741 | 19.3741 | 19.3741 | 19.3741 | -9.2662 | -10.5039 | 5.5938 | 12.0768 | 13.3146 | -2.7831 | -23.99 | -6.1166 | -13.9814 | 25.651 | 7.7775 | 15.6423 | 117.4848 | -2.5152 | -122.5152 | -62.5152 | 177.4848 | 57.4848 | 1.3274 | 0.62738 | 0.77727 | 1.4634 | 0.79589 | 0.82006 | 6.3657 | -152.3022 | 169.2907 | 2.2731 | -152.2244 | 157.5735
Line_1 | 0.83892 | 0.83892 | 0.83892 | 0.83892 | 0.83892 | 0.83892 | 9.6871 | 9.6871 | 9.6871 | 9.6871 | 9.6871 | 9.6871 | 6.7411 | 7.36 | -0.6889 | -6.0384 | -6.6573 | 1.3916 | 13.2407 | 4.304 | 8.2364 | -12.8255 | -3.8888 | -7.8212 | -62.5152 | 177.4848 | 57.4848 | 117.4848 | -2.5152 | -122.5152 | 1.5338 | 0.88015 | 0.85322 | 1.4634 | 0.79589 | 0.82006 | 0.50339 | -152.1966 | 152.266 | 2.2731 | -152.2244 | 157.5735
Line_2 | 0.83892 | 0.83892 | 0.83892 | 0.83892 | 0.83892 | 0.83892 | 9.6871 | 9.6871 | 9.6871 | 9.6871 | 9.6871 | 9.6871 | 6.7411 | 7.36 | -0.6889 | -6.0384 | -6.6573 | 1.3916 | 13.2407 | 4.304 | 8.2364 | -12.8255 | -3.8888 | -7.8212 | -62.5152 | 177.4848 | 57.4848 | 117.4848 | -2.5152 | -122.5152 | 1.5338 | 0.88015 | 0.85322 | 1.4634 | 0.79589 | 0.82006 | 0.50339 | -152.1966 | 152.266 | 2.2731 | -152.2244 | 157.5735
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.1854e-15 | 2.8163e-15 | -1.2613e-14 | 7.1854e-15 | -1.0074e-16 | 1.0732e-14 | -9.1454e-15 | -8.716e-16 | 2.0652e-15 | 9.1454e-15 | 4.6602e-15 | -5.6426e-15 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5338 | 0.88015 | 0.85322 | 1.5338 | 0.88015 | 0.85322 | 0.50339 | -152.1966 | 152.266 | 0.50339 | -152.1966 | 152.266

## LL_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.3903 | 1.3903 | 1.3903 | 1.3903 | 1.3903 | 1.3903 | 16.0533 | 16.0533 | 16.0533 | 16.0533 | 16.0533 | 16.0533 | -9.3789 | -10.2287 | 0.82345 | 11.3086 | 12.1584 | 1.1063 | -17.8566 | -5.5853 | -10.985 | 18.997 | 6.7257 | 12.1254 | 124.7745 | 4.7745 | -115.2255 | -55.2255 | -175.2255 | 64.7745 | 1.2564 | 0.72598 | 0.68621 | 1.3772 | 0.86553 | 0.75846 | 7.0645 | -146.5889 | 159.0614 | 4.0098 | -146.2753 | 149.5615
Line_1 | 0.69513 | 0.69513 | 0.69513 | 0.69513 | 0.69513 | 0.69513 | 8.0266 | 8.0266 | 8.0266 | 8.0266 | 8.0266 | 8.0266 | 6.1367 | 6.5616 | 1.0356 | -5.6543 | -6.0792 | -0.55313 | 9.7836 | 3.6479 | 6.3478 | -9.4985 | -3.3628 | -6.0627 | -55.2255 | -175.2255 | 64.7745 | 124.7745 | 4.7745 | -115.2255 | 1.4388 | 0.93532 | 0.8013 | 1.3772 | 0.86553 | 0.75846 | 2.6766 | -146.1536 | 145.5091 | 4.0098 | -146.2753 | 149.5615
Line_2 | 0.69513 | 0.69513 | 0.69513 | 0.69513 | 0.69513 | 0.69513 | 8.0266 | 8.0266 | 8.0266 | 8.0266 | 8.0266 | 8.0266 | 6.1367 | 6.5616 | 1.0356 | -5.6543 | -6.0792 | -0.55313 | 9.7836 | 3.6479 | 6.3478 | -9.4985 | -3.3628 | -6.0627 | -55.2255 | -175.2255 | 64.7745 | 124.7745 | 4.7745 | -115.2255 | 1.4388 | 0.93532 | 0.8013 | 1.3772 | 0.86553 | 0.75846 | 2.6766 | -146.1536 | 145.5091 | 4.0098 | -146.2753 | 149.5615
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.3378e-14 | -5.4978e-15 | -4.2988e-15 | 9.7349e-15 | 2.0877e-14 | 4.2988e-15 | -5.7427e-15 | -1.1689e-14 | -6.2569e-15 | 1.069e-14 | 4.665e-15 | 6.2569e-15 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4388 | 0.93532 | 0.8013 | 1.4388 | 0.93532 | 0.8013 | 2.6766 | -146.1536 | 145.5091 | 2.6766 | -146.1536 | 145.5091

## LL_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.3903 | 1.3903 | 1.3903 | 1.3903 | 1.3903 | 1.3903 | 16.0533 | 16.0533 | 16.0533 | 16.0533 | 16.0533 | 16.0533 | -9.3789 | -10.2287 | 0.82345 | 11.3086 | 12.1584 | 1.1063 | -17.8566 | -5.5853 | -10.985 | 18.997 | 6.7257 | 12.1254 | 124.7745 | 4.7745 | -115.2255 | -55.2255 | -175.2255 | 64.7745 | 1.2564 | 0.72598 | 0.68621 | 1.3772 | 0.86553 | 0.75846 | 7.0645 | -146.5889 | 159.0614 | 4.0098 | -146.2753 | 149.5615
Line_1 | 0.69513 | 0.69513 | 0.69513 | 0.69513 | 0.69513 | 0.69513 | 8.0266 | 8.0266 | 8.0266 | 8.0266 | 8.0266 | 8.0266 | 6.1367 | 6.5616 | 1.0356 | -5.6543 | -6.0792 | -0.55313 | 9.7836 | 3.6479 | 6.3478 | -9.4985 | -3.3628 | -6.0627 | -55.2255 | -175.2255 | 64.7745 | 124.7745 | 4.7745 | -115.2255 | 1.4388 | 0.93532 | 0.8013 | 1.3772 | 0.86553 | 0.75846 | 2.6766 | -146.1536 | 145.5091 | 4.0098 | -146.2753 | 149.5615
Line_2 | 0.69513 | 0.69513 | 0.69513 | 0.69513 | 0.69513 | 0.69513 | 8.0266 | 8.0266 | 8.0266 | 8.0266 | 8.0266 | 8.0266 | 6.1367 | 6.5616 | 1.0356 | -5.6543 | -6.0792 | -0.55313 | 9.7836 | 3.6479 | 6.3478 | -9.4985 | -3.3628 | -6.0627 | -55.2255 | -175.2255 | 64.7745 | 124.7745 | 4.7745 | -115.2255 | 1.4388 | 0.93532 | 0.8013 | 1.3772 | 0.86553 | 0.75846 | 2.6766 | -146.1536 | 145.5091 | 4.0098 | -146.2753 | 149.5615
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.3378e-14 | -5.4978e-15 | -4.2988e-15 | 9.7349e-15 | 2.0877e-14 | 4.2988e-15 | -5.7427e-15 | -1.1689e-14 | -6.2569e-15 | 1.069e-14 | 4.665e-15 | 6.2569e-15 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4388 | 0.93532 | 0.8013 | 1.4388 | 0.93532 | 0.8013 | 2.6766 | -146.1536 | 145.5091 | 2.6766 | -146.1536 | 145.5091

## LG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.3356 | 1.3356 | 1.3356 | 1.3356 | 1.3356 | 1.3356 | 15.4218 | 15.4218 | 15.4218 | 15.4218 | 15.4218 | 15.4218 | -1.6976 | 0.86033 | -9.0059 | 2.6251 | 0.067213 | 9.9334 | -9.033 | -18.9487 | -16.206 | 10.0854 | 20.0011 | 17.2584 | 105.9875 | -14.0125 | -134.0125 | -74.0125 | 165.9875 | 45.9875 |  | 0.59598 | 1.23 | 1.2022 | 0.67576 | 1.2969 | 1.2912 | 5.3441 | -101.4129 | 106.9261 | 1.3979 | -104.205 | 106.0641
Line_1 | 0.66778 | 0.66778 | 0.66778 | 0.66778 | 0.66778 | 0.66778 | 7.7109 | 7.7109 | 7.7109 | 7.7109 | 7.7109 | 7.7109 | 1.5444 | 0.26549 | 5.1986 | -1.3125 | -0.033607 | -4.9667 | 5.3058 | 10.2637 | 8.8923 | -5.0427 | -10.0006 | -8.6292 | -74.0125 | 165.9875 | 45.9875 | 105.9875 | -14.0125 | -134.0125 |  | 0.71665 | 1.3315 | 1.3358 | 0.67576 | 1.2969 | 1.2912 | -0.24197 | -105.4942 | 105.6762 | 1.3979 | -104.205 | 106.0641
Line_2 | 0.66778 | 0.66778 | 0.66778 | 0.66778 | 0.66778 | 0.66778 | 7.7109 | 7.7109 | 7.7109 | 7.7109 | 7.7109 | 7.7109 | 1.5444 | 0.26549 | 5.1986 | -1.3125 | -0.033607 | -4.9667 | 5.3058 | 10.2637 | 8.8923 | -5.0427 | -10.0006 | -8.6292 | -74.0125 | 165.9875 | 45.9875 | 105.9875 | -14.0125 | -134.0125 |  | 0.71665 | 1.3315 | 1.3358 | 0.67576 | 1.2969 | 1.2912 | -0.24197 | -105.4942 | 105.6762 | 1.3979 | -104.205 | 106.0641
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3586e-14 | 1.5195e-15 | 1.9397e-14 | 3.4054e-15 | -6.4089e-15 | -3.4195e-15 | 1.64e-15 | -4.2123e-16 | -3.399e-14 | 2.5317e-15 | -1.1314e-14 | 1.2185e-14 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.71665 | 1.3315 | 1.3358 | 0.71665 | 1.3315 | 1.3358 | -0.24197 | -105.4942 | 105.6762 | -0.24197 | -105.4942 | 105.6762

## LG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.3356 | 1.3356 | 1.3356 | 1.3356 | 1.3356 | 1.3356 | 15.4218 | 15.4218 | 15.4218 | 15.4218 | 15.4218 | 15.4218 | -1.6976 | 0.86033 | -9.0059 | 2.6251 | 0.067213 | 9.9334 | -9.033 | -18.9487 | -16.206 | 10.0854 | 20.0011 | 17.2584 | 105.9875 | -14.0125 | -134.0125 | -74.0125 | 165.9875 | 45.9875 |  | 0.59598 | 1.23 | 1.2022 | 0.67576 | 1.2969 | 1.2912 | 5.3441 | -101.4129 | 106.9261 | 1.3979 | -104.205 | 106.0641
Line_1 | 0.66778 | 0.66778 | 0.66778 | 0.66778 | 0.66778 | 0.66778 | 7.7109 | 7.7109 | 7.7109 | 7.7109 | 7.7109 | 7.7109 | 1.5444 | 0.26549 | 5.1986 | -1.3125 | -0.033607 | -4.9667 | 5.3058 | 10.2637 | 8.8923 | -5.0427 | -10.0006 | -8.6292 | -74.0125 | 165.9875 | 45.9875 | 105.9875 | -14.0125 | -134.0125 |  | 0.71665 | 1.3315 | 1.3358 | 0.67576 | 1.2969 | 1.2912 | -0.24197 | -105.4942 | 105.6762 | 1.3979 | -104.205 | 106.0641
Line_2 | 0.66778 | 0.66778 | 0.66778 | 0.66778 | 0.66778 | 0.66778 | 7.7109 | 7.7109 | 7.7109 | 7.7109 | 7.7109 | 7.7109 | 1.5444 | 0.26549 | 5.1986 | -1.3125 | -0.033607 | -4.9667 | 5.3058 | 10.2637 | 8.8923 | -5.0427 | -10.0006 | -8.6292 | -74.0125 | 165.9875 | 45.9875 | 105.9875 | -14.0125 | -134.0125 |  | 0.71665 | 1.3315 | 1.3358 | 0.67576 | 1.2969 | 1.2912 | -0.24197 | -105.4942 | 105.6762 | 1.3979 | -104.205 | 106.0641
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3586e-14 | 1.5195e-15 | 1.9397e-14 | 3.4054e-15 | -6.4089e-15 | -3.4195e-15 | 1.64e-15 | -4.2123e-16 | -3.399e-14 | 2.5317e-15 | -1.1314e-14 | 1.2185e-14 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.71665 | 1.3315 | 1.3358 | 0.71665 | 1.3315 | 1.3358 | -0.24197 | -105.4942 | 105.6762 | -0.24197 | -105.4942 | 105.6762

## LG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.90583 | 0.90583 | 0.90583 | 0.90583 | 0.90583 | 0.90583 | 10.4597 | 10.4597 | 10.4597 | 10.4597 | 10.4597 | 10.4597 | -4.324 | -3.1473 | -7.6859 | 4.7506 | 3.574 | 8.1125 | -6.6523 | -11.2136 | -9.952 | 7.1364 | 11.6978 | 10.4361 | 119.6531 | -0.34691 | -120.3469 | -60.3469 | 179.6531 | 59.6531 |  | 0.75854 | 1.1135 | 1.2022 | 0.81963 | 1.1694 | 1.2637 | -3.3704 | -106.0246 | 111.9744 | -3.9981 | -107.3362 | 111.7933
Line_1 | 0.45292 | 0.45292 | 0.45292 | 0.45292 | 0.45292 | 0.45292 | 5.2298 | 5.2298 | 5.2298 | 5.2298 | 5.2298 | 5.2298 | 2.482 | 1.8937 | 4.1629 | -2.3753 | -1.787 | -4.0563 | 3.6892 | 5.9699 | 5.3391 | -3.5682 | -5.8489 | -5.2181 | -60.3469 | 179.6531 | 59.6531 | 119.6531 | -0.34691 | -120.3469 |  | 0.85021 | 1.1976 | 1.2945 | 0.81963 | 1.1694 | 1.2637 | -4.2781 | -107.946 | 111.7092 | -3.9981 | -107.3362 | 111.7933
Line_2 | 0.45292 | 0.45292 | 0.45292 | 0.45292 | 0.45292 | 0.45292 | 5.2298 | 5.2298 | 5.2298 | 5.2298 | 5.2298 | 5.2298 | 2.482 | 1.8937 | 4.1629 | -2.3753 | -1.787 | -4.0563 | 3.6892 | 5.9699 | 5.3391 | -3.5682 | -5.8489 | -5.2181 | -60.3469 | 179.6531 | 59.6531 | 119.6531 | -0.34691 | -120.3469 |  | 0.85021 | 1.1976 | 1.2945 | 0.81963 | 1.1694 | 1.2637 | -4.2781 | -107.946 | 111.7092 | -3.9981 | -107.3362 | 111.7933
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6288e-16 | -1.3415e-14 | -1.4243e-14 | 9.9653e-15 | 1.4366e-14 | 1.878e-14 | 3.5141e-15 | -4.5994e-15 | -5.6707e-15 | -1.7551e-15 | -1.6714e-15 | -5.7238e-15 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.85021 | 1.1976 | 1.2945 | 0.85021 | 1.1976 | 1.2945 | -4.2781 | -107.946 | 111.7092 | -4.2781 | -107.946 | 111.7092

## LG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.90583 | 0.90583 | 0.90583 | 0.90583 | 0.90583 | 0.90583 | 10.4597 | 10.4597 | 10.4597 | 10.4597 | 10.4597 | 10.4597 | -4.324 | -3.1473 | -7.6859 | 4.7506 | 3.574 | 8.1125 | -6.6523 | -11.2136 | -9.952 | 7.1364 | 11.6978 | 10.4361 | 119.6531 | -0.34691 | -120.3469 | -60.3469 | 179.6531 | 59.6531 |  | 0.75854 | 1.1135 | 1.2022 | 0.81963 | 1.1694 | 1.2637 | -3.3704 | -106.0246 | 111.9744 | -3.9981 | -107.3362 | 111.7933
Line_1 | 0.45292 | 0.45292 | 0.45292 | 0.45292 | 0.45292 | 0.45292 | 5.2298 | 5.2298 | 5.2298 | 5.2298 | 5.2298 | 5.2298 | 2.482 | 1.8937 | 4.1629 | -2.3753 | -1.787 | -4.0563 | 3.6892 | 5.9699 | 5.3391 | -3.5682 | -5.8489 | -5.2181 | -60.3469 | 179.6531 | 59.6531 | 119.6531 | -0.34691 | -120.3469 |  | 0.85021 | 1.1976 | 1.2945 | 0.81963 | 1.1694 | 1.2637 | -4.2781 | -107.946 | 111.7092 | -3.9981 | -107.3362 | 111.7933
Line_2 | 0.45292 | 0.45292 | 0.45292 | 0.45292 | 0.45292 | 0.45292 | 5.2298 | 5.2298 | 5.2298 | 5.2298 | 5.2298 | 5.2298 | 2.482 | 1.8937 | 4.1629 | -2.3753 | -1.787 | -4.0563 | 3.6892 | 5.9699 | 5.3391 | -3.5682 | -5.8489 | -5.2181 | -60.3469 | 179.6531 | 59.6531 | 119.6531 | -0.34691 | -120.3469 |  | 0.85021 | 1.1976 | 1.2945 | 0.81963 | 1.1694 | 1.2637 | -4.2781 | -107.946 | 111.7092 | -3.9981 | -107.3362 | 111.7933
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6288e-16 | -1.3415e-14 | -1.4243e-14 | 9.9653e-15 | 1.4366e-14 | 1.878e-14 | 3.5141e-15 | -4.5994e-15 | -5.6707e-15 | -1.7551e-15 | -1.6714e-15 | -5.7238e-15 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.85021 | 1.1976 | 1.2945 | 0.85021 | 1.1976 | 1.2945 | -4.2781 | -107.946 | 111.7092 | -4.2781 | -107.946 | 111.7092

## LG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.0939 | 1.0939 | 1.0939 | 1.0939 | 1.0939 | 1.0939 | 12.6315 | 12.6315 | 12.6315 | 12.6315 | 12.6315 | 12.6315 | -2.0087 | -1.4825 | -8.3253 | 3.2034 | 2.6773 | 9.52 | -6.2469 | -13.8445 | -10.5013 | 6.9529 | 14.5505 | 11.2074 | 116.9814 | -3.0186 | -123.0186 | -63.0186 | 176.9814 | 56.9814 |  | 0.51949 | 1.1023 | 1.0609 | 0.60606 | 1.1713 | 1.1641 | 9.1565 | -99.1308 | 108.5747 | 2.2446 | -103.4443 | 106.6354
Line_1 | 0.54696 | 0.54696 | 0.54696 | 0.54696 | 0.54696 | 0.54696 | 6.3158 | 6.3158 | 6.3158 | 6.3158 | 6.3158 | 6.3158 | 1.9004 | 1.6373 | 5.0587 | -1.6017 | -1.3386 | -4.76 | 3.653 | 7.4518 | 5.7802 | -3.4765 | -7.2752 | -5.6037 | -63.0186 | 176.9814 | 56.9814 | 116.9814 | -3.0186 | -123.0186 |  | 0.65198 | 1.208 | 1.2162 | 0.60606 | 1.1713 | 1.1641 | -0.50339 | -105.4109 | 105.7897 | 2.2446 | -103.4443 | 106.6354
Line_2 | 0.54696 | 0.54696 | 0.54696 | 0.54696 | 0.54696 | 0.54696 | 6.3158 | 6.3158 | 6.3158 | 6.3158 | 6.3158 | 6.3158 | 1.9004 | 1.6373 | 5.0587 | -1.6017 | -1.3386 | -4.76 | 3.653 | 7.4518 | 5.7802 | -3.4765 | -7.2752 | -5.6037 | -63.0186 | 176.9814 | 56.9814 | 116.9814 | -3.0186 | -123.0186 |  | 0.65198 | 1.208 | 1.2162 | 0.60606 | 1.1713 | 1.1641 | -0.50339 | -105.4109 | 105.7897 | 2.2446 | -103.4443 | 106.6354
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3806e-15 | 2.113e-15 | 1.6268e-14 | -3.1493e-15 | -4.5619e-15 | -2.2175e-14 | 7.3143e-15 | 1.5741e-14 | 1.6574e-14 | -6.9215e-15 | -1.655e-14 | -6.2705e-15 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.65198 | 1.208 | 1.2162 | 0.65198 | 1.208 | 1.2162 | -0.50339 | -105.4109 | 105.7897 | -0.50339 | -105.4109 | 105.7897

## LG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.0939 | 1.0939 | 1.0939 | 1.0939 | 1.0939 | 1.0939 | 12.6315 | 12.6315 | 12.6315 | 12.6315 | 12.6315 | 12.6315 | -2.0087 | -1.4825 | -8.3253 | 3.2034 | 2.6773 | 9.52 | -6.2469 | -13.8445 | -10.5013 | 6.9529 | 14.5505 | 11.2074 | 116.9814 | -3.0186 | -123.0186 | -63.0186 | 176.9814 | 56.9814 |  | 0.51949 | 1.1023 | 1.0609 | 0.60606 | 1.1713 | 1.1641 | 9.1565 | -99.1308 | 108.5747 | 2.2446 | -103.4443 | 106.6354
Line_1 | 0.54696 | 0.54696 | 0.54696 | 0.54696 | 0.54696 | 0.54696 | 6.3158 | 6.3158 | 6.3158 | 6.3158 | 6.3158 | 6.3158 | 1.9004 | 1.6373 | 5.0587 | -1.6017 | -1.3386 | -4.76 | 3.653 | 7.4518 | 5.7802 | -3.4765 | -7.2752 | -5.6037 | -63.0186 | 176.9814 | 56.9814 | 116.9814 | -3.0186 | -123.0186 |  | 0.65198 | 1.208 | 1.2162 | 0.60606 | 1.1713 | 1.1641 | -0.50339 | -105.4109 | 105.7897 | 2.2446 | -103.4443 | 106.6354
Line_2 | 0.54696 | 0.54696 | 0.54696 | 0.54696 | 0.54696 | 0.54696 | 6.3158 | 6.3158 | 6.3158 | 6.3158 | 6.3158 | 6.3158 | 1.9004 | 1.6373 | 5.0587 | -1.6017 | -1.3386 | -4.76 | 3.653 | 7.4518 | 5.7802 | -3.4765 | -7.2752 | -5.6037 | -63.0186 | 176.9814 | 56.9814 | 116.9814 | -3.0186 | -123.0186 |  | 0.65198 | 1.208 | 1.2162 | 0.60606 | 1.1713 | 1.1641 | -0.50339 | -105.4109 | 105.7897 | 2.2446 | -103.4443 | 106.6354
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3806e-15 | 2.113e-15 | 1.6268e-14 | -3.1493e-15 | -4.5619e-15 | -2.2175e-14 | 7.3143e-15 | 1.5741e-14 | 1.6574e-14 | -6.9215e-15 | -1.655e-14 | -6.2705e-15 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.65198 | 1.208 | 1.2162 | 0.65198 | 1.208 | 1.2162 | -0.50339 | -105.4109 | 105.7897 | -0.50339 | -105.4109 | 105.7897

## LG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.77272 | 0.77272 | 0.77272 | 0.77272 | 0.77272 | 0.77272 | 8.9226 | 8.9226 | 8.9226 | 8.9226 | 8.9226 | 8.9226 | -3.7984 | -3.5359 | -6.9502 | 4.3946 | 4.132 | 7.5464 | -4.4015 | -8.1924 | -6.5243 | 4.7537 | 8.5447 | 6.8766 | 129.3358 | 9.3358 | -110.6642 | -50.6642 | -170.6642 | 69.3358 |  | 0.65159 | 1 | 1.0684 | 0.72555 | 1.0637 | 1.1442 | -1.4582 | -104.0096 | 112.5253 | -3.4158 | -106.4717 | 111.6769
Line_1 | 0.38636 | 0.38636 | 0.38636 | 0.38636 | 0.38636 | 0.38636 | 4.4613 | 4.4613 | 4.4613 | 4.4613 | 4.4613 | 4.4613 | 2.3463 | 2.2151 | 3.9222 | -2.1973 | -2.066 | -3.7732 | 2.4649 | 4.3604 | 3.5264 | -2.3769 | -4.2723 | -3.4383 | -50.6642 | -170.6642 | 69.3358 | 129.3358 | 9.3358 | -110.6642 |  | 0.76281 | 1.0963 | 1.1822 | 0.72555 | 1.0637 | 1.1442 | -4.2518 | -107.5944 | 111.2937 | -3.4158 | -106.4717 | 111.6769
Line_2 | 0.38636 | 0.38636 | 0.38636 | 0.38636 | 0.38636 | 0.38636 | 4.4613 | 4.4613 | 4.4613 | 4.4613 | 4.4613 | 4.4613 | 2.3463 | 2.2151 | 3.9222 | -2.1973 | -2.066 | -3.7732 | 2.4649 | 4.3604 | 3.5264 | -2.3769 | -4.2723 | -3.4383 | -50.6642 | -170.6642 | 69.3358 | 129.3358 | 9.3358 | -110.6642 |  | 0.76281 | 1.0963 | 1.1822 | 0.72555 | 1.0637 | 1.1442 | -4.2518 | -107.5944 | 111.2937 | -3.4158 | -106.4717 | 111.6769
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4386e-15 | 2.0224e-15 | -1.5921e-15 | -4.5043e-15 | -6.5197e-15 | 3.1842e-15 | 4.8585e-17 | 2.0826e-15 | -3.6258e-15 | 3.3487e-16 | -3.3803e-15 | 7.2516e-15 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.76281 | 1.0963 | 1.1822 | 0.76281 | 1.0963 | 1.1822 | -4.2518 | -107.5944 | 111.2937 | -4.2518 | -107.5944 | 111.2937

## LG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.77272 | 0.77272 | 0.77272 | 0.77272 | 0.77272 | 0.77272 | 8.9226 | 8.9226 | 8.9226 | 8.9226 | 8.9226 | 8.9226 | -3.7984 | -3.5359 | -6.9502 | 4.3946 | 4.132 | 7.5464 | -4.4015 | -8.1924 | -6.5243 | 4.7537 | 8.5447 | 6.8766 | 129.3358 | 9.3358 | -110.6642 | -50.6642 | -170.6642 | 69.3358 |  | 0.65159 | 1 | 1.0684 | 0.72555 | 1.0637 | 1.1442 | -1.4582 | -104.0096 | 112.5253 | -3.4158 | -106.4717 | 111.6769
Line_1 | 0.38636 | 0.38636 | 0.38636 | 0.38636 | 0.38636 | 0.38636 | 4.4613 | 4.4613 | 4.4613 | 4.4613 | 4.4613 | 4.4613 | 2.3463 | 2.2151 | 3.9222 | -2.1973 | -2.066 | -3.7732 | 2.4649 | 4.3604 | 3.5264 | -2.3769 | -4.2723 | -3.4383 | -50.6642 | -170.6642 | 69.3358 | 129.3358 | 9.3358 | -110.6642 |  | 0.76281 | 1.0963 | 1.1822 | 0.72555 | 1.0637 | 1.1442 | -4.2518 | -107.5944 | 111.2937 | -3.4158 | -106.4717 | 111.6769
Line_2 | 0.38636 | 0.38636 | 0.38636 | 0.38636 | 0.38636 | 0.38636 | 4.4613 | 4.4613 | 4.4613 | 4.4613 | 4.4613 | 4.4613 | 2.3463 | 2.2151 | 3.9222 | -2.1973 | -2.066 | -3.7732 | 2.4649 | 4.3604 | 3.5264 | -2.3769 | -4.2723 | -3.4383 | -50.6642 | -170.6642 | 69.3358 | 129.3358 | 9.3358 | -110.6642 |  | 0.76281 | 1.0963 | 1.1822 | 0.72555 | 1.0637 | 1.1442 | -4.2518 | -107.5944 | 111.2937 | -3.4158 | -106.4717 | 111.6769
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4386e-15 | 2.0224e-15 | -1.5921e-15 | -4.5043e-15 | -6.5197e-15 | 3.1842e-15 | 4.8585e-17 | 2.0826e-15 | -3.6258e-15 | 3.3487e-16 | -3.3803e-15 | 7.2516e-15 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.76281 | 1.0963 | 1.1822 | 0.76281 | 1.0963 | 1.1822 | -4.2518 | -107.5944 | 111.2937 | -4.2518 | -107.5944 | 111.2937

## LLG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 2.7984 | 2.7984 | 2.7984 | 2.7984 | 2.7984 | 2.7984 | 32.3135 | 32.3135 | 32.3135 | 32.3135 | 32.3135 | 32.3135 | -7.4528 | -13.0678 | 8.5902 | 11.525 | 17.14 | -4.5179 | -39.6577 | -17.891 | -23.9116 | 44.2781 | 22.5114 | 28.5321 | 106.483 | -13.517 | -133.517 | -73.517 | 166.483 | 46.483 |  | 1.2488 | 0.68564 | 0.78629 | 1.4159 | 0.87561 | 0.89398 | 5.8396 | -139.6618 | 156.2436 | 1.8933 | -140.8024 | 145.4809
Line_1 | 1.3992 | 1.3992 | 1.3992 | 1.3992 | 1.3992 | 1.3992 | 16.1567 | 16.1567 | 16.1567 | 16.1567 | 16.1567 | 16.1567 | 6.7806 | 9.5881 | -1.2409 | -5.7625 | -8.57 | 2.259 | 23.2942 | 12.4108 | 15.4211 | -22.139 | -11.2557 | -14.266 | -73.517 | 166.483 | 46.483 | 106.483 | -13.517 | -133.517 |  | 1.5016 | 0.97068 | 0.95756 | 1.4159 | 0.87561 | 0.89398 | 0.2535 | -141.2051 | 141.0836 | 1.8933 | -140.8024 | 145.4809
Line_2 | 1.3992 | 1.3992 | 1.3992 | 1.3992 | 1.3992 | 1.3992 | 16.1567 | 16.1567 | 16.1567 | 16.1567 | 16.1567 | 16.1567 | 6.7806 | 9.5881 | -1.2409 | -5.7625 | -8.57 | 2.259 | 23.2942 | 12.4108 | 15.4211 | -22.139 | -11.2557 | -14.266 | -73.517 | 166.483 | 46.483 | 106.483 | -13.517 | -133.517 |  | 1.5016 | 0.97068 | 0.95756 | 1.4159 | 0.87561 | 0.89398 | 0.2535 | -141.2051 | 141.0836 | 1.8933 | -140.8024 | 145.4809
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9338e-17 | 2.375e-14 | 1.1463e-14 | -7.0421e-15 | -1.2964e-14 | -1.5737e-14 | -8.8912e-15 | -2.2205e-14 | 2.8639e-14 | -1.6036e-14 | 1.6127e-14 | -3.3932e-14 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.5016 | 0.97068 | 0.95756 | 1.5016 | 0.97068 | 0.95756 | 0.2535 | -141.2051 | 141.0836 | 0.2535 | -141.2051 | 141.0836

## LLG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 2.7984 | 2.7984 | 2.7984 | 2.7984 | 2.7984 | 2.7984 | 32.3135 | 32.3135 | 32.3135 | 32.3135 | 32.3135 | 32.3135 | -7.4528 | -13.0678 | 8.5902 | 11.525 | 17.14 | -4.5179 | -39.6577 | -17.891 | -23.9116 | 44.2781 | 22.5114 | 28.5321 | 106.483 | -13.517 | -133.517 | -73.517 | 166.483 | 46.483 |  | 1.2488 | 0.68564 | 0.78629 | 1.4159 | 0.87561 | 0.89398 | 5.8396 | -139.6618 | 156.2436 | 1.8933 | -140.8024 | 145.4809
Line_1 | 1.3992 | 1.3992 | 1.3992 | 1.3992 | 1.3992 | 1.3992 | 16.1567 | 16.1567 | 16.1567 | 16.1567 | 16.1567 | 16.1567 | 6.7806 | 9.5881 | -1.2409 | -5.7625 | -8.57 | 2.259 | 23.2942 | 12.4108 | 15.4211 | -22.139 | -11.2557 | -14.266 | -73.517 | 166.483 | 46.483 | 106.483 | -13.517 | -133.517 |  | 1.5016 | 0.97068 | 0.95756 | 1.4159 | 0.87561 | 0.89398 | 0.2535 | -141.2051 | 141.0836 | 1.8933 | -140.8024 | 145.4809
Line_2 | 1.3992 | 1.3992 | 1.3992 | 1.3992 | 1.3992 | 1.3992 | 16.1567 | 16.1567 | 16.1567 | 16.1567 | 16.1567 | 16.1567 | 6.7806 | 9.5881 | -1.2409 | -5.7625 | -8.57 | 2.259 | 23.2942 | 12.4108 | 15.4211 | -22.139 | -11.2557 | -14.266 | -73.517 | 166.483 | 46.483 | 106.483 | -13.517 | -133.517 |  | 1.5016 | 0.97068 | 0.95756 | 1.4159 | 0.87561 | 0.89398 | 0.2535 | -141.2051 | 141.0836 | 1.8933 | -140.8024 | 145.4809
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9338e-17 | 2.375e-14 | 1.1463e-14 | -7.0421e-15 | -1.2964e-14 | -1.5737e-14 | -8.8912e-15 | -2.2205e-14 | 2.8639e-14 | -1.6036e-14 | 1.6127e-14 | -3.3932e-14 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.5016 | 0.97068 | 0.95756 | 1.5016 | 0.97068 | 0.95756 | 0.2535 | -141.2051 | 141.0836 | 0.2535 | -141.2051 | 141.0836

## LLG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.865 | 1.865 | 1.865 | 1.865 | 1.865 | 1.865 | 21.5352 | 21.5352 | 21.5352 | 21.5352 | 21.5352 | 21.5352 | -10.8196 | -13.3135 | -3.6941 | 12.6283 | 15.1222 | 5.5028 | -22.9064 | -13.2388 | -15.9129 | 24.9586 | 15.291 | 17.965 | 120.4042 | 0.4042 | -119.5958 | -59.5958 | -179.5958 | 60.4042 |  | 1.1764 | 0.87185 | 0.75857 | 1.2989 | 0.99863 | 0.87248 | 5.121 | -134.757 | 137.3346 | 3.5662 | -134.2779 | 133.374
Line_1 | 0.9325 | 0.9325 | 0.9325 | 0.9325 | 0.9325 | 0.9325 | 10.7676 | 10.7676 | 10.7676 | 10.7676 | 10.7676 | 10.7676 | 6.7663 | 8.0133 | 3.2036 | -6.3141 | -7.5611 | -2.7514 | 12.9923 | 8.1585 | 9.4955 | -12.4793 | -7.6455 | -8.9825 | -59.5958 | -179.5958 | 60.4042 | 120.4042 | 0.4042 | -119.5958 |  | 1.3604 | 1.062 | 0.9307 | 1.2989 | 0.99863 | 0.87248 | 2.894 | -134.0812 | 131.761 | 3.5662 | -134.2779 | 133.374
Line_2 | 0.9325 | 0.9325 | 0.9325 | 0.9325 | 0.9325 | 0.9325 | 10.7676 | 10.7676 | 10.7676 | 10.7676 | 10.7676 | 10.7676 | 6.7663 | 8.0133 | 3.2036 | -6.3141 | -7.5611 | -2.7514 | 12.9923 | 8.1585 | 9.4955 | -12.4793 | -7.6455 | -8.9825 | -59.5958 | -179.5958 | 60.4042 | 120.4042 | 0.4042 | -119.5958 |  | 1.3604 | 1.062 | 0.9307 | 1.2989 | 0.99863 | 0.87248 | 2.894 | -134.0812 | 131.761 | 3.5662 | -134.2779 | 133.374
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.6487e-15 | -3.0481e-15 | -3.2886e-15 | 8.1342e-17 | 6.5479e-15 | 3.5227e-16 | -1.1426e-14 | -4.0514e-15 | -2.9363e-15 | -1.609e-15 | 7.6653e-15 | 6.2249e-15 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3604 | 1.062 | 0.9307 | 1.3604 | 1.062 | 0.9307 | 2.894 | -134.0812 | 131.761 | 2.894 | -134.0812 | 131.761

## LLG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.865 | 1.865 | 1.865 | 1.865 | 1.865 | 1.865 | 21.5352 | 21.5352 | 21.5352 | 21.5352 | 21.5352 | 21.5352 | -10.8196 | -13.3135 | -3.6941 | 12.6283 | 15.1222 | 5.5028 | -22.9064 | -13.2388 | -15.9129 | 24.9586 | 15.291 | 17.965 | 120.4042 | 0.4042 | -119.5958 | -59.5958 | -179.5958 | 60.4042 |  | 1.1764 | 0.87185 | 0.75857 | 1.2989 | 0.99863 | 0.87248 | 5.121 | -134.757 | 137.3346 | 3.5662 | -134.2779 | 133.374
Line_1 | 0.9325 | 0.9325 | 0.9325 | 0.9325 | 0.9325 | 0.9325 | 10.7676 | 10.7676 | 10.7676 | 10.7676 | 10.7676 | 10.7676 | 6.7663 | 8.0133 | 3.2036 | -6.3141 | -7.5611 | -2.7514 | 12.9923 | 8.1585 | 9.4955 | -12.4793 | -7.6455 | -8.9825 | -59.5958 | -179.5958 | 60.4042 | 120.4042 | 0.4042 | -119.5958 |  | 1.3604 | 1.062 | 0.9307 | 1.2989 | 0.99863 | 0.87248 | 2.894 | -134.0812 | 131.761 | 3.5662 | -134.2779 | 133.374
Line_2 | 0.9325 | 0.9325 | 0.9325 | 0.9325 | 0.9325 | 0.9325 | 10.7676 | 10.7676 | 10.7676 | 10.7676 | 10.7676 | 10.7676 | 6.7663 | 8.0133 | 3.2036 | -6.3141 | -7.5611 | -2.7514 | 12.9923 | 8.1585 | 9.4955 | -12.4793 | -7.6455 | -8.9825 | -59.5958 | -179.5958 | 60.4042 | 120.4042 | 0.4042 | -119.5958 |  | 1.3604 | 1.062 | 0.9307 | 1.2989 | 0.99863 | 0.87248 | 2.894 | -134.0812 | 131.761 | 3.5662 | -134.2779 | 133.374
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.6487e-15 | -3.0481e-15 | -3.2886e-15 | 8.1342e-17 | 6.5479e-15 | 3.5227e-16 | -1.1426e-14 | -4.0514e-15 | -2.9363e-15 | -1.609e-15 | 7.6653e-15 | 6.2249e-15 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3604 | 1.062 | 0.9307 | 1.3604 | 1.062 | 0.9307 | 2.894 | -134.0812 | 131.761 | 2.894 | -134.0812 | 131.761

## LLG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 2.2885 | 2.2885 | 2.2885 | 2.2885 | 2.2885 | 2.2885 | 26.4254 | 26.4254 | 26.4254 | 26.4254 | 26.4254 | 26.4254 | -8.791 | -9.9423 | 5.0315 | 14.0199 | 15.1712 | 0.1974 | -27.3399 | -10.7144 | -18.0301 | 30.4299 | 13.8044 | 21.1201 | 118.0114 | -1.9886 | -121.9886 | -61.9886 | 178.0114 | 58.0114 |  | 1.0868 | 0.55313 | 0.70837 | 1.2679 | 0.77621 | 0.79927 | 10.1865 | -134.8482 | 163.6037 | 3.2746 | -139.6894 | 147.4759
Line_1 | 1.1443 | 1.1443 | 1.1443 | 1.1443 | 1.1443 | 1.1443 | 13.2127 | 13.2127 | 13.2127 | 13.2127 | 13.2127 | 13.2127 | 8.3172 | 8.8928 | 1.4059 | -7.0099 | -7.5856 | -0.098698 | 15.9874 | 7.6747 | 11.3325 | -15.215 | -6.9022 | -10.56 | -61.9886 | 178.0114 | 58.0114 | 118.0114 | -1.9886 | -121.9886 |  | 1.364 | 0.88904 | 0.86428 | 1.2679 | 0.77621 | 0.79927 | 0.52655 | -141.1938 | 140.9394 | 3.2746 | -139.6894 | 147.4759
Line_2 | 1.1443 | 1.1443 | 1.1443 | 1.1443 | 1.1443 | 1.1443 | 13.2127 | 13.2127 | 13.2127 | 13.2127 | 13.2127 | 13.2127 | 8.3172 | 8.8928 | 1.4059 | -7.0099 | -7.5856 | -0.098698 | 15.9874 | 7.6747 | 11.3325 | -15.215 | -6.9022 | -10.56 | -61.9886 | 178.0114 | 58.0114 | 118.0114 | -1.9886 | -121.9886 |  | 1.364 | 0.88904 | 0.86428 | 1.2679 | 0.77621 | 0.79927 | 0.52655 | -141.1938 | 140.9394 | 3.2746 | -139.6894 | 147.4759
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.4013e-15 | -6.5635e-15 | -9.6285e-15 | 1.9293e-14 | 6.8848e-15 | 3.2706e-15 | -6.5201e-15 | -5.2784e-15 | -5.3675e-15 | 9.8692e-15 | 8.2389e-15 | 1.0527e-14 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.364 | 0.88904 | 0.86428 | 1.364 | 0.88904 | 0.86428 | 0.52655 | -141.1938 | 140.9394 | 0.52655 | -141.1938 | 140.9394

## LLG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 2.2885 | 2.2885 | 2.2885 | 2.2885 | 2.2885 | 2.2885 | 26.4254 | 26.4254 | 26.4254 | 26.4254 | 26.4254 | 26.4254 | -8.791 | -9.9423 | 5.0315 | 14.0199 | 15.1712 | 0.1974 | -27.3399 | -10.7144 | -18.0301 | 30.4299 | 13.8044 | 21.1201 | 118.0114 | -1.9886 | -121.9886 | -61.9886 | 178.0114 | 58.0114 |  | 1.0868 | 0.55313 | 0.70837 | 1.2679 | 0.77621 | 0.79927 | 10.1865 | -134.8482 | 163.6037 | 3.2746 | -139.6894 | 147.4759
Line_1 | 1.1443 | 1.1443 | 1.1443 | 1.1443 | 1.1443 | 1.1443 | 13.2127 | 13.2127 | 13.2127 | 13.2127 | 13.2127 | 13.2127 | 8.3172 | 8.8928 | 1.4059 | -7.0099 | -7.5856 | -0.098698 | 15.9874 | 7.6747 | 11.3325 | -15.215 | -6.9022 | -10.56 | -61.9886 | 178.0114 | 58.0114 | 118.0114 | -1.9886 | -121.9886 |  | 1.364 | 0.88904 | 0.86428 | 1.2679 | 0.77621 | 0.79927 | 0.52655 | -141.1938 | 140.9394 | 3.2746 | -139.6894 | 147.4759
Line_2 | 1.1443 | 1.1443 | 1.1443 | 1.1443 | 1.1443 | 1.1443 | 13.2127 | 13.2127 | 13.2127 | 13.2127 | 13.2127 | 13.2127 | 8.3172 | 8.8928 | 1.4059 | -7.0099 | -7.5856 | -0.098698 | 15.9874 | 7.6747 | 11.3325 | -15.215 | -6.9022 | -10.56 | -61.9886 | 178.0114 | 58.0114 | 118.0114 | -1.9886 | -121.9886 |  | 1.364 | 0.88904 | 0.86428 | 1.2679 | 0.77621 | 0.79927 | 0.52655 | -141.1938 | 140.9394 | 3.2746 | -139.6894 | 147.4759
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.4013e-15 | -6.5635e-15 | -9.6285e-15 | 1.9293e-14 | 6.8848e-15 | 3.2706e-15 | -6.5201e-15 | -5.2784e-15 | -5.3675e-15 | 9.8692e-15 | 8.2389e-15 | 1.0527e-14 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.364 | 0.88904 | 0.86428 | 1.364 | 0.88904 | 0.86428 | 0.52655 | -141.1938 | 140.9394 | 0.52655 | -141.1938 | 140.9394

## LLG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.5894 | 1.5894 | 1.5894 | 1.5894 | 1.5894 | 1.5894 | 18.3533 | 18.3533 | 18.3533 | 18.3533 | 18.3533 | 18.3533 | -10.1559 | -10.7113 | -3.4883 | 12.6782 | 13.2336 | 6.0105 | -15.9054 | -7.8856 | -11.4146 | 17.396 | 9.3762 | 12.9051 | 130.4277 | 10.4277 | -109.5723 | -49.5723 | -169.5723 | 70.4277 |  | 1.0282 | 0.72471 | 0.65033 | 1.1729 | 0.88368 | 0.77567 | 7.8687 | -133.2118 | 143.4347 | 4.3431 | -134.2542 | 135.454
Line_1 | 0.79472 | 0.79472 | 0.79472 | 0.79472 | 0.79472 | 0.79472 | 9.1767 | 9.1767 | 9.1767 | 9.1767 | 9.1767 | 9.1767 | 6.9697 | 7.2474 | 3.6358 | -6.3391 | -6.6168 | -3.0053 | 9.0706 | 5.0607 | 6.8252 | -8.698 | -4.6881 | -6.4525 | -49.5723 | -169.5723 | 70.4277 | 130.4277 | 10.4277 | -109.5723 |  | 1.2465 | 0.96325 | 0.8427 | 1.1729 | 0.88368 | 0.77567 | 2.8898 | -134.6463 | 132.383 | 4.3431 | -134.2542 | 135.454
Line_2 | 0.79472 | 0.79472 | 0.79472 | 0.79472 | 0.79472 | 0.79472 | 9.1767 | 9.1767 | 9.1767 | 9.1767 | 9.1767 | 9.1767 | 6.9697 | 7.2474 | 3.6358 | -6.3391 | -6.6168 | -3.0053 | 9.0706 | 5.0607 | 6.8252 | -8.698 | -4.6881 | -6.4525 | -49.5723 | -169.5723 | 70.4277 | 130.4277 | 10.4277 | -109.5723 |  | 1.2465 | 0.96325 | 0.8427 | 1.1729 | 0.88368 | 0.77567 | 2.8898 | -134.6463 | 132.383 | 4.3431 | -134.2542 | 135.454
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.6274e-15 | -1.1668e-14 | -4.8095e-15 | 7.301e-16 | 9.6293e-15 | 6.155e-15 | -1.5115e-14 | -4.5085e-15 | -1.2495e-14 | 1.4818e-14 | 8.1257e-15 | 1.1021e-14 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.2465 | 0.96325 | 0.8427 | 1.2465 | 0.96325 | 0.8427 | 2.8898 | -134.6463 | 132.383 | 2.8898 | -134.6463 | 132.383

## LLG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.5894 | 1.5894 | 1.5894 | 1.5894 | 1.5894 | 1.5894 | 18.3533 | 18.3533 | 18.3533 | 18.3533 | 18.3533 | 18.3533 | -10.1559 | -10.7113 | -3.4883 | 12.6782 | 13.2336 | 6.0105 | -15.9054 | -7.8856 | -11.4146 | 17.396 | 9.3762 | 12.9051 | 130.4277 | 10.4277 | -109.5723 | -49.5723 | -169.5723 | 70.4277 |  | 1.0282 | 0.72471 | 0.65033 | 1.1729 | 0.88368 | 0.77567 | 7.8687 | -133.2118 | 143.4347 | 4.3431 | -134.2542 | 135.454
Line_1 | 0.79472 | 0.79472 | 0.79472 | 0.79472 | 0.79472 | 0.79472 | 9.1767 | 9.1767 | 9.1767 | 9.1767 | 9.1767 | 9.1767 | 6.9697 | 7.2474 | 3.6358 | -6.3391 | -6.6168 | -3.0053 | 9.0706 | 5.0607 | 6.8252 | -8.698 | -4.6881 | -6.4525 | -49.5723 | -169.5723 | 70.4277 | 130.4277 | 10.4277 | -109.5723 |  | 1.2465 | 0.96325 | 0.8427 | 1.1729 | 0.88368 | 0.77567 | 2.8898 | -134.6463 | 132.383 | 4.3431 | -134.2542 | 135.454
Line_2 | 0.79472 | 0.79472 | 0.79472 | 0.79472 | 0.79472 | 0.79472 | 9.1767 | 9.1767 | 9.1767 | 9.1767 | 9.1767 | 9.1767 | 6.9697 | 7.2474 | 3.6358 | -6.3391 | -6.6168 | -3.0053 | 9.0706 | 5.0607 | 6.8252 | -8.698 | -4.6881 | -6.4525 | -49.5723 | -169.5723 | 70.4277 | 130.4277 | 10.4277 | -109.5723 |  | 1.2465 | 0.96325 | 0.8427 | 1.1729 | 0.88368 | 0.77567 | 2.8898 | -134.6463 | 132.383 | 4.3431 | -134.2542 | 135.454
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.6274e-15 | -1.1668e-14 | -4.8095e-15 | 7.301e-16 | 9.6293e-15 | 6.155e-15 | -1.5115e-14 | -4.5085e-15 | -1.2495e-14 | 1.4818e-14 | 8.1257e-15 | 1.1021e-14 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.2465 | 0.96325 | 0.8427 | 1.2465 | 0.96325 | 0.8427 | 2.8898 | -134.6463 | 132.383 | 2.8898 | -134.6463 | 132.383