## LLL_max_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 3.3335 | 3.3335 | 0 | 0 | 115.4757 | 115.4757 | 37.4821 | -20.1471 | 43.2438 | -23.5752 | -71.1341 | 108.8659 | 0.49558 | 0.26855 | -22.0516 | -21.6509
Line_1 | 3.943 | 3.943 | 7.6252 | 0 | 136.59 | 136.59 | -1e-07 | 24.2539 | -1e-07 | 27.5188 | 109.7407 | -70.2593 | 0 | 0.26855 | 0 | -21.6509
Line_2 | 0.61203 | 0.61203 | 0 | 0 | 21.2012 | 21.2012 | 4.6911 | -4.1068 | 4.6066 | -3.9436 | -65.4896 | 114.5104 | 0.31011 | 0.26855 | -21.0105 | -21.6509

## LLL_max_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 3.3335 | 3.3335 | 0 | 0 | 115.4757 | 115.4757 | 37.4821 | -20.1471 | 43.2438 | -23.5752 | -71.1341 | 108.8659 | 0.49558 | 0.26855 | -22.0516 | -21.6509
Line_1 | 3.943 | 3.943 | 7.6252 | 0 | 136.59 | 136.59 | -1e-07 | 24.2539 | -1e-07 | 27.5188 | 109.7407 | -70.2593 | 0 | 0.26855 | 0 | -21.6509
Line_2 | 0.61203 | 0.61203 | 0 | 0 | 21.2012 | 21.2012 | 4.6911 | -4.1068 | 4.6066 | -3.9436 | -65.4896 | 114.5104 | 0.31011 | 0.26855 | -21.0105 | -21.6509

## LLL_max_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.93124 | 0.93124 | 0 | 0 | 32.2591 | 32.2591 | 21.4053 | -20.0525 | 22.082 | -20.547 | -52.3294 | 127.6706 | 0.95334 | 0.88999 | -6.4379 | -6.6315
Line_1 | 1.1015 | 1.1015 | 2.1302 | 0 | 38.1575 | 38.1575 | -22.1945 | 24.0873 | -21.7914 | 23.939 | 128.5454 | -51.4546 | 0.81515 | 0.88999 | -6.9796 | -6.6315
Line_2 | 0.17097 | 0.17097 | 0 | 0 | 5.9227 | 5.9227 | 4.0804 | -4.0348 | 3.4437 | -3.392 | -46.6849 | 133.3151 | 0.90151 | 0.88999 | -6.5214 | -6.6315

## LLL_max_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.93124 | 0.93124 | 0 | 0 | 32.2591 | 32.2591 | 21.4053 | -20.0525 | 22.082 | -20.547 | -52.3294 | 127.6706 | 0.95334 | 0.88999 | -6.4379 | -6.6315
Line_1 | 1.1015 | 1.1015 | 2.1302 | 0 | 38.1575 | 38.1575 | -22.1945 | 24.0873 | -21.7914 | 23.939 | 128.5454 | -51.4546 | 0.81515 | 0.88999 | -6.9796 | -6.6315
Line_2 | 0.17097 | 0.17097 | 0 | 0 | 5.9227 | 5.9227 | 4.0804 | -4.0348 | 3.4437 | -3.392 | -46.6849 | 133.3151 | 0.90151 | 0.88999 | -6.5214 | -6.6315

## LLL_min_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 2.6307 | 2.6307 | 0 | 0 | 91.1286 | 91.1286 | 45.9418 | -25.214 | 27.0858 | -14.8368 | -57.966 | 122.034 | 0.58524 | 0.32103 | -27.4438 | -27.4919
Line_1 | 3.1965 | 3.1965 | 5.555 | 0 | 110.73 | 110.73 | -1e-07 | 30.6038 | -1e-07 | 18.0852 | 121.9273 | -58.0727 | 0 | 0.32103 | 0 | -27.4919
Line_2 | 0.56587 | 0.56587 | 0 | 0 | 19.6023 | 19.6023 | 6.3489 | -5.3898 | 3.8151 | -3.2484 | -58.5686 | 121.4314 | 0.37786 | 0.32103 | -27.5665 | -27.4919

## LLL_min_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 2.6307 | 2.6307 | 0 | 0 | 91.1286 | 91.1286 | 45.9418 | -25.214 | 27.0858 | -14.8368 | -57.966 | 122.034 | 0.58524 | 0.32103 | -27.4438 | -27.4919
Line_1 | 3.1965 | 3.1965 | 5.555 | 0 | 110.73 | 110.73 | -1e-07 | 30.6038 | -1e-07 | 18.0852 | 121.9273 | -58.0727 | 0 | 0.32103 | 0 | -27.4919
Line_2 | 0.56587 | 0.56587 | 0 | 0 | 19.6023 | 19.6023 | 6.3489 | -5.3898 | 3.8151 | -3.2484 | -58.5686 | 121.4314 | 0.37786 | 0.32103 | -27.5665 | -27.4919

## LLL_min_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.76941 | 0.76941 | 0 | 0 | 26.6531 | 26.6531 | 18.1535 | -16.3803 | 15.0311 | -13.9833 | -46.4658 | 133.5342 | 0.88427 | 0.80805 | -6.841 | -5.9797
Line_1 | 0.93491 | 0.93491 | 1.6247 | 0 | 32.3861 | 32.3861 | -17.2541 | 19.872 | -15.481 | 17.028 | 133.4275 | -46.5725 | 0.71577 | 0.80805 | -4.6729 | -5.9797
Line_2 | 0.1655 | 0.1655 | 0 | 0 | 5.7333 | 5.7333 | 3.5737 | -3.4917 | 3.0933 | -3.0448 | -47.0684 | 132.9316 | 0.8244 | 0.80805 | -6.1904 | -5.9797

## LLL_min_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.76941 | 0.76941 | 0 | 0 | 26.6531 | 26.6531 | 18.1535 | -16.3803 | 15.0311 | -13.9833 | -46.4658 | 133.5342 | 0.88427 | 0.80805 | -6.841 | -5.9797
Line_1 | 0.93491 | 0.93491 | 1.6247 | 0 | 32.3861 | 32.3861 | -17.2541 | 19.872 | -15.481 | 17.028 | 133.4275 | -46.5725 | 0.71577 | 0.80805 | -4.6729 | -5.9797
Line_2 | 0.1655 | 0.1655 | 0 | 0 | 5.7333 | 5.7333 | 3.5737 | -3.4917 | 3.0933 | -3.0448 | -47.0684 | 132.9316 | 0.8244 | 0.80805 | -6.1904 | -5.9797

## LL_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.15358 | 2.8317 | 2.9656 | 0.15358 | 2.8317 | 2.9656 | 1.7734 | 32.6982 | 34.2437 | 1.7734 | 32.6982 | 34.2437 | -1.922 | 26.6301 | -8.5445 | 1.9343 | -22.4603 | 13.1178 | -0.4021 | 4.6792 | 16.5919 | 0.41602 | 0.051901 | -11.403 | 169.7339 | -160.1463 | 18.3646 | -10.2661 | 19.8537 | -161.6354 | 1.1073 | 0.8269 | 0.545 | 1.1157 | 0.6869 | 0.50757 | 1.5502 | -150.1806 | 135.6121 | 1.872 | -160.2787 | 157.3648
Line_1 | 0.091755 | 3.3594 | 3.4357 | 0.091755 | 3.3594 | 3.4357 | 1.0595 | 38.7909 | 39.6726 | 1.0595 | 38.7909 | 39.6726 | 1.136 | -20.7759 | 21.3439 | -1.1316 | 26.6443 | -15.2056 | 0.34653 | 6.4101 | -6.2369 | -0.34157 | 0.24834 | 13.2014 | -14.9237 | 19.1873 | -161.6708 | 165.0763 | -160.8127 | 18.3292 | 1.121 | 0.5605 | 0.5605 | 1.1157 | 0.6869 | 0.50757 | 2.0403 | -177.9597 | -177.9597 | 1.872 | -160.2787 | 157.3648
Line_2 | 0.062572 | 0.52886 | 0.47016 | 0.062572 | 0.52886 | 0.47016 | 0.72252 | 6.1068 | 5.429 | 0.72252 | 6.1068 | 5.429 | 0.80469 | 4.3294 | -1.9729 | -0.80265 | -4.184 | 2.0878 | 0.076762 | 0.46526 | 1.9288 | -0.074452 | -0.30024 | -1.7984 | -3.4275 | -164.3831 | 18.1058 | 176.5725 | 15.6169 | -161.8942 | 1.1188 | 0.71304 | 0.50822 | 1.1157 | 0.6869 | 0.50757 | 2.0217 | -158.2494 | 153.7525 | 1.872 | -160.2787 | 157.3648

## LL_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.15358 | 2.8317 | 2.9656 | 0.15358 | 2.8317 | 2.9656 | 1.7734 | 32.6982 | 34.2437 | 1.7734 | 32.6982 | 34.2437 | -1.922 | 26.6301 | -8.5445 | 1.9343 | -22.4603 | 13.1178 | -0.4021 | 4.6792 | 16.5919 | 0.41602 | 0.051901 | -11.403 | 169.7339 | -160.1463 | 18.3646 | -10.2661 | 19.8537 | -161.6354 | 1.1073 | 0.8269 | 0.545 | 1.1157 | 0.6869 | 0.50757 | 1.5502 | -150.1806 | 135.6121 | 1.872 | -160.2787 | 157.3648
Line_1 | 0.091755 | 3.3594 | 3.4357 | 0.091755 | 3.3594 | 3.4357 | 1.0595 | 38.7909 | 39.6726 | 1.0595 | 38.7909 | 39.6726 | 1.136 | -20.7759 | 21.3439 | -1.1316 | 26.6443 | -15.2056 | 0.34653 | 6.4101 | -6.2369 | -0.34157 | 0.24834 | 13.2014 | -14.9237 | 19.1873 | -161.6708 | 165.0763 | -160.8127 | 18.3292 | 1.121 | 0.5605 | 0.5605 | 1.1157 | 0.6869 | 0.50757 | 2.0403 | -177.9597 | -177.9597 | 1.872 | -160.2787 | 157.3648
Line_2 | 0.062572 | 0.52886 | 0.47016 | 0.062572 | 0.52886 | 0.47016 | 0.72252 | 6.1068 | 5.429 | 0.72252 | 6.1068 | 5.429 | 0.80469 | 4.3294 | -1.9729 | -0.80265 | -4.184 | 2.0878 | 0.076762 | 0.46526 | 1.9288 | -0.074452 | -0.30024 | -1.7984 | -3.4275 | -164.3831 | 18.1058 | 176.5725 | 15.6169 | -161.8942 | 1.1188 | 0.71304 | 0.50822 | 1.1157 | 0.6869 | 0.50757 | 2.0217 | -158.2494 | 153.7525 | 1.872 | -160.2787 | 157.3648

## LL_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.068683 | 1.2664 | 1.3263 | 0.068683 | 1.2664 | 1.3263 | 0.79309 | 14.6233 | 15.3145 | 0.79309 | 14.6233 | 15.3145 | -0.86881 | 14.4848 | 1.0401 | 0.87126 | -13.6509 | -0.12545 | 0.073563 | 2.9236 | 12.7405 | -0.07078 | -1.9773 | -11.7026 | -174.4448 | -144.325 | 34.1859 | 5.5552 | 35.675 | -145.8141 | 1.0994 | 1.0105 | 0.83469 | 1.1022 | 0.94324 | 0.7642 | 0.71549 | -132.9139 | 119.5186 | 0.91084 | -136.083 | 123.5717
Line_1 | 0.041035 | 1.5024 | 1.5365 | 0.041035 | 1.5024 | 1.5365 | 0.47383 | 17.3481 | 17.7424 | 0.47383 | 17.3481 | 17.7424 | 0.52312 | -14.9923 | 1.0907 | -0.52225 | 16.1661 | 0.13696 | 0.001114 | -1.2022 | -12.1651 | -0.00012049 | 2.534 | 13.558 | 0.89762 | 35.0086 | -145.8495 | -179.1024 | -144.9914 | 34.1505 | 1.104 | 0.86698 | 0.6884 | 1.1022 | 0.94324 | 0.7642 | 1.0196 | -140.4067 | 129.274 | 0.91084 | -136.083 | 123.5717
Line_2 | 0.027983 | 0.23652 | 0.21027 | 0.027983 | 0.23652 | 0.21027 | 0.32312 | 2.7311 | 2.4279 | 0.32312 | 2.7311 | 2.4279 | 0.34942 | 2.5443 | 0.034498 | -0.34902 | -2.5152 | -0.011508 | -0.070438 | 0.58964 | 1.8815 | 0.0709 | -0.55663 | -1.8554 | 12.3938 | -148.5618 | 33.9271 | -167.6062 | 31.4382 | -146.0729 | 1.1031 | 0.9563 | 0.77506 | 1.1022 | 0.94324 | 0.7642 | 0.99665 | -135.514 | 122.8767 | 0.91084 | -136.083 | 123.5717

## LL_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.068683 | 1.2664 | 1.3263 | 0.068683 | 1.2664 | 1.3263 | 0.79309 | 14.6233 | 15.3145 | 0.79309 | 14.6233 | 15.3145 | -0.86881 | 14.4848 | 1.0401 | 0.87126 | -13.6509 | -0.12545 | 0.073563 | 2.9236 | 12.7405 | -0.07078 | -1.9773 | -11.7026 | -174.4448 | -144.325 | 34.1859 | 5.5552 | 35.675 | -145.8141 | 1.0994 | 1.0105 | 0.83469 | 1.1022 | 0.94324 | 0.7642 | 0.71549 | -132.9139 | 119.5186 | 0.91084 | -136.083 | 123.5717
Line_1 | 0.041035 | 1.5024 | 1.5365 | 0.041035 | 1.5024 | 1.5365 | 0.47383 | 17.3481 | 17.7424 | 0.47383 | 17.3481 | 17.7424 | 0.52312 | -14.9923 | 1.0907 | -0.52225 | 16.1661 | 0.13696 | 0.001114 | -1.2022 | -12.1651 | -0.00012049 | 2.534 | 13.558 | 0.89762 | 35.0086 | -145.8495 | -179.1024 | -144.9914 | 34.1505 | 1.104 | 0.86698 | 0.6884 | 1.1022 | 0.94324 | 0.7642 | 1.0196 | -140.4067 | 129.274 | 0.91084 | -136.083 | 123.5717
Line_2 | 0.027983 | 0.23652 | 0.21027 | 0.027983 | 0.23652 | 0.21027 | 0.32312 | 2.7311 | 2.4279 | 0.32312 | 2.7311 | 2.4279 | 0.34942 | 2.5443 | 0.034498 | -0.34902 | -2.5152 | -0.011508 | -0.070438 | 0.58964 | 1.8815 | 0.0709 | -0.55663 | -1.8554 | 12.3938 | -148.5618 | 33.9271 | -167.6062 | 31.4382 | -146.0729 | 1.1031 | 0.9563 | 0.77506 | 1.1022 | 0.94324 | 0.7642 | 0.99665 | -135.514 | 122.8767 | 0.91084 | -136.083 | 123.5717

## LL_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.14068 | 2.2375 | 2.3511 | 0.14068 | 2.2375 | 2.3511 | 1.6245 | 25.8369 | 27.1481 | 1.6245 | 25.8369 | 27.1481 | -1.6231 | 22.5203 | -0.019694 | 1.6429 | -17.5218 | 5.5385 | -0.15684 | -0.52064 | 13.7841 | 0.16852 | 3.4745 | -10.5228 | 176.1521 | -146.6212 | 31.3043 | -3.8479 | 33.3788 | -148.6957 | 1.0038 | 0.87187 | 0.50774 | 1.0166 | 0.69137 | 0.43802 | 1.6715 | -147.9456 | 121.3861 | 2.0088 | -157.8373 | 149.0637
Line_1 | 0.088507 | 2.7229 | 2.7871 | 0.088507 | 2.7229 | 2.7871 | 1.022 | 31.441 | 32.1826 | 1.022 | 31.441 | 32.1826 | 1.0131 | -14.0477 | 14.5542 | -1.0053 | 21.4498 | -6.7988 | 0.26704 | 7.8991 | -7.7655 | -0.26242 | -3.5248 | 12.3486 | -12.6212 | 31.4946 | -149.7721 | 167.3788 | -148.5054 | 30.2279 | 1.0252 | 0.51259 | 0.51259 | 1.0166 | 0.69137 | 0.43802 | 2.1453 | -177.8547 | -177.8547 | 2.0088 | -157.8373 | 149.0637
Line_2 | 0.054898 | 0.49207 | 0.43864 | 0.054898 | 0.49207 | 0.43864 | 0.6339 | 5.682 | 5.065 | 0.6339 | 5.682 | 5.065 | 0.64057 | 4.1698 | -1.0682 | -0.63756 | -3.928 | 1.2602 | -0.092125 | 0.092595 | 1.9394 | 0.093903 | 0.050265 | -1.8258 | 10.3873 | -157.1042 | 24.4491 | -169.6127 | 22.8958 | -155.5509 | 1.0209 | 0.73405 | 0.43713 | 1.0166 | 0.69137 | 0.43802 | 2.2033 | -155.8321 | 143.2941 | 2.0088 | -157.8373 | 149.0637

## LL_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.14068 | 2.2375 | 2.3511 | 0.14068 | 2.2375 | 2.3511 | 1.6245 | 25.8369 | 27.1481 | 1.6245 | 25.8369 | 27.1481 | -1.6231 | 22.5203 | -0.019694 | 1.6429 | -17.5218 | 5.5385 | -0.15684 | -0.52064 | 13.7841 | 0.16852 | 3.4745 | -10.5228 | 176.1521 | -146.6212 | 31.3043 | -3.8479 | 33.3788 | -148.6957 | 1.0038 | 0.87187 | 0.50774 | 1.0166 | 0.69137 | 0.43802 | 1.6715 | -147.9456 | 121.3861 | 2.0088 | -157.8373 | 149.0637
Line_1 | 0.088507 | 2.7229 | 2.7871 | 0.088507 | 2.7229 | 2.7871 | 1.022 | 31.441 | 32.1826 | 1.022 | 31.441 | 32.1826 | 1.0131 | -14.0477 | 14.5542 | -1.0053 | 21.4498 | -6.7988 | 0.26704 | 7.8991 | -7.7655 | -0.26242 | -3.5248 | 12.3486 | -12.6212 | 31.4946 | -149.7721 | 167.3788 | -148.5054 | 30.2279 | 1.0252 | 0.51259 | 0.51259 | 1.0166 | 0.69137 | 0.43802 | 2.1453 | -177.8547 | -177.8547 | 2.0088 | -157.8373 | 149.0637
Line_2 | 0.054898 | 0.49207 | 0.43864 | 0.054898 | 0.49207 | 0.43864 | 0.6339 | 5.682 | 5.065 | 0.6339 | 5.682 | 5.065 | 0.64057 | 4.1698 | -1.0682 | -0.63756 | -3.928 | 1.2602 | -0.092125 | 0.092595 | 1.9394 | 0.093903 | 0.050265 | -1.8258 | 10.3873 | -157.1042 | 24.4491 | -169.6127 | 22.8958 | -155.5509 | 1.0209 | 0.73405 | 0.43713 | 1.0166 | 0.69137 | 0.43802 | 2.2033 | -155.8321 | 143.2941 | 2.0088 | -157.8373 | 149.0637

## LL_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.064934 | 1.0328 | 1.0852 | 0.064934 | 1.0328 | 1.0852 | 0.7498 | 11.9253 | 12.5306 | 0.7498 | 11.9253 | 12.5306 | -0.74591 | 11.3062 | 2.3283 | 0.75012 | -10.2413 | -1.1526 | 0.070648 | 0.82643 | 9.4403 | -0.06816 | -0.19713 | -8.7455 | -173.8109 | -136.5841 | 41.3413 | 6.1891 | 43.4159 | -138.6587 | 0.99927 | 0.95061 | 0.77596 | 1.0046 | 0.85895 | 0.70397 | 0.77863 | -132.4035 | 117.4865 | 0.99722 | -135.4814 | 123.8333
Line_1 | 0.040852 | 1.2568 | 1.2864 | 0.040852 | 1.2568 | 1.2864 | 0.47172 | 14.512 | 14.8543 | 0.47172 | 14.512 | 14.8543 | 0.47461 | -10.8711 | 0.48087 | -0.47294 | 12.4481 | 1.1714 | 0.030585 | 0.28236 | -9.4148 | -0.0296 | 0.64954 | 10.3912 | -2.5841 | 41.5316 | -139.7351 | 177.4159 | -138.4684 | 40.2649 | 1.0082 | 0.74937 | 0.63463 | 1.0046 | 0.85895 | 0.70397 | 1.1031 | -139.9562 | 133.1889 | 0.99722 | -135.4814 | 123.8333
Line_2 | 0.025339 | 0.22712 | 0.20246 | 0.025339 | 0.22712 | 0.20246 | 0.29259 | 2.6226 | 2.3378 | 0.29259 | 2.6226 | 2.3378 | 0.27783 | 2.2583 | 0.059675 | -0.27718 | -2.2068 | -0.018751 | -0.097381 | 0.48284 | 1.6698 | 0.09776 | -0.45241 | -1.6456 | 20.4244 | -147.0671 | 34.4862 | -159.5756 | 32.9329 | -145.5138 | 1.0062 | 0.88055 | 0.71472 | 1.0046 | 0.85895 | 0.70397 | 1.1082 | -134.9983 | 122.4394 | 0.99722 | -135.4814 | 123.8333

## LL_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.064934 | 1.0328 | 1.0852 | 0.064934 | 1.0328 | 1.0852 | 0.7498 | 11.9253 | 12.5306 | 0.7498 | 11.9253 | 12.5306 | -0.74591 | 11.3062 | 2.3283 | 0.75012 | -10.2413 | -1.1526 | 0.070648 | 0.82643 | 9.4403 | -0.06816 | -0.19713 | -8.7455 | -173.8109 | -136.5841 | 41.3413 | 6.1891 | 43.4159 | -138.6587 | 0.99927 | 0.95061 | 0.77596 | 1.0046 | 0.85895 | 0.70397 | 0.77863 | -132.4035 | 117.4865 | 0.99722 | -135.4814 | 123.8333
Line_1 | 0.040852 | 1.2568 | 1.2864 | 0.040852 | 1.2568 | 1.2864 | 0.47172 | 14.512 | 14.8543 | 0.47172 | 14.512 | 14.8543 | 0.47461 | -10.8711 | 0.48087 | -0.47294 | 12.4481 | 1.1714 | 0.030585 | 0.28236 | -9.4148 | -0.0296 | 0.64954 | 10.3912 | -2.5841 | 41.5316 | -139.7351 | 177.4159 | -138.4684 | 40.2649 | 1.0082 | 0.74937 | 0.63463 | 1.0046 | 0.85895 | 0.70397 | 1.1031 | -139.9562 | 133.1889 | 0.99722 | -135.4814 | 123.8333
Line_2 | 0.025339 | 0.22712 | 0.20246 | 0.025339 | 0.22712 | 0.20246 | 0.29259 | 2.6226 | 2.3378 | 0.29259 | 2.6226 | 2.3378 | 0.27783 | 2.2583 | 0.059675 | -0.27718 | -2.2068 | -0.018751 | -0.097381 | 0.48284 | 1.6698 | 0.09776 | -0.45241 | -1.6456 | 20.4244 | -147.0671 | 34.4862 | -159.5756 | 32.9329 | -145.5138 | 1.0062 | 0.88055 | 0.71472 | 1.0046 | 0.85895 | 0.70397 | 1.1082 | -134.9983 | 122.4394 | 0.99722 | -135.4814 | 123.8333

## LG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 2.3819 | 0.6243 | 0.48167 | 2.3814 | 0.62486 | 0.48222 | 27.504 | 7.2088 | 5.5619 | 27.498 | 7.2153 | 5.5682 | 15.9403 | -6.9662 | 4.6627 | -9.3334 | 7.2247 | -4.4509 | 14.006 | 1.0822 | 3.8396 | -7.3048 | -2.1554 | -4.7039 | -54.2741 | 76.0336 | 72.6013 | 125.7331 | -103.9478 | -107.3707 | 0.7715 | 0.97794 | 1.086 | 0.43102 | 1.0449 | 1.163 | -12.9698 | -112.7968 | 112.072 | -16.2185 | -120.5594 | 119.2123
Line_1 | 2.9258 | 0.52552 | 0.44024 | 2.9272 | 0.52375 | 0.43849 | 33.7844 | 6.0681 | 5.0835 | 33.8005 | 6.0477 | 5.0632 | 1.0244e-10 | 6.2513 | -3.7015 | 11.0741 | -6.1908 | 3.7442 | -1.433e-10 | -2.539 | -5.6409 | 9.4661 | 1.268 | 4.545 | 123.2805 | -108.94 | -111.2444 | -56.7421 | 71.0163 | 68.6941 | 0 | 1.1119 | 1.3272 | 0.43102 | 1.0449 | 1.163 | 0 | -131.0444 | 125.4834 | -16.2185 | -120.5594 | 119.2123
Line_2 | 0.55858 | 0.11392 | 0.054939 | 0.5576 | 0.11292 | 0.053941 | 6.4499 | 1.3155 | 0.63438 | 6.4386 | 1.3039 | 0.62285 | 2.3374 | 1.1316 | -0.67666 | -1.7407 | -1.0339 | 0.70674 | 2.4502 | -0.84833 | -0.14737 | -2.1613 | 0.88731 | 0.15893 | -67.3943 | -79.9295 | -73.5948 | 112.6296 | 100.0779 | 106.5386 | 0.52501 | 1.0751 | 1.0917 | 0.43102 | 1.0449 | 1.163 | -21.0456 | -116.7877 | 118.692 | -16.2185 | -120.5594 | 119.2123

## LG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 2.3819 | 0.6243 | 0.48167 | 2.3814 | 0.62486 | 0.48222 | 27.504 | 7.2088 | 5.5619 | 27.498 | 7.2153 | 5.5682 | 15.9403 | -6.9662 | 4.6627 | -9.3334 | 7.2247 | -4.4509 | 14.006 | 1.0822 | 3.8396 | -7.3048 | -2.1554 | -4.7039 | -54.2741 | 76.0336 | 72.6013 | 125.7331 | -103.9478 | -107.3707 | 0.7715 | 0.97794 | 1.086 | 0.43102 | 1.0449 | 1.163 | -12.9698 | -112.7968 | 112.072 | -16.2185 | -120.5594 | 119.2123
Line_1 | 2.9258 | 0.52552 | 0.44024 | 2.9272 | 0.52375 | 0.43849 | 33.7844 | 6.0681 | 5.0835 | 33.8005 | 6.0477 | 5.0632 | 1.0244e-10 | 6.2513 | -3.7015 | 11.0741 | -6.1908 | 3.7442 | -1.433e-10 | -2.539 | -5.6409 | 9.4661 | 1.268 | 4.545 | 123.2805 | -108.94 | -111.2444 | -56.7421 | 71.0163 | 68.6941 | 0 | 1.1119 | 1.3272 | 0.43102 | 1.0449 | 1.163 | 0 | -131.0444 | 125.4834 | -16.2185 | -120.5594 | 119.2123
Line_2 | 0.55858 | 0.11392 | 0.054939 | 0.5576 | 0.11292 | 0.053941 | 6.4499 | 1.3155 | 0.63438 | 6.4386 | 1.3039 | 0.62285 | 2.3374 | 1.1316 | -0.67666 | -1.7407 | -1.0339 | 0.70674 | 2.4502 | -0.84833 | -0.14737 | -2.1613 | 0.88731 | 0.15893 | -67.3943 | -79.9295 | -73.5948 | 112.6296 | 100.0779 | 106.5386 | 0.52501 | 1.0751 | 1.0917 | 0.43102 | 1.0449 | 1.163 | -21.0456 | -116.7877 | 118.692 | -16.2185 | -120.5594 | 119.2123

## LG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.7664 | 0.20087 | 0.15498 | 0.76623 | 0.20105 | 0.15516 | 8.8496 | 2.3195 | 1.7896 | 8.8477 | 2.3216 | 1.7916 | 7.2317 | -2.1444 | 1.6945 | -6.5469 | 2.1721 | -1.6743 | 5.2198 | 1.1564 | 1.0193 | -4.5246 | -1.2689 | -1.1088 | -40.4265 | 89.8812 | 86.4488 | 139.5806 | -90.1003 | -93.5232 | 1.0078 | 1.0504 | 1.105 | 0.89948 | 1.0836 | 1.1209 | -4.6047 | -118.4554 | 117.4754 | -5.7711 | -120.393 | 119.9923
Line_1 | 0.9414 | 0.16909 | 0.14165 | 0.94185 | 0.16852 | 0.14109 | 10.8704 | 1.9525 | 1.6356 | 10.8756 | 1.9459 | 1.6291 | -6.6521 | 1.9169 | -1.4502 | 7.7998 | -1.907 | 1.4497 | -4.919 | -1.0348 | -1.2253 | 5.9039 | 0.89967 | 1.1104 | 137.128 | -95.0924 | -97.3968 | -42.8945 | 84.8638 | 82.5416 | 0.76108 | 1.1157 | 1.1607 | 0.89948 | 1.0836 | 1.1209 | -6.3904 | -123.4537 | 122.7976 | -5.7711 | -120.393 | 119.9923
Line_2 | 0.17973 | 0.036656 | 0.017677 | 0.17941 | 0.036332 | 0.017356 | 2.0753 | 0.42327 | 0.20412 | 2.0717 | 0.41953 | 0.20041 | 1.316 | 0.27672 | -0.22436 | -1.2529 | -0.26516 | 0.22463 | 1.4118 | -0.36767 | 0.0027145 | -1.3794 | 0.36926 | -0.001544 | -53.5468 | -66.082 | -59.7472 | 126.4771 | 113.9255 | 120.3861 | 0.93 | 1.0872 | 1.0993 | 0.89948 | 1.0836 | 1.1209 | -6.5371 | -119.1161 | 119.5596 | -5.7711 | -120.393 | 119.9923

## LG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.7664 | 0.20087 | 0.15498 | 0.76623 | 0.20105 | 0.15516 | 8.8496 | 2.3195 | 1.7896 | 8.8477 | 2.3216 | 1.7916 | 7.2317 | -2.1444 | 1.6945 | -6.5469 | 2.1721 | -1.6743 | 5.2198 | 1.1564 | 1.0193 | -4.5246 | -1.2689 | -1.1088 | -40.4265 | 89.8812 | 86.4488 | 139.5806 | -90.1003 | -93.5232 | 1.0078 | 1.0504 | 1.105 | 0.89948 | 1.0836 | 1.1209 | -4.6047 | -118.4554 | 117.4754 | -5.7711 | -120.393 | 119.9923
Line_1 | 0.9414 | 0.16909 | 0.14165 | 0.94185 | 0.16852 | 0.14109 | 10.8704 | 1.9525 | 1.6356 | 10.8756 | 1.9459 | 1.6291 | -6.6521 | 1.9169 | -1.4502 | 7.7998 | -1.907 | 1.4497 | -4.919 | -1.0348 | -1.2253 | 5.9039 | 0.89967 | 1.1104 | 137.128 | -95.0924 | -97.3968 | -42.8945 | 84.8638 | 82.5416 | 0.76108 | 1.1157 | 1.1607 | 0.89948 | 1.0836 | 1.1209 | -6.3904 | -123.4537 | 122.7976 | -5.7711 | -120.393 | 119.9923
Line_2 | 0.17973 | 0.036656 | 0.017677 | 0.17941 | 0.036332 | 0.017356 | 2.0753 | 0.42327 | 0.20412 | 2.0717 | 0.41953 | 0.20041 | 1.316 | 0.27672 | -0.22436 | -1.2529 | -0.26516 | 0.22463 | 1.4118 | -0.36767 | 0.0027145 | -1.3794 | 0.36926 | -0.001544 | -53.5468 | -66.082 | -59.7472 | 126.4771 | 113.9255 | 120.3861 | 0.93 | 1.0872 | 1.0993 | 0.89948 | 1.0836 | 1.1209 | -6.5371 | -119.1161 | 119.5596 | -5.7711 | -120.393 | 119.9923

## LG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.5473 | 0.59529 | 0.47396 | 1.5468 | 0.59579 | 0.47446 | 17.8663 | 6.8738 | 5.4728 | 17.8611 | 6.8796 | 5.4785 | 11.0915 | -5.3577 | 5.2687 | -6.8197 | 5.6882 | -5.1039 | 8.2106 | 2.9486 | 1.5712 | -4.4726 | -3.8931 | -2.3545 | -47.9558 | 94.4285 | 96.4271 | 132.0531 | -85.5637 | -83.5652 | 0.7724 | 0.88967 | 1.0046 | 0.45661 | 1.0019 | 1.026 | -11.4445 | -114.3974 | 113.0328 | -14.6886 | -119.952 | 121.1988
Line_1 | 1.9978 | 0.56514 | 0.48868 | 1.9992 | 0.56343 | 0.48697 | 23.0686 | 6.5256 | 5.6428 | 23.0843 | 6.506 | 5.623 | -4.2089e-11 | 6.037 | -4.72 | 8.6183 | -5.8923 | 4.7458 | 1.2462e-11 | -4.2769 | -4.5866 | 6.0685 | 2.7879 | 3.2802 | 130.1905 | -94.6095 | -93.4317 | -49.8395 | 85.3688 | 86.5473 | 0 | 1.1337 | 1.1663 | 0.45661 | 1.0019 | 1.026 | 0 | -129.925 | 130.7472 | -14.6886 | -119.952 | 121.1988
Line_2 | 0.45683 | 0.097697 | 0.083992 | 0.45605 | 0.097144 | 0.083786 | 5.275 | 1.1281 | 0.96986 | 5.266 | 1.1217 | 0.96748 | 2.5195 | -0.076104 | -0.28828 | -1.7986 | 0.20411 | 0.35815 | 1.9231 | -1.1373 | 0.8585 | -1.5959 | 1.1052 | -0.92575 | -56.2863 | -19.8186 | 9.5289 | 123.7288 | 160.5116 | -169.9513 | 0.60086 | 1.0104 | 0.93376 | 0.45661 | 1.0019 | 1.026 | -18.9318 | -113.6469 | 118.0907 | -14.6886 | -119.952 | 121.1988

## LG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.5473 | 0.59529 | 0.47396 | 1.5468 | 0.59579 | 0.47446 | 17.8663 | 6.8738 | 5.4728 | 17.8611 | 6.8796 | 5.4785 | 11.0915 | -5.3577 | 5.2687 | -6.8197 | 5.6882 | -5.1039 | 8.2106 | 2.9486 | 1.5712 | -4.4726 | -3.8931 | -2.3545 | -47.9558 | 94.4285 | 96.4271 | 132.0531 | -85.5637 | -83.5652 | 0.7724 | 0.88967 | 1.0046 | 0.45661 | 1.0019 | 1.026 | -11.4445 | -114.3974 | 113.0328 | -14.6886 | -119.952 | 121.1988
Line_1 | 1.9978 | 0.56514 | 0.48868 | 1.9992 | 0.56343 | 0.48697 | 23.0686 | 6.5256 | 5.6428 | 23.0843 | 6.506 | 5.623 | -4.2089e-11 | 6.037 | -4.72 | 8.6183 | -5.8923 | 4.7458 | 1.2462e-11 | -4.2769 | -4.5866 | 6.0685 | 2.7879 | 3.2802 | 130.1905 | -94.6095 | -93.4317 | -49.8395 | 85.3688 | 86.5473 | 0 | 1.1337 | 1.1663 | 0.45661 | 1.0019 | 1.026 | 0 | -129.925 | 130.7472 | -14.6886 | -119.952 | 121.1988
Line_2 | 0.45683 | 0.097697 | 0.083992 | 0.45605 | 0.097144 | 0.083786 | 5.275 | 1.1281 | 0.96986 | 5.266 | 1.1217 | 0.96748 | 2.5195 | -0.076104 | -0.28828 | -1.7986 | 0.20411 | 0.35815 | 1.9231 | -1.1373 | 0.8585 | -1.5959 | 1.1052 | -0.92575 | -56.2863 | -19.8186 | 9.5289 | 123.7288 | 160.5116 | -169.9513 | 0.60086 | 1.0104 | 0.93376 | 0.45661 | 1.0019 | 1.026 | -18.9318 | -113.6469 | 118.0907 | -14.6886 | -119.952 | 121.1988

## LG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.55778 | 0.2146 | 0.17086 | 0.55762 | 0.21478 | 0.17104 | 6.4406 | 2.478 | 1.9729 | 6.4388 | 2.48 | 1.975 | 5.0689 | -1.682 | 1.9623 | -4.513 | 1.7256 | -1.9423 | 3.167 | 1.6594 | 0.33136 | -2.6801 | -1.7834 | -0.4331 | -36.4246 | 105.9597 | 107.9583 | 143.5843 | -74.0324 | -72.034 | 0.928 | 0.95353 | 1.0087 | 0.81518 | 1.0006 | 1.0076 | -4.4277 | -118.6525 | 117.5429 | -5.7117 | -119.975 | 120.5366
Line_1 | 0.72019 | 0.20373 | 0.17616 | 0.72068 | 0.20311 | 0.17555 | 8.316 | 2.3524 | 2.0342 | 8.3217 | 2.3454 | 2.0271 | -4.5936 | 1.8991 | -1.8888 | 5.7152 | -1.8773 | 1.8876 | -2.8616 | -1.6053 | -0.95078 | 3.6545 | 1.4083 | 0.78023 | 141.7217 | -83.0783 | -81.9005 | -38.3083 | 96.9 | 98.0785 | 0.65079 | 1.0571 | 1.0395 | 0.81518 | 1.0006 | 1.0076 | -6.3575 | -123.2868 | 124.8194 | -5.7117 | -119.975 | 120.5366
Line_2 | 0.16468 | 0.035219 | 0.030279 | 0.1644 | 0.035019 | 0.030204 | 1.9016 | 0.40667 | 0.34963 | 1.8984 | 0.40437 | 0.34877 | 1.2973 | -0.13443 | -0.047715 | -1.2022 | 0.15169 | 0.054712 | 1.0186 | -0.38132 | 0.33887 | -0.97448 | 0.37511 | -0.34713 | -44.7551 | -8.2874 | 21.0601 | 135.26 | 172.0428 | -158.4201 | 0.86736 | 0.99422 | 0.97879 | 0.81518 | 1.0006 | 1.0076 | -6.618 | -117.7062 | 119.0751 | -5.7117 | -119.975 | 120.5366

## LG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.55778 | 0.2146 | 0.17086 | 0.55762 | 0.21478 | 0.17104 | 6.4406 | 2.478 | 1.9729 | 6.4388 | 2.48 | 1.975 | 5.0689 | -1.682 | 1.9623 | -4.513 | 1.7256 | -1.9423 | 3.167 | 1.6594 | 0.33136 | -2.6801 | -1.7834 | -0.4331 | -36.4246 | 105.9597 | 107.9583 | 143.5843 | -74.0324 | -72.034 | 0.928 | 0.95353 | 1.0087 | 0.81518 | 1.0006 | 1.0076 | -4.4277 | -118.6525 | 117.5429 | -5.7117 | -119.975 | 120.5366
Line_1 | 0.72019 | 0.20373 | 0.17616 | 0.72068 | 0.20311 | 0.17555 | 8.316 | 2.3524 | 2.0342 | 8.3217 | 2.3454 | 2.0271 | -4.5936 | 1.8991 | -1.8888 | 5.7152 | -1.8773 | 1.8876 | -2.8616 | -1.6053 | -0.95078 | 3.6545 | 1.4083 | 0.78023 | 141.7217 | -83.0783 | -81.9005 | -38.3083 | 96.9 | 98.0785 | 0.65079 | 1.0571 | 1.0395 | 0.81518 | 1.0006 | 1.0076 | -6.3575 | -123.2868 | 124.8194 | -5.7117 | -119.975 | 120.5366
Line_2 | 0.16468 | 0.035219 | 0.030279 | 0.1644 | 0.035019 | 0.030204 | 1.9016 | 0.40667 | 0.34963 | 1.8984 | 0.40437 | 0.34877 | 1.2973 | -0.13443 | -0.047715 | -1.2022 | 0.15169 | 0.054712 | 1.0186 | -0.38132 | 0.33887 | -0.97448 | 0.37511 | -0.34713 | -44.7551 | -8.2874 | 21.0601 | 135.26 | 172.0428 | -158.4201 | 0.86736 | 0.99422 | 0.97879 | 0.81518 | 1.0006 | 1.0076 | -6.618 | -117.7062 | 119.0751 | -5.7117 | -119.975 | 120.5366

## LLG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.49447 | 3.4232 | 2.5333 | 0.49487 | 3.4231 | 2.5331 | 5.7097 | 39.5271 | 29.2519 | 5.7142 | 39.5266 | 29.2497 | -2.3067 | 26.9458 | -0.19158 | 2.7607 | -14.8677 | 0.018223 | 5.0961 | 10.3943 | 15.9092 | -5.7784 | -4.7368 | -9.2672 | -116.2123 | -172.5148 | 34.7182 | 63.8254 | 7.4937 | -145.2926 | 0.97971 | 0.73066 | 0.54391 | 1.1207 | 0.39477 | 0.31683 | -1.8585 | -151.4208 | 125.4081 | -0.63779 | -154.8347 | 124.8201
Line_1 | 0.4216 | 4.0485 | 3.0228 | 0.42021 | 4.0484 | 3.0238 | 4.8683 | 46.7485 | 34.9046 | 4.8522 | 46.7473 | 34.9153 | 2.5233 | 1.1467e-10 | 1.0947e-10 | -2.2691 | 17.3432 | 0.54299 | -5.8271 | -1.0247e-10 | -2.8326e-11 | 4.9418 | 6.3073 | 11.0489 | 64.7937 | 5.2021 | -142.3902 | -115.3006 | -174.8199 | 37.6336 | 1.3044 | 0 | 0 | 1.1207 | 0.39477 | 0.31683 | -1.7922 | 0 | 0 | -0.63779 | -154.8347 | 124.8201
Line_2 | 0.075565 | 0.64349 | 0.51111 | 0.074981 | 0.64314 | 0.5106 | 0.87255 | 7.4304 | 5.9017 | 0.86581 | 7.4264 | 5.8959 | 0.50579 | 3.028 | 0.75666 | -0.49162 | -2.4756 | -0.56121 | -0.79444 | 1.5387 | 2.2807 | 0.83657 | -1.5706 | -1.7817 | 59.4053 | 172.7025 | 52.3823 | -121.0788 | -7.2272 | -127.6963 | 1.0793 | 0.45711 | 0.40715 | 1.1207 | 0.39477 | 0.31683 | 1.889 | -160.3595 | 124.028 | -0.63779 | -154.8347 | 124.8201

## LLG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.49447 | 3.4232 | 2.5333 | 0.49487 | 3.4231 | 2.5331 | 5.7097 | 39.5271 | 29.2519 | 5.7142 | 39.5266 | 29.2497 | -2.3067 | 26.9458 | -0.19158 | 2.7607 | -14.8677 | 0.018223 | 5.0961 | 10.3943 | 15.9092 | -5.7784 | -4.7368 | -9.2672 | -116.2123 | -172.5148 | 34.7182 | 63.8254 | 7.4937 | -145.2926 | 0.97971 | 0.73066 | 0.54391 | 1.1207 | 0.39477 | 0.31683 | -1.8585 | -151.4208 | 125.4081 | -0.63779 | -154.8347 | 124.8201
Line_1 | 0.4216 | 4.0485 | 3.0228 | 0.42021 | 4.0484 | 3.0238 | 4.8683 | 46.7485 | 34.9046 | 4.8522 | 46.7473 | 34.9153 | 2.5233 | 1.1467e-10 | 1.0947e-10 | -2.2691 | 17.3432 | 0.54299 | -5.8271 | -1.0247e-10 | -2.8326e-11 | 4.9418 | 6.3073 | 11.0489 | 64.7937 | 5.2021 | -142.3902 | -115.3006 | -174.8199 | 37.6336 | 1.3044 | 0 | 0 | 1.1207 | 0.39477 | 0.31683 | -1.7922 | 0 | 0 | -0.63779 | -154.8347 | 124.8201
Line_2 | 0.075565 | 0.64349 | 0.51111 | 0.074981 | 0.64314 | 0.5106 | 0.87255 | 7.4304 | 5.9017 | 0.86581 | 7.4264 | 5.8959 | 0.50579 | 3.028 | 0.75666 | -0.49162 | -2.4756 | -0.56121 | -0.79444 | 1.5387 | 2.2807 | 0.83657 | -1.5706 | -1.7817 | 59.4053 | 172.7025 | 52.3823 | -121.0788 | -7.2272 | -127.6963 | 1.0793 | 0.45711 | 0.40715 | 1.1207 | 0.39477 | 0.31683 | 1.889 | -160.3595 | 124.028 | -0.63779 | -154.8347 | 124.8201

## LLG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.17996 | 0.96958 | 0.7596 | 0.1801 | 0.96958 | 0.75949 | 2.078 | 11.1957 | 8.7711 | 2.0797 | 11.1958 | 8.7698 | -0.48044 | 9.8526 | 4.5263 | 0.53052 | -8.7859 | -4.4896 | 2.1447 | 5.6293 | 6.9418 | -2.2358 | -5.2665 | -6.2033 | -103.6738 | -157.68 | 60.1579 | 76.3593 | 22.3306 | -119.8527 | 1.0577 | 1.0135 | 0.94481 | 1.1049 | 0.91494 | 0.87317 | -1.0475 | -127.9386 | 117.0523 | -0.29242 | -126.7297 | 114.2525
Line_1 | 0.15265 | 1.1414 | 0.9254 | 0.15215 | 1.1413 | 0.92584 | 1.7627 | 13.1794 | 10.6856 | 1.7568 | 13.1783 | 10.6906 | 0.49053 | -8.5319 | -5.6255 | -0.46517 | 10.0401 | 5.8194 | -2.0024 | -6.3317 | -6.0761 | 1.8846 | 6.6764 | 7.2988 | 75.9252 | 19.6749 | -117.202 | -104.1571 | -160.3522 | 62.8182 | 1.1696 | 0.80616 | 0.77492 | 1.1049 | 0.91494 | 0.87317 | -0.31032 | -123.7454 | 110.0032 | -0.29242 | -126.7297 | 114.2525
Line_2 | 0.028245 | 0.17872 | 0.17111 | 0.027997 | 0.17861 | 0.17088 | 0.32614 | 2.0637 | 1.9758 | 0.32328 | 2.0625 | 1.9731 | 0.067327 | 1.3005 | 1.3645 | -0.065347 | -1.2543 | -1.3298 | -0.34824 | 1.4019 | 1.1504 | 0.35118 | -1.4098 | -1.0954 | 79.5263 | -175.1633 | 74.8373 | -100.8336 | 4.9284 | -105.2283 | 1.0875 | 0.92661 | 0.90328 | 1.1049 | 0.91494 | 0.87317 | 0.46855 | -128.0131 | 114.9699 | -0.29242 | -126.7297 | 114.2525

## LLG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.17996 | 0.96958 | 0.7596 | 0.1801 | 0.96958 | 0.75949 | 2.078 | 11.1957 | 8.7711 | 2.0797 | 11.1958 | 8.7698 | -0.48044 | 9.8526 | 4.5263 | 0.53052 | -8.7859 | -4.4896 | 2.1447 | 5.6293 | 6.9418 | -2.2358 | -5.2665 | -6.2033 | -103.6738 | -157.68 | 60.1579 | 76.3593 | 22.3306 | -119.8527 | 1.0577 | 1.0135 | 0.94481 | 1.1049 | 0.91494 | 0.87317 | -1.0475 | -127.9386 | 117.0523 | -0.29242 | -126.7297 | 114.2525
Line_1 | 0.15265 | 1.1414 | 0.9254 | 0.15215 | 1.1413 | 0.92584 | 1.7627 | 13.1794 | 10.6856 | 1.7568 | 13.1783 | 10.6906 | 0.49053 | -8.5319 | -5.6255 | -0.46517 | 10.0401 | 5.8194 | -2.0024 | -6.3317 | -6.0761 | 1.8846 | 6.6764 | 7.2988 | 75.9252 | 19.6749 | -117.202 | -104.1571 | -160.3522 | 62.8182 | 1.1696 | 0.80616 | 0.77492 | 1.1049 | 0.91494 | 0.87317 | -0.31032 | -123.7454 | 110.0032 | -0.29242 | -126.7297 | 114.2525
Line_2 | 0.028245 | 0.17872 | 0.17111 | 0.027997 | 0.17861 | 0.17088 | 0.32614 | 2.0637 | 1.9758 | 0.32328 | 2.0625 | 1.9731 | 0.067327 | 1.3005 | 1.3645 | -0.065347 | -1.2543 | -1.3298 | -0.34824 | 1.4019 | 1.1504 | 0.35118 | -1.4098 | -1.0954 | 79.5263 | -175.1633 | 74.8373 | -100.8336 | 4.9284 | -105.2283 | 1.0875 | 0.92661 | 0.90328 | 1.1049 | 0.91494 | 0.87317 | 0.46855 | -128.0131 | 114.9699 | -0.29242 | -126.7297 | 114.2525

## LLG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.4355 | 2.4893 | 2.1555 | 0.43587 | 2.4894 | 2.1554 | 5.0288 | 28.7441 | 24.89 | 5.033 | 28.7447 | 24.8879 | -0.743 | 22.9921 | 4.0165 | 1.1257 | -13.037 | -2.119 | 4.4999 | 3.2284 | 12.3626 | -5.0578 | -0.78761 | -7.5625 | -100.7576 | -156.5469 | 42.4398 | 79.2671 | 23.4626 | -137.5701 | 0.90695 | 0.80774 | 0.52225 | 1.0295 | 0.45437 | 0.31556 | -1.3818 | -148.554 | 114.4413 | 1.8149 | -153.0802 | 116.777
Line_1 | 0.42667 | 3.0654 | 2.5762 | 0.42533 | 3.065 | 2.5771 | 4.9268 | 35.396 | 29.7475 | 4.9113 | 35.3919 | 29.7578 | 1.5984 | -1.0744e-10 | -4.1505e-11 | -1.3314 | 15.9605 | 2.8428 | -5.8268 | -6.9463e-11 | -9.9886e-11 | 4.8778 | 1.9658 | 8.9499 | 76.6082 | 19.9237 | -135.6255 | -103.452 | -160.1018 | 44.3988 | 1.2264 | 0 | 0 | 1.0295 | 0.45437 | 0.31556 | 1.9479 | 0 | 0 | 1.8149 | -153.0802 | 116.777
Line_2 | 0.023591 | 0.601 | 0.42975 | 0.022992 | 0.60075 | 0.42945 | 0.2724 | 6.9398 | 4.9623 | 0.26549 | 6.9369 | 4.9589 | -0.18535 | 3.7571 | 0.88606 | 0.20566 | -2.9234 | -0.72381 | -0.18353 | 1.0357 | 1.9202 | 0.18003 | -1.1782 | -1.3874 | 139.9969 | -175.0878 | 54.4054 | -39.3822 | 4.9694 | -125.6718 | 0.95755 | 0.56158 | 0.42618 | 1.0295 | 0.45437 | 0.31556 | 4.7145 | -159.6762 | 119.6354 | 1.8149 | -153.0802 | 116.777

## LLG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.4355 | 2.4893 | 2.1555 | 0.43587 | 2.4894 | 2.1554 | 5.0288 | 28.7441 | 24.89 | 5.033 | 28.7447 | 24.8879 | -0.743 | 22.9921 | 4.0165 | 1.1257 | -13.037 | -2.119 | 4.4999 | 3.2284 | 12.3626 | -5.0578 | -0.78761 | -7.5625 | -100.7576 | -156.5469 | 42.4398 | 79.2671 | 23.4626 | -137.5701 | 0.90695 | 0.80774 | 0.52225 | 1.0295 | 0.45437 | 0.31556 | -1.3818 | -148.554 | 114.4413 | 1.8149 | -153.0802 | 116.777
Line_1 | 0.42667 | 3.0654 | 2.5762 | 0.42533 | 3.065 | 2.5771 | 4.9268 | 35.396 | 29.7475 | 4.9113 | 35.3919 | 29.7578 | 1.5984 | -1.0744e-10 | -4.1505e-11 | -1.3314 | 15.9605 | 2.8428 | -5.8268 | -6.9463e-11 | -9.9886e-11 | 4.8778 | 1.9658 | 8.9499 | 76.6082 | 19.9237 | -135.6255 | -103.452 | -160.1018 | 44.3988 | 1.2264 | 0 | 0 | 1.0295 | 0.45437 | 0.31556 | 1.9479 | 0 | 0 | 1.8149 | -153.0802 | 116.777
Line_2 | 0.023591 | 0.601 | 0.42975 | 0.022992 | 0.60075 | 0.42945 | 0.2724 | 6.9398 | 4.9623 | 0.26549 | 6.9369 | 4.9589 | -0.18535 | 3.7571 | 0.88606 | 0.20566 | -2.9234 | -0.72381 | -0.18353 | 1.0357 | 1.9202 | 0.18003 | -1.1782 | -1.3874 | 139.9969 | -175.0878 | 54.4054 | -39.3822 | 4.9694 | -125.6718 | 0.95755 | 0.56158 | 0.42618 | 1.0295 | 0.45437 | 0.31556 | 4.7145 | -159.6762 | 119.6354 | 1.8149 | -153.0802 | 116.777

## LLG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.17763 | 0.76042 | 0.63681 | 0.17779 | 0.76045 | 0.63672 | 2.0511 | 8.7806 | 7.3533 | 2.0529 | 8.7809 | 7.3522 | 0.1474 | 7.7901 | 3.4972 | -0.094296 | -6.7478 | -3.3793 | 1.9714 | 2.8059 | 5.3318 | -2.0667 | -2.6135 | -4.8014 | -86.7849 | -147.6069 | 59.7796 | 93.2354 | 32.4057 | -120.2328 | 0.96384 | 0.94299 | 0.86715 | 1.0078 | 0.82409 | 0.79859 | -1.0609 | -127.7987 | 116.5178 | 0.62298 | -126.4226 | 114.6288
Line_1 | 0.17439 | 0.94016 | 0.77166 | 0.17384 | 0.94002 | 0.77209 | 2.0137 | 10.8561 | 8.9104 | 2.0074 | 10.8544 | 8.9153 | 0.10154 | -6.389 | -4.143 | -0.067979 | 8.0889 | 4.3883 | -2.1827 | -3.7299 | -4.5783 | 2.0218 | 3.8187 | 5.6065 | 88.7469 | 28.3394 | -117.3484 | -91.3027 | -151.6944 | 62.6797 | 1.0851 | 0.68147 | 0.69297 | 1.0078 | 0.82409 | 0.79859 | 1.4102 | -121.3847 | 110.5091 | 0.62298 | -126.4226 | 114.6288
Line_2 | 0.014675 | 0.1896 | 0.14015 | 0.014469 | 0.18949 | 0.13998 | 0.16945 | 2.1893 | 1.6183 | 0.16707 | 2.188 | 1.6164 | -0.15804 | 1.4385 | 1.0402 | 0.16228 | -1.3411 | -1.009 | -0.04804 | 1.1855 | 0.87144 | 0.044888 | -1.2053 | -0.80508 | 164.5186 | -168.4408 | 76.1252 | -14.8394 | 11.6313 | -103.9575 | 0.9748 | 0.85143 | 0.8385 | 1.0078 | 0.82409 | 0.79859 | 1.4268 | -128.9461 | 116.0808 | 0.62298 | -126.4226 | 114.6288

## LLG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.17763 | 0.76042 | 0.63681 | 0.17779 | 0.76045 | 0.63672 | 2.0511 | 8.7806 | 7.3533 | 2.0529 | 8.7809 | 7.3522 | 0.1474 | 7.7901 | 3.4972 | -0.094296 | -6.7478 | -3.3793 | 1.9714 | 2.8059 | 5.3318 | -2.0667 | -2.6135 | -4.8014 | -86.7849 | -147.6069 | 59.7796 | 93.2354 | 32.4057 | -120.2328 | 0.96384 | 0.94299 | 0.86715 | 1.0078 | 0.82409 | 0.79859 | -1.0609 | -127.7987 | 116.5178 | 0.62298 | -126.4226 | 114.6288
Line_1 | 0.17439 | 0.94016 | 0.77166 | 0.17384 | 0.94002 | 0.77209 | 2.0137 | 10.8561 | 8.9104 | 2.0074 | 10.8544 | 8.9153 | 0.10154 | -6.389 | -4.143 | -0.067979 | 8.0889 | 4.3883 | -2.1827 | -3.7299 | -4.5783 | 2.0218 | 3.8187 | 5.6065 | 88.7469 | 28.3394 | -117.3484 | -91.3027 | -151.6944 | 62.6797 | 1.0851 | 0.68147 | 0.69297 | 1.0078 | 0.82409 | 0.79859 | 1.4102 | -121.3847 | 110.5091 | 0.62298 | -126.4226 | 114.6288
Line_2 | 0.014675 | 0.1896 | 0.14015 | 0.014469 | 0.18949 | 0.13998 | 0.16945 | 2.1893 | 1.6183 | 0.16707 | 2.188 | 1.6164 | -0.15804 | 1.4385 | 1.0402 | 0.16228 | -1.3411 | -1.009 | -0.04804 | 1.1855 | 0.87144 | 0.044888 | -1.2053 | -0.80508 | 164.5186 | -168.4408 | 76.1252 | -14.8394 | 11.6313 | -103.9575 | 0.9748 | 0.85143 | 0.8385 | 1.0078 | 0.82409 | 0.79859 | 1.4268 | -128.9461 | 116.0808 | 0.62298 | -126.4226 | 114.6288