## LLL_max_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 3.6473 | 3.6473 | 0 | 0 | 126.3464 | 126.3464 | 35.9247 | -15.1722 | 40.9065 | -17.3604 | -73.1767 | 106.8233 | 0.43089 | 0.18248 | -24.4668 | -24.3287
Line_1 | 2.6793 | 2.6793 | 5.3365 | 0 | 92.8137 | 92.8137 | -1e-07 | 11.1987 | -1e-07 | 12.7062 | 107.0629 | -72.9371 | 0 | 0.18248 | 0 | -24.3287
Line_2 | 0.96809 | 0.96809 | 0 | 0 | 33.5358 | 33.5358 | -2.5115 | 3.9735 | -2.9954 | 4.6542 | 106.1604 | -73.8396 | 0.11656 | 0.18248 | -23.8181 | -24.3287
Line_3 | 1.7114 | 1.7114 | 3.4087 | 0 | 59.2845 | 59.2845 | -1e-07 | 4.569 | -1e-07 | 5.1841 | 107.5734 | -72.4266 | 0 | 0.11656 | 0 | -23.8181

## LLL_max_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 3.6473 | 3.6473 | 0 | 0 | 126.3464 | 126.3464 | 35.9247 | -15.1722 | 40.9065 | -17.3604 | -73.1767 | 106.8233 | 0.43089 | 0.18248 | -24.4668 | -24.3287
Line_1 | 2.6793 | 2.6793 | 5.3365 | 0 | 92.8137 | 92.8137 | -1e-07 | 11.1987 | -1e-07 | 12.7062 | 107.0629 | -72.9371 | 0 | 0.18248 | 0 | -24.3287
Line_2 | 0.96809 | 0.96809 | 0 | 0 | 33.5358 | 33.5358 | -2.5115 | 3.9735 | -2.9954 | 4.6542 | 106.1604 | -73.8396 | 0.11656 | 0.18248 | -23.8181 | -24.3287
Line_3 | 1.7114 | 1.7114 | 3.4087 | 0 | 59.2845 | 59.2845 | -1e-07 | 4.569 | -1e-07 | 5.1841 | 107.5734 | -72.4266 | 0 | 0.11656 | 0 | -23.8181

## LLL_max_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.95594 | 0.95594 | 0 | 0 | 33.1147 | 33.1147 | 21.9414 | -20.5158 | 22.5228 | -20.9053 | -52.3773 | 127.6227 | 0.94954 | 0.88451 | -6.6281 | -6.8385
Line_1 | 0.70223 | 0.70223 | 1.3987 | 0 | 24.326 | 24.326 | -14.3657 | 15.1349 | -14.421 | 15.2938 | 127.8623 | -52.1377 | 0.83677 | 0.88451 | -7.0275 | -6.8385
Line_2 | 0.25373 | 0.25373 | 0 | 0 | 8.7895 | 8.7895 | -5.2804 | 5.3809 | -5.4975 | 5.6115 | 126.9598 | -53.0402 | 0.86725 | 0.88451 | -6.8864 | -6.8385
Line_3 | 0.44855 | 0.44855 | 0.8934 | 0 | 15.5381 | 15.5381 | -9.2577 | 9.5716 | -9.1293 | 9.4854 | 128.3728 | -51.6272 | 0.83677 | 0.86725 | -7.0275 | -6.8864

## LLL_max_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.95594 | 0.95594 | 0 | 0 | 33.1147 | 33.1147 | 21.9414 | -20.5158 | 22.5228 | -20.9053 | -52.3773 | 127.6227 | 0.94954 | 0.88451 | -6.6281 | -6.8385
Line_1 | 0.70223 | 0.70223 | 1.3987 | 0 | 24.326 | 24.326 | -14.3657 | 15.1349 | -14.421 | 15.2938 | 127.8623 | -52.1377 | 0.83677 | 0.88451 | -7.0275 | -6.8385
Line_2 | 0.25373 | 0.25373 | 0 | 0 | 8.7895 | 8.7895 | -5.2804 | 5.3809 | -5.4975 | 5.6115 | 126.9598 | -53.0402 | 0.86725 | 0.88451 | -6.8864 | -6.8385
Line_3 | 0.44855 | 0.44855 | 0.8934 | 0 | 15.5381 | 15.5381 | -9.2577 | 9.5716 | -9.1293 | 9.4854 | 128.3728 | -51.6272 | 0.83677 | 0.86725 | -7.0275 | -6.8864

## LLL_min_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 2.9516 | 2.9516 | 0 | 0 | 102.2474 | 102.2474 | 45.756 | -19.6615 | 26.7104 | -11.29 | -61.5111 | 118.4889 | 0.51817 | 0.22174 | -31.2365 | -31.6459
Line_1 | 2.2078 | 2.2078 | 3.9682 | 0 | 76.4821 | 76.4821 | -1e-07 | 14.6004 | -1e-07 | 8.628 | 117.7734 | -62.2266 | 0 | 0.22174 | 0 | -31.6459
Line_2 | 0.74446 | 0.74446 | 0 | 0 | 25.7889 | 25.7889 | -3.4011 | 5.0611 | -1.681 | 2.6619 | 120.6115 | -59.3885 | 0.14711 | 0.22174 | -33.0879 | -31.6459
Line_3 | 1.4648 | 1.4648 | 2.6326 | 0 | 50.7409 | 50.7409 | -1e-07 | 6.4263 | -1e-07 | 3.7976 | 116.3313 | -63.6687 | 0 | 0.14711 | 0 | -33.0879

## LLL_min_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 2.9516 | 2.9516 | 0 | 0 | 102.2474 | 102.2474 | 45.756 | -19.6615 | 26.7104 | -11.29 | -61.5111 | 118.4889 | 0.51817 | 0.22174 | -31.2365 | -31.6459
Line_1 | 2.2078 | 2.2078 | 3.9682 | 0 | 76.4821 | 76.4821 | -1e-07 | 14.6004 | -1e-07 | 8.628 | 117.7734 | -62.2266 | 0 | 0.22174 | 0 | -31.6459
Line_2 | 0.74446 | 0.74446 | 0 | 0 | 25.7889 | 25.7889 | -3.4011 | 5.0611 | -1.681 | 2.6619 | 120.6115 | -59.3885 | 0.14711 | 0.22174 | -33.0879 | -31.6459
Line_3 | 1.4648 | 1.4648 | 2.6326 | 0 | 50.7409 | 50.7409 | -1e-07 | 6.4263 | -1e-07 | 3.7976 | 116.3313 | -63.6687 | 0 | 0.14711 | 0 | -33.0879

## LLL_min_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.79717 | 0.79717 | 0 | 0 | 27.6148 | 27.6148 | 18.6059 | -16.7025 | 15.5964 | -14.4716 | -47.0211 | 132.9789 | 0.87917 | 0.80029 | -7.0497 | -6.1144
Line_1 | 0.59629 | 0.59629 | 1.0717 | 0 | 20.6561 | 20.6561 | -11.2925 | 12.3575 | -10.3507 | 10.9801 | 132.2633 | -47.7367 | 0.7416 | 0.80029 | -5.2282 | -6.1144
Line_2 | 0.20106 | 0.20106 | 0 | 0 | 6.965 | 6.965 | -4.2239 | 4.345 | -3.4199 | 3.4915 | 135.1015 | -44.8985 | 0.78031 | 0.80029 | -5.9028 | -6.1144
Line_3 | 0.3956 | 0.3956 | 0.71101 | 0 | 13.704 | 13.704 | -7.3166 | 7.7854 | -7.0534 | 7.3304 | 130.8213 | -49.1787 | 0.7416 | 0.78031 | -5.2282 | -5.9028

## LLL_min_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.79717 | 0.79717 | 0 | 0 | 27.6148 | 27.6148 | 18.6059 | -16.7025 | 15.5964 | -14.4716 | -47.0211 | 132.9789 | 0.87917 | 0.80029 | -7.0497 | -6.1144
Line_1 | 0.59629 | 0.59629 | 1.0717 | 0 | 20.6561 | 20.6561 | -11.2925 | 12.3575 | -10.3507 | 10.9801 | 132.2633 | -47.7367 | 0.7416 | 0.80029 | -5.2282 | -6.1144
Line_2 | 0.20106 | 0.20106 | 0 | 0 | 6.965 | 6.965 | -4.2239 | 4.345 | -3.4199 | 3.4915 | 135.1015 | -44.8985 | 0.78031 | 0.80029 | -5.9028 | -6.1144
Line_3 | 0.3956 | 0.3956 | 0.71101 | 0 | 13.704 | 13.704 | -7.3166 | 7.7854 | -7.0534 | 7.3304 | 130.8213 | -49.1787 | 0.7416 | 0.78031 | -5.2282 | -5.9028

## LL_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.16767 | 3.0916 | 3.2377 | 0.16767 | 3.0916 | 3.2377 | 1.9361 | 35.6989 | 37.3862 | 1.9361 | 35.6989 | 37.3862 | -2.0827 | 27.9998 | -10.9539 | 2.0973 | -23.0296 | 16.405 | -0.52411 | 4.3805 | 15.7348 | 0.5407 | 1.2588 | -9.5499 | 167.548 | -162.3322 | 16.1787 | -12.452 | 17.6678 | -163.8213 | 1.1092 | 0.79387 | 0.51281 | 1.1187 | 0.64607 | 0.50773 | 1.6735 | -153.4406 | 141.0226 | 2.0047 | -165.4608 | 165.9736
Line_1 | 0.085685 | 2.2727 | 2.3472 | 0.085685 | 2.2727 | 2.3472 | 0.9894 | 26.2428 | 27.1034 | 0.9894 | 26.2428 | 27.1034 | 1.0722 | -14.2537 | 14.7898 | -1.0684 | 16.9395 | -11.9249 | 0.29329 | 3.7641 | -3.6175 | -0.28895 | -0.7167 | 6.8681 | -13.1289 | 16.9619 | -164.0868 | 166.8711 | -163.0381 | 15.9132 | 1.1235 | 0.56177 | 0.56177 | 1.1187 | 0.64607 | 0.50773 | 2.1688 | -177.8312 | -177.8312 | 2.0047 | -165.4608 | 165.9736
Line_2 | 0.082 | 0.81957 | 0.89061 | 0.082 | 0.81957 | 0.89061 | 0.94685 | 9.4636 | 10.2839 | 0.94685 | 9.4636 | 10.2839 | 1.0323 | -5.7408 | 4.8926 | -1.0289 | 6.0901 | -4.4801 | 0.25571 | 0.93837 | -2.2138 | -0.25175 | -0.54207 | 2.6818 | -11.7447 | 19.6256 | -163.1216 | 168.2553 | -160.3744 | 16.8784 | 1.1232 | 0.61467 | 0.52219 | 1.1187 | 0.64607 | 0.50773 | 2.1675 | -169.6577 | 172.5323 | 2.0047 | -165.4608 | 165.9736
Line_3 | 0.0042047 | 1.4545 | 1.4568 | 0.0042047 | 1.4545 | 1.4568 | 0.048552 | 16.7952 | 16.8219 | 0.048552 | 16.7952 | 16.8219 | 0.039633 | -9.1822 | 9.202 | -0.039624 | 10.2823 | -8.0984 | 0.037482 | 2.1693 | -2.1506 | -0.037472 | -0.92111 | 3.4027 | -41.2335 | 15.4613 | -164.6769 | 138.7665 | -164.5387 | 15.3231 | 1.1235 | 0.56177 | 0.56177 | 1.1232 | 0.61467 | 0.52219 | 2.1688 | -177.8312 | -177.8312 | 2.1675 | -169.6577 | 172.5323

## LL_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.16767 | 3.0916 | 3.2377 | 0.16767 | 3.0916 | 3.2377 | 1.9361 | 35.6989 | 37.3862 | 1.9361 | 35.6989 | 37.3862 | -2.0827 | 27.9998 | -10.9539 | 2.0973 | -23.0296 | 16.405 | -0.52411 | 4.3805 | 15.7348 | 0.5407 | 1.2588 | -9.5499 | 167.548 | -162.3322 | 16.1787 | -12.452 | 17.6678 | -163.8213 | 1.1092 | 0.79387 | 0.51281 | 1.1187 | 0.64607 | 0.50773 | 1.6735 | -153.4406 | 141.0226 | 2.0047 | -165.4608 | 165.9736
Line_1 | 0.085685 | 2.2727 | 2.3472 | 0.085685 | 2.2727 | 2.3472 | 0.9894 | 26.2428 | 27.1034 | 0.9894 | 26.2428 | 27.1034 | 1.0722 | -14.2537 | 14.7898 | -1.0684 | 16.9395 | -11.9249 | 0.29329 | 3.7641 | -3.6175 | -0.28895 | -0.7167 | 6.8681 | -13.1289 | 16.9619 | -164.0868 | 166.8711 | -163.0381 | 15.9132 | 1.1235 | 0.56177 | 0.56177 | 1.1187 | 0.64607 | 0.50773 | 2.1688 | -177.8312 | -177.8312 | 2.0047 | -165.4608 | 165.9736
Line_2 | 0.082 | 0.81957 | 0.89061 | 0.082 | 0.81957 | 0.89061 | 0.94685 | 9.4636 | 10.2839 | 0.94685 | 9.4636 | 10.2839 | 1.0323 | -5.7408 | 4.8926 | -1.0289 | 6.0901 | -4.4801 | 0.25571 | 0.93837 | -2.2138 | -0.25175 | -0.54207 | 2.6818 | -11.7447 | 19.6256 | -163.1216 | 168.2553 | -160.3744 | 16.8784 | 1.1232 | 0.61467 | 0.52219 | 1.1187 | 0.64607 | 0.50773 | 2.1675 | -169.6577 | 172.5323 | 2.0047 | -165.4608 | 165.9736
Line_3 | 0.0042047 | 1.4545 | 1.4568 | 0.0042047 | 1.4545 | 1.4568 | 0.048552 | 16.7952 | 16.8219 | 0.048552 | 16.7952 | 16.8219 | 0.039633 | -9.1822 | 9.202 | -0.039624 | 10.2823 | -8.0984 | 0.037482 | 2.1693 | -2.1506 | -0.037472 | -0.92111 | 3.4027 | -41.2335 | 15.4613 | -164.6769 | 138.7665 | -164.5387 | 15.3231 | 1.1235 | 0.56177 | 0.56177 | 1.1232 | 0.61467 | 0.52219 | 2.1688 | -177.8312 | -177.8312 | 2.1675 | -169.6577 | 172.5323

## LL_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.071598 | 1.3201 | 1.3825 | 0.071598 | 1.3201 | 1.3825 | 0.82674 | 15.2438 | 15.9643 | 0.82674 | 15.2438 | 15.9643 | -0.90611 | 15.0577 | 0.99002 | 0.90878 | -14.1515 | 0.0039296 | 0.071765 | 2.9587 | 13.1075 | -0.06874 | -1.9304 | -11.9797 | -174.7256 | -144.6058 | 33.905 | 5.2744 | 35.3942 | -146.095 | 1.0994 | 1.0067 | 0.82339 | 1.1024 | 0.93694 | 0.75041 | 0.74599 | -133.4895 | 119.5857 | 0.94877 | -136.8379 | 123.9238
Line_1 | 0.036588 | 0.97046 | 1.0023 | 0.036588 | 0.97046 | 1.0023 | 0.42248 | 11.2059 | 11.5734 | 0.42248 | 11.2059 | 11.5734 | 0.46549 | -9.895 | 0.56547 | -0.46479 | 10.3847 | -0.043093 | -0.028849 | -0.99149 | -8.092 | 0.029639 | 1.5471 | 8.6847 | 4.5975 | 34.6883 | -146.3605 | -175.4025 | -145.3117 | 33.6395 | 1.1039 | 0.88743 | 0.70089 | 1.1024 | 0.93694 | 0.75041 | 1.051 | -139.5897 | 127.6369 | 0.94877 | -136.8379 | 123.9238
Line_2 | 0.035015 | 0.34997 | 0.3803 | 0.035015 | 0.34997 | 0.3803 | 0.40431 | 4.041 | 4.3913 | 0.40431 | 4.041 | 4.3913 | 0.44463 | -3.7031 | 0.036043 | -0.44399 | 3.7668 | 0.039163 | -0.038378 | -0.31102 | -3.2097 | 0.039101 | 0.38328 | 3.2951 | 5.9817 | 37.352 | -145.3952 | -174.0183 | -142.648 | 34.6048 | 1.1038 | 0.9196 | 0.73097 | 1.1024 | 0.93694 | 0.75041 | 1.0485 | -137.847 | 125.2482 | 0.94877 | -136.8379 | 123.9238
Line_3 | 0.0017955 | 0.62109 | 0.62207 | 0.0017955 | 0.62109 | 0.62207 | 0.020732 | 7.1717 | 7.1831 | 0.020732 | 7.1717 | 7.1831 | 0.020816 | -6.3139 | 0.40267 | -0.020814 | 6.5145 | -0.20144 | 0.0095119 | -0.80016 | -5.0185 | -0.00951 | 1.0278 | 5.2468 | -23.5071 | 33.1877 | -146.9505 | 156.4929 | -146.8123 | 33.0495 | 1.1039 | 0.88743 | 0.70089 | 1.1038 | 0.9196 | 0.73097 | 1.051 | -139.5897 | 127.6369 | 1.0485 | -137.847 | 125.2482

## LL_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.071598 | 1.3201 | 1.3825 | 0.071598 | 1.3201 | 1.3825 | 0.82674 | 15.2438 | 15.9643 | 0.82674 | 15.2438 | 15.9643 | -0.90611 | 15.0577 | 0.99002 | 0.90878 | -14.1515 | 0.0039296 | 0.071765 | 2.9587 | 13.1075 | -0.06874 | -1.9304 | -11.9797 | -174.7256 | -144.6058 | 33.905 | 5.2744 | 35.3942 | -146.095 | 1.0994 | 1.0067 | 0.82339 | 1.1024 | 0.93694 | 0.75041 | 0.74599 | -133.4895 | 119.5857 | 0.94877 | -136.8379 | 123.9238
Line_1 | 0.036588 | 0.97046 | 1.0023 | 0.036588 | 0.97046 | 1.0023 | 0.42248 | 11.2059 | 11.5734 | 0.42248 | 11.2059 | 11.5734 | 0.46549 | -9.895 | 0.56547 | -0.46479 | 10.3847 | -0.043093 | -0.028849 | -0.99149 | -8.092 | 0.029639 | 1.5471 | 8.6847 | 4.5975 | 34.6883 | -146.3605 | -175.4025 | -145.3117 | 33.6395 | 1.1039 | 0.88743 | 0.70089 | 1.1024 | 0.93694 | 0.75041 | 1.051 | -139.5897 | 127.6369 | 0.94877 | -136.8379 | 123.9238
Line_2 | 0.035015 | 0.34997 | 0.3803 | 0.035015 | 0.34997 | 0.3803 | 0.40431 | 4.041 | 4.3913 | 0.40431 | 4.041 | 4.3913 | 0.44463 | -3.7031 | 0.036043 | -0.44399 | 3.7668 | 0.039163 | -0.038378 | -0.31102 | -3.2097 | 0.039101 | 0.38328 | 3.2951 | 5.9817 | 37.352 | -145.3952 | -174.0183 | -142.648 | 34.6048 | 1.1038 | 0.9196 | 0.73097 | 1.1024 | 0.93694 | 0.75041 | 1.0485 | -137.847 | 125.2482 | 0.94877 | -136.8379 | 123.9238
Line_3 | 0.0017955 | 0.62109 | 0.62207 | 0.0017955 | 0.62109 | 0.62207 | 0.020732 | 7.1717 | 7.1831 | 0.020732 | 7.1717 | 7.1831 | 0.020816 | -6.3139 | 0.40267 | -0.020814 | 6.5145 | -0.20144 | 0.0095119 | -0.80016 | -5.0185 | -0.00951 | 1.0278 | 5.2468 | -23.5071 | 33.1877 | -146.9505 | 156.4929 | -146.8123 | 33.0495 | 1.1039 | 0.88743 | 0.70089 | 1.1038 | 0.9196 | 0.73097 | 1.051 | -139.5897 | 127.6369 | 1.0485 | -137.847 | 125.2482

## LL_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.1573 | 2.5018 | 2.6288 | 0.1573 | 2.5018 | 2.6288 | 1.8163 | 28.8882 | 30.3543 | 1.8163 | 28.8882 | 30.3543 | -1.8033 | 24.2039 | -2.0881 | 1.828 | -17.955 | 8.9874 | -0.29968 | -0.52181 | 13.6286 | 0.31428 | 4.2146 | -9.5515 | 172.4103 | -150.363 | 27.5625 | -7.5897 | 29.637 | -152.4375 | 1.0064 | 0.83804 | 0.45422 | 1.0212 | 0.63843 | 0.43207 | 1.8461 | -151.598 | 126.2732 | 2.1658 | -163.5729 | 160.8196
Line_1 | 0.080807 | 1.868 | 1.9334 | 0.080807 | 1.868 | 1.9334 | 0.93307 | 21.5701 | 22.3245 | 0.93307 | 21.5701 | 22.3245 | 0.9414 | -10.0168 | 10.4875 | -0.93488 | 13.5007 | -6.7556 | 0.18797 | 4.7735 | -4.6795 | -0.18412 | -2.7146 | 6.8848 | -8.9755 | 27.7962 | -153.6375 | 171.0245 | -152.2038 | 26.3625 | 1.0288 | 0.51442 | 0.51442 | 1.0212 | 0.63843 | 0.43207 | 2.3162 | -177.6838 | -177.6838 | 2.1658 | -163.5729 | 160.8196
Line_2 | 0.07654 | 0.63756 | 0.697 | 0.07654 | 0.63756 | 0.697 | 0.88381 | 7.3619 | 8.0483 | 0.88381 | 7.3619 | 8.0483 | 0.89894 | -4.0484 | 2.7169 | -0.89309 | 4.4543 | -2.2318 | 0.13362 | 1.7398 | -2.3801 | -0.13017 | -1.4999 | 2.6667 | -6.1266 | 35.0378 | -149.1073 | 173.8734 | -144.9622 | 30.8927 | 1.0283 | 0.59855 | 0.44878 | 1.0212 | 0.63843 | 0.43207 | 2.3283 | -168.2174 | 169.6733 | 2.1658 | -163.5729 | 160.8196
Line_3 | 0.0057872 | 1.2382 | 1.2398 | 0.0057872 | 1.2382 | 1.2398 | 0.066825 | 14.2971 | 14.3155 | 0.066825 | 14.2971 | 14.3155 | 0.041958 | -6.8307 | 6.8517 | -0.041925 | 8.3613 | -5.3171 | 0.054463 | 2.7263 | -2.6991 | -0.054444 | -1.8218 | 3.6059 | -50.0733 | 24.0746 | -156.1827 | 129.9267 | -155.9254 | 23.8173 | 1.0288 | 0.51442 | 0.51442 | 1.0283 | 0.59855 | 0.44878 | 2.3162 | -177.6838 | -177.6838 | 2.3283 | -168.2174 | 169.6733

## LL_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.1573 | 2.5018 | 2.6288 | 0.1573 | 2.5018 | 2.6288 | 1.8163 | 28.8882 | 30.3543 | 1.8163 | 28.8882 | 30.3543 | -1.8033 | 24.2039 | -2.0881 | 1.828 | -17.955 | 8.9874 | -0.29968 | -0.52181 | 13.6286 | 0.31428 | 4.2146 | -9.5515 | 172.4103 | -150.363 | 27.5625 | -7.5897 | 29.637 | -152.4375 | 1.0064 | 0.83804 | 0.45422 | 1.0212 | 0.63843 | 0.43207 | 1.8461 | -151.598 | 126.2732 | 2.1658 | -163.5729 | 160.8196
Line_1 | 0.080807 | 1.868 | 1.9334 | 0.080807 | 1.868 | 1.9334 | 0.93307 | 21.5701 | 22.3245 | 0.93307 | 21.5701 | 22.3245 | 0.9414 | -10.0168 | 10.4875 | -0.93488 | 13.5007 | -6.7556 | 0.18797 | 4.7735 | -4.6795 | -0.18412 | -2.7146 | 6.8848 | -8.9755 | 27.7962 | -153.6375 | 171.0245 | -152.2038 | 26.3625 | 1.0288 | 0.51442 | 0.51442 | 1.0212 | 0.63843 | 0.43207 | 2.3162 | -177.6838 | -177.6838 | 2.1658 | -163.5729 | 160.8196
Line_2 | 0.07654 | 0.63756 | 0.697 | 0.07654 | 0.63756 | 0.697 | 0.88381 | 7.3619 | 8.0483 | 0.88381 | 7.3619 | 8.0483 | 0.89894 | -4.0484 | 2.7169 | -0.89309 | 4.4543 | -2.2318 | 0.13362 | 1.7398 | -2.3801 | -0.13017 | -1.4999 | 2.6667 | -6.1266 | 35.0378 | -149.1073 | 173.8734 | -144.9622 | 30.8927 | 1.0283 | 0.59855 | 0.44878 | 1.0212 | 0.63843 | 0.43207 | 2.3283 | -168.2174 | 169.6733 | 2.1658 | -163.5729 | 160.8196
Line_3 | 0.0057872 | 1.2382 | 1.2398 | 0.0057872 | 1.2382 | 1.2398 | 0.066825 | 14.2971 | 14.3155 | 0.066825 | 14.2971 | 14.3155 | 0.041958 | -6.8307 | 6.8517 | -0.041925 | 8.3613 | -5.3171 | 0.054463 | 2.7263 | -2.6991 | -0.054444 | -1.8218 | 3.6059 | -50.0733 | 24.0746 | -156.1827 | 129.9267 | -155.9254 | 23.8173 | 1.0288 | 0.51442 | 0.51442 | 1.0283 | 0.59855 | 0.44878 | 2.3162 | -177.6838 | -177.6838 | 2.3283 | -168.2174 | 169.6733

## LL_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.068597 | 1.091 | 1.1464 | 0.068597 | 1.091 | 1.1464 | 0.79209 | 12.5981 | 13.2375 | 0.79209 | 12.5981 | 13.2375 | -0.78949 | 11.8666 | 2.206 | 0.79419 | -10.6782 | -0.89388 | 0.059138 | 0.94684 | 9.8501 | -0.056362 | -0.24454 | -9.0747 | -174.893 | -137.6663 | 40.2592 | 5.107 | 42.3337 | -139.7408 | 0.99951 | 0.94493 | 0.76254 | 1.0052 | 0.84783 | 0.68885 | 0.82315 | -133.1043 | 117.6357 | 1.0476 | -136.3544 | 124.6336
Line_1 | 0.03524 | 0.81464 | 0.84313 | 0.03524 | 0.81464 | 0.84313 | 0.40691 | 9.4067 | 9.7357 | 0.40691 | 9.4067 | 9.7357 | 0.40981 | -7.3006 | 0.19224 | -0.40857 | 7.9632 | 0.5175 | -0.018346 | -0.047078 | -6.267 | 0.019079 | 0.43863 | 6.6864 | 3.7212 | 40.4929 | -140.9408 | -176.2788 | -139.5071 | 39.0592 | 1.0081 | 0.77612 | 0.64402 | 1.0052 | 0.84783 | 0.68885 | 1.1579 | -139.1377 | 130.8161 | 1.0476 | -136.3544 | 124.6336
Line_2 | 0.033379 | 0.27804 | 0.30396 | 0.033379 | 0.27804 | 0.30396 | 0.38543 | 3.2105 | 3.5098 | 0.38543 | 3.2105 | 3.5098 | 0.38673 | -2.6378 | -0.28414 | -0.38562 | 2.715 | 0.37638 | -0.036626 | 0.23969 | -2.3338 | 0.037283 | -0.19408 | 2.3883 | 6.5701 | 47.7344 | -136.4106 | -173.4299 | -132.2656 | 43.5894 | 1.0079 | 0.82502 | 0.66983 | 1.0052 | 0.84783 | 0.68885 | 1.1599 | -137.4576 | 126.6478 | 1.0476 | -136.3544 | 124.6336
Line_3 | 0.0025238 | 0.53996 | 0.54066 | 0.0025238 | 0.53996 | 0.54066 | 0.029142 | 6.2349 | 6.243 | 0.029142 | 6.2349 | 6.243 | 0.022981 | -4.8268 | 0.30161 | -0.022975 | 5.1178 | -0.0097645 | 0.018303 | -0.34522 | -4.0093 | -0.018299 | 0.51724 | 4.1817 | -37.3766 | 36.7713 | -143.486 | 142.6234 | -143.2287 | 36.514 | 1.0081 | 0.77612 | 0.64402 | 1.0079 | 0.82502 | 0.66983 | 1.1579 | -139.1377 | 130.8161 | 1.1599 | -137.4576 | 126.6478

## LL_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.068597 | 1.091 | 1.1464 | 0.068597 | 1.091 | 1.1464 | 0.79209 | 12.5981 | 13.2375 | 0.79209 | 12.5981 | 13.2375 | -0.78949 | 11.8666 | 2.206 | 0.79419 | -10.6782 | -0.89388 | 0.059138 | 0.94684 | 9.8501 | -0.056362 | -0.24454 | -9.0747 | -174.893 | -137.6663 | 40.2592 | 5.107 | 42.3337 | -139.7408 | 0.99951 | 0.94493 | 0.76254 | 1.0052 | 0.84783 | 0.68885 | 0.82315 | -133.1043 | 117.6357 | 1.0476 | -136.3544 | 124.6336
Line_1 | 0.03524 | 0.81464 | 0.84313 | 0.03524 | 0.81464 | 0.84313 | 0.40691 | 9.4067 | 9.7357 | 0.40691 | 9.4067 | 9.7357 | 0.40981 | -7.3006 | 0.19224 | -0.40857 | 7.9632 | 0.5175 | -0.018346 | -0.047078 | -6.267 | 0.019079 | 0.43863 | 6.6864 | 3.7212 | 40.4929 | -140.9408 | -176.2788 | -139.5071 | 39.0592 | 1.0081 | 0.77612 | 0.64402 | 1.0052 | 0.84783 | 0.68885 | 1.1579 | -139.1377 | 130.8161 | 1.0476 | -136.3544 | 124.6336
Line_2 | 0.033379 | 0.27804 | 0.30396 | 0.033379 | 0.27804 | 0.30396 | 0.38543 | 3.2105 | 3.5098 | 0.38543 | 3.2105 | 3.5098 | 0.38673 | -2.6378 | -0.28414 | -0.38562 | 2.715 | 0.37638 | -0.036626 | 0.23969 | -2.3338 | 0.037283 | -0.19408 | 2.3883 | 6.5701 | 47.7344 | -136.4106 | -173.4299 | -132.2656 | 43.5894 | 1.0079 | 0.82502 | 0.66983 | 1.0052 | 0.84783 | 0.68885 | 1.1599 | -137.4576 | 126.6478 | 1.0476 | -136.3544 | 124.6336
Line_3 | 0.0025238 | 0.53996 | 0.54066 | 0.0025238 | 0.53996 | 0.54066 | 0.029142 | 6.2349 | 6.243 | 0.029142 | 6.2349 | 6.243 | 0.022981 | -4.8268 | 0.30161 | -0.022975 | 5.1178 | -0.0097645 | 0.018303 | -0.34522 | -4.0093 | -0.018299 | 0.51724 | 4.1817 | -37.3766 | 36.7713 | -143.486 | 142.6234 | -143.2287 | 36.514 | 1.0081 | 0.77612 | 0.64402 | 1.0079 | 0.82502 | 0.66983 | 1.1579 | -139.1377 | 130.8161 | 1.1599 | -137.4576 | 126.6478

## LG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 2.77 | 0.72027 | 0.55174 | 2.7693 | 0.72097 | 0.55242 | 31.985 | 8.317 | 6.3709 | 31.9769 | 8.325 | 6.3788 | 16.55 | -8.2048 | 5.22 | -7.7084 | 8.4318 | -5.0475 | 14.7836 | 0.93681 | 4.3136 | -5.9362 | -2.3244 | -5.4309 | -58.2879 | 75.0869 | 72.3399 | 121.7183 | -104.889 | -107.6252 | 0.69381 | 0.99292 | 1.0629 | 0.30426 | 1.0506 | 1.1623 | -16.5144 | -111.4268 | 111.9087 | -20.6824 | -120.3011 | 119.47
Line_1 | 2.109 | 0.39186 | 0.3062 | 2.1105 | 0.39009 | 0.30445 | 24.3529 | 4.5248 | 3.5357 | 24.37 | 4.5043 | 3.5154 | 1.1682e-10 | 4.5671 | -2.7 | 5.6606 | -4.608 | 2.6483 | -1.0867e-10 | -1.722 | -3.6429 | 4.7892 | 1.0771 | 3.1118 | 119.1126 | -107.0924 | -110.0454 | -60.9154 | 72.8547 | 69.8697 | 0 | 1.0787 | 1.2825 | 0.30426 | 1.0506 | 1.1623 | 0 | -127.7509 | 123.4098 | -20.6824 | -120.3011 | 119.47
Line_2 | 0.66689 | 0.33298 | 0.25004 | 0.66808 | 0.33154 | 0.24862 | 7.7006 | 3.845 | 2.8872 | 7.7143 | 3.8283 | 2.8708 | -1.679 | 4.0099 | -2.2944 | 2.0478 | -3.8237 | 2.3992 | -0.48815 | -1.365 | -2.4176 | 1.147 | 1.2474 | 2.3191 | 130.1421 | -102.1666 | -104.4539 | -49.9352 | 77.7659 | 75.4429 | 0.22706 | 1.1017 | 1.1544 | 0.30426 | 1.0506 | 1.1623 | -33.6467 | -120.9649 | 122.044 | -20.6824 | -120.3011 | 119.47
Line_3 | 1.4593 | 0.067113 | 0.062856 | 1.461 | 0.065611 | 0.061365 | 16.8501 | 0.77496 | 0.7258 | 16.8701 | 0.75761 | 0.70858 | 8.7079e-11 | 0.83364 | -0.22654 | 3.2386 | -0.81603 | 0.202 | -6.7856e-11 | 0.06213 | -0.90282 | 2.0456 | -0.1752 | 0.79265 | 114.1098 | -132.0132 | -132.5039 | -65.9251 | 46.9176 | 46.3409 | 0 | 1.0787 | 1.2825 | 0.22706 | 1.1017 | 1.1544 | 0 | -127.7509 | 123.4098 | -33.6467 | -120.9649 | 122.044

## LG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 2.77 | 0.72027 | 0.55174 | 2.7693 | 0.72097 | 0.55242 | 31.985 | 8.317 | 6.3709 | 31.9769 | 8.325 | 6.3788 | 16.55 | -8.2048 | 5.22 | -7.7084 | 8.4318 | -5.0475 | 14.7836 | 0.93681 | 4.3136 | -5.9362 | -2.3244 | -5.4309 | -58.2879 | 75.0869 | 72.3399 | 121.7183 | -104.889 | -107.6252 | 0.69381 | 0.99292 | 1.0629 | 0.30426 | 1.0506 | 1.1623 | -16.5144 | -111.4268 | 111.9087 | -20.6824 | -120.3011 | 119.47
Line_1 | 2.109 | 0.39186 | 0.3062 | 2.1105 | 0.39009 | 0.30445 | 24.3529 | 4.5248 | 3.5357 | 24.37 | 4.5043 | 3.5154 | 1.1682e-10 | 4.5671 | -2.7 | 5.6606 | -4.608 | 2.6483 | -1.0867e-10 | -1.722 | -3.6429 | 4.7892 | 1.0771 | 3.1118 | 119.1126 | -107.0924 | -110.0454 | -60.9154 | 72.8547 | 69.8697 | 0 | 1.0787 | 1.2825 | 0.30426 | 1.0506 | 1.1623 | 0 | -127.7509 | 123.4098 | -20.6824 | -120.3011 | 119.47
Line_2 | 0.66689 | 0.33298 | 0.25004 | 0.66808 | 0.33154 | 0.24862 | 7.7006 | 3.845 | 2.8872 | 7.7143 | 3.8283 | 2.8708 | -1.679 | 4.0099 | -2.2944 | 2.0478 | -3.8237 | 2.3992 | -0.48815 | -1.365 | -2.4176 | 1.147 | 1.2474 | 2.3191 | 130.1421 | -102.1666 | -104.4539 | -49.9352 | 77.7659 | 75.4429 | 0.22706 | 1.1017 | 1.1544 | 0.30426 | 1.0506 | 1.1623 | -33.6467 | -120.9649 | 122.044 | -20.6824 | -120.3011 | 119.47
Line_3 | 1.4593 | 0.067113 | 0.062856 | 1.461 | 0.065611 | 0.061365 | 16.8501 | 0.77496 | 0.7258 | 16.8701 | 0.75761 | 0.70858 | 8.7079e-11 | 0.83364 | -0.22654 | 3.2386 | -0.81603 | 0.202 | -6.7856e-11 | 0.06213 | -0.90282 | 2.0456 | -0.1752 | 0.79265 | 114.1098 | -132.0132 | -132.5039 | -65.9251 | 46.9176 | 46.3409 | 0 | 1.0787 | 1.2825 | 0.22706 | 1.1017 | 1.1544 | 0 | -127.7509 | 123.4098 | -33.6467 | -120.9649 | 122.044

## LG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.80172 | 0.20847 | 0.15969 | 0.80152 | 0.20867 | 0.15989 | 9.2575 | 2.4072 | 1.8439 | 9.2552 | 2.4095 | 1.8462 | 7.4881 | -2.1909 | 1.7866 | -6.7463 | 2.2109 | -1.7741 | 5.4513 | 1.2853 | 0.96196 | -4.7085 | -1.4034 | -1.0555 | -41.2945 | 92.0803 | 89.3333 | 138.7117 | -87.8956 | -90.6318 | 1.0005 | 1.0552 | 1.1004 | 0.8889 | 1.0868 | 1.1182 | -5.2398 | -118.3179 | 117.6332 | -6.376 | -120.3009 | 120.1175
Line_1 | 0.61042 | 0.11342 | 0.088624 | 0.61085 | 0.1129 | 0.088117 | 7.0485 | 1.3096 | 1.0233 | 7.0535 | 1.3037 | 1.0175 | -4.4955 | 1.225 | -0.96047 | 4.9711 | -1.2252 | 0.9514 | -3.415 | -0.76925 | -0.66937 | 3.8208 | 0.71162 | 0.62387 | 136.106 | -90.099 | -93.052 | -43.922 | 89.8481 | 86.8631 | 0.80095 | 1.1045 | 1.144 | 0.8889 | 1.0868 | 1.1182 | -6.6713 | -122.2261 | 121.8212 | -6.376 | -120.3009 | 120.1175
Line_2 | 0.19302 | 0.096376 | 0.07237 | 0.19336 | 0.095959 | 0.071958 | 2.2288 | 1.1129 | 0.83566 | 2.2328 | 1.108 | 0.8309 | -1.7425 | 1.0035 | -0.81795 | 1.7752 | -0.98572 | 0.82274 | -0.82886 | -0.70494 | -0.44009 | 0.88762 | 0.69175 | 0.4316 | 147.1355 | -85.1732 | -87.4605 | -32.9418 | 94.7593 | 92.4363 | 0.86575 | 1.102 | 1.1115 | 0.8889 | 1.0868 | 1.1182 | -7.4252 | -120.2604 | 120.8216 | -6.376 | -120.3009 | 120.1175
Line_3 | 0.42236 | 0.019425 | 0.018192 | 0.42286 | 0.01899 | 0.017761 | 4.877 | 0.2243 | 0.21007 | 4.8827 | 0.21928 | 0.20509 | -2.8926 | 0.24578 | -0.12972 | 3.1657 | -0.241 | 0.12252 | -2.6252 | -0.031078 | -0.2023 | 2.8014 | 0.017577 | 0.19222 | 131.1032 | -115.0198 | -115.5105 | -48.9317 | 63.911 | 63.3343 | 0.80095 | 1.1045 | 1.144 | 0.86575 | 1.102 | 1.1115 | -6.6713 | -122.2261 | 121.8212 | -7.4252 | -120.2604 | 120.8216

## LG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.80172 | 0.20847 | 0.15969 | 0.80152 | 0.20867 | 0.15989 | 9.2575 | 2.4072 | 1.8439 | 9.2552 | 2.4095 | 1.8462 | 7.4881 | -2.1909 | 1.7866 | -6.7463 | 2.2109 | -1.7741 | 5.4513 | 1.2853 | 0.96196 | -4.7085 | -1.4034 | -1.0555 | -41.2945 | 92.0803 | 89.3333 | 138.7117 | -87.8956 | -90.6318 | 1.0005 | 1.0552 | 1.1004 | 0.8889 | 1.0868 | 1.1182 | -5.2398 | -118.3179 | 117.6332 | -6.376 | -120.3009 | 120.1175
Line_1 | 0.61042 | 0.11342 | 0.088624 | 0.61085 | 0.1129 | 0.088117 | 7.0485 | 1.3096 | 1.0233 | 7.0535 | 1.3037 | 1.0175 | -4.4955 | 1.225 | -0.96047 | 4.9711 | -1.2252 | 0.9514 | -3.415 | -0.76925 | -0.66937 | 3.8208 | 0.71162 | 0.62387 | 136.106 | -90.099 | -93.052 | -43.922 | 89.8481 | 86.8631 | 0.80095 | 1.1045 | 1.144 | 0.8889 | 1.0868 | 1.1182 | -6.6713 | -122.2261 | 121.8212 | -6.376 | -120.3009 | 120.1175
Line_2 | 0.19302 | 0.096376 | 0.07237 | 0.19336 | 0.095959 | 0.071958 | 2.2288 | 1.1129 | 0.83566 | 2.2328 | 1.108 | 0.8309 | -1.7425 | 1.0035 | -0.81795 | 1.7752 | -0.98572 | 0.82274 | -0.82886 | -0.70494 | -0.44009 | 0.88762 | 0.69175 | 0.4316 | 147.1355 | -85.1732 | -87.4605 | -32.9418 | 94.7593 | 92.4363 | 0.86575 | 1.102 | 1.1115 | 0.8889 | 1.0868 | 1.1182 | -7.4252 | -120.2604 | 120.8216 | -6.376 | -120.3009 | 120.1175
Line_3 | 0.42236 | 0.019425 | 0.018192 | 0.42286 | 0.01899 | 0.017761 | 4.877 | 0.2243 | 0.21007 | 4.8827 | 0.21928 | 0.20509 | -2.8926 | 0.24578 | -0.12972 | 3.1657 | -0.241 | 0.12252 | -2.6252 | -0.031078 | -0.2023 | 2.8014 | 0.017577 | 0.19222 | 131.1032 | -115.0198 | -115.5105 | -48.9317 | 63.911 | 63.3343 | 0.80095 | 1.1045 | 1.144 | 0.86575 | 1.102 | 1.1115 | -6.6713 | -122.2261 | 121.8212 | -7.4252 | -120.2604 | 120.8216

## LG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.8944 | 0.71869 | 0.57063 | 1.8938 | 0.71931 | 0.57126 | 21.8743 | 8.2987 | 6.5891 | 21.8675 | 8.3059 | 6.5964 | 12.872 | -6.6225 | 6.2548 | -6.4569 | 7.03 | -6.0785 | 8.9959 | 3.1969 | 1.8588 | -3.5364 | -4.5547 | -2.98 | -50.4234 | 93.2103 | 95.4557 | 129.5842 | -86.7782 | -84.5322 | 0.71792 | 0.88613 | 0.99029 | 0.33666 | 1.0085 | 1.0263 | -15.4747 | -112.5577 | 112.0069 | -21.7069 | -119.717 | 121.5843
Line_1 | 1.5135 | 0.40062 | 0.32384 | 1.5149 | 0.39892 | 0.32214 | 17.4764 | 4.626 | 3.7394 | 17.4927 | 4.6063 | 3.7197 | -4.0367e-11 | 4.0051 | -3.3811 | 4.9917 | -4.1031 | 3.2322 | 1.1505e-12 | -2.903 | -2.6286 | 3.1248 | 2.1783 | 2.0312 | 126.2836 | -91.7394 | -90.55 | -53.7532 | 88.2459 | 89.438 | 0 | 1.0693 | 1.1453 | 0.33666 | 1.0085 | 1.0263 | 0 | -127.6752 | 127.3133 | -21.7069 | -119.717 | 121.5843
Line_2 | 0.39042 | 0.32506 | 0.2545 | 0.3915 | 0.32375 | 0.25318 | 4.5082 | 3.7535 | 2.9387 | 4.5207 | 3.7384 | 2.9235 | -1.3855 | 3.2601 | -2.6343 | 1.4652 | -2.9269 | 2.8463 | -0.017637 | -2.4639 | -1.0338 | 0.41159 | 2.3764 | 0.9488 | 142.7145 | -80.6102 | -76.829 | -37.3974 | 99.357 | 103.1487 | 0.30735 | 1.0887 | 0.96296 | 0.33666 | 1.0085 | 1.0263 | -36.5562 | -117.6906 | 124.5986 | -21.7069 | -119.717 | 121.5843
Line_3 | 1.1436 | 0.10332 | 0.09787 | 1.1453 | 0.1021 | 0.096635 | 13.2057 | 1.1931 | 1.1301 | 13.2247 | 1.1789 | 1.1158 | -3.0444e-11 | 1.2754 | -0.31915 | 3.749 | -1.2557 | 0.30022 | -2.076e-12 | 0.027553 | -1.2543 | 1.5705 | -0.26583 | 1.0317 | 120.7502 | -128.9127 | -128.4111 | -59.285 | 50.3566 | 50.8233 | 0 | 1.0693 | 1.1453 | 0.30735 | 1.0887 | 0.96296 | 0 | -127.6752 | 127.3133 | -36.5562 | -117.6906 | 124.5986

## LG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.8944 | 0.71869 | 0.57063 | 1.8938 | 0.71931 | 0.57126 | 21.8743 | 8.2987 | 6.5891 | 21.8675 | 8.3059 | 6.5964 | 12.872 | -6.6225 | 6.2548 | -6.4569 | 7.03 | -6.0785 | 8.9959 | 3.1969 | 1.8588 | -3.5364 | -4.5547 | -2.98 | -50.4234 | 93.2103 | 95.4557 | 129.5842 | -86.7782 | -84.5322 | 0.71792 | 0.88613 | 0.99029 | 0.33666 | 1.0085 | 1.0263 | -15.4747 | -112.5577 | 112.0069 | -21.7069 | -119.717 | 121.5843
Line_1 | 1.5135 | 0.40062 | 0.32384 | 1.5149 | 0.39892 | 0.32214 | 17.4764 | 4.626 | 3.7394 | 17.4927 | 4.6063 | 3.7197 | -4.0367e-11 | 4.0051 | -3.3811 | 4.9917 | -4.1031 | 3.2322 | 1.1505e-12 | -2.903 | -2.6286 | 3.1248 | 2.1783 | 2.0312 | 126.2836 | -91.7394 | -90.55 | -53.7532 | 88.2459 | 89.438 | 0 | 1.0693 | 1.1453 | 0.33666 | 1.0085 | 1.0263 | 0 | -127.6752 | 127.3133 | -21.7069 | -119.717 | 121.5843
Line_2 | 0.39042 | 0.32506 | 0.2545 | 0.3915 | 0.32375 | 0.25318 | 4.5082 | 3.7535 | 2.9387 | 4.5207 | 3.7384 | 2.9235 | -1.3855 | 3.2601 | -2.6343 | 1.4652 | -2.9269 | 2.8463 | -0.017637 | -2.4639 | -1.0338 | 0.41159 | 2.3764 | 0.9488 | 142.7145 | -80.6102 | -76.829 | -37.3974 | 99.357 | 103.1487 | 0.30735 | 1.0887 | 0.96296 | 0.33666 | 1.0085 | 1.0263 | -36.5562 | -117.6906 | 124.5986 | -21.7069 | -119.717 | 121.5843
Line_3 | 1.1436 | 0.10332 | 0.09787 | 1.1453 | 0.1021 | 0.096635 | 13.2057 | 1.1931 | 1.1301 | 13.2247 | 1.1789 | 1.1158 | -3.0444e-11 | 1.2754 | -0.31915 | 3.749 | -1.2557 | 0.30022 | -2.076e-12 | 0.027553 | -1.2543 | 1.5705 | -0.26583 | 1.0317 | 120.7502 | -128.9127 | -128.4111 | -59.285 | 50.3566 | 50.8233 | 0 | 1.0693 | 1.1453 | 0.30735 | 1.0887 | 0.96296 | 0 | -127.6752 | 127.3133 | -36.5562 | -117.6906 | 124.5986

## LG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.59814 | 0.22692 | 0.18017 | 0.59795 | 0.22712 | 0.18037 | 6.9067 | 2.6203 | 2.0805 | 6.9046 | 2.6225 | 2.0828 | 5.4335 | -1.7563 | 2.0697 | -4.793 | 1.7976 | -2.0537 | 3.3409 | 1.7807 | 0.30202 | -2.7953 | -1.9176 | -0.41362 | -36.6719 | 106.9618 | 109.2073 | 143.3358 | -73.0266 | -70.7806 | 0.92352 | 0.95453 | 1.0054 | 0.80361 | 1.0022 | 1.0059 | -5.0861 | -118.4334 | 117.5097 | -6.4137 | -119.8762 | 120.6063
Line_1 | 0.47788 | 0.12649 | 0.10225 | 0.47833 | 0.12596 | 0.10171 | 5.5181 | 1.4606 | 1.1807 | 5.5232 | 1.4544 | 1.1745 | -3.1982 | 1.0783 | -1.1463 | 3.6975 | -1.0854 | 1.1272 | -2.1399 | -1.0486 | -0.4138 | 2.4555 | 0.97297 | 0.3536 | 140.0351 | -77.9878 | -76.7985 | -40.0016 | 101.9974 | 103.1895 | 0.69736 | 1.0298 | 1.0322 | 0.80361 | 1.0022 | 1.0059 | -6.1787 | -122.1881 | 123.0497 | -6.4137 | -119.8762 | 120.6063
Line_2 | 0.12327 | 0.10264 | 0.080357 | 0.12361 | 0.10222 | 0.079941 | 1.4234 | 1.1851 | 0.92789 | 1.4274 | 1.1804 | 0.92307 | -1.0856 | 0.74672 | -0.90874 | 1.0956 | -0.7122 | 0.92654 | -0.29786 | -0.95642 | -0.06806 | 0.33981 | 0.9446 | 0.060015 | 156.466 | -66.8587 | -63.0775 | -23.6458 | 113.1086 | 116.9003 | 0.79083 | 1.0238 | 0.98211 | 0.80361 | 1.0022 | 1.0059 | -8.1908 | -118.8781 | 121.2057 | -6.4137 | -119.8762 | 120.6063
Line_3 | 0.3611 | 0.032624 | 0.030902 | 0.36162 | 0.032238 | 0.030512 | 4.1696 | 0.37671 | 0.35682 | 4.1756 | 0.37225 | 0.35232 | -2.2495 | 0.38501 | -0.19676 | 2.6253 | -0.3806 | 0.19032 | -1.8425 | -0.047458 | -0.31136 | 2.0031 | 0.019855 | 0.28898 | 134.5018 | -115.1612 | -114.6595 | -45.5334 | 64.1081 | 64.5749 | 0.69736 | 1.0298 | 1.0322 | 0.79083 | 1.0238 | 0.98211 | -6.1787 | -122.1881 | 123.0497 | -8.1908 | -118.8781 | 121.2057

## LG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.59814 | 0.22692 | 0.18017 | 0.59795 | 0.22712 | 0.18037 | 6.9067 | 2.6203 | 2.0805 | 6.9046 | 2.6225 | 2.0828 | 5.4335 | -1.7563 | 2.0697 | -4.793 | 1.7976 | -2.0537 | 3.3409 | 1.7807 | 0.30202 | -2.7953 | -1.9176 | -0.41362 | -36.6719 | 106.9618 | 109.2073 | 143.3358 | -73.0266 | -70.7806 | 0.92352 | 0.95453 | 1.0054 | 0.80361 | 1.0022 | 1.0059 | -5.0861 | -118.4334 | 117.5097 | -6.4137 | -119.8762 | 120.6063
Line_1 | 0.47788 | 0.12649 | 0.10225 | 0.47833 | 0.12596 | 0.10171 | 5.5181 | 1.4606 | 1.1807 | 5.5232 | 1.4544 | 1.1745 | -3.1982 | 1.0783 | -1.1463 | 3.6975 | -1.0854 | 1.1272 | -2.1399 | -1.0486 | -0.4138 | 2.4555 | 0.97297 | 0.3536 | 140.0351 | -77.9878 | -76.7985 | -40.0016 | 101.9974 | 103.1895 | 0.69736 | 1.0298 | 1.0322 | 0.80361 | 1.0022 | 1.0059 | -6.1787 | -122.1881 | 123.0497 | -6.4137 | -119.8762 | 120.6063
Line_2 | 0.12327 | 0.10264 | 0.080357 | 0.12361 | 0.10222 | 0.079941 | 1.4234 | 1.1851 | 0.92789 | 1.4274 | 1.1804 | 0.92307 | -1.0856 | 0.74672 | -0.90874 | 1.0956 | -0.7122 | 0.92654 | -0.29786 | -0.95642 | -0.06806 | 0.33981 | 0.9446 | 0.060015 | 156.466 | -66.8587 | -63.0775 | -23.6458 | 113.1086 | 116.9003 | 0.79083 | 1.0238 | 0.98211 | 0.80361 | 1.0022 | 1.0059 | -8.1908 | -118.8781 | 121.2057 | -6.4137 | -119.8762 | 120.6063
Line_3 | 0.3611 | 0.032624 | 0.030902 | 0.36162 | 0.032238 | 0.030512 | 4.1696 | 0.37671 | 0.35682 | 4.1756 | 0.37225 | 0.35232 | -2.2495 | 0.38501 | -0.19676 | 2.6253 | -0.3806 | 0.19032 | -1.8425 | -0.047458 | -0.31136 | 2.0031 | 0.019855 | 0.28898 | 134.5018 | -115.1612 | -114.6595 | -45.5334 | 64.1081 | 64.5749 | 0.69736 | 1.0298 | 1.0322 | 0.79083 | 1.0238 | 0.98211 | -6.1787 | -122.1881 | 123.0497 | -8.1908 | -118.8781 | 121.2057

## LLG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.5925 | 3.7866 | 2.7776 | 0.59302 | 3.7865 | 2.7773 | 6.8416 | 43.7241 | 32.0725 | 6.8476 | 43.7224 | 32.0699 | -2.7162 | 26.9288 | -0.0090273 | 3.2428 | -11.6281 | -0.19898 | 5.9706 | 9.8894 | 16.1614 | -6.9836 | -3.2478 | -7.477 | -115.3404 | -176.3144 | 35.0088 | 64.7035 | 3.6958 | -145.0046 | 0.95876 | 0.6561 | 0.5039 | 1.1245 | 0.27613 | 0.23323 | -0.87806 | -156.149 | 125.0408 | -0.38898 | -160.6986 | 123.471
Line_1 | 0.32606 | 2.7709 | 2.0873 | 0.32461 | 2.7709 | 2.0883 | 3.765 | 31.9959 | 24.1025 | 3.7483 | 31.9961 | 24.1136 | 1.9687 | 7.1368e-11 | 7.4705e-11 | -1.8596 | 8.3928 | 0.38445 | -4.2967 | -8.8236e-11 | -3.9311e-11 | 3.7823 | 2.7606 | 5.6108 | 63.5657 | 1.1279 | -142.6459 | -116.5706 | -178.906 | 37.3907 | 1.2553 | 0 | 0 | 1.1245 | 0.27613 | 0.23323 | -1.8172 | 0 | 0 | -0.38898 | -160.6986 | 123.471
Line_2 | 0.26971 | 1.0261 | 0.69594 | 0.26858 | 1.0261 | 0.69635 | 3.1143 | 11.8488 | 8.0361 | 3.1013 | 11.8487 | 8.0408 | 1.5374 | -2.1368 | 0.048414 | -1.3832 | 3.2353 | -0.18547 | -3.2695 | 0.31203 | -1.5831 | 3.2013 | 0.48723 | 1.8661 | 66.4043 | 10.8128 | -152.3112 | -113.7565 | -169.2628 | 27.7951 | 1.1601 | 0.18225 | 0.19709 | 1.1245 | 0.27613 | 0.23323 | 1.5881 | -177.4953 | 119.4405 | -0.38898 | -160.6986 | 123.471
Line_3 | 0.058692 | 1.7676 | 1.4058 | 0.057419 | 1.7679 | 1.4069 | 0.67771 | 20.411 | 16.2324 | 0.66302 | 20.414 | 16.2449 | 0.51558 | 5.0786e-11 | 4.7952e-11 | -0.51384 | 3.6926 | 0.70446 | -0.67672 | -5.1593e-11 | -3.0542e-11 | 0.57235 | 0.45431 | 3.1232 | 50.88 | -4.4527 | -137.9057 | -130.3288 | 175.4907 | 42.1511 | 1.2553 | 0 | 0 | 1.1601 | 0.18225 | 0.19709 | -1.8172 | 0 | 0 | 1.5881 | -177.4953 | 119.4405

## LLG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.5925 | 3.7866 | 2.7776 | 0.59302 | 3.7865 | 2.7773 | 6.8416 | 43.7241 | 32.0725 | 6.8476 | 43.7224 | 32.0699 | -2.7162 | 26.9288 | -0.0090273 | 3.2428 | -11.6281 | -0.19898 | 5.9706 | 9.8894 | 16.1614 | -6.9836 | -3.2478 | -7.477 | -115.3404 | -176.3144 | 35.0088 | 64.7035 | 3.6958 | -145.0046 | 0.95876 | 0.6561 | 0.5039 | 1.1245 | 0.27613 | 0.23323 | -0.87806 | -156.149 | 125.0408 | -0.38898 | -160.6986 | 123.471
Line_1 | 0.32606 | 2.7709 | 2.0873 | 0.32461 | 2.7709 | 2.0883 | 3.765 | 31.9959 | 24.1025 | 3.7483 | 31.9961 | 24.1136 | 1.9687 | 7.1368e-11 | 7.4705e-11 | -1.8596 | 8.3928 | 0.38445 | -4.2967 | -8.8236e-11 | -3.9311e-11 | 3.7823 | 2.7606 | 5.6108 | 63.5657 | 1.1279 | -142.6459 | -116.5706 | -178.906 | 37.3907 | 1.2553 | 0 | 0 | 1.1245 | 0.27613 | 0.23323 | -1.8172 | 0 | 0 | -0.38898 | -160.6986 | 123.471
Line_2 | 0.26971 | 1.0261 | 0.69594 | 0.26858 | 1.0261 | 0.69635 | 3.1143 | 11.8488 | 8.0361 | 3.1013 | 11.8487 | 8.0408 | 1.5374 | -2.1368 | 0.048414 | -1.3832 | 3.2353 | -0.18547 | -3.2695 | 0.31203 | -1.5831 | 3.2013 | 0.48723 | 1.8661 | 66.4043 | 10.8128 | -152.3112 | -113.7565 | -169.2628 | 27.7951 | 1.1601 | 0.18225 | 0.19709 | 1.1245 | 0.27613 | 0.23323 | 1.5881 | -177.4953 | 119.4405 | -0.38898 | -160.6986 | 123.471
Line_3 | 0.058692 | 1.7676 | 1.4058 | 0.057419 | 1.7679 | 1.4069 | 0.67771 | 20.411 | 16.2324 | 0.66302 | 20.414 | 16.2449 | 0.51558 | 5.0786e-11 | 4.7952e-11 | -0.51384 | 3.6926 | 0.70446 | -0.67672 | -5.1593e-11 | -3.0542e-11 | 0.57235 | 0.45431 | 3.1232 | 50.88 | -4.4527 | -137.9057 | -130.3288 | 175.4907 | 42.1511 | 1.2553 | 0 | 0 | 1.1601 | 0.18225 | 0.19709 | -1.8172 | 0 | 0 | 1.5881 | -177.4953 | 119.4405

## LLG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.18809 | 0.99467 | 0.78791 | 0.18826 | 0.99465 | 0.78779 | 2.1719 | 11.4854 | 9.098 | 2.1738 | 11.4852 | 9.0966 | -0.41341 | 9.9522 | 4.8413 | 0.45846 | -8.8274 | -4.7824 | 2.2577 | 5.8014 | 7.1136 | -2.3586 | -5.4323 | -6.308 | -101.1559 | -158.4953 | 60.7956 | 78.8841 | 21.5169 | -119.2172 | 1.0568 | 1.003 | 0.94578 | 1.1053 | 0.90247 | 0.87021 | -0.7792 | -128.2563 | 116.5577 | -0.11603 | -126.8757 | 113.6154
Line_1 | 0.10321 | 0.72431 | 0.60013 | 0.10276 | 0.72426 | 0.60052 | 1.1918 | 8.3636 | 6.9298 | 1.1866 | 8.363 | 6.9342 | 0.28931 | -5.6163 | -3.7115 | -0.28241 | 6.2211 | 3.8073 | -1.3348 | -4.139 | -4.1681 | 1.2808 | 4.2732 | 4.6815 | 77.5695 | 18.6792 | -117.2956 | -102.551 | -161.3604 | 62.7354 | 1.146 | 0.83417 | 0.80538 | 1.1053 | 0.90247 | 0.87021 | -0.20171 | -124.9321 | 111.0206 | -0.11603 | -126.8757 | 113.6154
Line_2 | 0.085925 | 0.27378 | 0.18851 | 0.085569 | 0.27373 | 0.18874 | 0.99217 | 3.1614 | 2.1767 | 0.98806 | 3.1607 | 2.1793 | 0.18912 | -2.5231 | -0.984 | -0.17605 | 2.6063 | 0.97516 | -1.0882 | -1.1026 | -1.5971 | 1.0778 | 1.1591 | 1.6266 | 80.7501 | 29.2353 | -125.5469 | -99.3925 | -150.8509 | 54.559 | 1.1132 | 0.87099 | 0.86181 | 1.1053 | 0.90247 | 0.87021 | 0.60931 | -127.1595 | 112.8156 | -0.11603 | -126.8757 | 113.6154
Line_3 | 0.018204 | 0.45787 | 0.41431 | 0.01781 | 0.4579 | 0.41473 | 0.2102 | 5.287 | 4.784 | 0.20565 | 5.2873 | 4.7888 | 0.10925 | -3.2438 | -2.7435 | -0.11086 | 3.5024 | 2.849 | -0.21469 | -2.988 | -2.7052 | 0.20029 | 2.9902 | 2.986 | 62.8274 | 12.4189 | -113.5763 | -118.3545 | -167.6488 | 66.4709 | 1.146 | 0.83417 | 0.80538 | 1.1132 | 0.87099 | 0.86181 | -0.20171 | -124.9321 | 111.0206 | 0.60931 | -127.1595 | 112.8156

## LLG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.18809 | 0.99467 | 0.78791 | 0.18826 | 0.99465 | 0.78779 | 2.1719 | 11.4854 | 9.098 | 2.1738 | 11.4852 | 9.0966 | -0.41341 | 9.9522 | 4.8413 | 0.45846 | -8.8274 | -4.7824 | 2.2577 | 5.8014 | 7.1136 | -2.3586 | -5.4323 | -6.308 | -101.1559 | -158.4953 | 60.7956 | 78.8841 | 21.5169 | -119.2172 | 1.0568 | 1.003 | 0.94578 | 1.1053 | 0.90247 | 0.87021 | -0.7792 | -128.2563 | 116.5577 | -0.11603 | -126.8757 | 113.6154
Line_1 | 0.10321 | 0.72431 | 0.60013 | 0.10276 | 0.72426 | 0.60052 | 1.1918 | 8.3636 | 6.9298 | 1.1866 | 8.363 | 6.9342 | 0.28931 | -5.6163 | -3.7115 | -0.28241 | 6.2211 | 3.8073 | -1.3348 | -4.139 | -4.1681 | 1.2808 | 4.2732 | 4.6815 | 77.5695 | 18.6792 | -117.2956 | -102.551 | -161.3604 | 62.7354 | 1.146 | 0.83417 | 0.80538 | 1.1053 | 0.90247 | 0.87021 | -0.20171 | -124.9321 | 111.0206 | -0.11603 | -126.8757 | 113.6154
Line_2 | 0.085925 | 0.27378 | 0.18851 | 0.085569 | 0.27373 | 0.18874 | 0.99217 | 3.1614 | 2.1767 | 0.98806 | 3.1607 | 2.1793 | 0.18912 | -2.5231 | -0.984 | -0.17605 | 2.6063 | 0.97516 | -1.0882 | -1.1026 | -1.5971 | 1.0778 | 1.1591 | 1.6266 | 80.7501 | 29.2353 | -125.5469 | -99.3925 | -150.8509 | 54.559 | 1.1132 | 0.87099 | 0.86181 | 1.1053 | 0.90247 | 0.87021 | 0.60931 | -127.1595 | 112.8156 | -0.11603 | -126.8757 | 113.6154
Line_3 | 0.018204 | 0.45787 | 0.41431 | 0.01781 | 0.4579 | 0.41473 | 0.2102 | 5.287 | 4.784 | 0.20565 | 5.2873 | 4.7888 | 0.10925 | -3.2438 | -2.7435 | -0.11086 | 3.5024 | 2.849 | -0.21469 | -2.988 | -2.7052 | 0.20029 | 2.9902 | 2.986 | 62.8274 | 12.4189 | -113.5763 | -118.3545 | -167.6488 | 66.4709 | 1.146 | 0.83417 | 0.80538 | 1.1132 | 0.87099 | 0.86181 | -0.20171 | -124.9321 | 111.0206 | 0.60931 | -127.1595 | 112.8156

## LLG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.54514 | 2.8536 | 2.3663 | 0.54564 | 2.8536 | 2.3661 | 6.2948 | 32.9502 | 27.3234 | 6.3005 | 32.95 | 27.3211 | -0.66473 | 24.3988 | 3.5016 | 1.1768 | -10.7003 | -1.7198 | 5.5155 | 3.3222 | 12.577 | -6.4284 | -0.05202 | -6.3698 | -98.1442 | -161.3579 | 40.5286 | 81.8838 | 18.6533 | -139.4841 | 0.88254 | 0.74731 | 0.47781 | 1.0373 | 0.32475 | 0.24149 | -1.272 | -153.6041 | 114.9708 | 2.2576 | -161.0682 | 115.4071
Line_1 | 0.312 | 2.1385 | 1.7864 | 0.31058 | 2.1383 | 1.7874 | 3.6027 | 24.6931 | 20.6281 | 3.5862 | 24.6905 | 20.6385 | 0.97774 | -7.3406e-11 | -3.4397e-11 | -0.92748 | 7.9918 | 1.4894 | -4.144 | -4.3883e-11 | -6.3351e-11 | 3.6024 | 0.64969 | 4.7563 | 77.9039 | 14.3239 | -137.2434 | -102.1802 | -165.7158 | 42.7949 | 1.1818 | 0 | 0 | 1.0373 | 0.32475 | 0.24149 | 1.1794 | 0 | 0 | 2.2576 | -161.0682 | 115.4071
Line_2 | 0.23792 | 0.73987 | 0.58424 | 0.23687 | 0.73967 | 0.58448 | 2.7473 | 8.5433 | 6.7462 | 2.7351 | 8.541 | 6.749 | 0.45965 | -1.7645 | -0.20861 | -0.24933 | 2.7085 | 0.23033 | -2.8528 | 1.2505 | -1.6581 | 2.826 | -0.59767 | 1.6135 | 87.3298 | 31.464 | -146.5799 | -92.7844 | -148.6244 | 33.5313 | 1.0518 | 0.25315 | 0.24772 | 1.0373 | 0.32475 | 0.24149 | 6.4828 | 176.1383 | 116.2493 | 2.2576 | -161.0682 | 115.4071
Line_3 | 0.086814 | 1.4477 | 1.2134 | 0.085814 | 1.4479 | 1.2144 | 1.0024 | 16.7171 | 14.0116 | 0.9909 | 16.719 | 14.0222 | 0.75588 | -4.467e-11 | -2.6633e-11 | -0.74655 | 4.1745 | 1.2458 | -0.91226 | -3.6835e-11 | -4.1088e-11 | 0.72722 | -0.69754 | 3.2424 | 51.5351 | 5.6863 | -132.7926 | -129.2687 | -174.3755 | 47.2676 | 1.1818 | 0 | 0 | 1.0518 | 0.25315 | 0.24772 | 1.1794 | 0 | 0 | 6.4828 | 176.1383 | 116.2493

## LLG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.54514 | 2.8536 | 2.3663 | 0.54564 | 2.8536 | 2.3661 | 6.2948 | 32.9502 | 27.3234 | 6.3005 | 32.95 | 27.3211 | -0.66473 | 24.3988 | 3.5016 | 1.1768 | -10.7003 | -1.7198 | 5.5155 | 3.3222 | 12.577 | -6.4284 | -0.05202 | -6.3698 | -98.1442 | -161.3579 | 40.5286 | 81.8838 | 18.6533 | -139.4841 | 0.88254 | 0.74731 | 0.47781 | 1.0373 | 0.32475 | 0.24149 | -1.272 | -153.6041 | 114.9708 | 2.2576 | -161.0682 | 115.4071
Line_1 | 0.312 | 2.1385 | 1.7864 | 0.31058 | 2.1383 | 1.7874 | 3.6027 | 24.6931 | 20.6281 | 3.5862 | 24.6905 | 20.6385 | 0.97774 | -7.3406e-11 | -3.4397e-11 | -0.92748 | 7.9918 | 1.4894 | -4.144 | -4.3883e-11 | -6.3351e-11 | 3.6024 | 0.64969 | 4.7563 | 77.9039 | 14.3239 | -137.2434 | -102.1802 | -165.7158 | 42.7949 | 1.1818 | 0 | 0 | 1.0373 | 0.32475 | 0.24149 | 1.1794 | 0 | 0 | 2.2576 | -161.0682 | 115.4071
Line_2 | 0.23792 | 0.73987 | 0.58424 | 0.23687 | 0.73967 | 0.58448 | 2.7473 | 8.5433 | 6.7462 | 2.7351 | 8.541 | 6.749 | 0.45965 | -1.7645 | -0.20861 | -0.24933 | 2.7085 | 0.23033 | -2.8528 | 1.2505 | -1.6581 | 2.826 | -0.59767 | 1.6135 | 87.3298 | 31.464 | -146.5799 | -92.7844 | -148.6244 | 33.5313 | 1.0518 | 0.25315 | 0.24772 | 1.0373 | 0.32475 | 0.24149 | 6.4828 | 176.1383 | 116.2493 | 2.2576 | -161.0682 | 115.4071
Line_3 | 0.086814 | 1.4477 | 1.2134 | 0.085814 | 1.4479 | 1.2144 | 1.0024 | 16.7171 | 14.0116 | 0.9909 | 16.719 | 14.0222 | 0.75588 | -4.467e-11 | -2.6633e-11 | -0.74655 | 4.1745 | 1.2458 | -0.91226 | -3.6835e-11 | -4.1088e-11 | 0.72722 | -0.69754 | 3.2424 | 51.5351 | 5.6863 | -132.7926 | -129.2687 | -174.3755 | 47.2676 | 1.1818 | 0 | 0 | 1.0518 | 0.25315 | 0.24772 | 1.1794 | 0 | 0 | 6.4828 | 176.1383 | 116.2493

## LLG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.19111 | 0.79617 | 0.65666 | 0.19129 | 0.79617 | 0.65657 | 2.2068 | 9.1934 | 7.5825 | 2.2088 | 9.1934 | 7.5814 | 0.24109 | 8.0396 | 3.6736 | -0.18711 | -6.8803 | -3.5547 | 2.1066 | 3.0227 | 5.4532 | -2.2183 | -2.8132 | -4.8679 | -84.4371 | -148.8733 | 60.2016 | 95.5873 | 31.1405 | -119.8129 | 0.96083 | 0.93426 | 0.86715 | 1.0079 | 0.80854 | 0.79506 | -0.96578 | -128.2683 | 116.2348 | 0.76603 | -126.6211 | 114.0489
Line_1 | 0.10887 | 0.59617 | 0.50451 | 0.10837 | 0.59608 | 0.50488 | 1.2571 | 6.8839 | 5.8256 | 1.2514 | 6.8829 | 5.8299 | -0.0098004 | -4.2756 | -2.7633 | 0.010922 | 4.9499 | 2.9064 | -1.3291 | -2.5346 | -3.158 | 1.2612 | 2.5433 | 3.6107 | 91.3311 | 26.2333 | -117.1589 | -88.7378 | -153.8153 | 62.881 | 1.0573 | 0.72203 | 0.72032 | 1.0079 | 0.80854 | 0.79506 | 0.90868 | -123.1068 | 111.6553 | 0.76603 | -126.6211 | 114.0489
Line_2 | 0.083996 | 0.20887 | 0.15395 | 0.083623 | 0.20877 | 0.15408 | 0.9699 | 2.4118 | 1.7776 | 0.9656 | 2.4107 | 1.7792 | -0.15275 | -1.8478 | -0.65276 | 0.17619 | 1.9304 | 0.64831 | -0.96381 | -0.2117 | -1.2621 | 0.95714 | 0.26989 | 1.2572 | 101.2914 | 45.5258 | -128.8118 | -78.8039 | -134.5801 | 51.3276 | 1.0061 | 0.77116 | 0.79932 | 1.0079 | 0.80854 | 0.79506 | 2.2859 | -127.9384 | 113.8394 | 0.76603 | -126.6211 | 114.0489
Line_3 | 0.029996 | 0.40487 | 0.35499 | 0.029648 | 0.40492 | 0.35538 | 0.34636 | 4.675 | 4.0991 | 0.34234 | 4.6756 | 4.1036 | 0.17341 | -2.5689 | -2.1304 | -0.17445 | 2.9286 | 2.2808 | -0.32255 | -2.1897 | -2.0445 | 0.29699 | 2.1034 | 2.3573 | 62.6459 | 16.4502 | -112.1659 | -118.1437 | -163.6256 | 67.8946 | 1.0573 | 0.72203 | 0.72032 | 1.0061 | 0.77116 | 0.79932 | 0.90868 | -123.1068 | 111.6553 | 2.2859 | -127.9384 | 113.8394

## LLG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.19111 | 0.79617 | 0.65666 | 0.19129 | 0.79617 | 0.65657 | 2.2068 | 9.1934 | 7.5825 | 2.2088 | 9.1934 | 7.5814 | 0.24109 | 8.0396 | 3.6736 | -0.18711 | -6.8803 | -3.5547 | 2.1066 | 3.0227 | 5.4532 | -2.2183 | -2.8132 | -4.8679 | -84.4371 | -148.8733 | 60.2016 | 95.5873 | 31.1405 | -119.8129 | 0.96083 | 0.93426 | 0.86715 | 1.0079 | 0.80854 | 0.79506 | -0.96578 | -128.2683 | 116.2348 | 0.76603 | -126.6211 | 114.0489
Line_1 | 0.10887 | 0.59617 | 0.50451 | 0.10837 | 0.59608 | 0.50488 | 1.2571 | 6.8839 | 5.8256 | 1.2514 | 6.8829 | 5.8299 | -0.0098004 | -4.2756 | -2.7633 | 0.010922 | 4.9499 | 2.9064 | -1.3291 | -2.5346 | -3.158 | 1.2612 | 2.5433 | 3.6107 | 91.3311 | 26.2333 | -117.1589 | -88.7378 | -153.8153 | 62.881 | 1.0573 | 0.72203 | 0.72032 | 1.0079 | 0.80854 | 0.79506 | 0.90868 | -123.1068 | 111.6553 | 0.76603 | -126.6211 | 114.0489
Line_2 | 0.083996 | 0.20887 | 0.15395 | 0.083623 | 0.20877 | 0.15408 | 0.9699 | 2.4118 | 1.7776 | 0.9656 | 2.4107 | 1.7792 | -0.15275 | -1.8478 | -0.65276 | 0.17619 | 1.9304 | 0.64831 | -0.96381 | -0.2117 | -1.2621 | 0.95714 | 0.26989 | 1.2572 | 101.2914 | 45.5258 | -128.8118 | -78.8039 | -134.5801 | 51.3276 | 1.0061 | 0.77116 | 0.79932 | 1.0079 | 0.80854 | 0.79506 | 2.2859 | -127.9384 | 113.8394 | 0.76603 | -126.6211 | 114.0489
Line_3 | 0.029996 | 0.40487 | 0.35499 | 0.029648 | 0.40492 | 0.35538 | 0.34636 | 4.675 | 4.0991 | 0.34234 | 4.6756 | 4.1036 | 0.17341 | -2.5689 | -2.1304 | -0.17445 | 2.9286 | 2.2808 | -0.32255 | -2.1897 | -2.0445 | 0.29699 | 2.1034 | 2.3573 | 62.6459 | 16.4502 | -112.1659 | -118.1437 | -163.6256 | 67.8946 | 1.0573 | 0.72203 | 0.72032 | 1.0061 | 0.77116 | 0.79932 | 0.90868 | -123.1068 | 111.6553 | 2.2859 | -127.9384 | 113.8394