## LLL_max_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 3.6999 | 3.6999 | 0 | 0 | 128.1693 | 128.1693 | 35.5926 | -14.237 | 40.3839 | -16.1536 | -73.5107 | 106.4893 | 0.41999 | 0.168 | -24.9022 | -24.9022
Line_1 | 2.4666 | 2.4666 | 4.9647 | 0 | 85.4462 | 85.4462 | -1e-07 | 9.4914 | -1e-07 | 10.769 | 106.4893 | -73.5107 | 0 | 0.168 | 0 | -24.9022
Line_2 | 1.2333 | 1.2333 | 0 | 0 | 42.7231 | 42.7231 | -2.3728 | 4.7457 | -2.6923 | 5.3845 | 106.4893 | -73.5107 | 0.083999 | 0.168 | -24.9022 | -24.9022
Line_3 | 1.2333 | 1.2333 | 2.4824 | 0 | 42.7231 | 42.7231 | -1e-07 | 2.3728 | -1e-07 | 2.6923 | 106.4893 | -73.5107 | 0 | 0.083999 | 0 | -24.9022

## LLL_max_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 3.6999 | 3.6999 | 0 | 0 | 128.1693 | 128.1693 | 35.5926 | -14.237 | 40.3839 | -16.1536 | -73.5107 | 106.4893 | 0.41999 | 0.168 | -24.9022 | -24.9022
Line_1 | 2.4666 | 2.4666 | 4.9647 | 0 | 85.4462 | 85.4462 | -1e-07 | 9.4914 | -1e-07 | 10.769 | 106.4893 | -73.5107 | 0 | 0.168 | 0 | -24.9022
Line_2 | 1.2333 | 1.2333 | 0 | 0 | 42.7231 | 42.7231 | -2.3728 | 4.7457 | -2.6923 | 5.3845 | 106.4893 | -73.5107 | 0.083999 | 0.168 | -24.9022 | -24.9022
Line_3 | 1.2333 | 1.2333 | 2.4824 | 0 | 42.7231 | 42.7231 | -1e-07 | 2.3728 | -1e-07 | 2.6923 | 106.4893 | -73.5107 | 0 | 0.083999 | 0 | -24.9022

## LLL_max_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 1.2428 | 1.2428 | 0 | 0 | 43.0531 | 43.0531 | 27.1857 | -24.7761 | 27.7264 | -24.9923 | -54.2264 | 125.7736 | 0.90192 | 0.81741 | -8.6624 | -8.9775
Line_1 | 0.82856 | 0.82856 | 1.6677 | 0 | 28.7021 | 28.7021 | -15.4464 | 16.5174 | -15.4464 | 16.6616 | 125.7736 | -54.2264 | 0.76108 | 0.81741 | -9.2264 | -8.9775
Line_2 | 0.41428 | 0.41428 | 0 | 0 | 14.351 | 14.351 | -7.991 | 8.2587 | -8.027 | 8.3308 | 125.7736 | -54.2264 | 0.78924 | 0.81741 | -9.0975 | -8.9775
Line_3 | 0.41428 | 0.41428 | 0.83384 | 0 | 14.351 | 14.351 | -7.7232 | 7.991 | -7.7232 | 8.027 | 125.7736 | -54.2264 | 0.76108 | 0.78924 | -9.2264 | -9.0975

## LLL_max_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 1.2428 | 1.2428 | 0 | 0 | 43.0531 | 43.0531 | 27.1857 | -24.7761 | 27.7264 | -24.9923 | -54.2264 | 125.7736 | 0.90192 | 0.81741 | -8.6624 | -8.9775
Line_1 | 0.82856 | 0.82856 | 1.6677 | 0 | 28.7021 | 28.7021 | -15.4464 | 16.5174 | -15.4464 | 16.6616 | 125.7736 | -54.2264 | 0.76108 | 0.81741 | -9.2264 | -8.9775
Line_2 | 0.41428 | 0.41428 | 0 | 0 | 14.351 | 14.351 | -7.991 | 8.2587 | -8.027 | 8.3308 | 125.7736 | -54.2264 | 0.78924 | 0.81741 | -9.0975 | -8.9775
Line_3 | 0.41428 | 0.41428 | 0.83384 | 0 | 14.351 | 14.351 | -7.7232 | 7.991 | -7.7232 | 8.027 | 125.7736 | -54.2264 | 0.76108 | 0.78924 | -9.2264 | -9.0975

## LLL_min_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 3.0092 | 3.0092 | 0 | 0 | 104.2421 | 104.2421 | 45.2043 | -18.0817 | 26.7133 | -10.6853 | -62.3733 | 117.6267 | 0.50371 | 0.20148 | -31.7926 | -31.7926
Line_1 | 2.0061 | 2.0061 | 3.4722 | 0 | 69.4947 | 69.4947 | -1e-07 | 12.0545 | -1e-07 | 7.1235 | 117.6267 | -62.3733 | 0 | 0.20148 | 0 | -31.7926
Line_2 | 1.0031 | 1.0031 | 0 | 0 | 34.7474 | 34.7474 | -3.0136 | 6.0272 | -1.7809 | 3.5618 | 117.6267 | -62.3733 | 0.10074 | 0.20148 | -31.7926 | -31.7926
Line_3 | 1.0031 | 1.0031 | 1.7361 | 0 | 34.7474 | 34.7474 | -1e-07 | 3.0136 | -1e-07 | 1.7809 | 117.6267 | -62.3733 | 0 | 0.10074 | 0 | -31.7926

## LLL_min_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 3.0092 | 3.0092 | 0 | 0 | 104.2421 | 104.2421 | 45.2043 | -18.0817 | 26.7133 | -10.6853 | -62.3733 | 117.6267 | 0.50371 | 0.20148 | -31.7926 | -31.7926
Line_1 | 2.0061 | 2.0061 | 3.4722 | 0 | 69.4947 | 69.4947 | -1e-07 | 12.0545 | -1e-07 | 7.1235 | 117.6267 | -62.3733 | 0 | 0.20148 | 0 | -31.7926
Line_2 | 1.0031 | 1.0031 | 0 | 0 | 34.7474 | 34.7474 | -3.0136 | 6.0272 | -1.7809 | 3.5618 | 117.6267 | -62.3733 | 0.10074 | 0.20148 | -31.7926 | -31.7926
Line_3 | 1.0031 | 1.0031 | 1.7361 | 0 | 34.7474 | 34.7474 | -1e-07 | 3.0136 | -1e-07 | 1.7809 | 117.6267 | -62.3733 | 0 | 0.10074 | 0 | -31.7926

## LLL_min_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 1.0697 | 1.0697 | 0 | 0 | 37.0569 | 37.0569 | 22.8777 | -19.4502 | 20.541 | -18.5155 | -51.0933 | 128.9067 | 0.8297 | 0.72467 | -9.1739 | -7.5036
Line_1 | 0.71316 | 0.71316 | 1.2343 | 0 | 24.7046 | 24.7046 | -11.4434 | 12.9668 | -11.4434 | 12.3437 | 128.9067 | -51.0933 | 0.65508 | 0.72467 | -6.0933 | -7.5036
Line_2 | 0.35658 | 0.35658 | 0 | 0 | 12.3523 | 12.3523 | -6.1026 | 6.4834 | -5.9468 | 6.1718 | 128.9067 | -51.0933 | 0.68982 | 0.72467 | -6.834 | -7.5036
Line_3 | 0.35658 | 0.35658 | 0.61717 | 0 | 12.3523 | 12.3523 | -5.7217 | 6.1026 | -5.7217 | 5.9468 | 128.9067 | -51.0933 | 0.65508 | 0.68982 | -6.0933 | -6.834

## LLL_min_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 1.0697 | 1.0697 | 0 | 0 | 37.0569 | 37.0569 | 22.8777 | -19.4502 | 20.541 | -18.5155 | -51.0933 | 128.9067 | 0.8297 | 0.72467 | -9.1739 | -7.5036
Line_1 | 0.71316 | 0.71316 | 1.2343 | 0 | 24.7046 | 24.7046 | -11.4434 | 12.9668 | -11.4434 | 12.3437 | 128.9067 | -51.0933 | 0.65508 | 0.72467 | -6.0933 | -7.5036
Line_2 | 0.35658 | 0.35658 | 0 | 0 | 12.3523 | 12.3523 | -6.1026 | 6.4834 | -5.9468 | 6.1718 | 128.9067 | -51.0933 | 0.68982 | 0.72467 | -6.834 | -7.5036
Line_3 | 0.35658 | 0.35658 | 0.61717 | 0 | 12.3523 | 12.3523 | -5.7217 | 6.1026 | -5.7217 | 5.9468 | 128.9067 | -51.0933 | 0.65508 | 0.68982 | -6.0933 | -6.834

## LL_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 3.2042 | 3.2042 | 0 | 3.2042 | 3.2042 | 0 | 36.9993 | 36.9993 | 0 | 36.9993 | 36.9993 | -7.816e-14 | 28.4108 | -10.6145 | 6.7738e-14 | -23.0719 | 15.9534 | -1.6667e-27 | 4.32 | 15.8719 | 1.5354e-27 | 1.7376 | -9.8143 | 0 | -163.5107 | 16.4893 | 0 | 16.4893 | -163.5107 | 1.1 | 0.7767 | 0.51607 | 1.1 | 0.62534 | 0.50624 | 1.2218e-12 | -154.8648 | 140.2623 | 1.2987e-12 | -167.8176 | 164.89
Line_1 | 0 | 2.1362 | 2.1362 | 0 | 2.1362 | 2.1362 | 0 | 24.6662 | 24.6662 | 0 | 24.6662 | 24.6662 | 1.5632e-14 | -13.0085 | 13.0085 | -3.6475e-14 | 15.3813 | -10.6356 | 5.2106e-15 | 3.8506 | -3.8506 | -5.2106e-15 | -1.1584 | 6.5429 | 0 | 16.4893 | -163.5107 | 0 | -163.5107 | 16.4893 | 1.1 | 0.55 | 0.55 | 1.1 | 0.62534 | 0.50624 | 1.313e-12 | 180 | -180 | 1.2987e-12 | -167.8176 | 164.89
Line_2 | 0 | 1.0681 | 1.0681 | 0 | 1.0681 | 1.0681 | 0 | 12.3331 | 12.3331 | 0 | 12.3331 | 12.3331 | 1.5632e-14 | -7.0974 | 5.911 | -3.6475e-14 | 7.6906 | -5.3178 | 3.5792e-28 | 1.2523 | -2.5984 | -8.2678e-28 | -0.57919 | 3.2714 | 0 | 16.4893 | -163.5107 | 0 | -163.5107 | 16.4893 | 1.1 | 0.58437 | 0.52354 | 1.1 | 0.62534 | 0.50624 | 1.3119e-12 | -173.5168 | 172.7598 | 1.2987e-12 | -167.8176 | 164.89
Line_3 | 0 | 1.0681 | 1.0681 | 0 | 1.0681 | 1.0681 | 0 | 12.3331 | 12.3331 | 0 | 12.3331 | 12.3331 | -1.0421e-14 | -6.5042 | 6.5042 | -1.0421e-14 | 7.0974 | -5.911 | 5.2106e-15 | 1.9253 | -1.9253 | -5.2106e-15 | -1.2523 | 2.5984 | 0 | 16.4893 | -163.5107 | 0 | -163.5107 | 16.4893 | 1.1 | 0.55 | 0.55 | 1.1 | 0.58437 | 0.52354 | 1.313e-12 | 180 | -180 | 1.3119e-12 | -173.5168 | 172.7598

## LL_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 3.2042 | 3.2042 | 0 | 3.2042 | 3.2042 | 0 | 36.9993 | 36.9993 | 0 | 36.9993 | 36.9993 | -7.816e-14 | 28.4108 | -10.6145 | 6.7738e-14 | -23.0719 | 15.9534 | -1.6667e-27 | 4.32 | 15.8719 | 1.5354e-27 | 1.7376 | -9.8143 | 0 | -163.5107 | 16.4893 | 0 | 16.4893 | -163.5107 | 1.1 | 0.7767 | 0.51607 | 1.1 | 0.62534 | 0.50624 | 1.2218e-12 | -154.8648 | 140.2623 | 1.2987e-12 | -167.8176 | 164.89
Line_1 | 0 | 2.1362 | 2.1362 | 0 | 2.1362 | 2.1362 | 0 | 24.6662 | 24.6662 | 0 | 24.6662 | 24.6662 | 1.5632e-14 | -13.0085 | 13.0085 | -3.6475e-14 | 15.3813 | -10.6356 | 5.2106e-15 | 3.8506 | -3.8506 | -5.2106e-15 | -1.1584 | 6.5429 | 0 | 16.4893 | -163.5107 | 0 | -163.5107 | 16.4893 | 1.1 | 0.55 | 0.55 | 1.1 | 0.62534 | 0.50624 | 1.313e-12 | 180 | -180 | 1.2987e-12 | -167.8176 | 164.89
Line_2 | 0 | 1.0681 | 1.0681 | 0 | 1.0681 | 1.0681 | 0 | 12.3331 | 12.3331 | 0 | 12.3331 | 12.3331 | 1.5632e-14 | -7.0974 | 5.911 | -3.6475e-14 | 7.6906 | -5.3178 | 3.5792e-28 | 1.2523 | -2.5984 | -8.2678e-28 | -0.57919 | 3.2714 | 0 | 16.4893 | -163.5107 | 0 | -163.5107 | 16.4893 | 1.1 | 0.58437 | 0.52354 | 1.1 | 0.62534 | 0.50624 | 1.3119e-12 | -173.5168 | 172.7598 | 1.2987e-12 | -167.8176 | 164.89
Line_3 | 0 | 1.0681 | 1.0681 | 0 | 1.0681 | 1.0681 | 0 | 12.3331 | 12.3331 | 0 | 12.3331 | 12.3331 | -1.0421e-14 | -6.5042 | 6.5042 | -1.0421e-14 | 7.0974 | -5.911 | 5.2106e-15 | 1.9253 | -1.9253 | -5.2106e-15 | -1.2523 | 2.5984 | 0 | 16.4893 | -163.5107 | 0 | -163.5107 | 16.4893 | 1.1 | 0.55 | 0.55 | 1.1 | 0.58437 | 0.52354 | 1.313e-12 | 180 | -180 | 1.3119e-12 | -173.5168 | 172.7598

## LL_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 1.6287 | 1.6287 | 0 | 1.6287 | 1.6287 | 0 | 18.8063 | 18.8063 | 0 | 18.8063 | 18.8063 | -3.3869e-14 | 17.8002 | 0.06044 | 3.3869e-14 | -16.4209 | 1.3189 | -7.816e-15 | 3.9189 | 14.5607 | 1.0421e-14 | -2.3539 | -12.9957 | 0 | -149.0411 | 30.9589 | 0 | 30.9589 | -149.0411 | 1.1 | 0.96917 | 0.77425 | 1.1 | 0.88208 | 0.69458 | 5.804e-13 | -136.625 | 120.7211 | 6.1825e-13 | -140.8835 | 126.7539
Line_1 | 0 | 1.0858 | 1.0858 | 0 | 1.0858 | 1.0858 | 0 | 12.5375 | 12.5375 | 0 | 12.5375 | 12.5375 | 1.8237e-14 | -10.3342 | 1.4923 | -2.0843e-14 | 10.9473 | -0.87927 | 7.816e-15 | -0.87368 | -7.9682 | -7.816e-15 | 1.5692 | 8.6638 | 0 | 30.9589 | -149.0411 | 0 | -149.0411 | 30.9589 | 1.1 | 0.8272 | 0.6466 | 1.1 | 0.88208 | 0.69458 | 6.2572e-13 | -144.2087 | 131.5665 | 6.1825e-13 | -140.8835 | 126.7539
Line_2 | 0 | 0.54289 | 0.54289 | 0 | 0.54289 | 0.54289 | 0 | 6.2688 | 6.2688 | 0 | 6.2688 | 6.2688 | 1.3027e-14 | -5.3204 | 0.59289 | -1.8237e-14 | 5.4736 | -0.43963 | 7.816e-15 | -0.61073 | -4.158 | -5.2106e-15 | 0.78462 | 4.3319 | 0 | 30.9589 | -149.0411 | 0 | -149.0411 | 30.9589 | 1.1 | 0.85428 | 0.67 | 1.1 | 0.88208 | 0.69458 | 6.2508e-13 | -142.4927 | 129.0741 | 6.1825e-13 | -140.8835 | 126.7539
Line_3 | 0 | 0.54289 | 0.54289 | 0 | 0.54289 | 0.54289 | 0 | 6.2688 | 6.2688 | 0 | 6.2688 | 6.2688 | 2.6053e-15 | -5.1671 | 0.74615 | -1.0421e-14 | 5.3204 | -0.59289 | 2.6053e-15 | -0.43684 | -3.9841 | -1.1369e-28 | 0.61073 | 4.158 | 0 | 30.9589 | -149.0411 | 0 | -149.0411 | 30.9589 | 1.1 | 0.8272 | 0.6466 | 1.1 | 0.85428 | 0.67 | 6.2572e-13 | -144.2087 | 131.5665 | 6.2508e-13 | -142.4927 | 129.0741

## LL_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 1.6287 | 1.6287 | 0 | 1.6287 | 1.6287 | 0 | 18.8063 | 18.8063 | 0 | 18.8063 | 18.8063 | -3.3869e-14 | 17.8002 | 0.06044 | 3.3869e-14 | -16.4209 | 1.3189 | -7.816e-15 | 3.9189 | 14.5607 | 1.0421e-14 | -2.3539 | -12.9957 | 0 | -149.0411 | 30.9589 | 0 | 30.9589 | -149.0411 | 1.1 | 0.96917 | 0.77425 | 1.1 | 0.88208 | 0.69458 | 5.804e-13 | -136.625 | 120.7211 | 6.1825e-13 | -140.8835 | 126.7539
Line_1 | 0 | 1.0858 | 1.0858 | 0 | 1.0858 | 1.0858 | 0 | 12.5375 | 12.5375 | 0 | 12.5375 | 12.5375 | 1.8237e-14 | -10.3342 | 1.4923 | -2.0843e-14 | 10.9473 | -0.87927 | 7.816e-15 | -0.87368 | -7.9682 | -7.816e-15 | 1.5692 | 8.6638 | 0 | 30.9589 | -149.0411 | 0 | -149.0411 | 30.9589 | 1.1 | 0.8272 | 0.6466 | 1.1 | 0.88208 | 0.69458 | 6.2572e-13 | -144.2087 | 131.5665 | 6.1825e-13 | -140.8835 | 126.7539
Line_2 | 0 | 0.54289 | 0.54289 | 0 | 0.54289 | 0.54289 | 0 | 6.2688 | 6.2688 | 0 | 6.2688 | 6.2688 | 1.3027e-14 | -5.3204 | 0.59289 | -1.8237e-14 | 5.4736 | -0.43963 | 7.816e-15 | -0.61073 | -4.158 | -5.2106e-15 | 0.78462 | 4.3319 | 0 | 30.9589 | -149.0411 | 0 | -149.0411 | 30.9589 | 1.1 | 0.85428 | 0.67 | 1.1 | 0.88208 | 0.69458 | 6.2508e-13 | -142.4927 | 129.0741 | 6.1825e-13 | -140.8835 | 126.7539
Line_3 | 0 | 0.54289 | 0.54289 | 0 | 0.54289 | 0.54289 | 0 | 6.2688 | 6.2688 | 0 | 6.2688 | 6.2688 | 2.6053e-15 | -5.1671 | 0.74615 | -1.0421e-14 | 5.3204 | -0.59289 | 2.6053e-15 | -0.43684 | -3.9841 | -1.1369e-28 | 0.61073 | 4.158 | 0 | 30.9589 | -149.0411 | 0 | -149.0411 | 30.9589 | 1.1 | 0.8272 | 0.6466 | 1.1 | 0.85428 | 0.67 | 6.2572e-13 | -144.2087 | 131.5665 | 6.2508e-13 | -142.4927 | 129.0741

## LL_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 2.6061 | 2.6061 | 0 | 2.6061 | 2.6061 | 0 | 30.0921 | 30.0921 | 0 | 30.0921 | 30.0921 | -2.7237e-14 | 24.6317 | -2.0295 | 2.3685e-14 | -17.851 | 8.8102 | -1.4211e-14 | -0.29866 | 13.6553 | 9.4739e-15 | 4.3057 | -9.6483 | 0 | -152.3733 | 27.6267 | 0 | 27.6267 | -152.3733 | 1 | 0.8186 | 0.45877 | 1 | 0.61023 | 0.43419 | 1.2603e-12 | -153.068 | 126.0805 | 1.2546e-12 | -165.934 | 160.0269
Line_1 | 0 | 1.7374 | 1.7374 | 0 | 1.7374 | 1.7374 | 0 | 20.0614 | 20.0614 | 0 | 20.0614 | 20.0614 | -4.737e-15 | -8.8871 | 8.8871 | -1.1842e-15 | 11.9007 | -5.8735 | 1.1842e-14 | 4.6513 | -4.6513 | -1.6579e-14 | -2.8704 | 6.4322 | 0 | 27.6267 | -152.3733 | 0 | -152.3733 | 27.6267 | 1 | 0.5 | 0.5 | 1 | 0.61023 | 0.43419 | 1.2229e-12 | -180 | 180 | 1.2546e-12 | -165.934 | 160.0269
Line_2 | 0 | 0.86868 | 0.86868 | 0 | 0.86868 | 0.86868 | 0 | 10.0307 | 10.0307 | 0 | 10.0307 | 10.0307 | -9.4739e-15 | -5.1969 | 3.6901 | 3.5527e-15 | 5.9503 | -2.9367 | 1.6579e-14 | 1.8804 | -2.7709 | -1.6579e-14 | -1.4352 | 3.2161 | 0 | 27.6267 | -152.3733 | 0 | -152.3733 | 27.6267 | 1 | 0.55098 | 0.46005 | 1 | 0.61023 | 0.43419 | 1.2301e-12 | -172.2653 | 170.7242 | 1.2546e-12 | -165.934 | 160.0269
Line_3 | 0 | 0.86868 | 0.86868 | 0 | 0.86868 | 0.86868 | 0 | 10.0307 | 10.0307 | 0 | 10.0307 | 10.0307 | 2.3685e-15 | -4.4435 | 4.4435 | -7.1054e-15 | 5.1969 | -3.6901 | 5.0552e-29 | 2.3257 | -2.3257 | 4.737e-15 | -1.8804 | 2.7709 | 0 | 27.6267 | -152.3733 | 0 | -152.3733 | 27.6267 | 1 | 0.5 | 0.5 | 1 | 0.55098 | 0.46005 | 1.2229e-12 | -180 | 180 | 1.2301e-12 | -172.2653 | 170.7242

## LL_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 2.6061 | 2.6061 | 0 | 2.6061 | 2.6061 | 0 | 30.0921 | 30.0921 | 0 | 30.0921 | 30.0921 | -2.7237e-14 | 24.6317 | -2.0295 | 2.3685e-14 | -17.851 | 8.8102 | -1.4211e-14 | -0.29866 | 13.6553 | 9.4739e-15 | 4.3057 | -9.6483 | 0 | -152.3733 | 27.6267 | 0 | 27.6267 | -152.3733 | 1 | 0.8186 | 0.45877 | 1 | 0.61023 | 0.43419 | 1.2603e-12 | -153.068 | 126.0805 | 1.2546e-12 | -165.934 | 160.0269
Line_1 | 0 | 1.7374 | 1.7374 | 0 | 1.7374 | 1.7374 | 0 | 20.0614 | 20.0614 | 0 | 20.0614 | 20.0614 | -4.737e-15 | -8.8871 | 8.8871 | -1.1842e-15 | 11.9007 | -5.8735 | 1.1842e-14 | 4.6513 | -4.6513 | -1.6579e-14 | -2.8704 | 6.4322 | 0 | 27.6267 | -152.3733 | 0 | -152.3733 | 27.6267 | 1 | 0.5 | 0.5 | 1 | 0.61023 | 0.43419 | 1.2229e-12 | -180 | 180 | 1.2546e-12 | -165.934 | 160.0269
Line_2 | 0 | 0.86868 | 0.86868 | 0 | 0.86868 | 0.86868 | 0 | 10.0307 | 10.0307 | 0 | 10.0307 | 10.0307 | -9.4739e-15 | -5.1969 | 3.6901 | 3.5527e-15 | 5.9503 | -2.9367 | 1.6579e-14 | 1.8804 | -2.7709 | -1.6579e-14 | -1.4352 | 3.2161 | 0 | 27.6267 | -152.3733 | 0 | -152.3733 | 27.6267 | 1 | 0.55098 | 0.46005 | 1 | 0.61023 | 0.43419 | 1.2301e-12 | -172.2653 | 170.7242 | 1.2546e-12 | -165.934 | 160.0269
Line_3 | 0 | 0.86868 | 0.86868 | 0 | 0.86868 | 0.86868 | 0 | 10.0307 | 10.0307 | 0 | 10.0307 | 10.0307 | 2.3685e-15 | -4.4435 | 4.4435 | -7.1054e-15 | 5.1969 | -3.6901 | 5.0552e-29 | 2.3257 | -2.3257 | 4.737e-15 | -1.8804 | 2.7709 | 0 | 27.6267 | -152.3733 | 0 | -152.3733 | 27.6267 | 1 | 0.5 | 0.5 | 1 | 0.55098 | 0.46005 | 1.2229e-12 | -180 | 180 | 1.2301e-12 | -172.2653 | 170.7242

## LL_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 1.3721 | 1.3721 | 0 | 1.3721 | 1.3721 | 0 | 15.8432 | 15.8432 | 0 | 15.8432 | 15.8432 | -1.6579e-14 | 14.2512 | 1.4266 | 1.4803e-14 | -12.3717 | 0.45296 | -7.1054e-15 | 1.9064 | 11.2087 | 9.4739e-15 | -0.79565 | -10.098 | 0 | -144.0449 | 35.9551 | 0 | 35.9551 | -144.0449 | 1 | 0.90753 | 0.71319 | 1 | 0.7825 | 0.63801 | 6.1285e-13 | -136.4258 | 118.7019 | 6.0698e-13 | -140.3651 | 128.5235
Line_1 | 0 | 0.9147 | 0.9147 | 0 | 0.9147 | 0.9147 | 0 | 10.5621 | 10.5621 | 0 | 10.5621 | 10.5621 | -1.7764e-15 | -7.4125 | 1.1373 | 5.9212e-16 | 8.2478 | -0.30197 | 9.4739e-15 | -0.036791 | -6.2383 | -7.1054e-15 | 0.53044 | 6.732 | 0 | 35.9551 | -144.0449 | 0 | -144.0449 | 35.9551 | 1 | 0.70181 | 0.60037 | 1 | 0.7825 | 0.63801 | 5.8745e-13 | -143.7605 | 136.2873 | 6.0698e-13 | -140.3651 | 128.5235
Line_2 | 0 | 0.45735 | 0.45735 | 0 | 0.45735 | 0.45735 | 0 | 5.2811 | 5.2811 | 0 | 5.2811 | 5.2811 | -1.1842e-15 | -3.9151 | 0.35982 | 5.0182e-29 | 4.1239 | -0.15099 | 7.1054e-15 | -0.14181 | -3.2426 | -4.737e-15 | 0.26522 | 3.366 | 0 | 35.9551 | -144.0449 | 0 | -144.0449 | 35.9551 | 1 | 0.74183 | 0.61777 | 1 | 0.7825 | 0.63801 | 5.9209e-13 | -141.9705 | 132.2872 | 6.0698e-13 | -140.3651 | 128.5235
Line_3 | 0 | 0.45735 | 0.45735 | 0 | 0.45735 | 0.45735 | 0 | 5.2811 | 5.2811 | 0 | 5.2811 | 5.2811 | -5.9212e-16 | -3.7062 | 0.56866 | 5.9212e-16 | 3.9151 | -0.35982 | 2.3685e-15 | -0.018396 | -3.1192 | 6.1189e-30 | 0.14181 | 3.2426 | 0 | 35.9551 | -144.0449 | 0 | -144.0449 | 35.9551 | 1 | 0.70181 | 0.60037 | 1 | 0.74183 | 0.61777 | 5.8745e-13 | -143.7605 | 136.2873 | 5.9209e-13 | -141.9705 | 132.2872

## LL_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 1.3721 | 1.3721 | 0 | 1.3721 | 1.3721 | 0 | 15.8432 | 15.8432 | 0 | 15.8432 | 15.8432 | -1.6579e-14 | 14.2512 | 1.4266 | 1.4803e-14 | -12.3717 | 0.45296 | -7.1054e-15 | 1.9064 | 11.2087 | 9.4739e-15 | -0.79565 | -10.098 | 0 | -144.0449 | 35.9551 | 0 | 35.9551 | -144.0449 | 1 | 0.90753 | 0.71319 | 1 | 0.7825 | 0.63801 | 6.1285e-13 | -136.4258 | 118.7019 | 6.0698e-13 | -140.3651 | 128.5235
Line_1 | 0 | 0.9147 | 0.9147 | 0 | 0.9147 | 0.9147 | 0 | 10.5621 | 10.5621 | 0 | 10.5621 | 10.5621 | -1.7764e-15 | -7.4125 | 1.1373 | 5.9212e-16 | 8.2478 | -0.30197 | 9.4739e-15 | -0.036791 | -6.2383 | -7.1054e-15 | 0.53044 | 6.732 | 0 | 35.9551 | -144.0449 | 0 | -144.0449 | 35.9551 | 1 | 0.70181 | 0.60037 | 1 | 0.7825 | 0.63801 | 5.8745e-13 | -143.7605 | 136.2873 | 6.0698e-13 | -140.3651 | 128.5235
Line_2 | 0 | 0.45735 | 0.45735 | 0 | 0.45735 | 0.45735 | 0 | 5.2811 | 5.2811 | 0 | 5.2811 | 5.2811 | -1.1842e-15 | -3.9151 | 0.35982 | 5.0182e-29 | 4.1239 | -0.15099 | 7.1054e-15 | -0.14181 | -3.2426 | -4.737e-15 | 0.26522 | 3.366 | 0 | 35.9551 | -144.0449 | 0 | -144.0449 | 35.9551 | 1 | 0.74183 | 0.61777 | 1 | 0.7825 | 0.63801 | 5.9209e-13 | -141.9705 | 132.2872 | 6.0698e-13 | -140.3651 | 128.5235
Line_3 | 0 | 0.45735 | 0.45735 | 0 | 0.45735 | 0.45735 | 0 | 5.2811 | 5.2811 | 0 | 5.2811 | 5.2811 | -5.9212e-16 | -3.7062 | 0.56866 | 5.9212e-16 | 3.9151 | -0.35982 | 2.3685e-15 | -0.018396 | -3.1192 | 6.1189e-30 | 0.14181 | 3.2426 | 0 | 35.9551 | -144.0449 | 0 | -144.0449 | 35.9551 | 1 | 0.70181 | 0.60037 | 1 | 0.74183 | 0.61777 | 5.8745e-13 | -143.7605 | 136.2873 | 5.9209e-13 | -141.9705 | 132.2872

## LG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.62571 | 0.019067 | 0.019067 | 0.62105 | 0.014404 | 0.014404 | 7.2251 | 0.22016 | 0.22016 | 7.1713 | 0.16632 | 0.16632 | 1.0489 | 0.21918 | -0.19968 | -0.40749 | -0.15927 | 0.15737 | 0.57633 | -0.32701 | -0.30456 | -0.22595 | 0.24851 | 0.23608 | -81.9879 | -86.9314 | -86.9314 | 98.0302 | 92.2483 | 92.2483 |  | 0.16564 | 1.7881 | 1.6542 | 0.064973 | 1.7747 | 1.7059 | -53.1999 | -143.0993 | 149.8181 | -52.9614 | -145.0951 | 148.5612
Line_1 | 0.40688 | 0.0024101 | 0.0024101 | 0.41165 | 0.0072108 | 0.0072108 | 4.6982 | 0.027829 | 0.027829 | 4.7533 | 0.083263 | 0.083263 | 6.9464e-12 | -0.025927 | 0.027068 | 0.27018 | 0.080028 | -0.078502 | -3.3149e-12 | 0.041793 | 0.040114 | 0.14962 | -0.12422 | -0.11837 | 98.1297 | 91.8145 | 91.8145 | -81.9386 | -87.8866 | -87.8866 |  | 0 | 1.7673 | 1.7389 | 0.064973 | 1.7747 | 1.7059 | 0 | -146.3714 | 147.804 | -52.9614 | -145.0951 | 148.5612
Line_2 | 0.20464 | 0.0024191 | 0.0024191 | 0.2094 | 0.0071931 | 0.0071931 | 2.363 | 0.027934 | 0.027934 | 2.4179 | 0.083059 | 0.083059 | -0.065293 | -0.026815 | 0.02639 | 0.13731 | 0.079246 | -0.078865 | -0.036627 | 0.041564 | 0.040251 | 0.076331 | -0.12429 | -0.11771 | 98.0876 | 91.414 | 91.414 | -82.0311 | -87.6164 | -87.6164 |  | 0.031682 | 1.7707 | 1.723 | 0.064973 | 1.7747 | 1.7059 | -52.6218 | -145.7582 | 148.1635 | -52.9614 | -145.0951 | 148.5612
Line_3 | 0.19985 | 0.0024101 | 0.0024101 | 0.20464 | 0.0024191 | 0.0024191 | 2.3076 | 0.027829 | 0.027829 | 2.363 | 0.027934 | 0.027934 | 3.4086e-12 | 0.025927 | -0.027068 | 0.065293 | 0.026815 | -0.02639 | -1.6349e-12 | -0.041793 | -0.040114 | 0.036627 | -0.041564 | -0.040251 | 98.2437 | -88.1855 | -88.1855 | -81.9124 | -88.586 | -88.586 |  | 0 | 1.7673 | 1.7389 | 0.031682 | 1.7707 | 1.723 | 0 | -146.3714 | 147.804 | -52.6218 | -145.7582 | 148.1635

## LG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.62571 | 0.019067 | 0.019067 | 0.62105 | 0.014404 | 0.014404 | 7.2251 | 0.22016 | 0.22016 | 7.1713 | 0.16632 | 0.16632 | 1.0489 | 0.21918 | -0.19968 | -0.40749 | -0.15927 | 0.15737 | 0.57633 | -0.32701 | -0.30456 | -0.22595 | 0.24851 | 0.23608 | -81.9879 | -86.9314 | -86.9314 | 98.0302 | 92.2483 | 92.2483 |  | 0.16564 | 1.7881 | 1.6542 | 0.064973 | 1.7747 | 1.7059 | -53.1999 | -143.0993 | 149.8181 | -52.9614 | -145.0951 | 148.5612
Line_1 | 0.40688 | 0.0024101 | 0.0024101 | 0.41165 | 0.0072108 | 0.0072108 | 4.6982 | 0.027829 | 0.027829 | 4.7533 | 0.083263 | 0.083263 | 6.9464e-12 | -0.025927 | 0.027068 | 0.27018 | 0.080028 | -0.078502 | -3.3149e-12 | 0.041793 | 0.040114 | 0.14962 | -0.12422 | -0.11837 | 98.1297 | 91.8145 | 91.8145 | -81.9386 | -87.8866 | -87.8866 |  | 0 | 1.7673 | 1.7389 | 0.064973 | 1.7747 | 1.7059 | 0 | -146.3714 | 147.804 | -52.9614 | -145.0951 | 148.5612
Line_2 | 0.20464 | 0.0024191 | 0.0024191 | 0.2094 | 0.0071931 | 0.0071931 | 2.363 | 0.027934 | 0.027934 | 2.4179 | 0.083059 | 0.083059 | -0.065293 | -0.026815 | 0.02639 | 0.13731 | 0.079246 | -0.078865 | -0.036627 | 0.041564 | 0.040251 | 0.076331 | -0.12429 | -0.11771 | 98.0876 | 91.414 | 91.414 | -82.0311 | -87.6164 | -87.6164 |  | 0.031682 | 1.7707 | 1.723 | 0.064973 | 1.7747 | 1.7059 | -52.6218 | -145.7582 | 148.1635 | -52.9614 | -145.0951 | 148.5612
Line_3 | 0.19985 | 0.0024101 | 0.0024101 | 0.20464 | 0.0024191 | 0.0024191 | 2.3076 | 0.027829 | 0.027829 | 2.363 | 0.027934 | 0.027934 | 3.4086e-12 | 0.025927 | -0.027068 | 0.065293 | 0.026815 | -0.02639 | -1.6349e-12 | -0.041793 | -0.040114 | 0.036627 | -0.041564 | -0.040251 | 98.2437 | -88.1855 | -88.1855 | -81.9124 | -88.586 | -88.586 |  | 0 | 1.7673 | 1.7389 | 0.031682 | 1.7707 | 1.723 | 0 | -146.3714 | 147.804 | -52.6218 | -145.7582 | 148.1635

## LG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.48642 | 0.014822 | 0.014822 | 0.48279 | 0.011197 | 0.011197 | 5.6166 | 0.17115 | 0.17115 | 5.5748 | 0.12929 | 0.12929 | 1.7778 | 0.14944 | -0.16937 | -1.3821 | -0.10958 | 0.13197 | 1.4985 | -0.24404 | -0.17555 | -1.2778 | 0.18506 | 0.13677 | -72.9316 | -77.8751 | -77.8751 | 107.0866 | 101.3046 | 101.3046 |  | 0.41397 | 1.672 | 1.4253 | 0.33764 | 1.6634 | 1.47 | -32.8049 | -136.3934 | 148.1519 | -30.1581 | -138.063 | 147.327
Line_1 | 0.3163 | 0.0018735 | 0.0018735 | 0.32001 | 0.0056055 | 0.0056055 | 3.6523 | 0.021634 | 0.021634 | 3.6951 | 0.064727 | 0.064727 | -0.74542 | -0.017943 | 0.022535 | 0.91654 | 0.055078 | -0.065908 | -0.74639 | 0.031076 | 0.023302 | 0.84647 | -0.092515 | -0.068625 | 107.186 | 100.8708 | 100.8708 | -72.8823 | -78.8303 | -78.8303 |  | 0.28883 | 1.6587 | 1.4984 | 0.33764 | 1.6634 | 1.47 | -27.7764 | -139.1269 | 146.8297 | -30.1581 | -138.063 | 147.327
Line_2 | 0.15908 | 0.0018806 | 0.0018806 | 0.16278 | 0.0055917 | 0.0055917 | 1.837 | 0.021715 | 0.021715 | 1.8796 | 0.064568 | 0.064568 | -0.4141 | -0.018529 | 0.022155 | 0.46553 | 0.054507 | -0.066067 | -0.39782 | 0.030943 | 0.023425 | 0.43133 | -0.092545 | -0.068146 | 107.1439 | 100.4703 | 100.4703 | -72.9748 | -78.5601 | -78.5601 |  | 0.3126 | 1.6609 | 1.4848 | 0.33764 | 1.6634 | 1.47 | -29.0048 | -138.6161 | 147.0658 | -30.1581 | -138.063 | 147.327
Line_3 | 0.15535 | 0.0018735 | 0.0018735 | 0.15908 | 0.0018806 | 0.0018806 | 1.7939 | 0.021634 | 0.021634 | 1.837 | 0.021715 | 0.021715 | -0.36685 | 0.017943 | -0.022535 | 0.4141 | 0.018529 | -0.022155 | -0.36588 | -0.031076 | -0.023302 | 0.39782 | -0.030943 | -0.023425 | 107.3 | -79.1292 | -79.1292 | -72.8561 | -79.5297 | -79.5297 |  | 0.28883 | 1.6587 | 1.4984 | 0.3126 | 1.6609 | 1.4848 | -27.7764 | -139.1269 | 146.8297 | -29.0048 | -138.6161 | 147.0658

## LG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.48642 | 0.014822 | 0.014822 | 0.48279 | 0.011197 | 0.011197 | 5.6166 | 0.17115 | 0.17115 | 5.5748 | 0.12929 | 0.12929 | 1.7778 | 0.14944 | -0.16937 | -1.3821 | -0.10958 | 0.13197 | 1.4985 | -0.24404 | -0.17555 | -1.2778 | 0.18506 | 0.13677 | -72.9316 | -77.8751 | -77.8751 | 107.0866 | 101.3046 | 101.3046 |  | 0.41397 | 1.672 | 1.4253 | 0.33764 | 1.6634 | 1.47 | -32.8049 | -136.3934 | 148.1519 | -30.1581 | -138.063 | 147.327
Line_1 | 0.3163 | 0.0018735 | 0.0018735 | 0.32001 | 0.0056055 | 0.0056055 | 3.6523 | 0.021634 | 0.021634 | 3.6951 | 0.064727 | 0.064727 | -0.74542 | -0.017943 | 0.022535 | 0.91654 | 0.055078 | -0.065908 | -0.74639 | 0.031076 | 0.023302 | 0.84647 | -0.092515 | -0.068625 | 107.186 | 100.8708 | 100.8708 | -72.8823 | -78.8303 | -78.8303 |  | 0.28883 | 1.6587 | 1.4984 | 0.33764 | 1.6634 | 1.47 | -27.7764 | -139.1269 | 146.8297 | -30.1581 | -138.063 | 147.327
Line_2 | 0.15908 | 0.0018806 | 0.0018806 | 0.16278 | 0.0055917 | 0.0055917 | 1.837 | 0.021715 | 0.021715 | 1.8796 | 0.064568 | 0.064568 | -0.4141 | -0.018529 | 0.022155 | 0.46553 | 0.054507 | -0.066067 | -0.39782 | 0.030943 | 0.023425 | 0.43133 | -0.092545 | -0.068146 | 107.1439 | 100.4703 | 100.4703 | -72.9748 | -78.5601 | -78.5601 |  | 0.3126 | 1.6609 | 1.4848 | 0.33764 | 1.6634 | 1.47 | -29.0048 | -138.6161 | 147.0658 | -30.1581 | -138.063 | 147.327
Line_3 | 0.15535 | 0.0018735 | 0.0018735 | 0.15908 | 0.0018806 | 0.0018806 | 1.7939 | 0.021634 | 0.021634 | 1.837 | 0.021715 | 0.021715 | -0.36685 | 0.017943 | -0.022535 | 0.4141 | 0.018529 | -0.022155 | -0.36588 | -0.031076 | -0.023302 | 0.39782 | -0.030943 | -0.023425 | 107.3 | -79.1292 | -79.1292 | -72.8561 | -79.5297 | -79.5297 |  | 0.28883 | 1.6587 | 1.4984 | 0.3126 | 1.6609 | 1.4848 | -27.7764 | -139.1269 | 146.8297 | -29.0048 | -138.6161 | 147.0658

## LG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.55348 | 0.01702 | 0.01702 | 0.54936 | 0.012901 | 0.012901 | 6.3911 | 0.19653 | 0.19653 | 6.3434 | 0.14897 | 0.14897 | 1.5757 | 0.18408 | -0.15476 | -0.61217 | -0.13014 | 0.12727 | 0.446 | -0.26632 | -0.23376 | -0.1761 | 0.20307 | 0.18532 | -75.076 | -84.512 | -84.512 | 104.9588 | 93.9464 | 93.9464 |  | 0.25623 | 1.6473 | 1.4265 | 0.10042 | 1.6191 | 1.5091 | -59.2717 | -139.8591 | 151.982 | -58.9924 | -143.3999 | 149.4663
Line_1 | 0.35991 | 0.0021629 | 0.0021629 | 0.36413 | 0.0064626 | 0.0064626 | 4.1559 | 0.024975 | 0.024975 | 4.2047 | 0.074623 | 0.074623 | -3.3219e-12 | -0.020741 | 0.022452 | 0.40589 | 0.065638 | -0.063345 | -1.4137e-12 | 0.034297 | 0.031931 | 0.1163 | -0.10144 | -0.093111 | 105.1498 | 93.1353 | 93.1353 | -74.9813 | -86.3057 | -86.3057 |  | 0 | 1.6049 | 1.563 | 0.10042 | 1.6191 | 1.5091 | 0 | -145.702 | 148.0232 | -58.9924 | -143.3999 | 149.4663
Line_2 | 0.18102 | 0.0021755 | 0.0021755 | 0.18522 | 0.0064385 | 0.0064385 | 2.0903 | 0.02512 | 0.02512 | 2.1388 | 0.074346 | 0.074346 | -0.098094 | -0.022054 | 0.021417 | 0.20628 | 0.064501 | -0.063924 | -0.028794 | 0.033937 | 0.032122 | 0.059799 | -0.10163 | -0.092204 | 105.069 | 92.3909 | 92.3909 | -75.1589 | -85.8005 | -85.8005 |  | 0.048909 | 1.6112 | 1.5369 | 0.10042 | 1.6191 | 1.5091 | -58.5722 | -144.591 | 148.6977 | -58.9924 | -143.3999 | 149.4663
Line_3 | 0.17679 | 0.0021629 | 0.0021629 | 0.18102 | 0.0021755 | 0.0021755 | 2.0413 | 0.024975 | 0.024975 | 2.0903 | 0.02512 | 0.02512 | -1.6343e-12 | 0.020741 | -0.022452 | 0.098094 | 0.022054 | -0.021417 | -6.8815e-13 | -0.034297 | -0.031931 | 0.028794 | -0.033937 | -0.032122 | 105.3687 | -86.8647 | -86.8647 | -74.931 | -87.6091 | -87.6091 |  | 0 | 1.6049 | 1.563 | 0.048909 | 1.6112 | 1.5369 | 0 | -145.702 | 148.0232 | -58.5722 | -144.591 | 148.6977

## LG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.55348 | 0.01702 | 0.01702 | 0.54936 | 0.012901 | 0.012901 | 6.3911 | 0.19653 | 0.19653 | 6.3434 | 0.14897 | 0.14897 | 1.5757 | 0.18408 | -0.15476 | -0.61217 | -0.13014 | 0.12727 | 0.446 | -0.26632 | -0.23376 | -0.1761 | 0.20307 | 0.18532 | -75.076 | -84.512 | -84.512 | 104.9588 | 93.9464 | 93.9464 |  | 0.25623 | 1.6473 | 1.4265 | 0.10042 | 1.6191 | 1.5091 | -59.2717 | -139.8591 | 151.982 | -58.9924 | -143.3999 | 149.4663
Line_1 | 0.35991 | 0.0021629 | 0.0021629 | 0.36413 | 0.0064626 | 0.0064626 | 4.1559 | 0.024975 | 0.024975 | 4.2047 | 0.074623 | 0.074623 | -3.3219e-12 | -0.020741 | 0.022452 | 0.40589 | 0.065638 | -0.063345 | -1.4137e-12 | 0.034297 | 0.031931 | 0.1163 | -0.10144 | -0.093111 | 105.1498 | 93.1353 | 93.1353 | -74.9813 | -86.3057 | -86.3057 |  | 0 | 1.6049 | 1.563 | 0.10042 | 1.6191 | 1.5091 | 0 | -145.702 | 148.0232 | -58.9924 | -143.3999 | 149.4663
Line_2 | 0.18102 | 0.0021755 | 0.0021755 | 0.18522 | 0.0064385 | 0.0064385 | 2.0903 | 0.02512 | 0.02512 | 2.1388 | 0.074346 | 0.074346 | -0.098094 | -0.022054 | 0.021417 | 0.20628 | 0.064501 | -0.063924 | -0.028794 | 0.033937 | 0.032122 | 0.059799 | -0.10163 | -0.092204 | 105.069 | 92.3909 | 92.3909 | -75.1589 | -85.8005 | -85.8005 |  | 0.048909 | 1.6112 | 1.5369 | 0.10042 | 1.6191 | 1.5091 | -58.5722 | -144.591 | 148.6977 | -58.9924 | -143.3999 | 149.4663
Line_3 | 0.17679 | 0.0021629 | 0.0021629 | 0.18102 | 0.0021755 | 0.0021755 | 2.0413 | 0.024975 | 0.024975 | 2.0903 | 0.02512 | 0.02512 | -1.6343e-12 | 0.020741 | -0.022452 | 0.098094 | 0.022054 | -0.021417 | -6.8815e-13 | -0.034297 | -0.031931 | 0.028794 | -0.033937 | -0.032122 | 105.3687 | -86.8647 | -86.8647 | -74.931 | -87.6091 | -87.6091 |  | 0 | 1.6049 | 1.563 | 0.048909 | 1.6112 | 1.5369 | 0 | -145.702 | 148.0232 | -58.5722 | -144.591 | 148.6977

## LG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.42721 | 0.013137 | 0.013137 | 0.42402 | 0.0099576 | 0.0099576 | 4.9329 | 0.15169 | 0.15169 | 4.8962 | 0.11498 | 0.11498 | 1.819 | 0.12577 | -0.13052 | -1.2389 | -0.090443 | 0.10493 | 1.1551 | -0.19361 | -0.13573 | -0.9872 | 0.14714 | 0.10851 | -67.8383 | -77.2742 | -77.2742 | 112.1965 | 101.1841 | 101.1841 |  | 0.43681 | 1.522 | 1.2413 | 0.32354 | 1.5021 | 1.3128 | -35.4202 | -134.2666 | 148.8481 | -29.2549 | -137.2371 | 147.1452
Line_1 | 0.2778 | 0.0016694 | 0.0016694 | 0.28106 | 0.0049882 | 0.0049882 | 3.2078 | 0.019277 | 0.019277 | 3.2454 | 0.057598 | 0.057598 | -0.57467 | -0.014583 | 0.018259 | 0.82189 | 0.04563 | -0.052322 | -0.57612 | 0.024786 | 0.018775 | 0.65349 | -0.073506 | -0.054586 | 112.3875 | 100.3731 | 100.3731 | -67.7436 | -79.068 | -79.068 |  | 0.25368 | 1.4919 | 1.3586 | 0.32354 | 1.5021 | 1.3128 | -22.5404 | -139.1568 | 146.1701 | -29.2549 | -137.2371 | 147.1452
Line_2 | 0.13972 | 0.0016791 | 0.0016791 | 0.14297 | 0.0049696 | 0.0049696 | 1.6134 | 0.019389 | 0.019389 | 1.6508 | 0.057384 | 0.057384 | -0.34707 | -0.015435 | 0.017674 | 0.41704 | 0.044813 | -0.052605 | -0.30733 | 0.024568 | 0.018951 | 0.33371 | -0.07363 | -0.053921 | 112.3067 | 99.6287 | 99.6287 | -67.9212 | -78.5628 | -78.5628 |  | 0.28734 | 1.4964 | 1.3365 | 0.32354 | 1.5021 | 1.3128 | -26.1686 | -138.2314 | 146.6244 | -29.2549 | -137.2371 | 147.1452
Line_3 | 0.13645 | 0.0016694 | 0.0016694 | 0.13972 | 0.0016791 | 0.0016791 | 1.5756 | 0.019277 | 0.019277 | 1.6134 | 0.019389 | 0.019389 | -0.28335 | 0.014583 | -0.018259 | 0.34707 | 0.015435 | -0.017674 | -0.2819 | -0.024786 | -0.018775 | 0.30733 | -0.024568 | -0.018951 | 112.6064 | -79.6269 | -79.6269 | -67.6933 | -80.3713 | -80.3713 |  | 0.25368 | 1.4919 | 1.3586 | 0.28734 | 1.4964 | 1.3365 | -22.5404 | -139.1568 | 146.1701 | -26.1686 | -138.2314 | 146.6244

## LG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.42721 | 0.013137 | 0.013137 | 0.42402 | 0.0099576 | 0.0099576 | 4.9329 | 0.15169 | 0.15169 | 4.8962 | 0.11498 | 0.11498 | 1.819 | 0.12577 | -0.13052 | -1.2389 | -0.090443 | 0.10493 | 1.1551 | -0.19361 | -0.13573 | -0.9872 | 0.14714 | 0.10851 | -67.8383 | -77.2742 | -77.2742 | 112.1965 | 101.1841 | 101.1841 |  | 0.43681 | 1.522 | 1.2413 | 0.32354 | 1.5021 | 1.3128 | -35.4202 | -134.2666 | 148.8481 | -29.2549 | -137.2371 | 147.1452
Line_1 | 0.2778 | 0.0016694 | 0.0016694 | 0.28106 | 0.0049882 | 0.0049882 | 3.2078 | 0.019277 | 0.019277 | 3.2454 | 0.057598 | 0.057598 | -0.57467 | -0.014583 | 0.018259 | 0.82189 | 0.04563 | -0.052322 | -0.57612 | 0.024786 | 0.018775 | 0.65349 | -0.073506 | -0.054586 | 112.3875 | 100.3731 | 100.3731 | -67.7436 | -79.068 | -79.068 |  | 0.25368 | 1.4919 | 1.3586 | 0.32354 | 1.5021 | 1.3128 | -22.5404 | -139.1568 | 146.1701 | -29.2549 | -137.2371 | 147.1452
Line_2 | 0.13972 | 0.0016791 | 0.0016791 | 0.14297 | 0.0049696 | 0.0049696 | 1.6134 | 0.019389 | 0.019389 | 1.6508 | 0.057384 | 0.057384 | -0.34707 | -0.015435 | 0.017674 | 0.41704 | 0.044813 | -0.052605 | -0.30733 | 0.024568 | 0.018951 | 0.33371 | -0.07363 | -0.053921 | 112.3067 | 99.6287 | 99.6287 | -67.9212 | -78.5628 | -78.5628 |  | 0.28734 | 1.4964 | 1.3365 | 0.32354 | 1.5021 | 1.3128 | -26.1686 | -138.2314 | 146.6244 | -29.2549 | -137.2371 | 147.1452
Line_3 | 0.13645 | 0.0016694 | 0.0016694 | 0.13972 | 0.0016791 | 0.0016791 | 1.5756 | 0.019277 | 0.019277 | 1.6134 | 0.019389 | 0.019389 | -0.28335 | 0.014583 | -0.018259 | 0.34707 | 0.015435 | -0.017674 | -0.2819 | -0.024786 | -0.018775 | 0.30733 | -0.024568 | -0.018951 | 112.6064 | -79.6269 | -79.6269 | -67.6933 | -80.3713 | -80.3713 |  | 0.25368 | 1.4919 | 1.3586 | 0.28734 | 1.4964 | 1.3365 | -22.5404 | -139.1568 | 146.1701 | -26.1686 | -138.2314 | 146.6244

## LLG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.010374 | 3.1804 | 3.2374 | 0.0078371 | 3.1808 | 3.2368 | 0.11979 | 36.7242 | 37.3822 | 0.090495 | 36.7285 | 37.3748 | -0.00054867 | 9.084 | 8.9819 | 0.0012758 | -3.6317 | -3.5904 | -0.18935 | 7.939 | 12.3724 | 0.14418 | -3.1989 | -4.9241 | 92.3287 | -166.6299 | 19.5535 | -88.4916 | 13.4154 | -160.49 |  | 1.5807 | 0.32851 | 0.40899 | 1.5933 | 0.13177 | 0.16305 | 2.1627 | -125.478 | 73.5753 | 1.0014 | -125.2103 | 73.4122
Line_1 | 0.0013113 | 2.1213 | 2.1566 | 0.0039234 | 2.1208 | 2.1574 | 0.015142 | 24.4949 | 24.9027 | 0.045304 | 24.4887 | 24.912 | 0.00033778 | 4.7606e-11 | 5.4184e-11 | -0.00046873 | 2.4227 | 2.3913 | 0.024248 | -3.2826e-11 | 1.7962e-11 | -0.07218 | 2.1314 | 3.2835 | -88.9254 | 13.5188 | -160.5889 | 91.3735 | -166.5502 | 19.4771 |  | 1.6016 | 0 | 0 | 1.5933 | 0.13177 | 0.16305 | 0.27651 | 0 | 0 | 1.0014 | -125.2103 | 73.4122
Line_2 | 0.0013163 | 1.0605 | 1.0785 | 0.0039138 | 1.06 | 1.0793 | 0.015199 | 12.2457 | 12.4539 | 0.045192 | 12.2399 | 12.4628 | 2.1579e-05 | -0.60513 | -0.59762 | -0.00080708 | 1.209 | 1.1991 | 0.024281 | -0.53797 | -0.81549 | -0.072 | 1.0675 | 1.6406 | -89.326 | 13.4841 | -160.5558 | 91.6437 | -166.6536 | 19.5759 |  | 1.5976 | 0.06612 | 0.081182 | 1.5933 | 0.13177 | 0.16305 | 0.62313 | -124.8782 | 73.2091 | 1.0014 | -125.2103 | 73.4122
Line_3 | 0.0013113 | 1.0611 | 1.0777 | 0.0013163 | 1.0605 | 1.0785 | 0.015142 | 12.2524 | 12.4442 | 0.015199 | 12.2457 | 12.4539 | -0.00033779 | 2.3783e-11 | 2.7061e-11 | -2.1582e-05 | 0.60513 | 0.59762 | -0.024248 | -1.6463e-11 | 9.023e-12 | -0.024281 | 0.53797 | 0.81549 | 91.0746 | 13.6225 | -160.6882 | 90.6741 | -166.5159 | 19.4442 |  | 1.6016 | 0 | 0 | 1.5976 | 0.06612 | 0.081182 | 0.27651 | 0 | 0 | 0.62313 | -124.8782 | 73.2091

## LLG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.010374 | 3.1804 | 3.2374 | 0.0078371 | 3.1808 | 3.2368 | 0.11979 | 36.7242 | 37.3822 | 0.090495 | 36.7285 | 37.3748 | -0.00054867 | 9.084 | 8.9819 | 0.0012758 | -3.6317 | -3.5904 | -0.18935 | 7.939 | 12.3724 | 0.14418 | -3.1989 | -4.9241 | 92.3287 | -166.6299 | 19.5535 | -88.4916 | 13.4154 | -160.49 |  | 1.5807 | 0.32851 | 0.40899 | 1.5933 | 0.13177 | 0.16305 | 2.1627 | -125.478 | 73.5753 | 1.0014 | -125.2103 | 73.4122
Line_1 | 0.0013113 | 2.1213 | 2.1566 | 0.0039234 | 2.1208 | 2.1574 | 0.015142 | 24.4949 | 24.9027 | 0.045304 | 24.4887 | 24.912 | 0.00033778 | 4.7606e-11 | 5.4184e-11 | -0.00046873 | 2.4227 | 2.3913 | 0.024248 | -3.2826e-11 | 1.7962e-11 | -0.07218 | 2.1314 | 3.2835 | -88.9254 | 13.5188 | -160.5889 | 91.3735 | -166.5502 | 19.4771 |  | 1.6016 | 0 | 0 | 1.5933 | 0.13177 | 0.16305 | 0.27651 | 0 | 0 | 1.0014 | -125.2103 | 73.4122
Line_2 | 0.0013163 | 1.0605 | 1.0785 | 0.0039138 | 1.06 | 1.0793 | 0.015199 | 12.2457 | 12.4539 | 0.045192 | 12.2399 | 12.4628 | 2.1579e-05 | -0.60513 | -0.59762 | -0.00080708 | 1.209 | 1.1991 | 0.024281 | -0.53797 | -0.81549 | -0.072 | 1.0675 | 1.6406 | -89.326 | 13.4841 | -160.5558 | 91.6437 | -166.6536 | 19.5759 |  | 1.5976 | 0.06612 | 0.081182 | 1.5933 | 0.13177 | 0.16305 | 0.62313 | -124.8782 | 73.2091 | 1.0014 | -125.2103 | 73.4122
Line_3 | 0.0013113 | 1.0611 | 1.0777 | 0.0013163 | 1.0605 | 1.0785 | 0.015142 | 12.2524 | 12.4442 | 0.015199 | 12.2457 | 12.4539 | -0.00033779 | 2.3783e-11 | 2.7061e-11 | -2.1582e-05 | 0.60513 | 0.59762 | -0.024248 | -1.6463e-11 | 9.023e-12 | -0.024281 | 0.53797 | 0.81549 | 91.0746 | 13.6225 | -160.6882 | 90.6741 | -166.5159 | 19.4442 |  | 1.6016 | 0 | 0 | 1.5976 | 0.06612 | 0.081182 | 0.27651 | 0 | 0 | 0.62313 | -124.8782 | 73.2091

## LLG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.0090122 | 1.0263 | 1.1446 | 0.0068082 | 1.0269 | 1.1435 | 0.10406 | 11.8503 | 13.217 | 0.078615 | 11.858 | 13.2034 | -0.012137 | 6.1515 | 7.8621 | 0.0096663 | -5.6184 | -7.0621 | -0.15692 | 5.7913 | 8.3816 | 0.11952 | -5.5112 | -7.2362 | 97.9152 | -152.0778 | 42.8087 | -82.905 | 28.0396 | -137.2847 |  | 1.5124 | 0.71295 | 0.86948 | 1.5253 | 0.6637 | 0.7658 | 3.4924 | -108.8054 | 89.6404 | 2.4713 | -107.5124 | 88.4127
Line_1 | 0.0011392 | 0.68583 | 0.76033 | 0.0034083 | 0.68502 | 0.76165 | 0.013154 | 7.9193 | 8.7796 | 0.039356 | 7.9099 | 8.7948 | 0.0016976 | -3.5245 | -4.3372 | -0.0046982 | 3.7535 | 4.6982 | 0.020104 | -3.5354 | -4.3267 | -0.059847 | 3.6705 | 4.8257 | -83.3389 | 28.3051 | -137.4934 | 96.96 | -151.8718 | 42.6458 |  | 1.5338 | 0.63037 | 0.6978 | 1.5253 | 0.6637 | 0.7658 | 1.8344 | -106.6064 | 87.437 | 2.4713 | -107.5124 | 88.4127
Line_2 | 0.0011435 | 0.3427 | 0.38051 | 0.0033999 | 0.34192 | 0.3818 | 0.013203 | 3.9571 | 4.3937 | 0.039259 | 3.9481 | 4.4087 | 0.0014517 | -1.8195 | -2.2583 | -0.0049681 | 1.8649 | 2.3639 | 0.020145 | -1.8029 | -2.2865 | -0.059677 | 1.8407 | 2.4105 | -83.7394 | 28.2165 | -137.424 | 97.2302 | -152.1378 | 42.8539 |  | 1.5297 | 0.64729 | 0.73144 | 1.5253 | 0.6637 | 0.7658 | 2.1389 | -107.0463 | 87.9318 | 2.4713 | -107.5124 | 88.4127
Line_3 | 0.0011392 | 0.34355 | 0.37917 | 0.0011435 | 0.3427 | 0.38051 | 0.013154 | 3.967 | 4.3783 | 0.013203 | 3.9571 | 4.3937 | -0.0016976 | -1.7737 | -2.155 | -0.0014517 | 1.8195 | 2.2583 | -0.020104 | -1.7628 | -2.1656 | -0.020145 | 1.8029 | 2.2865 | 96.6611 | 28.57 | -137.7027 | 96.2606 | -151.7835 | 42.576 |  | 1.5338 | 0.63037 | 0.6978 | 1.5297 | 0.64729 | 0.73144 | 1.8344 | -106.6064 | 87.437 | 2.1389 | -107.0463 | 87.9318

## LLG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.0090122 | 1.0263 | 1.1446 | 0.0068082 | 1.0269 | 1.1435 | 0.10406 | 11.8503 | 13.217 | 0.078615 | 11.858 | 13.2034 | -0.012137 | 6.1515 | 7.8621 | 0.0096663 | -5.6184 | -7.0621 | -0.15692 | 5.7913 | 8.3816 | 0.11952 | -5.5112 | -7.2362 | 97.9152 | -152.0778 | 42.8087 | -82.905 | 28.0396 | -137.2847 |  | 1.5124 | 0.71295 | 0.86948 | 1.5253 | 0.6637 | 0.7658 | 3.4924 | -108.8054 | 89.6404 | 2.4713 | -107.5124 | 88.4127
Line_1 | 0.0011392 | 0.68583 | 0.76033 | 0.0034083 | 0.68502 | 0.76165 | 0.013154 | 7.9193 | 8.7796 | 0.039356 | 7.9099 | 8.7948 | 0.0016976 | -3.5245 | -4.3372 | -0.0046982 | 3.7535 | 4.6982 | 0.020104 | -3.5354 | -4.3267 | -0.059847 | 3.6705 | 4.8257 | -83.3389 | 28.3051 | -137.4934 | 96.96 | -151.8718 | 42.6458 |  | 1.5338 | 0.63037 | 0.6978 | 1.5253 | 0.6637 | 0.7658 | 1.8344 | -106.6064 | 87.437 | 2.4713 | -107.5124 | 88.4127
Line_2 | 0.0011435 | 0.3427 | 0.38051 | 0.0033999 | 0.34192 | 0.3818 | 0.013203 | 3.9571 | 4.3937 | 0.039259 | 3.9481 | 4.4087 | 0.0014517 | -1.8195 | -2.2583 | -0.0049681 | 1.8649 | 2.3639 | 0.020145 | -1.8029 | -2.2865 | -0.059677 | 1.8407 | 2.4105 | -83.7394 | 28.2165 | -137.424 | 97.2302 | -152.1378 | 42.8539 |  | 1.5297 | 0.64729 | 0.73144 | 1.5253 | 0.6637 | 0.7658 | 2.1389 | -107.0463 | 87.9318 | 2.4713 | -107.5124 | 88.4127
Line_3 | 0.0011392 | 0.34355 | 0.37917 | 0.0011435 | 0.3427 | 0.38051 | 0.013154 | 3.967 | 4.3783 | 0.013203 | 3.9571 | 4.3937 | -0.0016976 | -1.7737 | -2.155 | -0.0014517 | 1.8195 | 2.2583 | -0.020104 | -1.7628 | -2.1656 | -0.020145 | 1.8029 | 2.2865 | 96.6611 | 28.57 | -137.7027 | 96.2606 | -151.7835 | 42.576 |  | 1.5338 | 0.63037 | 0.6978 | 1.5297 | 0.64729 | 0.73144 | 1.8344 | -106.6064 | 87.437 | 2.1389 | -107.0463 | 87.9318

## LLG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.0093199 | 2.5722 | 2.6486 | 0.0070643 | 2.5728 | 2.6478 | 0.10762 | 29.7018 | 30.5839 | 0.081572 | 29.7086 | 30.5742 | -0.00082833 | 10.8762 | 12.1362 | 0.0019381 | -4.3576 | -4.8408 | -0.15296 | 3.772 | 9.6789 | 0.11743 | -1.5398 | -3.8397 | 94.2859 | -155.7471 | 30.903 | -87.2557 | 24.3016 | -149.1425 |  | 1.4214 | 0.38758 | 0.50756 | 1.4397 | 0.15557 | 0.20209 | 3.9756 | -136.62 | 69.4764 | 1.7987 | -136.2374 | 69.2783
Line_1 | 0.0011843 | 1.7165 | 1.7636 | 0.0035388 | 1.7156 | 1.7647 | 0.013676 | 19.8206 | 20.3638 | 0.040862 | 19.8106 | 20.3766 | 0.00051309 | -9.2451e-11 | 2.6563e-12 | -0.00071204 | 2.9064 | 3.2247 | 0.019858 | -7.3318e-11 | -1.218e-10 | -0.058827 | 1.0249 | 2.5609 | -88.0668 | 24.4112 | -149.2438 | 92.4922 | -155.6619 | 30.8237 |  | 1.4526 | 0 | 0 | 1.4397 | 0.15557 | 0.20209 | 0.45314 | 0 | 0 | 1.7987 | -136.2374 | 69.2783
Line_2 | 0.0011912 | 0.85801 | 0.88208 | 0.0035256 | 0.8572 | 0.88314 | 0.013755 | 9.9075 | 10.1854 | 0.04071 | 9.8981 | 10.1976 | 3.2768e-05 | -0.7282 | -0.80345 | -0.0012261 | 1.4512 | 1.6161 | 0.019893 | -0.26303 | -0.6333 | -0.058599 | 0.51487 | 1.2788 | -88.8112 | 24.3747 | -149.2102 | 92.9973 | -155.7716 | 30.925 |  | 1.4462 | 0.078148 | 0.10044 | 1.4397 | 0.15557 | 0.20209 | 1.0944 | -135.7653 | 69.0358 | 1.7987 | -136.2374 | 69.2783
Line_3 | 0.0011843 | 0.85894 | 0.88092 | 0.0011912 | 0.85801 | 0.88208 | 0.013676 | 9.9181 | 10.172 | 0.013755 | 9.9075 | 10.1854 | -0.00051309 | -4.6332e-11 | 1.4343e-12 | -3.277e-05 | 0.7282 | 0.80345 | -0.019858 | -3.6599e-11 | -6.0836e-11 | -0.019893 | 0.26303 | 0.6333 | 91.9332 | 24.5207 | -149.345 | 91.1888 | -155.6253 | 30.7898 |  | 1.4526 | 0 | 0 | 1.4462 | 0.078148 | 0.10044 | 0.45314 | 0 | 0 | 1.0944 | -135.7653 | 69.0358

## LLG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.0093199 | 2.5722 | 2.6486 | 0.0070643 | 2.5728 | 2.6478 | 0.10762 | 29.7018 | 30.5839 | 0.081572 | 29.7086 | 30.5742 | -0.00082833 | 10.8762 | 12.1362 | 0.0019381 | -4.3576 | -4.8408 | -0.15296 | 3.772 | 9.6789 | 0.11743 | -1.5398 | -3.8397 | 94.2859 | -155.7471 | 30.903 | -87.2557 | 24.3016 | -149.1425 |  | 1.4214 | 0.38758 | 0.50756 | 1.4397 | 0.15557 | 0.20209 | 3.9756 | -136.62 | 69.4764 | 1.7987 | -136.2374 | 69.2783
Line_1 | 0.0011843 | 1.7165 | 1.7636 | 0.0035388 | 1.7156 | 1.7647 | 0.013676 | 19.8206 | 20.3638 | 0.040862 | 19.8106 | 20.3766 | 0.00051309 | -9.2451e-11 | 2.6563e-12 | -0.00071204 | 2.9064 | 3.2247 | 0.019858 | -7.3318e-11 | -1.218e-10 | -0.058827 | 1.0249 | 2.5609 | -88.0668 | 24.4112 | -149.2438 | 92.4922 | -155.6619 | 30.8237 |  | 1.4526 | 0 | 0 | 1.4397 | 0.15557 | 0.20209 | 0.45314 | 0 | 0 | 1.7987 | -136.2374 | 69.2783
Line_2 | 0.0011912 | 0.85801 | 0.88208 | 0.0035256 | 0.8572 | 0.88314 | 0.013755 | 9.9075 | 10.1854 | 0.04071 | 9.8981 | 10.1976 | 3.2768e-05 | -0.7282 | -0.80345 | -0.0012261 | 1.4512 | 1.6161 | 0.019893 | -0.26303 | -0.6333 | -0.058599 | 0.51487 | 1.2788 | -88.8112 | 24.3747 | -149.2102 | 92.9973 | -155.7716 | 30.925 |  | 1.4462 | 0.078148 | 0.10044 | 1.4397 | 0.15557 | 0.20209 | 1.0944 | -135.7653 | 69.0358 | 1.7987 | -136.2374 | 69.2783
Line_3 | 0.0011843 | 0.85894 | 0.88092 | 0.0011912 | 0.85801 | 0.88208 | 0.013676 | 9.9181 | 10.172 | 0.013755 | 9.9075 | 10.1854 | -0.00051309 | -4.6332e-11 | 1.4343e-12 | -3.277e-05 | 0.7282 | 0.80345 | -0.019858 | -3.6599e-11 | -6.0836e-11 | -0.019893 | 0.26303 | 0.6333 | 91.9332 | 24.5207 | -149.345 | 91.1888 | -155.6253 | 30.7898 |  | 1.4526 | 0 | 0 | 1.4462 | 0.078148 | 0.10044 | 0.45314 | 0 | 0 | 1.0944 | -135.7653 | 69.0358

## LLG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.0080483 | 0.88736 | 0.98258 | 0.0061004 | 0.88794 | 0.98153 | 0.092933 | 10.2464 | 11.3459 | 0.070442 | 10.253 | 11.3337 | -0.0089567 | 5.1606 | 6.7535 | 0.0075233 | -4.4276 | -5.5821 | -0.12586 | 3.945 | 6.5686 | 0.096673 | -3.9715 | -5.4838 | 98.8743 | -149.2553 | 46.2731 | -82.6673 | 30.8654 | -133.8231 |  | 1.3577 | 0.63396 | 0.83035 | 1.3765 | 0.58011 | 0.69042 | 4.8037 | -111.8594 | 90.4779 | 2.8827 | -107.2426 | 90.6676
Line_1 | 0.0010227 | 0.59317 | 0.65246 | 0.0030559 | 0.59235 | 0.65373 | 0.01181 | 6.8493 | 7.5339 | 0.035287 | 6.8399 | 7.5486 | 0.0013799 | -2.6366 | -3.1934 | -0.0035556 | 2.9579 | 3.7134 | 0.01635 | -2.6449 | -3.1857 | -0.048443 | 2.6448 | 3.6569 | -83.4784 | 31.1356 | -134.0322 | 97.0806 | -149.0444 | 46.1071 |  | 1.3894 | 0.54525 | 0.59872 | 1.3765 | 0.58011 | 0.69042 | 1.6973 | -103.7746 | 90.8984 | 2.8827 | -107.2426 | 90.6676
Line_2 | 0.0010287 | 0.29636 | 0.32657 | 0.0030446 | 0.29559 | 0.3278 | 0.011878 | 3.422 | 3.7709 | 0.035156 | 3.4132 | 3.7851 | 0.0010073 | -1.399 | -1.7254 | -0.0039677 | 1.4697 | 1.8687 | 0.016398 | -1.3243 | -1.7087 | -0.04823 | 1.3267 | 1.8269 | -84.2228 | 31.0458 | -133.9636 | 97.5857 | -149.3153 | 46.316 |  | 1.3831 | 0.56295 | 0.64397 | 1.3765 | 0.58011 | 0.69042 | 2.2619 | -105.5255 | 90.7571 | 2.8827 | -107.2426 | 90.6676
Line_3 | 0.0010227 | 0.29723 | 0.32526 | 0.0010287 | 0.29636 | 0.32657 | 0.01181 | 3.4321 | 3.7557 | 0.011878 | 3.422 | 3.7709 | -0.0013799 | -1.3274 | -1.5862 | -0.0010073 | 1.399 | 1.7254 | -0.01635 | -1.3191 | -1.5939 | -0.016398 | 1.3243 | 1.7087 | 96.5216 | 31.4045 | -134.2408 | 95.7772 | -148.9542 | 46.0364 |  | 1.3894 | 0.54525 | 0.59872 | 1.3831 | 0.56295 | 0.64397 | 1.6973 | -103.7746 | 90.8984 | 2.2619 | -105.5255 | 90.7571

## LLG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.0080483 | 0.88736 | 0.98258 | 0.0061004 | 0.88794 | 0.98153 | 0.092933 | 10.2464 | 11.3459 | 0.070442 | 10.253 | 11.3337 | -0.0089567 | 5.1606 | 6.7535 | 0.0075233 | -4.4276 | -5.5821 | -0.12586 | 3.945 | 6.5686 | 0.096673 | -3.9715 | -5.4838 | 98.8743 | -149.2553 | 46.2731 | -82.6673 | 30.8654 | -133.8231 |  | 1.3577 | 0.63396 | 0.83035 | 1.3765 | 0.58011 | 0.69042 | 4.8037 | -111.8594 | 90.4779 | 2.8827 | -107.2426 | 90.6676
Line_1 | 0.0010227 | 0.59317 | 0.65246 | 0.0030559 | 0.59235 | 0.65373 | 0.01181 | 6.8493 | 7.5339 | 0.035287 | 6.8399 | 7.5486 | 0.0013799 | -2.6366 | -3.1934 | -0.0035556 | 2.9579 | 3.7134 | 0.01635 | -2.6449 | -3.1857 | -0.048443 | 2.6448 | 3.6569 | -83.4784 | 31.1356 | -134.0322 | 97.0806 | -149.0444 | 46.1071 |  | 1.3894 | 0.54525 | 0.59872 | 1.3765 | 0.58011 | 0.69042 | 1.6973 | -103.7746 | 90.8984 | 2.8827 | -107.2426 | 90.6676
Line_2 | 0.0010287 | 0.29636 | 0.32657 | 0.0030446 | 0.29559 | 0.3278 | 0.011878 | 3.422 | 3.7709 | 0.035156 | 3.4132 | 3.7851 | 0.0010073 | -1.399 | -1.7254 | -0.0039677 | 1.4697 | 1.8687 | 0.016398 | -1.3243 | -1.7087 | -0.04823 | 1.3267 | 1.8269 | -84.2228 | 31.0458 | -133.9636 | 97.5857 | -149.3153 | 46.316 |  | 1.3831 | 0.56295 | 0.64397 | 1.3765 | 0.58011 | 0.69042 | 2.2619 | -105.5255 | 90.7571 | 2.8827 | -107.2426 | 90.6676
Line_3 | 0.0010227 | 0.29723 | 0.32526 | 0.0010287 | 0.29636 | 0.32657 | 0.01181 | 3.4321 | 3.7557 | 0.011878 | 3.422 | 3.7709 | -0.0013799 | -1.3274 | -1.5862 | -0.0010073 | 1.399 | 1.7254 | -0.01635 | -1.3191 | -1.5939 | -0.016398 | 1.3243 | 1.7087 | 96.5216 | 31.4045 | -134.2408 | 95.7772 | -148.9542 | 46.0364 |  | 1.3894 | 0.54525 | 0.59872 | 1.3831 | 0.56295 | 0.64397 | 1.6973 | -103.7746 | 90.8984 | 2.2619 | -105.5255 | 90.7571