## LLL_max_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0_3ph | 1.7069 | 1.7069 | 0 | 0 | 59.1291 | 59.1291 | 33.2581 | -28.713 | 15.166 | -10.009 | -55.2381 | 124.7619 | 0.61819 | 0.51426 | -30.7247 | -36.0201
Line_1_3-2ph | 1.7069 | 1.7069 | 0 | 2.7571 | 59.1291 | 59.1291 | 28.713 | -1e-07 | 10.009 | -1e-07 | -55.2381 | 124.7619 | 0.51426 | 0 | -36.0201 | 0
Line_2_3-2ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.51426 | 0.51426 | -36.0201 | -36.0201
Line_3_3-1ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.51426 | 0.51426 | -36.0201 | -36.0201

## LLL_max_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0_3ph | 1.7069 | 1.7069 | 0 | 0 | 59.1291 | 59.1291 | 33.2581 | -28.713 | 15.166 | -10.009 | -55.2381 | 124.7619 | 0.61819 | 0.51426 | -30.7247 | -36.0201
Line_1_3-2ph | 1.7069 | 1.7069 | 0 | 2.7571 | 59.1291 | 59.1291 | 28.713 | -1e-07 | 10.009 | -1e-07 | -55.2381 | 124.7619 | 0.51426 | 0 | -36.0201 | 0
Line_2_3-2ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.51426 | 0.51426 | -36.0201 | -36.0201
Line_3_3-1ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.51426 | 0.51426 | -36.0201 | -36.0201

## LLL_max_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0_3ph | 0.87873 | 0.87873 | 0 | 0 | 30.4402 | 30.4402 | 20.3969 | -19.1923 | 15.602 | -14.2352 | -50.25 | 129.75 | 0.84362 | 0.78499 | -12.8369 | -13.6851
Line_1_3-2ph | 0.87873 | 0.87873 | 0 | 1.4194 | 30.4402 | 30.4402 | 19.1923 | -11.5826 | 14.2352 | -11.5826 | -50.25 | 129.75 | 0.78499 | 0.53811 | -13.6851 | -5.25
Line_2_3-2ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.78499 | 0.78499 | -13.6851 | -13.6851
Line_3_3-1ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.78499 | 0.78499 | -13.6851 | -13.6851

## LLL_max_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0_3ph | 0.87873 | 0.87873 | 0 | 0 | 30.4402 | 30.4402 | 20.3969 | -19.1923 | 15.602 | -14.2352 | -50.25 | 129.75 | 0.84362 | 0.78499 | -12.8369 | -13.6851
Line_1_3-2ph | 0.87873 | 0.87873 | 0 | 1.4194 | 30.4402 | 30.4402 | 19.1923 | -11.5826 | 14.2352 | -11.5826 | -50.25 | 129.75 | 0.78499 | 0.53811 | -13.6851 | -5.25
Line_2_3-2ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.78499 | 0.78499 | -13.6851 | -13.6851
Line_3_3-1ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.78499 | 0.78499 | -13.6851 | -13.6851

## LLL_min_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0_3ph | 1.122 | 1.122 | 0 | 0 | 38.8667 | 38.8667 | 27.59 | -23.8195 | 6.5527 | -4.3246 | -40.6939 | 139.3061 | 0.72961 | 0.62287 | -27.3335 | -30.4036
Line_1_3-2ph | 1.122 | 1.122 | 0 | 1.666 | 38.8667 | 38.8667 | 23.8195 | -1e-07 | 4.3246 | -1e-07 | -40.6939 | 139.3061 | 0.62287 | 0 | -30.4036 | 0
Line_2_3-2ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.62287 | 0.62287 | -30.4036 | -30.4036
Line_3_3-1ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.62287 | 0.62287 | -30.4036 | -30.4036

## LLL_min_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0_3ph | 1.122 | 1.122 | 0 | 0 | 38.8667 | 38.8667 | 27.59 | -23.8195 | 6.5527 | -4.3246 | -40.6939 | 139.3061 | 0.72961 | 0.62287 | -27.3335 | -30.4036
Line_1_3-2ph | 1.122 | 1.122 | 0 | 1.666 | 38.8667 | 38.8667 | 23.8195 | -1e-07 | 4.3246 | -1e-07 | -40.6939 | 139.3061 | 0.62287 | 0 | -30.4036 | 0
Line_2_3-2ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.62287 | 0.62287 | -30.4036 | -30.4036
Line_3_3-1ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.62287 | 0.62287 | -30.4036 | -30.4036

## LLL_min_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0_3ph | 0.6655 | 0.6655 | 0 | 0 | 23.0537 | 23.0537 | 16.3502 | -15.0236 | 8.9488 | -8.1649 | -42.4474 | 137.5526 | 0.8085 | 0.7417 | -13.7546 | -13.9247
Line_1_3-2ph | 0.6655 | 0.6655 | 0 | 0.98816 | 23.0537 | 23.0537 | 15.0236 | -6.6434 | 8.1649 | -6.6434 | -42.4474 | 137.5526 | 0.7417 | 0.40754 | -13.9247 | 2.5526
Line_2_3-2ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7417 | 0.7417 | -13.9247 | -13.9247
Line_3_3-1ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7417 | 0.7417 | -13.9247 | -13.9247

## LLL_min_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0_3ph | 0.6655 | 0.6655 | 0 | 0 | 23.0537 | 23.0537 | 16.3502 | -15.0236 | 8.9488 | -8.1649 | -42.4474 | 137.5526 | 0.8085 | 0.7417 | -13.7546 | -13.9247
Line_1_3-2ph | 0.6655 | 0.6655 | 0 | 0.98816 | 23.0537 | 23.0537 | 15.0236 | -6.6434 | 8.1649 | -6.6434 | -42.4474 | 137.5526 | 0.7417 | 0.40754 | -13.9247 | 2.5526
Line_2_3-2ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7417 | 0.7417 | -13.9247 | -13.9247
Line_3_3-1ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7417 | 0.7417 | -13.9247 | -13.9247

## LL_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0_3ph | 0 | 1.4782 | 1.4782 | 0 | 1.4782 | 1.4782 | 0 | 17.0691 | 17.0691 | 0 | 17.0691 | 17.0691 | 5.2106e-15 | 16.027 | 0.60201 | -7.816e-15 | -14.8908 | 0.53427 | 5.2106e-15 | -1.5613 | 9.1442 | -5.2988e-29 | 2.8505 | -7.855 | 0 | -145.2381 | 34.7619 | 0 | 34.7619 | -145.2381 | 1.1 | 0.94339 | 0.53688 | 1.1 | 0.88822 | 0.46125 | 3.7815e-13 | -150.8019 | 120.9953 | 3.8843e-13 | -156.0749 | 128.653
Line_1_3-2ph | 0 | 1.4782 | 1.4782 | 0 | 1.4782 | 1.4782 | 0 | 17.0691 | 17.0691 | 0 | 17.0691 | 17.0691 | -1.3027e-15 | 14.8908 | -0.53427 | 8.7645e-30 | -7.7125 | 7.7125 | 1.3027e-15 | -2.8505 | 7.855 | -1.3027e-15 | 5.3527 | -5.3527 | 0 | -145.2381 | 34.7619 | 0 | 34.7619 | -145.2381 | 1.1 | 0.88822 | 0.46125 | 1.1 | 0.55 | 0.55 | 3.8843e-13 | -156.0749 | 128.653 | 3.855e-13 | 180 | 180
Line_2_3-2ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.7452e-15 | -5.552e-12 | -2.1182e-09 | 2.6867e-15 | 5.5526e-12 | 2.1182e-09 | 3.908e-15 | 4.219e-09 | -5.5979e-10 | -3.908e-15 | -4.219e-09 | 5.5979e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.88822 | 0.46125 | 1.1 | 0.88822 | 0.46125 | 3.8843e-13 | -156.0749 | 128.653 | 3.9184e-13 | -156.0749 | 128.653
Line_3_3-1ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.7452e-15 | -5.552e-12 | -2.1182e-09 | 2.6867e-15 | 5.5526e-12 | 2.1182e-09 | 3.908e-15 | 4.219e-09 | -5.5979e-10 | -3.908e-15 | -4.219e-09 | 5.5979e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.88822 | 0.46125 | 1.1 | 0.88822 | 0.46125 | 3.8843e-13 | -156.0749 | 128.653 | 3.9184e-13 | -156.0749 | 128.653

## LL_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0_3ph | 0 | 1.4782 | 1.4782 | 0 | 1.4782 | 1.4782 | 0 | 17.0691 | 17.0691 | 0 | 17.0691 | 17.0691 | -5.2106e-15 | 16.027 | 0.60201 | -2.6053e-15 | -14.8908 | 0.53427 | -3.4519e-29 | -1.5613 | 9.1442 | 5.2106e-15 | 2.8505 | -7.855 | 0 | -145.2381 | 34.7619 | 0 | 34.7619 | -145.2381 | 1.1 | 0.94339 | 0.53688 | 1.1 | 0.88822 | 0.46125 | 3.7957e-13 | -150.8019 | 120.9953 | 3.8848e-13 | -156.0749 | 128.653
Line_1_3-2ph | 0 | 1.4782 | 1.4782 | 0 | 1.4782 | 1.4782 | 0 | 17.0691 | 17.0691 | 0 | 17.0691 | 17.0691 | -3.2567e-15 | 14.8908 | -0.53427 | 2.2797e-15 | -7.7125 | 7.7125 | -2.6053e-15 | -2.8505 | 7.855 | 1.5484e-29 | 5.3527 | -5.3527 | 0 | -145.2381 | 34.7619 | 0 | 34.7619 | -145.2381 | 1.1 | 0.88822 | 0.46125 | 1.1 | 0.55 | 0.55 | 3.8848e-13 | -156.0749 | 128.653 | 3.8918e-13 | 180 | 180
Line_2_3-2ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5239e-15 | -5.5532e-12 | -2.1182e-09 | 1.7912e-15 | 5.5539e-12 | 2.1182e-09 | -2.6053e-15 | 4.2191e-09 | -5.5979e-10 | 1.3027e-15 | -4.2191e-09 | 5.5979e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.88822 | 0.46125 | 1.1 | 0.88822 | 0.46125 | 3.8848e-13 | -156.0749 | 128.653 | 3.8553e-13 | -156.0749 | 128.653
Line_3_3-1ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5239e-15 | -5.5532e-12 | -2.1182e-09 | 1.7912e-15 | 5.5539e-12 | 2.1182e-09 | -2.6053e-15 | 4.2191e-09 | -5.5979e-10 | 1.3027e-15 | -4.2191e-09 | 5.5979e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.88822 | 0.46125 | 1.1 | 0.88822 | 0.46125 | 3.8848e-13 | -156.0749 | 128.653 | 3.8553e-13 | -156.0749 | 128.653

## LL_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0_3ph | 0 | 1.0056 | 1.0056 | 0 | 1.0056 | 1.0056 | 0 | 11.6118 | 11.6118 | 0 | 11.6118 | 11.6118 | -5.2106e-15 | 11.4047 | 1.3471 | 1.1579e-29 | -10.8789 | -0.82126 | -2.2218e-29 | 0.34599 | 8.2195 | -2.6053e-15 | 0.25064 | -7.6229 | 0 | -141.9447 | 38.0553 | 0 | 38.0553 | -141.9447 | 1.1 | 0.98262 | 0.7173 | 1.1 | 0.93713 | 0.66028 | 2.4431e-13 | -140.2071 | 118.7477 | 2.5465e-13 | -143.2646 | 121.9062
Line_1_3-2ph | 0 | 1.0056 | 1.0056 | 0 | 1.0056 | 1.0056 | 0 | 11.6118 | 11.6118 | 0 | 11.6118 | 11.6118 | -9.77e-16 | 10.8789 | 0.82126 | 3.2567e-16 | -7.5569 | 2.5007 | -4.3423e-30 | -0.25064 | 7.6229 | 6.5133e-16 | 1.4086 | -6.4649 | 0 | -141.9447 | 38.0553 | 0 | 38.0553 | -141.9447 | 1.1 | 0.93713 | 0.66028 | 1.1 | 0.66201 | 0.59695 | 2.5465e-13 | -143.2646 | 121.9062 | 2.5114e-13 | -152.5037 | 149.2023
Line_2_3-2ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.954e-15 | -5.0461e-10 | -2.1262e-09 | 1.3027e-15 | 5.0461e-10 | 2.1262e-09 | 6.5133e-16 | 2.9858e-09 | -1.7716e-10 | -6.5133e-16 | -2.9858e-09 | 1.7716e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.93713 | 0.66028 | 1.1 | 0.93713 | 0.66028 | 2.5465e-13 | -143.2646 | 121.9062 | 2.5681e-13 | -143.2646 | 121.9062
Line_3_3-1ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.954e-15 | -5.0461e-10 | -2.1262e-09 | 1.3027e-15 | 5.0461e-10 | 2.1262e-09 | 6.5133e-16 | 2.9858e-09 | -1.7716e-10 | -6.5133e-16 | -2.9858e-09 | 1.7716e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.93713 | 0.66028 | 1.1 | 0.93713 | 0.66028 | 2.5465e-13 | -143.2646 | 121.9062 | 2.5681e-13 | -143.2646 | 121.9062

## LL_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0_3ph | 0 | 1.0056 | 1.0056 | 0 | 1.0056 | 1.0056 | 0 | 11.6118 | 11.6118 | 0 | 11.6118 | 11.6118 | -3.908e-15 | 11.4047 | 1.3471 | 3.908e-15 | -10.8789 | -0.82126 | -1.6857e-29 | 0.34599 | 8.2195 | -2.6053e-15 | 0.25064 | -7.6229 | 0 | -141.9447 | 38.0553 | 0 | 38.0553 | -141.9447 | 1.1 | 0.98262 | 0.7173 | 1.1 | 0.93713 | 0.66028 | 2.4714e-13 | -140.2071 | 118.7477 | 2.5499e-13 | -143.2646 | 121.9062
Line_1_3-2ph | 0 | 1.0056 | 1.0056 | 0 | 1.0056 | 1.0056 | 0 | 11.6118 | 11.6118 | 0 | 11.6118 | 11.6118 | -2.6053e-15 | 10.8789 | 0.82126 | 2.2797e-15 | -7.5569 | 2.5007 | 6.5133e-16 | -0.25064 | 7.6229 | -1.3027e-15 | 1.4086 | -6.4649 | 0 | -141.9447 | 38.0553 | 0 | 38.0553 | -141.9447 | 1.1 | 0.93713 | 0.66028 | 1.1 | 0.66201 | 0.59695 | 2.5499e-13 | -143.2646 | 121.9062 | 2.5406e-13 | -152.5037 | 149.2023
Line_2_3-2ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.1168e-15 | -5.0461e-10 | -2.1262e-09 | 1.3027e-15 | 5.0461e-10 | 2.1262e-09 | -6.5133e-16 | 2.9859e-09 | -1.7716e-10 | 5.7508e-30 | -2.9859e-09 | 1.7716e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.93713 | 0.66028 | 1.1 | 0.93713 | 0.66028 | 2.5499e-13 | -143.2646 | 121.9062 | 2.5294e-13 | -143.2646 | 121.9062
Line_3_3-1ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.1168e-15 | -5.0461e-10 | -2.1262e-09 | 1.3027e-15 | 5.0461e-10 | 2.1262e-09 | -6.5133e-16 | 2.9859e-09 | -1.7716e-10 | 5.7508e-30 | -2.9859e-09 | 1.7716e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.93713 | 0.66028 | 1.1 | 0.93713 | 0.66028 | 2.5499e-13 | -143.2646 | 121.9062 | 2.5294e-13 | -143.2646 | 121.9062

## LL_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0_3ph | 0 | 0.97167 | 0.97167 | 0 | 0.97167 | 0.97167 | 0 | 11.2199 | 11.2199 | 0 | 11.2199 | 11.2199 | 2.3685e-15 | 10.5553 | 3.2397 | -1.2305e-15 | -9.6126 | -2.2971 | 9.9124e-30 | -2.6153 | 5.8916 | 2.3685e-15 | 3.1723 | -5.3346 | 0 | -130.6939 | 49.3061 | 0 | 49.3061 | -130.6939 | 1 | 0.96921 | 0.59926 | 1 | 0.9022 | 0.51767 | 2.3979e-13 | -144.6099 | 110.5004 | 2.4697e-13 | -148.9576 | 116.0093
Line_1_3-2ph | 0 | 0.97167 | 0.97167 | 0 | 0.97167 | 0.97167 | 0 | 11.2199 | 11.2199 | 0 | 11.2199 | 11.2199 | 1.1102e-15 | 9.6126 | 2.2971 | -2.4425e-15 | -3.6578 | 3.6578 | 1.7764e-15 | -3.1723 | 5.3346 | -1.1842e-15 | 4.2535 | -4.2535 | 0 | -130.6939 | 49.3061 | 0 | 49.3061 | -130.6939 | 1 | 0.9022 | 0.51767 | 1 | 0.5 | 0.5 | 2.4697e-13 | -148.9576 | 116.0093 | 2.4715e-13 | -180 | 180
Line_2_3-2ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.9212e-16 | 1.8012e-10 | -1.8218e-09 | -4.4409e-16 | -1.8012e-10 | 1.8218e-09 | 1.1842e-15 | 3.2033e-09 | 2.642e-10 | -8.8818e-16 | -3.2033e-09 | -2.642e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.9022 | 0.51767 | 1 | 0.9022 | 0.51767 | 2.4697e-13 | -148.9576 | 116.0093 | 2.5318e-13 | -148.9576 | 116.0093
Line_3_3-1ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.9212e-16 | 1.8012e-10 | -1.8218e-09 | -4.4409e-16 | -1.8012e-10 | 1.8218e-09 | 1.1842e-15 | 3.2033e-09 | 2.642e-10 | -8.8818e-16 | -3.2033e-09 | -2.642e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.9022 | 0.51767 | 1 | 0.9022 | 0.51767 | 2.4697e-13 | -148.9576 | 116.0093 | 2.5318e-13 | -148.9576 | 116.0093

## LL_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0_3ph | 0 | 0.97167 | 0.97167 | 0 | 0.97167 | 0.97167 | 0 | 11.2199 | 11.2199 | 0 | 11.2199 | 11.2199 | 2.3685e-15 | 10.5553 | 3.2397 | -1.2305e-15 | -9.6126 | -2.2971 | 9.9124e-30 | -2.6153 | 5.8916 | 2.3685e-15 | 3.1723 | -5.3346 | 0 | -130.6939 | 49.3061 | 0 | 49.3061 | -130.6939 | 1 | 0.96921 | 0.59926 | 1 | 0.9022 | 0.51767 | 2.3979e-13 | -144.6099 | 110.5004 | 2.4697e-13 | -148.9576 | 116.0093
Line_1_3-2ph | 0 | 0.97167 | 0.97167 | 0 | 0.97167 | 0.97167 | 0 | 11.2199 | 11.2199 | 0 | 11.2199 | 11.2199 | 1.1102e-15 | 9.6126 | 2.2971 | -2.4425e-15 | -3.6578 | 3.6578 | 1.7764e-15 | -3.1723 | 5.3346 | -1.1842e-15 | 4.2535 | -4.2535 | 0 | -130.6939 | 49.3061 | 0 | 49.3061 | -130.6939 | 1 | 0.9022 | 0.51767 | 1 | 0.5 | 0.5 | 2.4697e-13 | -148.9576 | 116.0093 | 2.4715e-13 | -180 | 180
Line_2_3-2ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.9212e-16 | 1.8012e-10 | -1.8218e-09 | -4.4409e-16 | -1.8012e-10 | 1.8218e-09 | 1.1842e-15 | 3.2033e-09 | 2.642e-10 | -8.8818e-16 | -3.2033e-09 | -2.642e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.9022 | 0.51767 | 1 | 0.9022 | 0.51767 | 2.4697e-13 | -148.9576 | 116.0093 | 2.5318e-13 | -148.9576 | 116.0093
Line_3_3-1ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.9212e-16 | 1.8012e-10 | -1.8218e-09 | -4.4409e-16 | -1.8012e-10 | 1.8218e-09 | 1.1842e-15 | 3.2033e-09 | 2.642e-10 | -8.8818e-16 | -3.2033e-09 | -2.642e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.9022 | 0.51767 | 1 | 0.9022 | 0.51767 | 2.4697e-13 | -148.9576 | 116.0093 | 2.5318e-13 | -148.9576 | 116.0093

## LL_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0_3ph | 0 | 0.72361 | 0.72361 | 0 | 0.72361 | 0.72361 | 0 | 8.3555 | 8.3555 | 0 | 8.3555 | 8.3555 | 3.3307e-16 | 7.9186 | 2.35 | 2.2204e-16 | -7.3958 | -1.8272 | -2.3685e-15 | -0.89714 | 5.3322 | 7.3458e-31 | 1.2061 | -5.0233 | 0 | -131.7946 | 48.2054 | 0 | 48.2054 | -131.7946 | 1 | 0.95377 | 0.69739 | 1 | 0.89684 | 0.63973 | 1.8482e-13 | -138.2584 | 114.4218 | 1.8955e-13 | -141.0566 | 118.2168
Line_1_3-2ph | 0 | 0.72361 | 0.72361 | 0 | 0.72361 | 0.72361 | 0 | 8.3555 | 8.3555 | 0 | 8.3555 | 8.3555 | 2.9606e-16 | 7.3958 | 1.8272 | -1.0362e-15 | -4.0933 | 1.4753 | 1.1842e-15 | -1.2061 | 5.0233 | -1.1842e-15 | 1.8057 | -4.4237 | 0 | -131.7946 | 48.2054 | 0 | 48.2054 | -131.7946 | 1 | 0.89684 | 0.63973 | 1 | 0.53544 | 0.5581 | 1.8955e-13 | -141.0566 | 118.2168 | 1.9225e-13 | -155.598 | 156.6489
Line_2_3-2ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.9606e-16 | -2.3933e-10 | -1.6879e-09 | -2.2204e-16 | 2.3933e-10 | 1.6879e-09 | 2.9606e-16 | 2.363e-09 | 1.4598e-10 | -2.9606e-16 | -2.363e-09 | -1.4598e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.89684 | 0.63973 | 1 | 0.89684 | 0.63973 | 1.8955e-13 | -141.0566 | 118.2168 | 1.9418e-13 | -141.0566 | 118.2168
Line_3_3-1ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.9606e-16 | -2.3933e-10 | -1.6879e-09 | -2.2204e-16 | 2.3933e-10 | 1.6879e-09 | 2.9606e-16 | 2.363e-09 | 1.4598e-10 | -2.9606e-16 | -2.363e-09 | -1.4598e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.89684 | 0.63973 | 1 | 0.89684 | 0.63973 | 1.8955e-13 | -141.0566 | 118.2168 | 1.9418e-13 | -141.0566 | 118.2168

## LL_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0_3ph | 0 | 0.72361 | 0.72361 | 0 | 0.72361 | 0.72361 | 0 | 8.3555 | 8.3555 | 0 | 8.3555 | 8.3555 | 3.3307e-16 | 7.9186 | 2.35 | 2.2204e-16 | -7.3958 | -1.8272 | -2.3685e-15 | -0.89714 | 5.3322 | 7.3458e-31 | 1.2061 | -5.0233 | 0 | -131.7946 | 48.2054 | 0 | 48.2054 | -131.7946 | 1 | 0.95377 | 0.69739 | 1 | 0.89684 | 0.63973 | 1.8482e-13 | -138.2584 | 114.4218 | 1.8955e-13 | -141.0566 | 118.2168
Line_1_3-2ph | 0 | 0.72361 | 0.72361 | 0 | 0.72361 | 0.72361 | 0 | 8.3555 | 8.3555 | 0 | 8.3555 | 8.3555 | 2.9606e-16 | 7.3958 | 1.8272 | -1.0362e-15 | -4.0933 | 1.4753 | 1.1842e-15 | -1.2061 | 5.0233 | -1.1842e-15 | 1.8057 | -4.4237 | 0 | -131.7946 | 48.2054 | 0 | 48.2054 | -131.7946 | 1 | 0.89684 | 0.63973 | 1 | 0.53544 | 0.5581 | 1.8955e-13 | -141.0566 | 118.2168 | 1.9225e-13 | -155.598 | 156.6489
Line_2_3-2ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.9606e-16 | -2.3933e-10 | -1.6879e-09 | -2.2204e-16 | 2.3933e-10 | 1.6879e-09 | 2.9606e-16 | 2.363e-09 | 1.4598e-10 | -2.9606e-16 | -2.363e-09 | -1.4598e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.89684 | 0.63973 | 1 | 0.89684 | 0.63973 | 1.8955e-13 | -141.0566 | 118.2168 | 1.9418e-13 | -141.0566 | 118.2168
Line_3_3-1ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.9606e-16 | -2.3933e-10 | -1.6879e-09 | -2.2204e-16 | 2.3933e-10 | 1.6879e-09 | 2.9606e-16 | 2.363e-09 | 1.4598e-10 | -2.9606e-16 | -2.363e-09 | -1.4598e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.89684 | 0.63973 | 1 | 0.89684 | 0.63973 | 1.8955e-13 | -141.0566 | 118.2168 | 1.9418e-13 | -141.0566 | 118.2168

## LG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0_3ph | 1.2331 | 0.0038894 | 0.0038894 | 1.2322 | 0.0029309 | 0.0029309 | 14.2382 | 0.044911 | 0.044911 | 14.2277 | 0.033844 | 0.033844 | 10.4307 | 0.038929 | -0.045808 | -8.0181 | -0.028786 | 0.035562 | 4.3962 | -0.030473 | -0.018582 | -3.0527 | 0.024031 | 0.019896 | -44.8877 | -82.0114 | -82.0114 | 135.1313 | 93.6773 | 93.6773 |  | 0.795 | 1.1008 | 1.1007 | 0.60302 | 1.108 | 1.204 | -22.0337 | -120.0652 | 120.0683 | -24.0257 | -126.1783 | 122.9032
Line_1_3-2ph | 1.2308 | 0.0013244 | 0.0013244 | 1.23 | 0 | 0 | 14.2124 | 0.015293 | 0.015293 | 14.2024 | 0 | 0 | 8.0118 | 0.014284 | -0.014794 | 6.0756e-12 | -3.5449e-09 | -6.5607e-09 | 3.0433 | -0.0091145 | -0.010963 | 1.7615e-11 | -5.8604e-09 | 4.6996e-09 | -44.8247 | -93.6371 | -93.6371 | 135.2217 | 0 | 0 |  | 0.60302 | 1.108 | 1.204 | 0 | 1.1882 | 1.4001 | -24.0257 | -126.1783 | 122.9032 | 0 | -137.1079 | 128.4462
Line_2_3-2ph | 0.00081305 | 0.00081305 | 0.00081305 | 0 | 0 | 0 | 0.0093883 | 0.0093883 | 0.0093883 | 0 | 0 | 0 | 0.0031374 | 0.0072511 | -0.010384 | 2.4848e-09 | -1.2351e-09 | -1.606e-09 | 0.0047124 | -0.0074584 | -0.0044665 | -2.4481e-09 | -2.0531e-09 | 2.0507e-09 | -80.3709 | -80.3709 | -80.3709 | 0 | 0 | 0 |  | 0.60302 | 1.108 | 1.204 | 0.60273 | 1.1079 | 1.2044 | -24.0257 | -126.1783 | 122.9032 | -24.0068 | -126.1952 | 122.9028
Line_3_3-1ph | 0.00081305 | 0.00081305 | 0.00081305 | 0 | 0 | 0 | 0.0093883 | 0.0093883 | 0.0093883 | 0 | 0 | 0 | 0.0031374 | 0.0072511 | -0.010384 | 2.4848e-09 | -1.2351e-09 | -1.606e-09 | 0.0047124 | -0.0074584 | -0.0044665 | -2.4481e-09 | -2.0531e-09 | 2.0507e-09 | -80.3709 | -80.3709 | -80.3709 | 0 | 0 | 0 |  | 0.60302 | 1.108 | 1.204 | 0.60273 | 1.1079 | 1.2044 | -24.0257 | -126.1783 | 122.9032 | -24.0068 | -126.1952 | 122.9028

## LG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0_3ph | 1.2331 | 0.0038894 | 0.0038894 | 1.2322 | 0.0029309 | 0.0029309 | 14.2382 | 0.044911 | 0.044911 | 14.2277 | 0.033844 | 0.033844 | 10.4307 | 0.038929 | -0.045808 | -8.0181 | -0.028786 | 0.035562 | 4.3962 | -0.030473 | -0.018582 | -3.0527 | 0.024031 | 0.019896 | -44.8877 | -82.0114 | -82.0114 | 135.1313 | 93.6773 | 93.6773 |  | 0.795 | 1.1008 | 1.1007 | 0.60302 | 1.108 | 1.204 | -22.0337 | -120.0652 | 120.0683 | -24.0257 | -126.1783 | 122.9032
Line_1_3-2ph | 1.2308 | 0.0013244 | 0.0013244 | 1.23 | 0 | 0 | 14.2124 | 0.015293 | 0.015293 | 14.2024 | 0 | 0 | 8.0118 | 0.014284 | -0.014794 | 6.0805e-12 | -3.5449e-09 | -6.5607e-09 | 3.0433 | -0.0091145 | -0.010963 | 1.7597e-11 | -5.8604e-09 | 4.6996e-09 | -44.8247 | -93.6371 | -93.6371 | 135.2217 | 0 | 0 |  | 0.60302 | 1.108 | 1.204 | 0 | 1.1882 | 1.4001 | -24.0257 | -126.1783 | 122.9032 | 0 | -137.1079 | 128.4462
Line_2_3-2ph | 0.00081305 | 0.00081305 | 0.00081305 | 0 | 0 | 0 | 0.0093883 | 0.0093883 | 0.0093883 | 0 | 0 | 0 | 0.0031374 | 0.0072511 | -0.010384 | 2.4848e-09 | -1.2351e-09 | -1.606e-09 | 0.0047124 | -0.0074584 | -0.0044665 | -2.4481e-09 | -2.0531e-09 | 2.0507e-09 | -80.3709 | -80.3709 | -80.3709 | 0 | 0 | 0 |  | 0.60302 | 1.108 | 1.204 | 0.60273 | 1.1079 | 1.2044 | -24.0257 | -126.1783 | 122.9032 | -24.0068 | -126.1952 | 122.9028
Line_3_3-1ph | 0.00081305 | 0.00081305 | 0.00081305 | 0 | 0 | 0 | 0.0093883 | 0.0093883 | 0.0093883 | 0 | 0 | 0 | 0.0031374 | 0.0072511 | -0.010384 | 2.4848e-09 | -1.2351e-09 | -1.606e-09 | 0.0047124 | -0.0074584 | -0.0044665 | -2.4481e-09 | -2.0531e-09 | 2.0507e-09 | -80.3709 | -80.3709 | -80.3709 | 0 | 0 | 0 |  | 0.60302 | 1.108 | 1.204 | 0.60273 | 1.1079 | 1.2044 | -24.0257 | -126.1783 | 122.9032 | -24.0068 | -126.1952 | 122.9028

## LG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0_3ph | 0.73191 | 0.0023086 | 0.0023086 | 0.73137 | 0.0017397 | 0.0017397 | 8.4514 | 0.026658 | 0.026658 | 8.4452 | 0.020089 | 0.020089 | 6.3416 | 0.023137 | -0.027171 | -5.4905 | -0.017635 | 0.020564 | 4.2257 | -0.018036 | -0.011056 | -3.7495 | 0.013418 | 0.011023 | -44.9778 | -82.1015 | -82.1015 | 135.0412 | 93.5872 | 93.5872 |  | 0.9017 | 1.1005 | 1.1004 | 0.78728 | 1.1031 | 1.1615 | -11.3004 | -120.0388 | 120.0405 | -10.6295 | -123.6791 | 121.7812
Line_1_3-2ph | 0.73059 | 0.00078612 | 0.00078612 | 0.73007 | 0 | 0 | 8.4361 | 0.0090773 | 0.0090773 | 8.4301 | 0 | 0 | 5.4875 | 0.0086758 | -0.0085822 | -2.665 | -1.6148e-09 | -3.4148e-09 | 3.7413 | -0.0049993 | -0.0061235 | -2.665 | -3.55e-09 | 2.7153e-09 | -44.9148 | -93.7272 | -93.7272 | 135.1316 | 0 | 0 |  | 0.78728 | 1.1031 | 1.1615 | 0.44707 | 1.1399 | 1.2751 | -10.6295 | -123.6791 | 121.7812 | 0.13159 | -130.489 | 125.4811
Line_2_3-2ph | 0.0004826 | 0.0004826 | 0.0004826 | 0 | 0 | 0 | 0.0055726 | 0.0055726 | 0.0055726 | 0 | 0 | 0 | 0.0015126 | 0.0044797 | -0.0059907 | 2.3154e-09 | -6.7421e-10 | -8.9817e-10 | 0.0041182 | -0.0042094 | -0.0024499 | -1.3965e-09 | -1.2451e-09 | 1.1904e-09 | -80.461 | -80.461 | -80.461 | 0 | 0 | 0 |  | 0.78728 | 1.1031 | 1.1615 | 0.78714 | 1.103 | 1.1617 | -10.6295 | -123.6791 | 121.7812 | -10.6182 | -123.6889 | 121.7812
Line_3_3-1ph | 0.0004826 | 0.0004826 | 0.0004826 | 0 | 0 | 0 | 0.0055726 | 0.0055726 | 0.0055726 | 0 | 0 | 0 | 0.0015126 | 0.0044797 | -0.0059907 | 2.3154e-09 | -6.7421e-10 | -8.9817e-10 | 0.0041182 | -0.0042094 | -0.0024499 | -1.3965e-09 | -1.2451e-09 | 1.1904e-09 | -80.461 | -80.461 | -80.461 | 0 | 0 | 0 |  | 0.78728 | 1.1031 | 1.1615 | 0.78714 | 1.103 | 1.1617 | -10.6295 | -123.6791 | 121.7812 | -10.6182 | -123.6889 | 121.7812

## LG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0_3ph | 0.73191 | 0.0023086 | 0.0023086 | 0.73137 | 0.0017397 | 0.0017397 | 8.4514 | 0.026658 | 0.026658 | 8.4452 | 0.020089 | 0.020089 | 6.3416 | 0.023137 | -0.027171 | -5.4905 | -0.017635 | 0.020564 | 4.2257 | -0.018036 | -0.011056 | -3.7495 | 0.013418 | 0.011023 | -44.9778 | -82.1015 | -82.1015 | 135.0412 | 93.5872 | 93.5872 |  | 0.9017 | 1.1005 | 1.1004 | 0.78728 | 1.1031 | 1.1615 | -11.3004 | -120.0388 | 120.0405 | -10.6295 | -123.6791 | 121.7812
Line_1_3-2ph | 0.73059 | 0.00078612 | 0.00078612 | 0.73007 | 0 | 0 | 8.4361 | 0.0090773 | 0.0090773 | 8.4301 | 0 | 0 | 5.4875 | 0.0086758 | -0.0085822 | -2.665 | -1.6148e-09 | -3.4148e-09 | 3.7413 | -0.0049993 | -0.0061235 | -2.665 | -3.55e-09 | 2.7153e-09 | -44.9148 | -93.7272 | -93.7272 | 135.1316 | 0 | 0 |  | 0.78728 | 1.1031 | 1.1615 | 0.44707 | 1.1399 | 1.2751 | -10.6295 | -123.6791 | 121.7812 | 0.13159 | -130.489 | 125.4811
Line_2_3-2ph | 0.0004826 | 0.0004826 | 0.0004826 | 0 | 0 | 0 | 0.0055726 | 0.0055726 | 0.0055726 | 0 | 0 | 0 | 0.0015126 | 0.0044797 | -0.0059907 | 2.3154e-09 | -6.7421e-10 | -8.9817e-10 | 0.0041182 | -0.0042094 | -0.0024499 | -1.3965e-09 | -1.2451e-09 | 1.1904e-09 | -80.461 | -80.461 | -80.461 | 0 | 0 | 0 |  | 0.78728 | 1.1031 | 1.1615 | 0.78714 | 1.103 | 1.1617 | -10.6295 | -123.6791 | 121.7812 | -10.6182 | -123.6889 | 121.7812
Line_3_3-1ph | 0.0004826 | 0.0004826 | 0.0004826 | 0 | 0 | 0 | 0.0055726 | 0.0055726 | 0.0055726 | 0 | 0 | 0 | 0.0015126 | 0.0044797 | -0.0059907 | 2.3154e-09 | -6.7421e-10 | -8.9817e-10 | 0.0041182 | -0.0042094 | -0.0024499 | -1.3965e-09 | -1.2451e-09 | 1.1904e-09 | -80.461 | -80.461 | -80.461 | 0 | 0 | 0 |  | 0.78728 | 1.1031 | 1.1615 | 0.78714 | 1.103 | 1.1617 | -10.6295 | -123.6791 | 121.7812 | -10.6182 | -123.6889 | 121.7812

## LG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0_3ph | 0.73219 | 0.0032678 | 0.0032678 | 0.7316 | 0.0025695 | 0.0025695 | 8.4547 | 0.037734 | 0.037734 | 8.4478 | 0.02967 | 0.02967 | 7.0609 | 0.029666 | -0.03503 | -5.4268 | -0.023034 | 0.028257 | 1.5502 | -0.023366 | -0.014093 | -1.0795 | 0.019948 | 0.016753 | -29.9224 | -81.8433 | -81.8433 | 150.1112 | 93.5647 | 93.5647 |  | 0.85504 | 1.0008 | 1.0007 | 0.65498 | 1.027 | 1.1072 | -17.5401 | -120.0684 | 120.0718 | -18.6388 | -127.3285 | 124.2269
Line_1_3-2ph | 0.73074 | 0.0012438 | 0.0012438 | 0.73018 | 0 | 0 | 8.4378 | 0.014362 | 0.014362 | 8.4314 | 0 | 0 | 5.4219 | 0.01223 | -0.012603 | 5.336e-12 | -3.9878e-09 | -6.348e-09 | 1.0705 | -0.0082441 | -0.009696 | 1.2604e-12 | -5.4819e-09 | 4.5735e-09 | -29.8079 | -93.3459 | -93.3459 | 150.2795 | 0 | 0 |  | 0.65498 | 1.027 | 1.1072 | 0 | 1.1368 | 1.312 | -18.6388 | -127.3285 | 124.2269 | 0 | -139.2435 | 131.0195
Line_2_3-2ph | 0.00067158 | 0.00067158 | 0.00067158 | 0 | 0 | 0 | 0.0077547 | 0.0077547 | 0.0077547 | 0 | 0 | 0 | 0.0024314 | 0.0054018 | -0.0078272 | 2.0768e-09 | -1.1406e-09 | -1.4279e-09 | 0.0044594 | -0.0058519 | -0.0035284 | -1.895e-09 | -1.775e-09 | 1.7727e-09 | -80.0382 | -80.0382 | -80.0382 | 0 | 0 | 0 |  | 0.65498 | 1.027 | 1.1072 | 0.65464 | 1.0267 | 1.1077 | -18.6388 | -127.3285 | 124.2269 | -18.6034 | -127.3539 | 124.221
Line_3_3-1ph | 0.00067158 | 0.00067158 | 0.00067158 | 0 | 0 | 0 | 0.0077547 | 0.0077547 | 0.0077547 | 0 | 0 | 0 | 0.0024314 | 0.0054018 | -0.0078272 | 2.0768e-09 | -1.1406e-09 | -1.4279e-09 | 0.0044594 | -0.0058519 | -0.0035284 | -1.895e-09 | -1.775e-09 | 1.7727e-09 | -80.0382 | -80.0382 | -80.0382 | 0 | 0 | 0 |  | 0.65498 | 1.027 | 1.1072 | 0.65464 | 1.0267 | 1.1077 | -18.6388 | -127.3285 | 124.2269 | -18.6034 | -127.3539 | 124.221

## LG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0_3ph | 0.73219 | 0.0032678 | 0.0032678 | 0.7316 | 0.0025695 | 0.0025695 | 8.4547 | 0.037734 | 0.037734 | 8.4478 | 0.02967 | 0.02967 | 7.0609 | 0.029666 | -0.03503 | -5.4268 | -0.023034 | 0.028257 | 1.5502 | -0.023366 | -0.014093 | -1.0795 | 0.019948 | 0.016753 | -29.9224 | -81.8433 | -81.8433 | 150.1112 | 93.5647 | 93.5647 |  | 0.85504 | 1.0008 | 1.0007 | 0.65498 | 1.027 | 1.1072 | -17.5401 | -120.0684 | 120.0718 | -18.6388 | -127.3285 | 124.2269
Line_1_3-2ph | 0.73074 | 0.0012438 | 0.0012438 | 0.73018 | 0 | 0 | 8.4378 | 0.014362 | 0.014362 | 8.4314 | 0 | 0 | 5.4219 | 0.01223 | -0.012603 | 5.336e-12 | -3.9878e-09 | -6.348e-09 | 1.0705 | -0.0082441 | -0.009696 | 1.2604e-12 | -5.4819e-09 | 4.5735e-09 | -29.8079 | -93.3459 | -93.3459 | 150.2795 | 0 | 0 |  | 0.65498 | 1.027 | 1.1072 | 0 | 1.1368 | 1.312 | -18.6388 | -127.3285 | 124.2269 | 0 | -139.2435 | 131.0195
Line_2_3-2ph | 0.00067158 | 0.00067158 | 0.00067158 | 0 | 0 | 0 | 0.0077547 | 0.0077547 | 0.0077547 | 0 | 0 | 0 | 0.0024314 | 0.0054018 | -0.0078272 | 2.0768e-09 | -1.1406e-09 | -1.4279e-09 | 0.0044594 | -0.0058519 | -0.0035284 | -1.895e-09 | -1.775e-09 | 1.7727e-09 | -80.0382 | -80.0382 | -80.0382 | 0 | 0 | 0 |  | 0.65498 | 1.027 | 1.1072 | 0.65464 | 1.0267 | 1.1077 | -18.6388 | -127.3285 | 124.2269 | -18.6034 | -127.3539 | 124.221
Line_3_3-1ph | 0.00067158 | 0.00067158 | 0.00067158 | 0 | 0 | 0 | 0.0077547 | 0.0077547 | 0.0077547 | 0 | 0 | 0 | 0.0024314 | 0.0054018 | -0.0078272 | 2.0768e-09 | -1.1406e-09 | -1.4279e-09 | 0.0044594 | -0.0058519 | -0.0035284 | -1.895e-09 | -1.775e-09 | 1.7727e-09 | -80.0382 | -80.0382 | -80.0382 | 0 | 0 | 0 |  | 0.65498 | 1.027 | 1.1072 | 0.65464 | 1.0267 | 1.1077 | -18.6388 | -127.3285 | 124.2269 | -18.6034 | -127.3539 | 124.221

## LG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0_3ph | 0.50982 | 0.0022754 | 0.0022754 | 0.5094 | 0.0017891 | 0.0017891 | 5.8869 | 0.026274 | 0.026274 | 5.8821 | 0.020659 | 0.020659 | 4.7147 | 0.021919 | -0.023506 | -3.9222 | -0.017275 | 0.018501 | 2.0521 | -0.014508 | -0.011769 | -1.8221 | 0.011689 | 0.012402 | -34.6286 | -86.5496 | -86.5496 | 145.405 | 88.8585 | 88.8585 |  | 0.87346 | 1.0005 | 1.0005 | 0.73524 | 1.0096 | 1.0781 | -11.1072 | -120.0499 | 120.0477 | -9.6772 | -125.2265 | 122.6943
Line_1_3-2ph | 0.50881 | 0.00086603 | 0.00086603 | 0.50842 | 0 | 0 | 5.8752 | 0.01 | 0.01 | 5.8707 | 0 | 0 | 3.9201 | 0.0089819 | -0.008168 | -1.2925 | -1.9675e-09 | -4.1798e-09 | 1.8144 | -0.004611 | -0.0070372 | -1.2925 | -3.95e-09 | 2.893e-09 | -34.5142 | -98.0522 | -98.0522 | 145.5732 | 0 | 0 |  | 0.73524 | 1.0096 | 1.0781 | 0.31134 | 1.0628 | 1.2243 | -9.6772 | -125.2265 | 122.6943 | 10.5732 | -134.393 | 127.3957
Line_2_3-2ph | 0.00046761 | 0.00046761 | 0.00046761 | 0 | 0 | 0 | 0.0053995 | 0.0053995 | 0.0053995 | 0 | 0 | 0 | 0.001023 | 0.0041464 | -0.0051665 | 1.9277e-09 | -6.3102e-10 | -1.0331e-09 | 0.0038359 | -0.0035392 | -0.0026825 | -1.0563e-09 | -1.2992e-09 | 1.1463e-09 | -84.7444 | -84.7444 | -84.7444 | 0 | 0 | 0 |  | 0.73524 | 1.0096 | 1.0781 | 0.73508 | 1.0094 | 1.0785 | -9.6772 | -125.2265 | 122.6943 | -9.6515 | -125.2431 | 122.689
Line_3_3-1ph | 0.00046761 | 0.00046761 | 0.00046761 | 0 | 0 | 0 | 0.0053995 | 0.0053995 | 0.0053995 | 0 | 0 | 0 | 0.001023 | 0.0041464 | -0.0051665 | 1.9277e-09 | -6.3102e-10 | -1.0331e-09 | 0.0038359 | -0.0035392 | -0.0026825 | -1.0563e-09 | -1.2992e-09 | 1.1463e-09 | -84.7444 | -84.7444 | -84.7444 | 0 | 0 | 0 |  | 0.73524 | 1.0096 | 1.0781 | 0.73508 | 1.0094 | 1.0785 | -9.6772 | -125.2265 | 122.6943 | -9.6515 | -125.2431 | 122.689

## LG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0_3ph | 0.50982 | 0.0022754 | 0.0022754 | 0.5094 | 0.0017891 | 0.0017891 | 5.8869 | 0.026274 | 0.026274 | 5.8821 | 0.020659 | 0.020659 | 4.7147 | 0.021919 | -0.023506 | -3.9222 | -0.017275 | 0.018501 | 2.0521 | -0.014508 | -0.011769 | -1.8221 | 0.011689 | 0.012402 | -34.6286 | -86.5496 | -86.5496 | 145.405 | 88.8585 | 88.8585 |  | 0.87346 | 1.0005 | 1.0005 | 0.73524 | 1.0096 | 1.0781 | -11.1072 | -120.0499 | 120.0477 | -9.6772 | -125.2265 | 122.6943
Line_1_3-2ph | 0.50881 | 0.00086603 | 0.00086603 | 0.50842 | 0 | 0 | 5.8752 | 0.01 | 0.01 | 5.8707 | 0 | 0 | 3.9201 | 0.0089819 | -0.008168 | -1.2925 | -1.9675e-09 | -4.1798e-09 | 1.8144 | -0.004611 | -0.0070372 | -1.2925 | -3.95e-09 | 2.893e-09 | -34.5142 | -98.0522 | -98.0522 | 145.5732 | 0 | 0 |  | 0.73524 | 1.0096 | 1.0781 | 0.31134 | 1.0628 | 1.2243 | -9.6772 | -125.2265 | 122.6943 | 10.5732 | -134.393 | 127.3957
Line_2_3-2ph | 0.00046761 | 0.00046761 | 0.00046761 | 0 | 0 | 0 | 0.0053995 | 0.0053995 | 0.0053995 | 0 | 0 | 0 | 0.001023 | 0.0041464 | -0.0051665 | 1.9277e-09 | -6.3102e-10 | -1.0331e-09 | 0.0038359 | -0.0035392 | -0.0026825 | -1.0563e-09 | -1.2992e-09 | 1.1463e-09 | -84.7444 | -84.7444 | -84.7444 | 0 | 0 | 0 |  | 0.73524 | 1.0096 | 1.0781 | 0.73508 | 1.0094 | 1.0785 | -9.6772 | -125.2265 | 122.6943 | -9.6515 | -125.2431 | 122.689
Line_3_3-1ph | 0.00046761 | 0.00046761 | 0.00046761 | 0 | 0 | 0 | 0.0053995 | 0.0053995 | 0.0053995 | 0 | 0 | 0 | 0.001023 | 0.0041464 | -0.0051665 | 1.9277e-09 | -6.3102e-10 | -1.0331e-09 | 0.0038359 | -0.0035392 | -0.0026825 | -1.0563e-09 | -1.2992e-09 | 1.1463e-09 | -84.7444 | -84.7444 | -84.7444 | 0 | 0 | 0 |  | 0.73524 | 1.0096 | 1.0781 | 0.73508 | 1.0094 | 1.0785 | -9.6772 | -125.2265 | 122.6943 | -9.6515 | -125.2431 | 122.689

## LLG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0_3ph | 0.0029964 | 1.6735 | 1.4224 | 0.002258 | 1.6734 | 1.4221 | 0.0346 | 19.3238 | 16.4246 | 0.026074 | 19.3226 | 16.4206 | -0.009065 | 14.7893 | 6.3274 | 0.0060168 | -12.0452 | -5.5975 | -0.037005 | 1.7147 | 7.7065 | 0.030302 | -1.2459 | -5.0606 | 103.7729 | -161.1098 | 53.5313 | -80.5384 | 18.9161 | -126.4962 |  | 1.1011 | 0.77047 | 0.6071 | 1.1848 | 0.6267 | 0.45954 | 0.0083325 | -154.4963 | 104.1435 | -1.7692 | -155.1784 | 95.6197
Line_1_3-2ph | 0.0010203 | 1.6735 | 1.4213 | 0 | 1.6738 | 1.4205 | 0.011782 | 19.3235 | 16.4117 | 0 | 19.3269 | 16.4025 | -0.00095344 | 12.0467 | 5.591 | -5.998e-09 | 3.0315e-12 | -1.6984e-12 | -0.013927 | 1.237 | 5.0617 | -6.8897e-10 | 8.2673e-12 | 7.5757e-12 | 92.1472 | -161.0411 | 53.4641 | 0 | 18.9924 | -126.5617 |  | 1.1848 | 0.6267 | 0.45954 | 1.3595 | 0 | 0 | -1.7692 | -155.1784 | 95.6197 | -3.6018 | 0 | 0
Line_2_3-2ph | 0.00062638 | 0.00062638 | 0.00062638 | 0 | 0 | 0 | 0.0072328 | 0.0072328 | 0.0072328 | 0 | 0 | 0 | -0.0025317 | -0.00074097 | 0.0032754 | -1.9727e-09 | 1.9243e-09 | 1.7425e-09 | -0.0081873 | 0.0044718 | -0.00056538 | 8.2667e-11 | -2.7986e-09 | -2.0219e-09 | 105.4134 | 105.4134 | 105.4134 | 0 | 0 | 0 |  | 1.1848 | 0.6267 | 0.45954 | 1.185 | 0.62664 | 0.45931 | -1.7692 | -155.1784 | 95.6197 | -1.7794 | -155.1541 | 95.6019
Line_3_3-1ph | 0.00062638 | 0.00062638 | 0.00062638 | 0 | 0 | 0 | 0.0072328 | 0.0072328 | 0.0072328 | 0 | 0 | 0 | -0.0025317 | -0.00074097 | 0.0032754 | -1.9727e-09 | 1.9243e-09 | 1.7425e-09 | -0.0081873 | 0.0044718 | -0.00056538 | 8.2667e-11 | -2.7986e-09 | -2.0219e-09 | 105.4134 | 105.4134 | 105.4134 | 0 | 0 | 0 |  | 1.1848 | 0.6267 | 0.45954 | 1.185 | 0.62664 | 0.45931 | -1.7692 | -155.1784 | 95.6197 | -1.7794 | -155.1541 | 95.6019

## LLG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0_3ph | 0.0029964 | 1.6735 | 1.4224 | 0.002258 | 1.6734 | 1.4221 | 0.0346 | 19.3238 | 16.4246 | 0.026074 | 19.3226 | 16.4206 | -0.009065 | 14.7893 | 6.3274 | 0.0060168 | -12.0452 | -5.5975 | -0.037005 | 1.7147 | 7.7065 | 0.030302 | -1.2459 | -5.0606 | 103.7729 | -161.1098 | 53.5313 | -80.5384 | 18.9161 | -126.4962 |  | 1.1011 | 0.77047 | 0.6071 | 1.1848 | 0.6267 | 0.45954 | 0.0083325 | -154.4963 | 104.1435 | -1.7692 | -155.1784 | 95.6197
Line_1_3-2ph | 0.0010203 | 1.6735 | 1.4213 | 0 | 1.6738 | 1.4205 | 0.011782 | 19.3235 | 16.4117 | 0 | 19.3269 | 16.4025 | -0.00095344 | 12.0467 | 5.591 | -5.998e-09 | 3.0219e-12 | -1.683e-12 | -0.013927 | 1.237 | 5.0617 | -6.8897e-10 | 8.2593e-12 | 7.5825e-12 | 92.1472 | -161.0411 | 53.4641 | 0 | 18.9924 | -126.5617 |  | 1.1848 | 0.6267 | 0.45954 | 1.3595 | 0 | 0 | -1.7692 | -155.1784 | 95.6197 | -3.6018 | 0 | 0
Line_2_3-2ph | 0.00062638 | 0.00062638 | 0.00062638 | 0 | 0 | 0 | 0.0072328 | 0.0072328 | 0.0072328 | 0 | 0 | 0 | -0.0025317 | -0.00074097 | 0.0032754 | -1.9727e-09 | 1.9243e-09 | 1.7425e-09 | -0.0081873 | 0.0044718 | -0.00056538 | 8.2671e-11 | -2.7986e-09 | -2.0219e-09 | 105.4134 | 105.4134 | 105.4134 | 0 | 0 | 0 |  | 1.1848 | 0.6267 | 0.45954 | 1.185 | 0.62664 | 0.45931 | -1.7692 | -155.1784 | 95.6197 | -1.7794 | -155.1541 | 95.6019
Line_3_3-1ph | 0.00062638 | 0.00062638 | 0.00062638 | 0 | 0 | 0 | 0.0072328 | 0.0072328 | 0.0072328 | 0 | 0 | 0 | -0.0025317 | -0.00074097 | 0.0032754 | -1.9727e-09 | 1.9243e-09 | 1.7425e-09 | -0.0081873 | 0.0044718 | -0.00056538 | 8.2671e-11 | -2.7986e-09 | -2.0219e-09 | 105.4134 | 105.4134 | 105.4134 | 0 | 0 | 0 |  | 1.1848 | 0.6267 | 0.45954 | 1.185 | 0.62664 | 0.45931 | -1.7692 | -155.1784 | 95.6197 | -1.7794 | -155.1541 | 95.6019

## LLG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0_3ph | 0.0019641 | 0.86636 | 0.77622 | 0.0014801 | 0.86631 | 0.77591 | 0.022679 | 10.0038 | 8.9631 | 0.01709 | 10.0032 | 8.9595 | -0.0050605 | 7.9642 | 5.128 | 0.0029769 | -7.1537 | -4.8192 | -0.024446 | 3.9473 | 5.6165 | 0.019507 | -3.9192 | -4.7287 | 101.6996 | -161.0966 | 63.1526 | -82.6118 | 18.9363 | -116.8763 |  | 1.1007 | 0.88853 | 0.84852 | 1.1546 | 0.81543 | 0.75358 | 0.0040646 | -134.7323 | 110.7556 | -1.2883 | -132.3472 | 107.581
Line_1_3-2ph | 0.00066879 | 0.86639 | 0.77529 | 0 | 0.8666 | 0.77469 | 0.0077226 | 10.0042 | 8.9522 | 0 | 10.0067 | 8.9453 | -0.00021196 | 7.1581 | 4.812 | -3.6404e-09 | -3.755 | -3.0007 | -0.0089142 | 3.9128 | 4.7282 | -6.0415e-10 | -3.755 | -3.0007 | 90.0738 | -161.0096 | 63.0845 | 0 | 19.0322 | -116.9379 |  | 1.1546 | 0.81543 | 0.75358 | 1.2677 | 0.53068 | 0.4744 | -1.2883 | -132.3472 | 107.581 | -2.8049 | -115.9678 | 108.0621
Line_2_3-2ph | 0.00041058 | 0.00041058 | 0.00041058 | 0 | 0 | 0 | 0.0047409 | 0.0047409 | 0.0047409 | 0 | 0 | 0 | -0.0013825 | -0.0021792 | 0.0035629 | -1.2611e-09 | 2.0287e-09 | 1.8126e-09 | -0.0052966 | 0.0031931 | 0.0002642 | -3.4723e-12 | -1.0777e-09 | -1.8421e-09 | 103.34 | 103.34 | 103.34 | 0 | 0 | 0 |  | 1.1546 | 0.81543 | 0.75358 | 1.1547 | 0.81547 | 0.75341 | -1.2883 | -132.3472 | 107.581 | -1.2954 | -132.335 | 107.5769
Line_3_3-1ph | 0.00041058 | 0.00041058 | 0.00041058 | 0 | 0 | 0 | 0.0047409 | 0.0047409 | 0.0047409 | 0 | 0 | 0 | -0.0013825 | -0.0021792 | 0.0035629 | -1.2611e-09 | 2.0287e-09 | 1.8126e-09 | -0.0052966 | 0.0031931 | 0.0002642 | -3.4723e-12 | -1.0777e-09 | -1.8421e-09 | 103.34 | 103.34 | 103.34 | 0 | 0 | 0 |  | 1.1546 | 0.81543 | 0.75358 | 1.1547 | 0.81547 | 0.75341 | -1.2883 | -132.3472 | 107.581 | -1.2954 | -132.335 | 107.5769

## LLG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0_3ph | 0.0019641 | 0.86636 | 0.77622 | 0.0014801 | 0.86631 | 0.77591 | 0.022679 | 10.0038 | 8.9631 | 0.01709 | 10.0032 | 8.9595 | -0.0050605 | 7.9642 | 5.128 | 0.0029769 | -7.1537 | -4.8192 | -0.024446 | 3.9473 | 5.6165 | 0.019507 | -3.9192 | -4.7287 | 101.6996 | -161.0966 | 63.1526 | -82.6118 | 18.9363 | -116.8763 |  | 1.1007 | 0.88853 | 0.84852 | 1.1546 | 0.81543 | 0.75358 | 0.0040646 | -134.7323 | 110.7556 | -1.2883 | -132.3472 | 107.581
Line_1_3-2ph | 0.00066879 | 0.86639 | 0.77529 | 0 | 0.8666 | 0.77469 | 0.0077226 | 10.0042 | 8.9522 | 0 | 10.0067 | 8.9453 | -0.00021196 | 7.1581 | 4.812 | -3.6404e-09 | -3.755 | -3.0007 | -0.0089142 | 3.9128 | 4.7282 | -6.0415e-10 | -3.755 | -3.0007 | 90.0738 | -161.0096 | 63.0845 | 0 | 19.0322 | -116.9379 |  | 1.1546 | 0.81543 | 0.75358 | 1.2677 | 0.53068 | 0.4744 | -1.2883 | -132.3472 | 107.581 | -2.8049 | -115.9678 | 108.0621
Line_2_3-2ph | 0.00041058 | 0.00041058 | 0.00041058 | 0 | 0 | 0 | 0.0047409 | 0.0047409 | 0.0047409 | 0 | 0 | 0 | -0.0013825 | -0.0021792 | 0.0035629 | -1.2611e-09 | 2.0287e-09 | 1.8126e-09 | -0.0052966 | 0.0031931 | 0.0002642 | -3.4695e-12 | -1.0777e-09 | -1.8421e-09 | 103.34 | 103.34 | 103.34 | 0 | 0 | 0 |  | 1.1546 | 0.81543 | 0.75358 | 1.1547 | 0.81547 | 0.75341 | -1.2883 | -132.3472 | 107.581 | -1.2954 | -132.335 | 107.5769
Line_3_3-1ph | 0.00041058 | 0.00041058 | 0.00041058 | 0 | 0 | 0 | 0.0047409 | 0.0047409 | 0.0047409 | 0 | 0 | 0 | -0.0013825 | -0.0021792 | 0.0035629 | -1.2611e-09 | 2.0287e-09 | 1.8126e-09 | -0.0052966 | 0.0031931 | 0.0002642 | -3.4695e-12 | -1.0777e-09 | -1.8421e-09 | 103.34 | 103.34 | 103.34 | 0 | 0 | 0 |  | 1.1546 | 0.81543 | 0.75358 | 1.1547 | 0.81547 | 0.75341 | -1.2883 | -132.3472 | 107.581 | -1.2954 | -132.335 | 107.5769

## LLG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0_3ph | 0.002391 | 1.0762 | 0.9351 | 0.0018801 | 1.0762 | 0.93479 | 0.027609 | 12.4266 | 10.7976 | 0.021709 | 12.4273 | 10.794 | -0.006381 | 10.7233 | 5.8127 | 0.0042124 | -8.8405 | -5.0757 | -0.02689 | -0.59069 | 4.4561 | 0.023353 | 0.33771 | -2.9182 | 103.3571 | -144.5919 | 65.3534 | -81.2349 | 35.4366 | -114.6733 |  | 1.001 | 0.86423 | 0.67832 | 1.0931 | 0.7119 | 0.54241 | 0.0078851 | -147.7448 | 102.8282 | -1.4601 | -146.751 | 95.2225
Line_1_3-2ph | 0.00091004 | 1.0766 | 0.93403 | 0 | 1.0771 | 0.93322 | 0.010508 | 12.4312 | 10.7853 | 0 | 12.437 | 10.7759 | -0.00066411 | 8.843 | 5.0696 | -5.5333e-09 | -1.7778e-11 | -1.5979e-11 | -0.011467 | -0.34539 | 2.9192 | -4.8634e-10 | 4.8172e-12 | -3.9399e-12 | 91.8545 | -144.5143 | 65.288 | 0 | 35.526 | -114.7369 |  | 1.0931 | 0.7119 | 0.54241 | 1.2731 | 0 | 0 | -1.4601 | -146.751 | 95.2225 | -2.9861 | 0 | 0
Line_2_3-2ph | 0.00049138 | 0.00049138 | 0.00049138 | 0 | 0 | 0 | 0.0056739 | 0.0056739 | 0.0056739 | 0 | 0 | 0 | -0.0017742 | -0.001254 | 0.0030314 | -1.6427e-09 | 1.5224e-09 | 1.3747e-09 | -0.0059428 | 0.0038397 | -0.00053124 | 5.8747e-11 | -2.1582e-09 | -2.1217e-09 | 105.1623 | 105.1623 | 105.1623 | 0 | 0 | 0 |  | 1.0931 | 0.7119 | 0.54241 | 1.0933 | 0.71194 | 0.54205 | -1.4601 | -146.751 | 95.2225 | -1.478 | -146.72 | 95.2073
Line_3_3-1ph | 0.00049138 | 0.00049138 | 0.00049138 | 0 | 0 | 0 | 0.0056739 | 0.0056739 | 0.0056739 | 0 | 0 | 0 | -0.0017742 | -0.001254 | 0.0030314 | -1.6427e-09 | 1.5224e-09 | 1.3747e-09 | -0.0059428 | 0.0038397 | -0.00053124 | 5.8747e-11 | -2.1582e-09 | -2.1217e-09 | 105.1623 | 105.1623 | 105.1623 | 0 | 0 | 0 |  | 1.0931 | 0.7119 | 0.54241 | 1.0933 | 0.71194 | 0.54205 | -1.4601 | -146.751 | 95.2225 | -1.478 | -146.72 | 95.2073

## LLG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0_3ph | 0.002391 | 1.0762 | 0.9351 | 0.0018801 | 1.0762 | 0.93479 | 0.027609 | 12.4266 | 10.7976 | 0.021709 | 12.4273 | 10.794 | -0.006381 | 10.7233 | 5.8127 | 0.0042124 | -8.8405 | -5.0757 | -0.02689 | -0.59069 | 4.4561 | 0.023353 | 0.33771 | -2.9182 | 103.3571 | -144.5919 | 65.3534 | -81.2349 | 35.4366 | -114.6733 |  | 1.001 | 0.86423 | 0.67832 | 1.0931 | 0.7119 | 0.54241 | 0.0078851 | -147.7448 | 102.8282 | -1.4601 | -146.751 | 95.2225
Line_1_3-2ph | 0.00091004 | 1.0766 | 0.93403 | 0 | 1.0771 | 0.93322 | 0.010508 | 12.4312 | 10.7853 | 0 | 12.437 | 10.7759 | -0.00066411 | 8.843 | 5.0696 | -5.5333e-09 | -1.7778e-11 | -1.5979e-11 | -0.011467 | -0.34539 | 2.9192 | -4.8634e-10 | 4.8172e-12 | -3.9399e-12 | 91.8545 | -144.5143 | 65.288 | 0 | 35.526 | -114.7369 |  | 1.0931 | 0.7119 | 0.54241 | 1.2731 | 0 | 0 | -1.4601 | -146.751 | 95.2225 | -2.9861 | 0 | 0
Line_2_3-2ph | 0.00049138 | 0.00049138 | 0.00049138 | 0 | 0 | 0 | 0.0056739 | 0.0056739 | 0.0056739 | 0 | 0 | 0 | -0.0017742 | -0.001254 | 0.0030314 | -1.6427e-09 | 1.5224e-09 | 1.3747e-09 | -0.0059428 | 0.0038397 | -0.00053124 | 5.8747e-11 | -2.1582e-09 | -2.1217e-09 | 105.1623 | 105.1623 | 105.1623 | 0 | 0 | 0 |  | 1.0931 | 0.7119 | 0.54241 | 1.0933 | 0.71194 | 0.54205 | -1.4601 | -146.751 | 95.2225 | -1.478 | -146.72 | 95.2073
Line_3_3-1ph | 0.00049138 | 0.00049138 | 0.00049138 | 0 | 0 | 0 | 0.0056739 | 0.0056739 | 0.0056739 | 0 | 0 | 0 | -0.0017742 | -0.001254 | 0.0030314 | -1.6427e-09 | 1.5224e-09 | 1.3747e-09 | -0.0059428 | 0.0038397 | -0.00053124 | 5.8747e-11 | -2.1582e-09 | -2.1217e-09 | 105.1623 | 105.1623 | 105.1623 | 0 | 0 | 0 |  | 1.0931 | 0.7119 | 0.54241 | 1.0933 | 0.71194 | 0.54205 | -1.4601 | -146.751 | 95.2225 | -1.478 | -146.72 | 95.2073

## LLG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0_3ph | 0.0018231 | 0.65214 | 0.56829 | 0.0014335 | 0.65217 | 0.568 | 0.021051 | 7.5302 | 6.562 | 0.016553 | 7.5307 | 6.5587 | -0.0030587 | 6.2899 | 3.893 | 0.0016107 | -5.5257 | -3.5667 | -0.020845 | 1.6835 | 3.5535 | 0.01762 | -1.8597 | -2.8847 | 98.35 | -150.3013 | 68.1518 | -86.242 | 29.7347 | -111.8782 |  | 1.0008 | 0.86469 | 0.80325 | 1.0689 | 0.7742 | 0.69942 | 0.0020812 | -135.3173 | 110.5413 | -1.4649 | -131.6642 | 107.0875
Line_1_3-2ph | 0.0006939 | 0.65243 | 0.56737 | 0 | 0.6528 | 0.56671 | 0.0080125 | 7.5336 | 6.5514 | 0 | 7.5379 | 6.5438 | 0.00025226 | 5.5298 | 3.5607 | -3.9464e-09 | -2.1308 | -1.6058 | -0.008561 | 1.8545 | 2.884 | -6.7862e-10 | -2.1308 | -1.6058 | 86.8473 | -150.2033 | 68.0816 | 0 | 29.8478 | -111.9409 |  | 1.0689 | 0.7742 | 0.69942 | 1.2036 | 0.39976 | 0.34704 | -1.4649 | -131.6642 | 107.0875 | -3.2593 | -105.1522 | 113.0591
Line_2_3-2ph | 0.00037467 | 0.00037467 | 0.00037467 | 0 | 0 | 0 | 0.0043263 | 0.0043263 | 0.0043263 | 0 | 0 | 0 | -0.00093146 | -0.0020704 | 0.0030038 | -1.224e-09 | 1.5593e-09 | 1.4682e-09 | -0.0045297 | 0.0026329 | 0.00036522 | -6.3237e-11 | -8.347e-10 | -1.5965e-09 | 100.1551 | 100.1551 | 100.1551 | 0 | 0 | 0 |  | 1.0689 | 0.7742 | 0.69942 | 1.069 | 0.77433 | 0.69912 | -1.4649 | -131.6642 | 107.0875 | -1.4794 | -131.6446 | 107.0854
Line_3_3-1ph | 0.00037467 | 0.00037467 | 0.00037467 | 0 | 0 | 0 | 0.0043263 | 0.0043263 | 0.0043263 | 0 | 0 | 0 | -0.00093146 | -0.0020704 | 0.0030038 | -1.224e-09 | 1.5593e-09 | 1.4682e-09 | -0.0045297 | 0.0026329 | 0.00036522 | -6.3237e-11 | -8.347e-10 | -1.5965e-09 | 100.1551 | 100.1551 | 100.1551 | 0 | 0 | 0 |  | 1.0689 | 0.7742 | 0.69942 | 1.069 | 0.77433 | 0.69912 | -1.4649 | -131.6642 | 107.0875 | -1.4794 | -131.6446 | 107.0854

## LLG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0_3ph | 0.0018231 | 0.65214 | 0.56829 | 0.0014335 | 0.65217 | 0.568 | 0.021051 | 7.5302 | 6.562 | 0.016553 | 7.5307 | 6.5587 | -0.0030587 | 6.2899 | 3.893 | 0.0016107 | -5.5257 | -3.5667 | -0.020845 | 1.6835 | 3.5535 | 0.01762 | -1.8597 | -2.8847 | 98.35 | -150.3013 | 68.1518 | -86.242 | 29.7347 | -111.8782 |  | 1.0008 | 0.86469 | 0.80325 | 1.0689 | 0.7742 | 0.69942 | 0.0020812 | -135.3173 | 110.5413 | -1.4649 | -131.6642 | 107.0875
Line_1_3-2ph | 0.0006939 | 0.65243 | 0.56737 | 0 | 0.6528 | 0.56671 | 0.0080125 | 7.5336 | 6.5514 | 0 | 7.5379 | 6.5438 | 0.00025226 | 5.5298 | 3.5607 | -3.9464e-09 | -2.1308 | -1.6058 | -0.008561 | 1.8545 | 2.884 | -6.7862e-10 | -2.1308 | -1.6058 | 86.8473 | -150.2033 | 68.0816 | 0 | 29.8478 | -111.9409 |  | 1.0689 | 0.7742 | 0.69942 | 1.2036 | 0.39976 | 0.34704 | -1.4649 | -131.6642 | 107.0875 | -3.2593 | -105.1522 | 113.0591
Line_2_3-2ph | 0.00037467 | 0.00037467 | 0.00037467 | 0 | 0 | 0 | 0.0043263 | 0.0043263 | 0.0043263 | 0 | 0 | 0 | -0.00093146 | -0.0020704 | 0.0030038 | -1.224e-09 | 1.5593e-09 | 1.4682e-09 | -0.0045297 | 0.0026329 | 0.00036522 | -6.3237e-11 | -8.347e-10 | -1.5965e-09 | 100.1551 | 100.1551 | 100.1551 | 0 | 0 | 0 |  | 1.0689 | 0.7742 | 0.69942 | 1.069 | 0.77433 | 0.69912 | -1.4649 | -131.6642 | 107.0875 | -1.4794 | -131.6446 | 107.0854
Line_3_3-1ph | 0.00037467 | 0.00037467 | 0.00037467 | 0 | 0 | 0 | 0.0043263 | 0.0043263 | 0.0043263 | 0 | 0 | 0 | -0.00093146 | -0.0020704 | 0.0030038 | -1.224e-09 | 1.5593e-09 | 1.4682e-09 | -0.0045297 | 0.0026329 | 0.00036522 | -6.3237e-11 | -8.347e-10 | -1.5965e-09 | 100.1551 | 100.1551 | 100.1551 | 0 | 0 | 0 |  | 1.0689 | 0.7742 | 0.69942 | 1.069 | 0.77433 | 0.69912 | -1.4649 | -131.6642 | 107.0875 | -1.4794 | -131.6446 | 107.0854