## LLL_max_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.70184 | 0.70184 | -7.4193 | -7.4193
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.70184 | 0.70184 | -7.4193 | -7.4193
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.70184 | 0.70184 | -7.4193 | -7.4193
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.70184 | 0.70184 | -7.4193 | -7.4193
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.70184 | 0.70184 | -7.4193 | -7.4193
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.70184 | 0.70184 | -7.4193 | -7.4193
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.70184 | 0.70184 | -7.4193 | -7.4193
Line16_4_18 | 3.6243 | 3.6243 | 0 | 7.0007 | 2.511 | 2.511 | 0.39406 | -1e-07 | 0.78812 | -1e-07 | -70.8543 | 109.1457 | 0.35092 | 0 | -7.4193 | 0
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.70184 | 0.70184 | -7.4193 | -7.4193
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.70184 | 0.70184 | -7.4193 | -7.4193
Line2_1_4 | 3.6243 | 3.6243 | 0 | 0 | 2.511 | 2.511 | 0.78812 | -0.39406 | 1.5762 | -0.78812 | -70.8543 | 109.1457 | 0.70184 | 0.35092 | -7.4193 | -7.4193
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.70184 | 0.70184 | -7.4193 | -7.4193
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.70184 | 0.70184 | -7.4193 | -7.4193
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.70184 | 0.70184 | -7.4193 | -7.4193
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.70184 | 0.70184 | -7.4193 | -7.4193
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.70184 | 0.70184 | -7.4193 | -7.4193
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.70184 | 0.70184 | -7.4193 | -7.4193
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.70184 | 0.70184 | -7.4193 | -7.4193

## LLL_max_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72372 | 0.72372 | -7.6495 | -7.6495
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72372 | 0.72372 | -7.6495 | -7.6495
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72372 | 0.72372 | -7.6495 | -7.6495
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72372 | 0.72372 | -7.6495 | -7.6495
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72372 | 0.72372 | -7.6495 | -7.6495
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72372 | 0.72372 | -7.6495 | -7.6495
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72372 | 0.72372 | -7.6495 | -7.6495
Line16_4_18 | 3.7373 | 3.7373 | 0 | 7.2438 | 2.5893 | 2.5893 | 0.41902 | -1e-07 | 0.83803 | -1e-07 | -71.0844 | 108.9156 | 0.36186 | 0 | -7.6495 | 0
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72372 | 0.72372 | -7.6495 | -7.6495
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72372 | 0.72372 | -7.6495 | -7.6495
Line2_1_4 | 3.7373 | 3.7373 | 0 | 0 | 2.5893 | 2.5893 | 0.83803 | -0.41902 | 1.6761 | -0.83803 | -71.0844 | 108.9156 | 0.72372 | 0.36186 | -7.6495 | -7.6495
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72372 | 0.72372 | -7.6495 | -7.6495
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72372 | 0.72372 | -7.6495 | -7.6495
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72372 | 0.72372 | -7.6495 | -7.6495
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72372 | 0.72372 | -7.6495 | -7.6495
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72372 | 0.72372 | -7.6495 | -7.6495
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72372 | 0.72372 | -7.6495 | -7.6495
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72372 | 0.72372 | -7.6495 | -7.6495

## LLL_max_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.12051 | -0.12051
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.12051 | -0.12051
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.12051 | -0.12051
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.12051 | -0.12051
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.12051 | -0.12051
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.12051 | -0.12051
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.12051 | -0.12051
Line16_4_18 | 0.034003 | 0.034003 | 0 | 0.065681 | 0.023558 | 0.023558 | 0.017378 | -0.017343 | 0.017412 | -0.017343 | -45.2344 | 134.7656 | 1.0442 | 1.0411 | -0.17729 | -0.23442
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.12051 | -0.12051
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.12051 | -0.12051
Line2_1_4 | 0.034003 | 0.034003 | 0 | 0 | 0.023558 | 0.023558 | 0.017412 | -0.017378 | 0.017482 | -0.017412 | -45.2344 | 134.7656 | 1.0474 | 1.0442 | -0.12051 | -0.17729
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.12051 | -0.12051
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.12051 | -0.12051
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.12051 | -0.12051
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.12051 | -0.12051
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.12051 | -0.12051
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.12051 | -0.12051
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.12051 | -0.12051

## LLL_max_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12619 | -0.12619
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12619 | -0.12619
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12619 | -0.12619
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12619 | -0.12619
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12619 | -0.12619
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12619 | -0.12619
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12619 | -0.12619
Line16_4_18 | 0.035618 | 0.035618 | 0 | 0.069037 | 0.024677 | 0.024677 | 0.019068 | -0.01903 | 0.019106 | -0.01903 | -45.2401 | 134.7599 | 1.0938 | 1.0906 | -0.18297 | -0.2401
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12619 | -0.12619
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12619 | -0.12619
Line2_1_4 | 0.035618 | 0.035618 | 0 | 0 | 0.024677 | 0.024677 | 0.019106 | -0.019068 | 0.019182 | -0.019106 | -45.2401 | 134.7599 | 1.0971 | 1.0938 | -0.12619 | -0.18297
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12619 | -0.12619
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12619 | -0.12619
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12619 | -0.12619
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12619 | -0.12619
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12619 | -0.12619
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12619 | -0.12619
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12619 | -0.12619

## LLL_min_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.695 | 0.695 | -11.6026 | -11.6026
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.695 | 0.695 | -11.6026 | -11.6026
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.695 | 0.695 | -11.6026 | -11.6026
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.695 | 0.695 | -11.6026 | -11.6026
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.695 | 0.695 | -11.6026 | -11.6026
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.695 | 0.695 | -11.6026 | -11.6026
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.695 | 0.695 | -11.6026 | -11.6026
Line16_4_18 | 2.8946 | 2.8946 | 0 | 4.7808 | 2.0055 | 2.0055 | 0.48263 | -1e-07 | 0.50274 | -1e-07 | -57.7717 | 122.2283 | 0.3475 | 0 | -11.6026 | 0
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.695 | 0.695 | -11.6026 | -11.6026
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.695 | 0.695 | -11.6026 | -11.6026
Line2_1_4 | 2.8946 | 2.8946 | 0 | 0 | 2.0055 | 2.0055 | 0.96525 | -0.48263 | 1.0055 | -0.50274 | -57.7717 | 122.2283 | 0.695 | 0.3475 | -11.6026 | -11.6026
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.695 | 0.695 | -11.6026 | -11.6026
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.695 | 0.695 | -11.6026 | -11.6026
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.695 | 0.695 | -11.6026 | -11.6026
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.695 | 0.695 | -11.6026 | -11.6026
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.695 | 0.695 | -11.6026 | -11.6026
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.695 | 0.695 | -11.6026 | -11.6026
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.695 | 0.695 | -11.6026 | -11.6026

## LLL_min_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65842 | 0.65842 | -11.6026 | -11.6026
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65842 | 0.65842 | -11.6026 | -11.6026
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65842 | 0.65842 | -11.6026 | -11.6026
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65842 | 0.65842 | -11.6026 | -11.6026
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65842 | 0.65842 | -11.6026 | -11.6026
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65842 | 0.65842 | -11.6026 | -11.6026
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65842 | 0.65842 | -11.6026 | -11.6026
Line16_4_18 | 2.7423 | 2.7423 | 0 | 4.5292 | 1.8999 | 1.8999 | 0.43316 | -1e-07 | 0.45121 | -1e-07 | -57.7717 | 122.2283 | 0.32921 | 0 | -11.6026 | 0
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65842 | 0.65842 | -11.6026 | -11.6026
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65842 | 0.65842 | -11.6026 | -11.6026
Line2_1_4 | 2.7423 | 2.7423 | 0 | 0 | 1.8999 | 1.8999 | 0.86632 | -0.43316 | 0.90242 | -0.45121 | -57.7717 | 122.2283 | 0.65842 | 0.32921 | -11.6026 | -11.6026
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65842 | 0.65842 | -11.6026 | -11.6026
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65842 | 0.65842 | -11.6026 | -11.6026
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65842 | 0.65842 | -11.6026 | -11.6026
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65842 | 0.65842 | -11.6026 | -11.6026
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65842 | 0.65842 | -11.6026 | -11.6026
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65842 | 0.65842 | -11.6026 | -11.6026
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65842 | 0.65842 | -11.6026 | -11.6026

## LLL_min_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94754 | 0.94754 | -0.12527 | -0.12527
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94754 | 0.94754 | -0.12527 | -0.12527
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94754 | 0.94754 | -0.12527 | -0.12527
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94754 | 0.94754 | -0.12527 | -0.12527
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94754 | 0.94754 | -0.12527 | -0.12527
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94754 | 0.94754 | -0.12527 | -0.12527
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94754 | 0.94754 | -0.12527 | -0.12527
Line16_4_18 | 0.030706 | 0.030706 | 0 | 0.050714 | 0.021274 | 0.021274 | 0.014197 | -0.014143 | 0.014199 | -0.014143 | -45.1344 | 134.8656 | 0.94385 | 0.94017 | -0.1298 | -0.13436
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94754 | 0.94754 | -0.12527 | -0.12527
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94754 | 0.94754 | -0.12527 | -0.12527
Line2_1_4 | 0.030706 | 0.030706 | 0 | 0 | 0.021274 | 0.021274 | 0.014251 | -0.014197 | 0.014256 | -0.014199 | -45.1344 | 134.8656 | 0.94754 | 0.94385 | -0.12527 | -0.1298
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94754 | 0.94754 | -0.12527 | -0.12527
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94754 | 0.94754 | -0.12527 | -0.12527
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94754 | 0.94754 | -0.12527 | -0.12527
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94754 | 0.94754 | -0.12527 | -0.12527
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94754 | 0.94754 | -0.12527 | -0.12527
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94754 | 0.94754 | -0.12527 | -0.12527
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94754 | 0.94754 | -0.12527 | -0.12527

## LLL_min_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89767 | 0.89767 | -0.12527 | -0.12527
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89767 | 0.89767 | -0.12527 | -0.12527
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89767 | 0.89767 | -0.12527 | -0.12527
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89767 | 0.89767 | -0.12527 | -0.12527
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89767 | 0.89767 | -0.12527 | -0.12527
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89767 | 0.89767 | -0.12527 | -0.12527
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89767 | 0.89767 | -0.12527 | -0.12527
Line16_4_18 | 0.02909 | 0.02909 | 0 | 0.048045 | 0.020154 | 0.020154 | 0.012742 | -0.012693 | 0.012744 | -0.012693 | -45.1344 | 134.8656 | 0.89418 | 0.89069 | -0.1298 | -0.13436
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89767 | 0.89767 | -0.12527 | -0.12527
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89767 | 0.89767 | -0.12527 | -0.12527
Line2_1_4 | 0.02909 | 0.02909 | 0 | 0 | 0.020154 | 0.020154 | 0.012791 | -0.012742 | 0.012795 | -0.012744 | -45.1344 | 134.8656 | 0.89767 | 0.89418 | -0.12527 | -0.1298
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89767 | 0.89767 | -0.12527 | -0.12527
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89767 | 0.89767 | -0.12527 | -0.12527
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89767 | 0.89767 | -0.12527 | -0.12527
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89767 | 0.89767 | -0.12527 | -0.12527
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89767 | 0.89767 | -0.12527 | -0.12527
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89767 | 0.89767 | -0.12527 | -0.12527
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89767 | 0.89767 | -0.12527 | -0.12527

## LL_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.6629e-16 | -3.0235e-09 | -4.8365e-09 | -4.2744e-16 | 3.0235e-09 | 4.8365e-09 | 5.8287e-17 | 5.1114e-09 | -1.9712e-09 | -3.8858e-17 | -5.1114e-09 | 1.9712e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.85292 | 0.7501 | 1.05 | 0.85292 | 0.7501 | -1.6584e-11 | -135.0364 | 126.5322 | -1.6589e-11 | -135.0364 | 126.5322
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4401e-16 | -3.0235e-09 | -4.8365e-09 | -5.4401e-16 | 3.0235e-09 | 4.8365e-09 | 5.8287e-17 | 5.1114e-09 | -1.9712e-09 | -5.8287e-17 | -5.1114e-09 | 1.9712e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.85292 | 0.7501 | 1.05 | 0.85292 | 0.7501 | -1.6605e-11 | -135.0364 | 126.5322 | -1.6615e-11 | -135.0364 | 126.5322
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2744e-16 | -2.5196e-09 | -4.0305e-09 | -5.0515e-16 | 2.5196e-09 | 4.0305e-09 | -1.9429e-17 | 4.2595e-09 | -1.6426e-09 | 1.4655e-28 | -4.2595e-09 | 1.6426e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.85292 | 0.7501 | 1.05 | 0.85292 | 0.7501 | -1.6615e-11 | -135.0364 | 126.5322 | -1.6622e-11 | -135.0364 | 126.5322
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3315e-16 | -1.5118e-09 | -2.4183e-09 | -2.3315e-16 | 1.5118e-09 | 2.4183e-09 | 3.8858e-17 | 2.5557e-09 | -9.8558e-10 | 6.7651e-29 | -2.5557e-09 | 9.8558e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.85292 | 0.7501 | 1.05 | 0.85292 | 0.7501 | -1.6622e-11 | -135.0364 | 126.5322 | -1.6625e-11 | -135.0364 | 126.5322
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.7716e-17 | -5.0392e-10 | -8.0609e-10 | 3.8858e-17 | 5.0392e-10 | 8.0609e-10 | 3.8858e-17 | 8.5191e-10 | -3.2853e-10 | 3.8858e-17 | -8.5191e-10 | 3.2853e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.85292 | 0.7501 | 1.05 | 0.85292 | 0.7501 | -1.6622e-11 | -135.0364 | 126.5322 | -1.6623e-11 | -135.0364 | 126.5322
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1657e-16 | -1.0078e-09 | -1.6122e-09 | -7.7716e-17 | 1.0078e-09 | 1.6122e-09 | 3.8858e-17 | 1.7038e-09 | -6.5706e-10 | -7.7716e-17 | -1.7038e-09 | 6.5706e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.85292 | 0.7501 | 1.05 | 0.85292 | 0.7501 | -1.6625e-11 | -135.0364 | 126.5322 | -1.6627e-11 | -135.0364 | 126.5322
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.8858e-17 | -5.0392e-10 | -8.0609e-10 | 3.8858e-17 | 5.0392e-10 | 8.0609e-10 | 1.9429e-17 | 8.5191e-10 | -3.2853e-10 | -1.1277e-29 | -8.5191e-10 | 3.2853e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.85292 | 0.7501 | 1.05 | 0.85292 | 0.7501 | -1.6627e-11 | -135.0364 | 126.5322 | -1.6628e-11 | -135.0364 | 126.5322
Line16_4_18 | 0 | 3.1387 | 3.1387 | 0 | 3.1387 | 3.1387 | 0 | 0.72485 | 0.72485 | 0 | 0.72485 | 0.72485 | 7.7716e-17 | 0.45801 | -0.26098 | 7.7716e-17 | -0.3595 | 0.3595 | -7.7716e-17 | 0.072221 | 0.32184 | 3.8858e-17 | 0.12481 | -0.12481 | 0 | -160.8543 | 19.1457 | 0 | 19.1457 | -160.8543 | 1.05 | 0.63968 | 0.57164 | 1.05 | 0.525 | 0.525 | -1.6589e-11 | -151.8935 | 148.1848 | -1.6592e-11 | -180 | -180
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.8858e-17 | -5.0392e-10 | -8.0609e-10 | 3.8858e-17 | 5.0392e-10 | 8.0609e-10 | 1.1248e-29 | 8.5191e-10 | -3.2853e-10 | -1.9429e-17 | -8.5191e-10 | 3.2853e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.85292 | 0.7501 | 1.05 | 0.85292 | 0.7501 | -1.6586e-11 | -135.0364 | 126.5322 | -1.6586e-11 | -135.0364 | 126.5322
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.383e-16 | -4.0313e-09 | -6.4487e-09 | -6.9944e-16 | 4.0313e-09 | 6.4487e-09 | 1.36e-16 | 6.8153e-09 | -2.6282e-09 | -1.36e-16 | -6.8153e-09 | 2.6282e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.85292 | 0.7501 | 1.05 | 0.85292 | 0.7501 | -1.6584e-11 | -135.0364 | 126.5322 | -1.6595e-11 | -135.0364 | 126.5322
Line2_1_4 | 0 | 3.1387 | 3.1387 | 0 | 3.1387 | 3.1387 | 0 | 0.72485 | 0.72485 | 0 | 0.72485 | 0.72485 | 3.1086e-16 | 0.55653 | -0.16247 | -2.3315e-16 | -0.45801 | 0.26098 | -7.7716e-17 | 0.26925 | 0.51887 | 7.7716e-17 | -0.072221 | -0.32184 | 0 | -160.8543 | 19.1457 | 0 | 19.1457 | -160.8543 | 1.05 | 0.85292 | 0.7501 | 1.05 | 0.63968 | 0.57164 | -1.6584e-11 | -135.0364 | 126.5322 | -1.6589e-11 | -151.8935 | 148.1848
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1657e-16 | -1.0078e-09 | -1.6122e-09 | -7.7716e-17 | 1.0078e-09 | 1.6122e-09 | 1.9429e-17 | 1.7038e-09 | -6.5706e-10 | -1.9429e-17 | -1.7038e-09 | 6.5706e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.85292 | 0.7501 | 1.05 | 0.85292 | 0.7501 | -1.6584e-11 | -135.0364 | 126.5322 | -1.6586e-11 | -135.0364 | 126.5322
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4972e-16 | -2.5196e-09 | -4.0305e-09 | -3.8858e-16 | 2.5196e-09 | 4.0305e-09 | -5.8287e-17 | 4.2595e-09 | -1.6426e-09 | 5.8287e-17 | -4.2595e-09 | 1.6426e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.85292 | 0.7501 | 1.05 | 0.85292 | 0.7501 | -1.6589e-11 | -135.0364 | 126.5322 | -1.6595e-11 | -135.0364 | 126.5322
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3315e-16 | -2.0157e-09 | -3.2244e-09 | -1.9429e-16 | 2.0157e-09 | 3.2244e-09 | -7.7716e-17 | 3.4076e-09 | -1.3141e-09 | 7.7716e-17 | -3.4076e-09 | 1.3141e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.85292 | 0.7501 | 1.05 | 0.85292 | 0.7501 | -1.6595e-11 | -135.0364 | 126.5322 | -1.6599e-11 | -135.0364 | 126.5322
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5543e-16 | -1.5118e-09 | -2.4183e-09 | -1.9429e-16 | 1.5118e-09 | 2.4183e-09 | -3.8858e-17 | 2.5557e-09 | -9.8558e-10 | 1.9429e-17 | -2.5557e-09 | 9.8558e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.85292 | 0.7501 | 1.05 | 0.85292 | 0.7501 | -1.6599e-11 | -135.0364 | 126.5322 | -1.6602e-11 | -135.0364 | 126.5322
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.126e-29 | -5.0392e-10 | -8.0609e-10 | -1.126e-29 | 5.0392e-10 | 8.0609e-10 | 3.8858e-17 | 8.5191e-10 | -3.2853e-10 | -3.8858e-17 | -8.5191e-10 | 3.2853e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.85292 | 0.7501 | 1.05 | 0.85292 | 0.7501 | -1.6602e-11 | -135.0364 | 126.5322 | -1.6603e-11 | -135.0364 | 126.5322
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.126e-29 | -5.0392e-10 | -8.0609e-10 | -1.6891e-29 | 5.0392e-10 | 8.0609e-10 | 3.8858e-17 | 8.5191e-10 | -3.2853e-10 | -5.8287e-17 | -8.5191e-10 | 3.2853e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.85292 | 0.7501 | 1.05 | 0.85292 | 0.7501 | -1.6602e-11 | -135.0364 | 126.5322 | -1.6603e-11 | -135.0364 | 126.5322
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.9944e-16 | -3.5274e-09 | -5.6426e-09 | -6.6058e-16 | 3.5274e-09 | 5.6426e-09 | 3.8858e-17 | 5.9633e-09 | -2.2997e-09 | -5.8287e-17 | -5.9633e-09 | 2.2997e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.85292 | 0.7501 | 1.05 | 0.85292 | 0.7501 | -1.6595e-11 | -135.0364 | 126.5322 | -1.6605e-11 | -135.0364 | 126.5322

## LL_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.5133e-16 | -3.3669e-09 | -5.3859e-09 | -6.5133e-16 | 3.3669e-09 | 5.3859e-09 | 4.0708e-17 | 5.759e-09 | -2.262e-09 | -1.0289e-28 | -5.759e-09 | 2.262e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.88719 | 0.77689 | 1.1 | 0.88719 | 0.77689 | 9.0604e-12 | -135.5593 | 126.9102 | 9.0507e-12 | -135.5593 | 126.9102
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.885e-16 | -3.3669e-09 | -5.3859e-09 | -4.4779e-16 | 3.3669e-09 | 5.3859e-09 | 8.1416e-17 | 5.759e-09 | -2.262e-09 | -8.1416e-17 | -5.759e-09 | 2.262e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.88719 | 0.77689 | 1.1 | 0.88719 | 0.77689 | 9.0367e-12 | -135.5593 | 126.9102 | 9.0271e-12 | -135.5593 | 126.9102
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2921e-16 | -2.8058e-09 | -4.4883e-09 | -5.2921e-16 | 2.8058e-09 | 4.4883e-09 | -4.0708e-17 | 4.7992e-09 | -1.885e-09 | 8.1416e-17 | -4.7992e-09 | 1.885e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.88719 | 0.77689 | 1.1 | 0.88719 | 0.77689 | 9.0271e-12 | -135.5593 | 126.9102 | 9.0197e-12 | -135.5593 | 126.9102
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8496e-16 | -1.6835e-09 | -2.693e-09 | -2.8496e-16 | 1.6835e-09 | 2.693e-09 | 4.4859e-29 | 2.8795e-09 | -1.131e-09 | -8.1416e-17 | -2.8795e-09 | 1.131e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.88719 | 0.77689 | 1.1 | 0.88719 | 0.77689 | 9.0197e-12 | -135.5593 | 126.9102 | 9.0161e-12 | -135.5593 | 126.9102
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.4084e-30 | -5.6115e-10 | -8.9765e-10 | 0 | 5.6115e-10 | 8.9765e-10 | -4.0708e-17 | 9.5983e-10 | -3.77e-10 | 0 | -9.5983e-10 | 3.77e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.88719 | 0.77689 | 1.1 | 0.88719 | 0.77689 | 9.0197e-12 | -135.5593 | 126.9102 | 9.0186e-12 | -135.5593 | 126.9102
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.1416e-17 | -1.1223e-09 | -1.7953e-09 | -8.1416e-17 | 1.1223e-09 | 1.7953e-09 | 8.1416e-17 | 1.9197e-09 | -7.54e-10 | -8.1416e-17 | -1.9197e-09 | 7.54e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.88719 | 0.77689 | 1.1 | 0.88719 | 0.77689 | 9.0161e-12 | -135.5593 | 126.9102 | 9.0142e-12 | -135.5593 | 126.9102
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.0708e-17 | -5.6115e-10 | -8.9765e-10 | 4.0708e-17 | 5.6115e-10 | 8.9765e-10 | -4.0708e-17 | 9.5983e-10 | -3.77e-10 | 8.1416e-17 | -9.5983e-10 | 3.77e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.88719 | 0.77689 | 1.1 | 0.88719 | 0.77689 | 9.0142e-12 | -135.5593 | 126.9102 | 9.0137e-12 | -135.5593 | 126.9102
Line16_4_18 | 0 | 3.2366 | 3.2366 | 0 | 3.2366 | 3.2366 | 0 | 0.74746 | 0.74746 | 0 | 0.74746 | 0.74746 | -1.6283e-16 | 0.49365 | -0.28415 | 1.6283e-16 | -0.3889 | 0.3889 | -8.1416e-17 | 0.07624 | 0.34278 | 8.1416e-17 | 0.13327 | -0.13327 | 0 | -161.0844 | 18.9156 | 0 | 18.9156 | -161.0844 | 1.1 | 0.66828 | 0.59567 | 1.1 | 0.55 | 0.55 | 9.0547e-12 | -152.305 | 148.5727 | 9.0521e-12 | 180 | 180
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.0708e-17 | -5.6115e-10 | -8.9765e-10 | 6.4356e-30 | 5.6115e-10 | 8.9765e-10 | -4.0708e-17 | 9.5983e-10 | -3.77e-10 | -4.0708e-17 | -9.5983e-10 | 3.77e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.88719 | 0.77689 | 1.1 | 0.88719 | 0.77689 | 9.0585e-12 | -135.5593 | 126.9102 | 9.058e-12 | -135.5593 | 126.9102
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.9558e-16 | -4.4892e-09 | -7.1812e-09 | -8.9558e-16 | 4.4892e-09 | 7.1812e-09 | 1.2212e-16 | 7.6787e-09 | -3.016e-09 | -1.2212e-16 | -7.6787e-09 | 3.016e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.88719 | 0.77689 | 1.1 | 0.88719 | 0.77689 | 9.0604e-12 | -135.5593 | 126.9102 | 9.0475e-12 | -135.5593 | 126.9102
Line2_1_4 | 0 | 3.2366 | 3.2366 | 0 | 3.2366 | 3.2366 | 0 | 0.74746 | 0.74746 | 0 | 0.74746 | 0.74746 | 4.0708e-16 | 0.59841 | -0.17939 | -4.0708e-16 | -0.49365 | 0.28415 | -4.0708e-17 | 0.28575 | 0.55229 | 4.0708e-17 | -0.07624 | -0.34278 | 0 | -161.0844 | 18.9156 | 0 | 18.9156 | -161.0844 | 1.1 | 0.88719 | 0.77689 | 1.1 | 0.66828 | 0.59567 | 9.0604e-12 | -135.5593 | 126.9102 | 9.0547e-12 | -152.305 | 148.5727
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.1416e-17 | -1.1223e-09 | -1.7953e-09 | -1.2212e-16 | 1.1223e-09 | 1.7953e-09 | 4.0708e-17 | 1.9197e-09 | -7.5399e-10 | -1.9308e-29 | -1.9197e-09 | 7.5399e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.88719 | 0.77689 | 1.1 | 0.88719 | 0.77689 | 9.0604e-12 | -135.5593 | 126.9102 | 9.0585e-12 | -135.5593 | 126.9102
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2921e-16 | -2.8058e-09 | -4.4883e-09 | -4.885e-16 | 2.8058e-09 | 4.4883e-09 | 4.0708e-17 | 4.7992e-09 | -1.885e-09 | -4.0708e-17 | -4.7992e-09 | 1.885e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.88719 | 0.77689 | 1.1 | 0.88719 | 0.77689 | 9.0507e-12 | -135.5593 | 126.9102 | 9.0434e-12 | -135.5593 | 126.9102
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0708e-16 | -2.2446e-09 | -3.5906e-09 | -3.6637e-16 | 2.2446e-09 | 3.5906e-09 | -4.0708e-17 | 3.8393e-09 | -1.508e-09 | 4.0708e-17 | -3.8393e-09 | 1.508e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.88719 | 0.77689 | 1.1 | 0.88719 | 0.77689 | 9.0434e-12 | -135.5593 | 126.9102 | 9.0372e-12 | -135.5593 | 126.9102
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0354e-16 | -1.6835e-09 | -2.693e-09 | -1.6283e-16 | 1.6835e-09 | 2.693e-09 | -8.1416e-17 | 2.8795e-09 | -1.131e-09 | 4.0708e-17 | -2.8795e-09 | 1.131e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.88719 | 0.77689 | 1.1 | 0.88719 | 0.77689 | 9.0372e-12 | -135.5593 | 126.9102 | 9.0336e-12 | -135.5593 | 126.9102
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.6115e-10 | -8.9765e-10 | -6.4176e-30 | 5.6115e-10 | 8.9765e-10 | 0 | 9.5983e-10 | -3.77e-10 | 4.0708e-17 | -9.5983e-10 | 3.77e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.88719 | 0.77689 | 1.1 | 0.88719 | 0.77689 | 9.0336e-12 | -135.5593 | 126.9102 | 9.0326e-12 | -135.5593 | 126.9102
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.0708e-17 | -5.6115e-10 | -8.9765e-10 | 4.0708e-17 | 5.6115e-10 | 8.9765e-10 | -4.0708e-17 | 9.5983e-10 | -3.77e-10 | 8.1416e-17 | -9.5983e-10 | 3.77e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.88719 | 0.77689 | 1.1 | 0.88719 | 0.77689 | 9.0336e-12 | -135.5593 | 126.9102 | 9.0325e-12 | -135.5593 | 126.9102
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.3275e-16 | -3.9281e-09 | -6.2836e-09 | -7.3275e-16 | 3.9281e-09 | 6.2836e-09 | 8.1416e-17 | 6.7188e-09 | -2.639e-09 | -8.1416e-17 | -6.7188e-09 | 2.639e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.88719 | 0.77689 | 1.1 | 0.88719 | 0.77689 | 9.0475e-12 | -135.5593 | 126.9102 | 9.0367e-12 | -135.5593 | 126.9102

## LL_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.1073e-18 | -4.6325e-11 | -1.333e-10 | -9.1073e-18 | 4.6325e-11 | 1.333e-10 | 3.6429e-18 | 1.2762e-10 | 2.3032e-11 | -3.0358e-18 | -1.2762e-10 | -2.3032e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0442 | 1.05 | 1.048 | 1.0442 | -1.8714e-13 | -120.3021 | 119.9453 | -1.8723e-13 | -120.3021 | 119.9453
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.3751e-18 | -4.6325e-11 | -1.333e-10 | -6.3751e-18 | 4.6325e-11 | 1.333e-10 | 4.2501e-18 | 1.2762e-10 | 2.3032e-11 | -4.8572e-18 | -1.2762e-10 | -2.3032e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0442 | 1.05 | 1.048 | 1.0442 | -1.8747e-13 | -120.3021 | 119.9453 | -1.8762e-13 | -120.3021 | 119.9453
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.9823e-18 | -3.8604e-11 | -1.1109e-10 | -6.3751e-18 | 3.8604e-11 | 1.1109e-10 | 1.2143e-18 | 1.0635e-10 | 1.9193e-11 | -6.0715e-19 | -1.0635e-10 | -1.9193e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0442 | 1.05 | 1.048 | 1.0442 | -1.8762e-13 | -120.3021 | 119.9453 | -1.8774e-13 | -120.3021 | 119.9453
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2501e-18 | -2.3162e-11 | -6.6652e-11 | -4.2501e-18 | 2.3162e-11 | 6.6652e-11 | 2.4286e-18 | 6.3811e-11 | 1.1516e-11 | -3.0358e-18 | -6.3811e-11 | -1.1516e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0442 | 1.05 | 1.048 | 1.0442 | -1.8774e-13 | -120.3021 | 119.9453 | -1.878e-13 | -120.3021 | 119.9453
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5179e-18 | -7.7208e-12 | -2.2217e-11 | -1.5179e-18 | 7.7208e-12 | 2.2217e-11 | -6.0715e-19 | 2.127e-11 | 3.8387e-12 | -6.0715e-19 | -2.127e-11 | -3.8387e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0442 | 1.05 | 1.048 | 1.0442 | -1.8774e-13 | -120.3021 | 119.9453 | -1.8776e-13 | -120.3021 | 119.9453
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4286e-18 | -1.5442e-11 | -4.4435e-11 | -2.4286e-18 | 1.5442e-11 | 4.4435e-11 | -7.9605e-33 | 4.2541e-11 | 7.6773e-12 | 7.9617e-33 | -4.2541e-11 | -7.6773e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0442 | 1.05 | 1.048 | 1.0442 | -1.878e-13 | -120.3021 | 119.9453 | -1.8783e-13 | -120.3021 | 119.9453
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2143e-18 | -7.7208e-12 | -2.2217e-11 | -6.0715e-19 | 7.7208e-12 | 2.2217e-11 | -1.2143e-18 | 2.127e-11 | 3.8387e-12 | 1.9906e-33 | -2.127e-11 | -3.8387e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0442 | 1.05 | 1.048 | 1.0442 | -1.8783e-13 | -120.3021 | 119.9453 | -1.8785e-13 | -120.3021 | 119.9453
Line16_4_18 | 0 | 0.0584 | 0.0584 | 0 | 0.0584 | 0.0584 | 0 | 0.013487 | 0.013487 | 0 | 0.013487 | 0.013487 | -2.4286e-18 | 0.013608 | 0.0035134 | -1.2143e-18 | -0.013574 | -0.0034793 | 2.4286e-18 | 0.0036287 | 0.013561 | 3.9689e-33 | -0.0035605 | -0.013493 | 0 | -135.4649 | 44.5351 | 0 | 44.5351 | -135.4649 | 1.05 | 1.0442 | 1.0387 | 1.05 | 1.0405 | 1.0331 | -1.8722e-13 | -120.5336 | 120.01 | -1.8727e-13 | -120.7668 | 120.0754
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.0715e-19 | -7.7208e-12 | -2.2217e-11 | 6.0715e-19 | 7.7208e-12 | 2.2217e-11 | -1.8215e-18 | 2.127e-11 | 3.8387e-12 | 1.8215e-18 | -2.127e-11 | -3.8387e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0442 | 1.05 | 1.048 | 1.0442 | -1.8717e-13 | -120.3021 | 119.9453 | -1.8719e-13 | -120.3021 | 119.9453
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0929e-17 | -6.1766e-11 | -1.7774e-10 | -1.0929e-17 | 6.1766e-11 | 1.7774e-10 | 6.6787e-18 | 1.7016e-10 | 3.0709e-11 | -6.6787e-18 | -1.7016e-10 | -3.0709e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0442 | 1.05 | 1.048 | 1.0442 | -1.8714e-13 | -120.3021 | 119.9453 | -1.873e-13 | -120.3021 | 119.9453
Line2_1_4 | 0 | 0.0584 | 0.0584 | 0 | 0.0584 | 0.0584 | 0 | 0.013487 | 0.013487 | 0 | 0.013487 | 0.013487 | 4.2501e-18 | 0.013642 | 0.0035475 | -5.4644e-18 | -0.013608 | -0.0035134 | 2.4286e-18 | 0.003697 | 0.013629 | -2.4286e-18 | -0.0036287 | -0.013561 | 0 | -135.4649 | 44.5351 | 0 | 44.5351 | -135.4649 | 1.05 | 1.048 | 1.0442 | 1.05 | 1.0442 | 1.0387 | -1.8714e-13 | -120.3021 | 119.9453 | -1.8722e-13 | -120.5336 | 120.01
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0358e-18 | -1.5442e-11 | -4.4435e-11 | -3.0358e-18 | 1.5442e-11 | 4.4435e-11 | 6.0715e-19 | 4.2541e-11 | 7.6773e-12 | -6.0715e-19 | -4.2541e-11 | -7.6773e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0442 | 1.05 | 1.048 | 1.0442 | -1.8714e-13 | -120.3021 | 119.9453 | -1.8717e-13 | -120.3021 | 119.9453
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0715e-18 | -3.8604e-11 | -1.1109e-10 | -6.0715e-18 | 3.8604e-11 | 1.1109e-10 | 2.4286e-18 | 1.0635e-10 | 1.9193e-11 | -1.8215e-18 | -1.0635e-10 | -1.9193e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0442 | 1.05 | 1.048 | 1.0442 | -1.8723e-13 | -120.3021 | 119.9453 | -1.8734e-13 | -120.3021 | 119.9453
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6429e-18 | -3.0883e-11 | -8.887e-11 | -4.2501e-18 | 3.0883e-11 | 8.887e-11 | 1.2143e-18 | 8.5081e-11 | 1.5355e-11 | -1.8215e-18 | -8.5081e-11 | -1.5355e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0442 | 1.05 | 1.048 | 1.0442 | -1.8734e-13 | -120.3021 | 119.9453 | -1.8743e-13 | -120.3021 | 119.9453
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2501e-18 | -2.3162e-11 | -6.6652e-11 | -4.2501e-18 | 2.3162e-11 | 6.6652e-11 | -1.3903e-32 | 6.3811e-11 | 1.1516e-11 | 1.8215e-18 | -6.3811e-11 | -1.1516e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0442 | 1.05 | 1.048 | 1.0442 | -1.8743e-13 | -120.3021 | 119.9453 | -1.875e-13 | -120.3021 | 119.9453
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.1073e-19 | -7.7208e-12 | -2.2217e-11 | -3.0358e-19 | 7.7208e-12 | 2.2217e-11 | -1.2143e-18 | 2.127e-11 | 3.8387e-12 | 9.9355e-34 | -2.127e-11 | -3.8387e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0442 | 1.05 | 1.048 | 1.0442 | -1.875e-13 | -120.3021 | 119.9453 | -1.8752e-13 | -120.3021 | 119.9453
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.1073e-19 | -7.7208e-12 | -2.2217e-11 | -3.0358e-19 | 7.7208e-12 | 2.2217e-11 | -2.9804e-33 | 2.127e-11 | 3.8387e-12 | -1.2143e-18 | -2.127e-11 | -3.8387e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0442 | 1.05 | 1.048 | 1.0442 | -1.875e-13 | -120.3021 | 119.9453 | -1.8752e-13 | -120.3021 | 119.9453
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0018e-17 | -5.4045e-11 | -1.5552e-10 | -1.0018e-17 | 5.4045e-11 | 1.5552e-10 | 4.2501e-18 | 1.4889e-10 | 2.6871e-11 | -3.6429e-18 | -1.4889e-10 | -2.6871e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0442 | 1.05 | 1.048 | 1.0442 | -1.873e-13 | -120.3021 | 119.9453 | -1.8747e-13 | -120.3021 | 119.9453

## LL_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.541e-18 | -5.3219e-11 | -1.5314e-10 | -1.0177e-17 | 5.3219e-11 | 1.5314e-10 | 5.0885e-18 | 1.4664e-10 | 2.6437e-11 | -5.7246e-18 | -1.4664e-10 | -2.6437e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0936 | 1.1 | 1.0978 | 1.0936 | 2.1196e-13 | -120.3163 | 119.9428 | 2.1182e-13 | -120.3163 | 119.9428
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.9049e-18 | -5.3219e-11 | -1.5314e-10 | -8.9049e-18 | 5.3219e-11 | 1.5314e-10 | 6.3607e-19 | 1.4664e-10 | 2.6437e-11 | -2.5443e-18 | -1.4664e-10 | -2.6437e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0936 | 1.1 | 1.0978 | 1.0936 | 2.1158e-13 | -120.3163 | 119.9428 | 2.1142e-13 | -120.3163 | 119.9428
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.5869e-18 | -4.4349e-11 | -1.2762e-10 | -8.5869e-18 | 4.4349e-11 | 1.2762e-10 | 6.3607e-19 | 1.222e-10 | 2.2031e-11 | -6.3607e-19 | -1.222e-10 | -2.2031e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0936 | 1.1 | 1.0978 | 1.0936 | 2.1142e-13 | -120.3163 | 119.9428 | 2.113e-13 | -120.3163 | 119.9428
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1344e-18 | -2.6609e-11 | -7.6572e-11 | -4.1344e-18 | 2.6609e-11 | 7.6572e-11 | 3.1803e-18 | 7.332e-11 | 1.3218e-11 | -3.8164e-18 | -7.332e-11 | -1.3218e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0936 | 1.1 | 1.0978 | 1.0936 | 2.113e-13 | -120.3163 | 119.9428 | 2.1123e-13 | -120.3163 | 119.9428
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1803e-19 | -8.8698e-12 | -2.5524e-11 | -3.1803e-19 | 8.8698e-12 | 2.5524e-11 | -6.3607e-19 | 2.444e-11 | 4.4061e-12 | 6.3607e-19 | -2.444e-11 | -4.4061e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0936 | 1.1 | 1.0978 | 1.0936 | 2.113e-13 | -120.3163 | 119.9428 | 2.1128e-13 | -120.3163 | 119.9428
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5443e-18 | -1.7739e-11 | -5.1048e-11 | -3.1803e-18 | 1.774e-11 | 5.1048e-11 | 9.3799e-33 | 4.888e-11 | 8.8123e-12 | -1.2721e-18 | -4.888e-11 | -8.8123e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0936 | 1.1 | 1.0978 | 1.0936 | 2.1123e-13 | -120.3163 | 119.9428 | 2.112e-13 | -120.3163 | 119.9428
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.1803e-19 | -8.8697e-12 | -2.5524e-11 | -3.1803e-19 | 8.8697e-12 | 2.5524e-11 | 1.2721e-18 | 2.444e-11 | 4.4061e-12 | -6.3607e-19 | -2.444e-11 | -4.4061e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0936 | 1.1 | 1.0978 | 1.0936 | 2.112e-13 | -120.3163 | 119.9428 | 2.1118e-13 | -120.3163 | 119.9428
Line16_4_18 | 0 | 0.061167 | 0.061167 | 0 | 0.061167 | 0.061167 | 0 | 0.014126 | 0.014126 | 0 | 0.014126 | 0.014126 | -1.2721e-18 | 0.01493 | 0.0038518 | 2.5443e-18 | -0.014893 | -0.0038144 | -2.5443e-18 | 0.0039805 | 0.014876 | 9.4067e-33 | -0.0039057 | -0.014801 | 0 | -135.4761 | 44.5239 | 0 | 44.5239 | -135.4761 | 1.1 | 1.0938 | 1.0878 | 1.1 | 1.0899 | 1.0821 | 2.1188e-13 | -120.5478 | 120.0075 | 2.1184e-13 | -120.781 | 120.073
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2721e-18 | -8.8697e-12 | -2.5524e-11 | -1.2721e-18 | 8.8698e-12 | 2.5524e-11 | -6.3607e-19 | 2.444e-11 | 4.4061e-12 | 6.3607e-19 | -2.444e-11 | -4.4061e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0936 | 1.1 | 1.0978 | 1.0936 | 2.1193e-13 | -120.3163 | 119.9428 | 2.1191e-13 | -120.3163 | 119.9428
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2403e-17 | -7.0958e-11 | -2.0419e-10 | -1.3039e-17 | 7.0958e-11 | 2.0419e-10 | 7.6328e-18 | 1.9552e-10 | 3.5249e-11 | -8.2688e-18 | -1.9552e-10 | -3.5249e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0936 | 1.1 | 1.0978 | 1.0936 | 2.1196e-13 | -120.3163 | 119.9428 | 2.1176e-13 | -120.3163 | 119.9428
Line2_1_4 | 0 | 0.061167 | 0.061167 | 0 | 0.061167 | 0.061167 | 0 | 0.014126 | 0.014126 | 0 | 0.014126 | 0.014126 | 7.6328e-18 | 0.014968 | 0.0038892 | -7.6328e-18 | -0.01493 | -0.0038518 | 1.2721e-18 | 0.0040553 | 0.014951 | -1.2721e-18 | -0.0039805 | -0.014876 | 0 | -135.4761 | 44.5239 | 0 | 44.5239 | -135.4761 | 1.1 | 1.0978 | 1.0936 | 1.1 | 1.0938 | 1.0878 | 2.1196e-13 | -120.3163 | 119.9428 | 2.1188e-13 | -120.5478 | 120.0075
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1803e-18 | -1.7739e-11 | -5.1048e-11 | -3.1803e-18 | 1.774e-11 | 5.1048e-11 | 6.3607e-19 | 4.888e-11 | 8.8123e-12 | -1.2721e-18 | -4.888e-11 | -8.8123e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0936 | 1.1 | 1.0978 | 1.0936 | 2.1196e-13 | -120.3163 | 119.9428 | 2.1193e-13 | -120.3163 | 119.9428
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.5869e-18 | -4.4349e-11 | -1.2762e-10 | -7.9508e-18 | 4.4349e-11 | 1.2762e-10 | 3.8164e-18 | 1.222e-10 | 2.2031e-11 | -3.8164e-18 | -1.222e-10 | -2.2031e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0936 | 1.1 | 1.0978 | 1.0936 | 2.1182e-13 | -120.3163 | 119.9428 | 2.1173e-13 | -120.3163 | 119.9428
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.3607e-18 | -3.5479e-11 | -1.021e-10 | -6.3607e-18 | 3.5479e-11 | 1.021e-10 | 2.5443e-18 | 9.776e-11 | 1.7625e-11 | -2.5443e-18 | -9.776e-11 | -1.7625e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0936 | 1.1 | 1.0978 | 1.0936 | 2.1173e-13 | -120.3163 | 119.9428 | 2.1166e-13 | -120.3163 | 119.9428
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2262e-18 | -2.6609e-11 | -7.6572e-11 | -2.8623e-18 | 2.6609e-11 | 7.6572e-11 | 1.2721e-18 | 7.332e-11 | 1.3218e-11 | -1.2721e-18 | -7.332e-11 | -1.3218e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0936 | 1.1 | 1.0978 | 1.0936 | 2.1166e-13 | -120.3163 | 119.9428 | 2.1159e-13 | -120.3163 | 119.9428
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1803e-19 | -8.8698e-12 | -2.5524e-11 | -3.1803e-19 | 8.8698e-12 | 2.5524e-11 | 6.3607e-19 | 2.444e-11 | 4.4061e-12 | -6.3607e-19 | -2.444e-11 | -4.4061e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0936 | 1.1 | 1.0978 | 1.0936 | 2.1159e-13 | -120.3163 | 119.9428 | 2.1158e-13 | -120.3163 | 119.9428
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.1803e-19 | -8.8698e-12 | -2.5524e-11 | 3.1803e-19 | 8.8698e-12 | 2.5524e-11 | -2.5443e-18 | 2.444e-11 | 4.4061e-12 | 2.5443e-18 | -2.444e-11 | -4.4061e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0936 | 1.1 | 1.0978 | 1.0936 | 2.1159e-13 | -120.3163 | 119.9428 | 2.1157e-13 | -120.3163 | 119.9428
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3039e-17 | -6.2088e-11 | -1.7867e-10 | -1.2403e-17 | 6.2088e-11 | 1.7867e-10 | 5.0885e-18 | 1.7108e-10 | 3.0843e-11 | -4.4525e-18 | -1.7108e-10 | -3.0843e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0936 | 1.1 | 1.0978 | 1.0936 | 2.1176e-13 | -120.3163 | 119.9428 | 2.1158e-13 | -120.3163 | 119.9428

## LL_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3946e-17 | -1.4366e-09 | -3.9666e-09 | -4.3946e-17 | 1.4366e-09 | 3.9666e-09 | 1.7579e-17 | 4.6273e-09 | -2.4518e-10 | -8.9558e-31 | -4.6273e-09 | 2.4518e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.83839 | 0.68767 | 0.95 | 0.83839 | 0.68767 | 1.1678e-12 | -135.3123 | 120.9775 | 1.1676e-12 | -135.3123 | 120.9775
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.5157e-17 | -1.4366e-09 | -3.9666e-09 | 3.5157e-17 | 1.4366e-09 | 3.9666e-09 | 1.2305e-16 | 4.6273e-09 | -2.4518e-10 | -1.2305e-16 | -4.6273e-09 | 2.4518e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.83839 | 0.68767 | 0.95 | 0.83839 | 0.68767 | 1.1754e-12 | -135.3123 | 120.9775 | 1.1795e-12 | -135.3123 | 120.9775
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.1712e-30 | -1.1971e-09 | -3.3055e-09 | 3.5157e-17 | 1.1971e-09 | 3.3055e-09 | 1.0547e-16 | 3.8561e-09 | -2.0432e-10 | -1.4063e-16 | -3.8561e-09 | 2.0432e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.83839 | 0.68767 | 0.95 | 0.83839 | 0.68767 | 1.1795e-12 | -135.3123 | 120.9775 | 1.1832e-12 | -135.3123 | 120.9775
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.7579e-17 | -7.1829e-10 | -1.9833e-09 | 3.5157e-17 | 7.1829e-10 | 1.9833e-09 | 1.7579e-17 | 2.3137e-09 | -1.2259e-10 | 1.7579e-17 | -2.3137e-09 | 1.2259e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.83839 | 0.68767 | 0.95 | 0.83839 | 0.68767 | 1.1832e-12 | -135.3123 | 120.9775 | 1.1848e-12 | -135.3123 | 120.9775
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5157e-17 | -2.3943e-10 | -6.611e-10 | -1.7579e-17 | 2.3943e-10 | 6.611e-10 | 3.5157e-17 | 7.7122e-10 | -4.0864e-11 | -3.5157e-17 | -7.7122e-10 | 4.0864e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.83839 | 0.68767 | 0.95 | 0.83839 | 0.68767 | 1.1832e-12 | -135.3123 | 120.9775 | 1.183e-12 | -135.3123 | 120.9775
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.5157e-17 | -4.7886e-10 | -1.3222e-09 | 1.7579e-17 | 4.7886e-10 | 1.3222e-09 | 3.5157e-17 | 1.5424e-09 | -8.1728e-11 | -3.5157e-17 | -1.5424e-09 | 8.1728e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.83839 | 0.68767 | 0.95 | 0.83839 | 0.68767 | 1.1848e-12 | -135.3123 | 120.9775 | 1.186e-12 | -135.3123 | 120.9775
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.3943e-10 | -6.611e-10 | -1.7579e-17 | 2.3943e-10 | 6.611e-10 | 0 | 7.7122e-10 | -4.0864e-11 | 1.7579e-17 | -7.7122e-10 | 4.0864e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.83839 | 0.68767 | 0.95 | 0.83839 | 0.68767 | 1.186e-12 | -135.3123 | 120.9775 | 1.1863e-12 | -135.3123 | 120.9775
Line16_4_18 | 0 | 2.5068 | 2.5068 | 0 | 2.5068 | 2.5068 | 0 | 0.57893 | 0.57893 | 0 | 0.57893 | 0.57893 | -7.0314e-17 | 0.35328 | -0.11197 | -1.4333e-30 | -0.23262 | 0.23262 | -7.0314e-17 | -0.020967 | 0.27233 | 7.0314e-17 | 0.14665 | -0.14665 | 0 | -147.7717 | 32.2283 | 0 | 32.2283 | -147.7717 | 0.95 | 0.6113 | 0.50862 | 0.95 | 0.475 | 0.475 | 1.1688e-12 | -151.1682 | 144.5775 | 1.168e-12 | -180 | 180
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.7893e-18 | -2.3943e-10 | -6.611e-10 | 8.7893e-18 | 2.3943e-10 | 6.611e-10 | -1.7938e-31 | 7.7122e-10 | -4.0864e-11 | 1.7942e-31 | -7.7122e-10 | 4.0864e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.83839 | 0.68767 | 0.95 | 0.83839 | 0.68767 | 1.1694e-12 | -135.3123 | 120.9775 | 1.1696e-12 | -135.3123 | 120.9775
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.7893e-18 | -1.9154e-09 | -5.2888e-09 | -8.7893e-18 | 1.9154e-09 | 5.2888e-09 | 1.2305e-16 | 6.1697e-09 | -3.2691e-10 | -1.0547e-16 | -6.1697e-09 | 3.2691e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.83839 | 0.68767 | 0.95 | 0.83839 | 0.68767 | 1.1678e-12 | -135.3123 | 120.9775 | 1.1713e-12 | -135.3123 | 120.9775
Line2_1_4 | 0 | 2.5068 | 2.5068 | 0 | 2.5068 | 2.5068 | 0 | 0.57893 | 0.57893 | 0 | 0.57893 | 0.57893 | -3.5157e-17 | 0.47394 | 0.0086903 | 7.0314e-17 | -0.35328 | 0.11197 | 3.5157e-17 | 0.10472 | 0.39802 | 1.4344e-30 | 0.020967 | -0.27233 | 0 | -147.7717 | 32.2283 | 0 | 32.2283 | -147.7717 | 0.95 | 0.83839 | 0.68767 | 0.95 | 0.6113 | 0.50862 | 1.1678e-12 | -135.3123 | 120.9775 | 1.1688e-12 | -151.1682 | 144.5775
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.4331e-30 | -4.7886e-10 | -1.3222e-09 | 1.435e-30 | 4.7886e-10 | 1.3222e-09 | 7.0314e-17 | 1.5424e-09 | -8.1728e-11 | -7.0314e-17 | -1.5424e-09 | 8.1728e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.83839 | 0.68767 | 0.95 | 0.83839 | 0.68767 | 1.1678e-12 | -135.3123 | 120.9775 | 1.1694e-12 | -135.3123 | 120.9775
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7579e-17 | -1.1971e-09 | -3.3055e-09 | -3.5157e-17 | 1.1971e-09 | 3.3055e-09 | -1.7579e-17 | 3.8561e-09 | -2.0432e-10 | 3.5157e-17 | -3.8561e-09 | 2.0432e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.83839 | 0.68767 | 0.95 | 0.83839 | 0.68767 | 1.1676e-12 | -135.3123 | 120.9775 | 1.1668e-12 | -135.3123 | 120.9775
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.1525e-17 | -9.5772e-10 | -2.6444e-09 | -6.1525e-17 | 9.5772e-10 | 2.6444e-09 | 1.7579e-17 | 3.0849e-09 | -1.6346e-10 | -3.5157e-17 | -3.0849e-09 | 1.6346e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.83839 | 0.68767 | 0.95 | 0.83839 | 0.68767 | 1.1668e-12 | -135.3123 | 120.9775 | 1.1663e-12 | -135.3123 | 120.9775
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2736e-17 | -7.1829e-10 | -1.9833e-09 | -5.2736e-17 | 7.1829e-10 | 1.9833e-09 | 8.7893e-17 | 2.3136e-09 | -1.2259e-10 | -8.7893e-17 | -2.3136e-09 | 1.2259e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.83839 | 0.68767 | 0.95 | 0.83839 | 0.68767 | 1.1663e-12 | -135.3123 | 120.9775 | 1.1668e-12 | -135.3123 | 120.9775
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.7893e-18 | -2.3943e-10 | -6.611e-10 | 8.7893e-18 | 2.3943e-10 | 6.611e-10 | 3.5157e-17 | 7.7122e-10 | -4.0864e-11 | -3.5157e-17 | -7.7122e-10 | 4.0864e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.83839 | 0.68767 | 0.95 | 0.83839 | 0.68767 | 1.1668e-12 | -135.3123 | 120.9775 | 1.1666e-12 | -135.3123 | 120.9775
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.7579e-17 | -2.3943e-10 | -6.611e-10 | 1.7579e-17 | 2.3943e-10 | 6.611e-10 | 1.7579e-17 | 7.7122e-10 | -4.0864e-11 | -1.7579e-17 | -7.7122e-10 | 4.0864e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.83839 | 0.68767 | 0.95 | 0.83839 | 0.68767 | 1.1668e-12 | -135.3123 | 120.9775 | 1.167e-12 | -135.3123 | 120.9775
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.7893e-18 | -1.676e-09 | -4.6277e-09 | -8.7893e-18 | 1.676e-09 | 4.6277e-09 | 8.7893e-17 | 5.3985e-09 | -2.8605e-10 | -7.0314e-17 | -5.3985e-09 | 2.8605e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.83839 | 0.68767 | 0.95 | 0.83839 | 0.68767 | 1.1713e-12 | -135.3123 | 120.9775 | 1.1754e-12 | -135.3123 | 120.9775

## LL_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.8287e-17 | -1.2893e-09 | -3.56e-09 | -4.1633e-17 | 1.2893e-09 | 3.56e-09 | 1.6653e-17 | 4.153e-09 | -2.2005e-10 | -2.0181e-30 | -4.153e-09 | 2.2005e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.79426 | 0.65148 | 0.9 | 0.79426 | 0.65148 | 2.7773e-12 | -135.3123 | 120.9775 | 2.7773e-12 | -135.3123 | 120.9775
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.498e-17 | -1.2893e-09 | -3.56e-09 | 2.498e-17 | 1.2893e-09 | 3.56e-09 | 8.3267e-17 | 4.153e-09 | -2.2006e-10 | -8.3267e-17 | -4.153e-09 | 2.2006e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.79426 | 0.65148 | 0.9 | 0.79426 | 0.65148 | 2.7849e-12 | -135.3123 | 120.9775 | 2.789e-12 | -135.3123 | 120.9775
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.996e-17 | -1.0744e-09 | -2.9667e-09 | 4.996e-17 | 1.0744e-09 | 2.9667e-09 | 1.3323e-16 | 3.4609e-09 | -1.8338e-10 | -1.3323e-16 | -3.4609e-09 | 1.8338e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.79426 | 0.65148 | 0.9 | 0.79426 | 0.65148 | 2.789e-12 | -135.3123 | 120.9775 | 2.7926e-12 | -135.3123 | 120.9775
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.1633e-17 | -6.4467e-10 | -1.78e-09 | 8.3267e-18 | 6.4467e-10 | 1.78e-09 | -1.6653e-17 | 2.0765e-09 | -1.1003e-10 | 4.0608e-31 | -2.0765e-09 | 1.1003e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.79426 | 0.65148 | 0.9 | 0.79426 | 0.65148 | 2.7926e-12 | -135.3123 | 120.9775 | 2.7943e-12 | -135.3123 | 120.9775
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3267e-18 | -2.1489e-10 | -5.9334e-10 | -2.498e-17 | 2.1489e-10 | 5.9334e-10 | -1.6653e-17 | 6.9217e-10 | -3.6676e-11 | -3.3307e-17 | -6.9217e-10 | 3.6676e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.79426 | 0.65148 | 0.9 | 0.79426 | 0.65148 | 2.7926e-12 | -135.3123 | 120.9775 | 2.7925e-12 | -135.3123 | 120.9775
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.6653e-17 | -4.2978e-10 | -1.1867e-09 | 1.6653e-17 | 4.2978e-10 | 1.1867e-09 | 4.996e-17 | 1.3843e-09 | -7.3352e-11 | -6.6613e-17 | -1.3843e-09 | 7.3352e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.79426 | 0.65148 | 0.9 | 0.79426 | 0.65148 | 2.7943e-12 | -135.3123 | 120.9775 | 2.7955e-12 | -135.3123 | 120.9775
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.3267e-18 | -2.1489e-10 | -5.9334e-10 | 4.1633e-17 | 2.1489e-10 | 5.9334e-10 | 6.6613e-17 | 6.9217e-10 | -3.6676e-11 | -3.3307e-17 | -6.9217e-10 | 3.6676e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.79426 | 0.65148 | 0.9 | 0.79426 | 0.65148 | 2.7955e-12 | -135.3123 | 120.9775 | 2.7958e-12 | -135.3123 | 120.9775
Line16_4_18 | 0 | 2.3749 | 2.3749 | 0 | 2.3749 | 2.3749 | 0 | 0.54846 | 0.54846 | 0 | 0.54846 | 0.54846 | -6.6613e-17 | 0.31707 | -0.10049 | 6.6613e-17 | -0.20878 | 0.20878 | -3.2311e-30 | -0.018818 | 0.24442 | -6.6613e-17 | 0.13162 | -0.13162 | 0 | -147.7717 | 32.2283 | 0 | 32.2283 | -147.7717 | 0.9 | 0.57913 | 0.48185 | 0.9 | 0.45 | 0.45 | 2.7792e-12 | -151.1682 | 144.5775 | 2.7787e-12 | 180 | 180
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.6653e-17 | -2.1489e-10 | -5.9334e-10 | 1.6653e-17 | 2.1489e-10 | 5.9334e-10 | 3.3307e-17 | 6.9217e-10 | -3.6676e-11 | -1.6653e-17 | -6.9217e-10 | 3.6676e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.79426 | 0.65148 | 0.9 | 0.79426 | 0.65148 | 2.7788e-12 | -135.3123 | 120.9775 | 2.7791e-12 | -135.3123 | 120.9775
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6653e-17 | -1.7191e-09 | -4.7467e-09 | 4.0412e-30 | 1.7191e-09 | 4.7467e-09 | 9.992e-17 | 5.5374e-09 | -2.9341e-10 | -8.3267e-17 | -5.5374e-09 | 2.9341e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.79426 | 0.65148 | 0.9 | 0.79426 | 0.65148 | 2.7773e-12 | -135.3123 | 120.9775 | 2.7808e-12 | -135.3123 | 120.9775
Line2_1_4 | 0 | 2.3749 | 2.3749 | 0 | 2.3749 | 2.3749 | 0 | 0.54846 | 0.54846 | 0 | 0.54846 | 0.54846 | 1.6145e-30 | 0.42536 | 0.0077996 | 3.3307e-17 | -0.31707 | 0.10049 | -3.3307e-17 | 0.093984 | 0.35722 | 3.3307e-17 | 0.018818 | -0.24442 | 0 | -147.7717 | 32.2283 | 0 | 32.2283 | -147.7717 | 0.9 | 0.79426 | 0.65148 | 0.9 | 0.57913 | 0.48185 | 2.7773e-12 | -135.3123 | 120.9775 | 2.7792e-12 | -151.1682 | 144.5775
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3267e-18 | -4.2978e-10 | -1.1867e-09 | 8.3267e-18 | 4.2978e-10 | 1.1867e-09 | 4.996e-17 | 1.3843e-09 | -7.3352e-11 | -1.6653e-17 | -1.3843e-09 | 7.3352e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.79426 | 0.65148 | 0.9 | 0.79426 | 0.65148 | 2.7773e-12 | -135.3123 | 120.9775 | 2.7788e-12 | -135.3123 | 120.9775
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3307e-17 | -1.0744e-09 | -2.9667e-09 | -3.3307e-17 | 1.0744e-09 | 2.9667e-09 | -1.6653e-17 | 3.4609e-09 | -1.8338e-10 | -1.6142e-30 | -3.4609e-09 | 1.8338e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.79426 | 0.65148 | 0.9 | 0.79426 | 0.65148 | 2.7773e-12 | -135.3123 | 120.9775 | 2.7769e-12 | -135.3123 | 120.9775
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.498e-17 | -8.5956e-10 | -2.3734e-09 | -2.498e-17 | 8.5956e-10 | 2.3734e-09 | 1.2107e-30 | 2.7687e-09 | -1.467e-10 | -1.6653e-17 | -2.7687e-09 | 1.467e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.79426 | 0.65148 | 0.9 | 0.79426 | 0.65148 | 2.7769e-12 | -135.3123 | 120.9775 | 2.7771e-12 | -135.3123 | 120.9775
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.498e-17 | -6.4467e-10 | -1.78e-09 | 2.498e-17 | 6.4467e-10 | 1.78e-09 | 6.6613e-17 | 2.0765e-09 | -1.1003e-10 | -9.992e-17 | -2.0765e-09 | 1.1003e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.79426 | 0.65148 | 0.9 | 0.79426 | 0.65148 | 2.7771e-12 | -135.3123 | 120.9775 | 2.7775e-12 | -135.3123 | 120.9775
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6653e-17 | -2.1489e-10 | -5.9334e-10 | -3.3307e-17 | 2.1489e-10 | 5.9334e-10 | -3.3307e-17 | 6.9217e-10 | -3.6676e-11 | 3.3307e-17 | -6.9217e-10 | 3.6676e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.79426 | 0.65148 | 0.9 | 0.79426 | 0.65148 | 2.7775e-12 | -135.3123 | 120.9775 | 2.7774e-12 | -135.3123 | 120.9775
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.3267e-18 | -2.1489e-10 | -5.9334e-10 | 8.3267e-18 | 2.1489e-10 | 5.9334e-10 | -1.6653e-17 | 6.9217e-10 | -3.6676e-11 | 1.6653e-17 | -6.9217e-10 | 3.6676e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.79426 | 0.65148 | 0.9 | 0.79426 | 0.65148 | 2.7775e-12 | -135.3123 | 120.9775 | 2.7775e-12 | -135.3123 | 120.9775
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.3267e-18 | -1.5042e-09 | -4.1534e-09 | 8.3267e-18 | 1.5042e-09 | 4.1534e-09 | 8.3267e-17 | 4.8452e-09 | -2.5673e-10 | -8.3267e-17 | -4.8452e-09 | 2.5673e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.79426 | 0.65148 | 0.9 | 0.79426 | 0.65148 | 2.7808e-12 | -135.3123 | 120.9775 | 2.7849e-12 | -135.3123 | 120.9775

## LL_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.648e-18 | -3.8862e-11 | -1.1288e-10 | -1.3733e-18 | 3.8862e-11 | 1.1288e-10 | -5.4933e-19 | 1.0829e-10 | 1.9912e-11 | 1.0987e-18 | -1.0829e-10 | -1.9912e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94812 | 0.94457 | 0.95 | 0.94812 | 0.94457 | 6.0682e-14 | -120.3131 | 119.9422 | 6.0645e-14 | -120.3131 | 119.9422
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8066e-19 | -3.8862e-11 | -1.1288e-10 | -4.8066e-19 | 3.8862e-11 | 1.1288e-10 | 1.648e-18 | 1.0829e-10 | 1.9912e-11 | -2.1973e-18 | -1.0829e-10 | -1.9912e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94812 | 0.94457 | 0.95 | 0.94812 | 0.94457 | 6.0824e-14 | -120.3131 | 119.9422 | 6.0899e-14 | -120.3131 | 119.9422
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.03e-18 | -3.2385e-11 | -9.4068e-11 | 1.03e-18 | 3.2385e-11 | 9.4068e-11 | 3.8453e-18 | 9.0245e-11 | 1.6593e-11 | -3.8453e-18 | -9.0245e-11 | -1.6593e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94812 | 0.94457 | 0.95 | 0.94812 | 0.94457 | 6.0899e-14 | -120.3131 | 119.9422 | 6.097e-14 | -120.3131 | 119.9422
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.06e-19 | -1.9431e-11 | -5.6441e-11 | -2.06e-19 | 1.9431e-11 | 5.6441e-11 | 1.0987e-18 | 5.4147e-11 | 9.9561e-12 | -1.0987e-18 | -5.4147e-11 | -9.9561e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94812 | 0.94457 | 0.95 | 0.94812 | 0.94457 | 6.097e-14 | -120.3131 | 119.9422 | 6.1007e-14 | -120.3131 | 119.9422
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.8666e-20 | -6.477e-12 | -1.8814e-11 | 3.4333e-19 | 6.477e-12 | 1.8814e-11 | -7.307e-35 | 1.8049e-11 | 3.3187e-12 | 5.4933e-19 | -1.8049e-11 | -3.3187e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94812 | 0.94457 | 0.95 | 0.94812 | 0.94457 | 6.097e-14 | -120.3131 | 119.9422 | 6.0969e-14 | -120.3131 | 119.9422
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.03e-18 | -1.2954e-11 | -3.7627e-11 | 1.03e-18 | 1.2954e-11 | 3.7627e-11 | 2.1973e-18 | 3.6098e-11 | 6.6374e-12 | -2.1973e-18 | -3.6098e-11 | -6.6374e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94812 | 0.94457 | 0.95 | 0.94812 | 0.94457 | 6.1007e-14 | -120.3131 | 119.9422 | 6.104e-14 | -120.3131 | 119.9422
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.4933e-19 | -6.477e-12 | -1.8814e-11 | 5.4933e-19 | 6.477e-12 | 1.8814e-11 | -5.8523e-34 | 1.8049e-11 | 3.3187e-12 | 1.0987e-18 | -1.8049e-11 | -3.3187e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94812 | 0.94457 | 0.95 | 0.94812 | 0.94457 | 6.104e-14 | -120.3131 | 119.9422 | 6.1052e-14 | -120.3131 | 119.9422
Line16_4_18 | 0 | 0.052639 | 0.052639 | 0 | 0.052639 | 0.052639 | 0 | 0.012156 | 0.012156 | 0 | 0.012156 | 0.012156 | -1.0987e-18 | 0.011082 | 0.0028784 | 1.0987e-18 | -0.011029 | -0.0028252 | 2.1973e-18 | 0.0029185 | 0.011047 | -2.1973e-18 | -0.0028631 | -0.010991 | 0 | -135.266 | 44.734 | 0 | 44.734 | -135.266 | 0.95 | 0.94272 | 0.93905 | 0.95 | 0.93734 | 0.93354 | 6.0735e-14 | -120.5122 | 120.1294 | 6.0745e-14 | -120.7135 | 120.3187
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.4933e-19 | -6.477e-12 | -1.8814e-11 | 8.2399e-19 | 6.477e-12 | 1.8814e-11 | 1.0987e-18 | 1.8049e-11 | 3.3187e-12 | -5.4933e-19 | -1.8049e-11 | -3.3187e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94812 | 0.94457 | 0.95 | 0.94812 | 0.94457 | 6.0722e-14 | -120.3131 | 119.9422 | 6.0734e-14 | -120.3131 | 119.9422
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.9266e-19 | -5.1816e-11 | -1.5051e-10 | -1.1673e-18 | 5.1816e-11 | 1.5051e-10 | 3.296e-18 | 1.4439e-10 | 2.655e-11 | -2.1973e-18 | -1.4439e-10 | -2.655e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94812 | 0.94457 | 0.95 | 0.94812 | 0.94457 | 6.0682e-14 | -120.3131 | 119.9422 | 6.075e-14 | -120.3131 | 119.9422
Line2_1_4 | 0 | 0.052639 | 0.052639 | 0 | 0.052639 | 0.052639 | 0 | 0.012156 | 0.012156 | 0 | 0.012156 | 0.012156 | -2.1973e-18 | 0.011136 | 0.0029316 | 1.648e-18 | -0.011082 | -0.0028784 | 1.0987e-18 | 0.0029739 | 0.011102 | -1.0987e-18 | -0.0029185 | -0.011047 | 0 | -135.266 | 44.734 | 0 | 44.734 | -135.266 | 0.95 | 0.94812 | 0.94457 | 0.95 | 0.94272 | 0.93905 | 6.0682e-14 | -120.3131 | 119.9422 | 6.0735e-14 | -120.5122 | 120.1294
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.2399e-19 | -1.2954e-11 | -3.7627e-11 | 8.2399e-19 | 1.2954e-11 | 3.7627e-11 | 2.1973e-18 | 3.6098e-11 | 6.6374e-12 | -1.0987e-18 | -3.6098e-11 | -6.6374e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94812 | 0.94457 | 0.95 | 0.94812 | 0.94457 | 6.0682e-14 | -120.3131 | 119.9422 | 6.0722e-14 | -120.3131 | 119.9422
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.5533e-19 | -3.2385e-11 | -9.4068e-11 | -1.03e-18 | 3.2385e-11 | 9.4068e-11 | 7.9948e-34 | 9.0245e-11 | 1.6593e-11 | -1.0897e-33 | -9.0245e-11 | -1.6593e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94812 | 0.94457 | 0.95 | 0.94812 | 0.94457 | 6.0645e-14 | -120.3131 | 119.9422 | 6.062e-14 | -120.3131 | 119.9422
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.648e-18 | -2.5908e-11 | -7.5255e-11 | -1.3733e-18 | 2.5908e-11 | 7.5255e-11 | 1.0987e-18 | 7.2196e-11 | 1.3275e-11 | -1.0987e-18 | -7.2196e-11 | -1.3275e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94812 | 0.94457 | 0.95 | 0.94812 | 0.94457 | 6.062e-14 | -120.3131 | 119.9422 | 6.0606e-14 | -120.3131 | 119.9422
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.3733e-19 | -1.9431e-11 | -5.6441e-11 | 1.3733e-19 | 1.9431e-11 | 5.6441e-11 | -1.4527e-34 | 5.4147e-11 | 9.9561e-12 | -5.4933e-19 | -5.4147e-11 | -9.9561e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94812 | 0.94457 | 0.95 | 0.94812 | 0.94457 | 6.0606e-14 | -120.3131 | 119.9422 | 6.0612e-14 | -120.3131 | 119.9422
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.18e-19 | -6.477e-12 | -1.8814e-11 | 3.4333e-19 | 6.477e-12 | 1.8814e-11 | 1.648e-18 | 1.8049e-11 | 3.3187e-12 | -1.648e-18 | -1.8049e-11 | -3.3187e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94812 | 0.94457 | 0.95 | 0.94812 | 0.94457 | 6.0612e-14 | -120.3131 | 119.9422 | 6.061e-14 | -120.3131 | 119.9422
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.5533e-19 | -6.477e-12 | -1.8814e-11 | 4.8066e-19 | 6.477e-12 | 1.8814e-11 | 5.4933e-19 | 1.8049e-11 | 3.3187e-12 | -5.4933e-19 | -1.8049e-11 | -3.3187e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94812 | 0.94457 | 0.95 | 0.94812 | 0.94457 | 6.0612e-14 | -120.3131 | 119.9422 | 6.0615e-14 | -120.3131 | 119.9422
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0987e-18 | -4.5339e-11 | -1.317e-10 | -1.0987e-18 | 4.5339e-11 | 1.317e-10 | 2.7466e-18 | 1.2634e-10 | 2.3231e-11 | -2.7466e-18 | -1.2634e-10 | -2.3231e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94812 | 0.94457 | 0.95 | 0.94812 | 0.94457 | 6.075e-14 | -120.3131 | 119.9422 | 6.0824e-14 | -120.3131 | 119.9422

## LL_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4311e-18 | -3.4879e-11 | -1.0131e-10 | -1.4311e-18 | 3.4879e-11 | 1.0131e-10 | -5.2042e-19 | 9.7195e-11 | 1.7871e-11 | -1.5011e-33 | -9.7195e-11 | -1.7871e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89822 | 0.89485 | 0.9 | 0.89822 | 0.89485 | 6.0098e-14 | -120.3131 | 119.9422 | 6.0096e-14 | -120.3131 | 119.9422
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.5052e-19 | -3.4879e-11 | -1.0131e-10 | -6.5052e-19 | 3.4879e-11 | 1.0131e-10 | 1.5613e-18 | 9.7195e-11 | 1.7871e-11 | -1.0408e-18 | -9.7195e-11 | -1.7871e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89822 | 0.89485 | 0.9 | 0.89822 | 0.89485 | 6.0239e-14 | -120.3131 | 119.9422 | 6.0314e-14 | -120.3131 | 119.9422
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.6021e-19 | -2.9066e-11 | -8.4427e-11 | 2.6021e-19 | 2.9066e-11 | 8.4427e-11 | 2.6021e-18 | 8.0996e-11 | 1.4893e-11 | -3.1225e-18 | -8.0996e-11 | -1.4893e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89822 | 0.89485 | 0.9 | 0.89822 | 0.89485 | 6.0314e-14 | -120.3131 | 119.9422 | 6.0385e-14 | -120.3131 | 119.9422
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.8547e-19 | -1.7439e-11 | -5.0656e-11 | 8.4568e-19 | 1.7439e-11 | 5.0656e-11 | 5.2042e-19 | 4.8598e-11 | 8.9356e-12 | 8.9183e-34 | -4.8598e-11 | -8.9356e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89822 | 0.89485 | 0.9 | 0.89822 | 0.89485 | 6.0385e-14 | -120.3131 | 119.9422 | 6.0422e-14 | -120.3131 | 119.9422
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.2526e-19 | -5.8131e-12 | -1.6885e-11 | 6.5052e-20 | 5.8131e-12 | 1.6885e-11 | 5.2042e-19 | 1.6199e-11 | 2.9786e-12 | 5.2042e-19 | -1.6199e-11 | -2.9786e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89822 | 0.89485 | 0.9 | 0.89822 | 0.89485 | 6.0385e-14 | -120.3131 | 119.9422 | 6.0384e-14 | -120.3131 | 119.9422
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.5536e-19 | -1.1626e-11 | -3.3771e-11 | 7.1557e-19 | 1.1626e-11 | 3.3771e-11 | 1.5613e-18 | 3.2398e-11 | 5.9571e-12 | -1.0408e-18 | -3.2398e-11 | -5.9571e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89822 | 0.89485 | 0.9 | 0.89822 | 0.89485 | 6.0422e-14 | -120.3131 | 119.9422 | 6.0455e-14 | -120.3131 | 119.9422
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.5536e-19 | -5.8131e-12 | -1.6885e-11 | 4.5536e-19 | 5.8131e-12 | 1.6885e-11 | 5.2042e-19 | 1.6199e-11 | 2.9785e-12 | 4.8057e-34 | -1.6199e-11 | -2.9786e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89822 | 0.89485 | 0.9 | 0.89822 | 0.89485 | 6.0455e-14 | -120.3131 | 119.9422 | 6.0467e-14 | -120.3131 | 119.9422
Line16_4_18 | 0 | 0.049869 | 0.049869 | 0 | 0.049869 | 0.049869 | 0 | 0.011517 | 0.011517 | 0 | 0.011517 | 0.011517 | -1.0408e-18 | 0.0099465 | 0.0025834 | -1.0925e-33 | -0.0098987 | -0.0025356 | -2.0817e-18 | 0.0026194 | 0.0099144 | 1.0408e-18 | -0.0025697 | -0.0098647 | 0 | -135.266 | 44.734 | 0 | 44.734 | -135.266 | 0.9 | 0.89311 | 0.88962 | 0.9 | 0.888 | 0.8844 | 6.0142e-14 | -120.5122 | 120.1294 | 6.0139e-14 | -120.7135 | 120.3187
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.9516e-19 | -5.8131e-12 | -1.6885e-11 | 4.5536e-19 | 5.8131e-12 | 1.6885e-11 | -5.2042e-19 | 1.6199e-11 | 2.9786e-12 | 5.2042e-19 | -1.6199e-11 | -2.9785e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89822 | 0.89485 | 0.9 | 0.89822 | 0.89485 | 6.0137e-14 | -120.3131 | 119.9422 | 6.0149e-14 | -120.3131 | 119.9422
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1709e-18 | -4.6505e-11 | -1.3508e-10 | -1.1709e-18 | 4.6505e-11 | 1.3508e-10 | 3.1225e-18 | 1.2959e-10 | 2.3828e-11 | -2.0817e-18 | -1.2959e-10 | -2.3828e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89822 | 0.89485 | 0.9 | 0.89822 | 0.89485 | 6.0098e-14 | -120.3131 | 119.9422 | 6.0165e-14 | -120.3131 | 119.9422
Line2_1_4 | 0 | 0.049869 | 0.049869 | 0 | 0.049869 | 0.049869 | 0 | 0.011517 | 0.011517 | 0 | 0.011517 | 0.011517 | -1.0408e-18 | 0.0099942 | 0.0026311 | 5.2042e-19 | -0.0099465 | -0.0025834 | 1.0408e-18 | 0.0026691 | 0.0099642 | -1.0408e-18 | -0.0026194 | -0.0099144 | 0 | -135.266 | 44.734 | 0 | 44.734 | -135.266 | 0.9 | 0.89822 | 0.89485 | 0.9 | 0.89311 | 0.88962 | 6.0098e-14 | -120.3131 | 119.9422 | 6.0142e-14 | -120.5122 | 120.1294
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2042e-19 | -1.1626e-11 | -3.3771e-11 | -2.6021e-19 | 1.1626e-11 | 3.3771e-11 | 5.2042e-19 | 3.2398e-11 | 5.9571e-12 | -5.2042e-19 | -3.2398e-11 | -5.9571e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89822 | 0.89485 | 0.9 | 0.89822 | 0.89485 | 6.0098e-14 | -120.3131 | 119.9422 | 6.0137e-14 | -120.3131 | 119.9422
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.5052e-20 | -2.9066e-11 | -8.4427e-11 | 6.5052e-20 | 2.9066e-11 | 8.4427e-11 | 5.2042e-19 | 8.0996e-11 | 1.4893e-11 | -1.0408e-18 | -8.0996e-11 | -1.4893e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89822 | 0.89485 | 0.9 | 0.89822 | 0.89485 | 6.0096e-14 | -120.3131 | 119.9422 | 6.0088e-14 | -120.3131 | 119.9422
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2042e-19 | -2.3253e-11 | -6.7542e-11 | -5.2042e-19 | 2.3253e-11 | 6.7542e-11 | 5.2042e-19 | 6.4797e-11 | 1.1914e-11 | -1.5613e-18 | -6.4797e-11 | -1.1914e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89822 | 0.89485 | 0.9 | 0.89822 | 0.89485 | 6.0088e-14 | -120.3131 | 119.9422 | 6.0081e-14 | -120.3131 | 119.9422
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9031e-19 | -1.7439e-11 | -5.0656e-11 | -3.9031e-19 | 1.7439e-11 | 5.0656e-11 | 4.0929e-34 | 4.8598e-11 | 8.9357e-12 | -5.2042e-19 | -4.8598e-11 | -8.9357e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89822 | 0.89485 | 0.9 | 0.89822 | 0.89485 | 6.0081e-14 | -120.3131 | 119.9422 | 6.0098e-14 | -120.3131 | 119.9422
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.5052e-19 | -5.8131e-12 | -1.6885e-11 | 6.5052e-19 | 5.8131e-12 | 1.6885e-11 | 2.0817e-18 | 1.6199e-11 | 2.9785e-12 | -2.0817e-18 | -1.6199e-11 | -2.9785e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89822 | 0.89485 | 0.9 | 0.89822 | 0.89485 | 6.0098e-14 | -120.3131 | 119.9422 | 6.0096e-14 | -120.3131 | 119.9422
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.1059e-18 | -5.8131e-12 | -1.6885e-11 | 1.1059e-18 | 5.8131e-12 | 1.6885e-11 | 5.2042e-19 | 1.6199e-11 | 2.9785e-12 | -1.0408e-18 | -1.6199e-11 | -2.9785e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89822 | 0.89485 | 0.9 | 0.89822 | 0.89485 | 6.0098e-14 | -120.3131 | 119.9422 | 6.0101e-14 | -120.3131 | 119.9422
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.236e-18 | -4.0692e-11 | -1.182e-10 | -1.236e-18 | 4.0692e-11 | 1.182e-10 | 3.6429e-18 | 1.1339e-10 | 2.085e-11 | -3.1225e-18 | -1.1339e-10 | -2.085e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89822 | 0.89485 | 0.9 | 0.89822 | 0.89485 | 6.0165e-14 | -120.3131 | 119.9422 | 6.0239e-14 | -120.3131 | 119.9422

## LG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 2.2655e-06 | 2.2655e-06 | 2.2655e-06 | 1.8887e-06 | 1.8887e-06 | 1.8887e-06 | 5.2319e-07 | 5.2319e-07 | 5.2319e-07 | 4.3617e-07 | 4.3617e-07 | 4.3617e-07 | 1.6497e-09 | 5.1017e-07 | -4.4056e-07 | -1.3483e-09 | -4.3111e-07 | 3.612e-07 | 3.6991e-09 | -7.9805e-07 | -8.3622e-07 | -3.0958e-09 | 6.6159e-07 | 7.0032e-07 | -92.3104 | -92.2988 | -92.2988 | 87.1877 | 87.2016 | 87.2016 | 0.0077417 | 1.8104 | 1.8066 | 0.0077416 | 1.8104 | 1.8066 | -26.3459 | -149.7092 | 149.9185 | -26.3459 | -149.7092 | 149.9185
Line10_11_12 | 2.2655e-06 | 2.2655e-06 | 2.2655e-06 | 1.8887e-06 | 1.8887e-06 | 1.8887e-06 | 5.2319e-07 | 5.2319e-07 | 5.2319e-07 | 4.3617e-07 | 4.3617e-07 | 4.3617e-07 | 1.6497e-09 | 5.1017e-07 | -4.4057e-07 | -1.3482e-09 | -4.3111e-07 | 3.612e-07 | 3.699e-09 | -7.9805e-07 | -8.3622e-07 | -3.0957e-09 | 6.6159e-07 | 7.0032e-07 | -92.3104 | -92.2988 | -92.2988 | 87.1877 | 87.2016 | 87.2016 | 0.0077414 | 1.8104 | 1.8066 | 0.0077413 | 1.8104 | 1.8066 | -26.3458 | -149.7092 | 149.9185 | -26.3458 | -149.7092 | 149.9185
Line11_12_13 | 1.8879e-06 | 1.8879e-06 | 1.8879e-06 | 1.5111e-06 | 1.5111e-06 | 1.5111e-06 | 4.3599e-07 | 4.3599e-07 | 4.3599e-07 | 3.4898e-07 | 3.4898e-07 | 3.4898e-07 | 1.3747e-09 | 4.2514e-07 | -3.6714e-07 | -1.0733e-09 | -3.4608e-07 | 2.8777e-07 | 3.0825e-09 | -6.6504e-07 | -6.9685e-07 | -2.4792e-09 | 5.2858e-07 | 5.6095e-07 | -92.3104 | -92.2988 | -92.2988 | 87.0622 | 87.0768 | 87.0768 | 0.0077413 | 1.8104 | 1.8066 | 0.0077412 | 1.8104 | 1.8066 | -26.3458 | -149.7092 | 149.9185 | -26.3458 | -149.7092 | 149.9185
Line12_13_15 | 1.1327e-06 | 1.1327e-06 | 1.1327e-06 | 0 | 0 | 0 | 2.6159e-07 | 2.6159e-07 | 2.6159e-07 | 0 | 0 | 0 | 8.2481e-10 | 2.5509e-07 | -2.2028e-07 | -5.2338e-10 | -1.7602e-07 | 1.4092e-07 | 1.8495e-09 | -3.9903e-07 | -4.1811e-07 | -1.2462e-09 | 2.6256e-07 | 2.8221e-07 | -92.3104 | -92.2988 | -92.2988 | 0 | 0 | 0 | 0.0077412 | 1.8104 | 1.8066 | 0.0077412 | 1.8104 | 1.8066 | -26.3458 | -149.7092 | 149.9185 | -26.3458 | -149.7092 | 149.9185
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7494e-10 | 8.5028e-08 | -7.3428e-08 | 2.6488e-11 | -5.9639e-09 | -5.9384e-09 | 6.1649e-10 | -1.3301e-07 | -1.3937e-07 | -1.3227e-11 | -3.4543e-09 | 3.4691e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0077412 | 1.8104 | 1.8066 | 0.0077412 | 1.8104 | 1.8066 | -26.3458 | -149.7092 | 149.9185 | -26.3458 | -149.7092 | 149.9185
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4987e-10 | 1.7006e-07 | -1.4686e-07 | -2.4844e-10 | -9.0992e-08 | 6.7489e-08 | 1.233e-09 | -2.6602e-07 | -2.7874e-07 | -6.2971e-10 | 1.2955e-07 | 1.4284e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0077412 | 1.8104 | 1.8066 | 0.0077412 | 1.8104 | 1.8066 | -26.3458 | -149.7092 | 149.9185 | -26.3457 | -149.7092 | 149.9185
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7493e-10 | 8.5028e-08 | -7.3428e-08 | 2.6488e-11 | -5.9639e-09 | -5.9384e-09 | 6.1648e-10 | -1.3301e-07 | -1.3937e-07 | -1.3226e-11 | -3.4543e-09 | 3.4691e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0077412 | 1.8104 | 1.8066 | 0.0077412 | 1.8104 | 1.8066 | -26.3457 | -149.7092 | 149.9185 | -26.3457 | -149.7092 | 149.9185
Line16_4_18 | 0.047974 | 0 | 0 | 0.047973 | 0 | 0 | 0.011079 | 0 | 0 | 0.011079 | 0 | 0 | 1.9179e-05 | 8.5197e-08 | -7.3422e-08 | -2.4582e-14 | -5.9529e-09 | -5.9229e-09 | 3.8358e-05 | -1.3305e-07 | -1.3948e-07 | 1.5794e-14 | -3.4484e-09 | 3.4658e-09 | -89.7809 | 0 | 0 | 90.2191 | 0 | 0 | 0.0038708 | 1.81 | 1.8058 | 0 | 1.8096 | 1.805 | -26.3459 | -149.6887 | 149.9169 | 0 | -149.6682 | 149.9153
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7495e-10 | 8.5028e-08 | -7.3427e-08 | 2.649e-11 | -5.9639e-09 | -5.9384e-09 | 6.1652e-10 | -1.3301e-07 | -1.3937e-07 | -1.3227e-11 | -3.4543e-09 | 3.4691e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0077417 | 1.8104 | 1.8066 | 0.0077417 | 1.8104 | 1.8066 | -26.3459 | -149.7092 | 149.9185 | -26.3459 | -149.7092 | 149.9185
Line1_1_3 | 3.0206e-06 | 3.0206e-06 | 3.0206e-06 | 2.6438e-06 | 2.6438e-06 | 2.6438e-06 | 6.9758e-07 | 6.9759e-07 | 6.9759e-07 | 6.1056e-07 | 6.1057e-07 | 6.1057e-07 | 2.1996e-09 | 6.8023e-07 | -5.8742e-07 | -1.8981e-09 | -6.0116e-07 | 5.0805e-07 | 4.9322e-09 | -1.0641e-06 | -1.115e-06 | -4.3288e-09 | 9.276e-07 | 9.7905e-07 | -92.3104 | -92.2988 | -92.2988 | 87.331 | 87.3443 | 87.3443 | 0.0077417 | 1.8104 | 1.8066 | 0.0077416 | 1.8104 | 1.8066 | -26.3459 | -149.7092 | 149.9185 | -26.3459 | -149.7092 | 149.9185
Line2_1_4 | 0.047974 | 0 | 0 | 0.047974 | 0 | 0 | 0.011079 | 0 | 0 | 0.011079 | 0 | 0 | 3.8358e-05 | 1.7024e-07 | -1.4689e-07 | -1.9179e-05 | -9.1156e-08 | 6.7491e-08 | 7.6716e-05 | -2.6616e-07 | -2.7897e-07 | -3.8358e-05 | 1.296e-07 | 1.4295e-07 | -89.7809 | 0 | 0 | 90.2191 | 0 | 0 | 0.0077417 | 1.8104 | 1.8066 | 0.0038708 | 1.81 | 1.8058 | -26.3459 | -149.7092 | 149.9185 | -26.3459 | -149.6887 | 149.9169
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.499e-10 | 1.7006e-07 | -1.4685e-07 | -2.4846e-10 | -9.0992e-08 | 6.7489e-08 | 1.233e-09 | -2.6602e-07 | -2.7874e-07 | -6.2975e-10 | 1.2955e-07 | 1.4284e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0077417 | 1.8104 | 1.8066 | 0.0077417 | 1.8104 | 1.8066 | -26.3459 | -149.7092 | 149.9185 | -26.3459 | -149.7092 | 149.9185
Line4_2_6 | 1.8879e-06 | 1.8879e-06 | 1.8879e-06 | 1.5111e-06 | 1.5111e-06 | 1.5111e-06 | 4.3599e-07 | 4.3599e-07 | 4.3599e-07 | 3.4898e-07 | 3.4898e-07 | 3.4898e-07 | 1.3747e-09 | 4.2514e-07 | -3.6714e-07 | -1.0733e-09 | -3.4608e-07 | 2.8777e-07 | 3.0826e-09 | -6.6504e-07 | -6.9685e-07 | -2.4793e-09 | 5.2858e-07 | 5.6095e-07 | -92.3104 | -92.2988 | -92.2988 | 87.0622 | 87.0768 | 87.0768 | 0.0077416 | 1.8104 | 1.8066 | 0.0077415 | 1.8104 | 1.8066 | -26.3459 | -149.7092 | 149.9185 | -26.3459 | -149.7092 | 149.9185
Line5_6_7 | 1.5103e-06 | 1.5103e-06 | 1.5103e-06 | 1.1336e-06 | 1.1336e-06 | 1.1336e-06 | 3.4879e-07 | 3.4879e-07 | 3.4879e-07 | 2.6179e-07 | 2.6179e-07 | 2.6179e-07 | 1.0998e-09 | 3.4011e-07 | -2.9371e-07 | -7.9834e-10 | -2.6105e-07 | 2.1434e-07 | 2.466e-09 | -5.3203e-07 | -5.5748e-07 | -1.8627e-09 | 3.9557e-07 | 4.2158e-07 | -92.3104 | -92.2988 | -92.2988 | 86.8533 | 86.8688 | 86.8688 | 0.0077415 | 1.8104 | 1.8066 | 0.0077414 | 1.8104 | 1.8066 | -26.3459 | -149.7092 | 149.9185 | -26.3458 | -149.7092 | 149.9185
Line6_7_8 | 1.1327e-06 | 1.1327e-06 | 1.1327e-06 | 0 | 0 | 0 | 2.6159e-07 | 2.6159e-07 | 2.6159e-07 | 0 | 0 | 0 | 8.2483e-10 | 2.5508e-07 | -2.2028e-07 | -5.2339e-10 | -1.7602e-07 | 1.4092e-07 | 1.8495e-09 | -3.9903e-07 | -4.1811e-07 | -1.2462e-09 | 2.6256e-07 | 2.8221e-07 | -92.3104 | -92.2988 | -92.2988 | 0 | 0 | 0 | 0.0077414 | 1.8104 | 1.8066 | 0.0077414 | 1.8104 | 1.8066 | -26.3458 | -149.7092 | 149.9185 | -26.3458 | -149.7092 | 149.9185
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7494e-10 | 8.5028e-08 | -7.3428e-08 | 2.6489e-11 | -5.9639e-09 | -5.9384e-09 | 6.165e-10 | -1.3301e-07 | -1.3937e-07 | -1.3227e-11 | -3.4543e-09 | 3.4691e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0077414 | 1.8104 | 1.8066 | 0.0077414 | 1.8104 | 1.8066 | -26.3458 | -149.7092 | 149.9185 | -26.3458 | -149.7092 | 149.9185
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7494e-10 | 8.5028e-08 | -7.3428e-08 | 2.6489e-11 | -5.9639e-09 | -5.9384e-09 | 6.165e-10 | -1.3301e-07 | -1.3937e-07 | -1.3227e-11 | -3.4543e-09 | 3.4691e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0077414 | 1.8104 | 1.8066 | 0.0077414 | 1.8104 | 1.8066 | -26.3458 | -149.7092 | 149.9185 | -26.3458 | -149.7092 | 149.9185
Line9_3_11 | 2.643e-06 | 2.6431e-06 | 2.6431e-06 | 2.2662e-06 | 2.2663e-06 | 2.2663e-06 | 6.1038e-07 | 6.1039e-07 | 6.1039e-07 | 5.2337e-07 | 5.2337e-07 | 5.2337e-07 | 1.9246e-09 | 5.952e-07 | -5.1399e-07 | -1.6232e-09 | -5.1613e-07 | 4.3463e-07 | 4.3156e-09 | -9.3106e-07 | -9.7558e-07 | -3.7123e-09 | 7.946e-07 | 8.3968e-07 | -92.3104 | -92.2988 | -92.2988 | 87.2713 | 87.2849 | 87.2849 | 0.0077416 | 1.8104 | 1.8066 | 0.0077414 | 1.8104 | 1.8066 | -26.3459 | -149.7092 | 149.9185 | -26.3458 | -149.7092 | 149.9185

## LG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 2.373e-06 | 2.373e-06 | 2.373e-06 | 1.9783e-06 | 1.9783e-06 | 1.9783e-06 | 5.4802e-07 | 5.4802e-07 | 5.4802e-07 | 4.5688e-07 | 4.5688e-07 | 4.5688e-07 | 1.8099e-09 | 5.5983e-07 | -4.8346e-07 | -1.4792e-09 | -4.7306e-07 | 3.9637e-07 | 4.0586e-09 | -8.7562e-07 | -9.1748e-07 | -3.3966e-09 | 7.2589e-07 | 7.6837e-07 | -92.3101 | -92.2979 | -92.2979 | 87.1879 | 87.2025 | 87.2025 | 0.0081089 | 1.8964 | 1.8924 | 0.0081088 | 1.8964 | 1.8924 | -26.3446 | -149.7051 | 149.9153 | -26.3446 | -149.7051 | 149.9153
Line10_11_12 | 2.373e-06 | 2.373e-06 | 2.373e-06 | 1.9783e-06 | 1.9783e-06 | 1.9783e-06 | 5.4802e-07 | 5.4802e-07 | 5.4802e-07 | 4.5688e-07 | 4.5688e-07 | 4.5688e-07 | 1.8098e-09 | 5.5983e-07 | -4.8346e-07 | -1.4791e-09 | -4.7306e-07 | 3.9637e-07 | 4.0584e-09 | -8.7562e-07 | -9.1748e-07 | -3.3965e-09 | 7.2589e-07 | 7.6838e-07 | -92.3101 | -92.2979 | -92.2979 | 87.1879 | 87.2025 | 87.2025 | 0.0081086 | 1.8964 | 1.8924 | 0.0081085 | 1.8964 | 1.8924 | -26.3445 | -149.7051 | 149.9153 | -26.3445 | -149.7051 | 149.9153
Line11_12_13 | 1.9775e-06 | 1.9775e-06 | 1.9775e-06 | 1.5828e-06 | 1.5829e-06 | 1.5829e-06 | 4.5668e-07 | 4.5669e-07 | 4.5669e-07 | 3.6554e-07 | 3.6555e-07 | 3.6555e-07 | 1.5082e-09 | 4.6652e-07 | -4.0288e-07 | -1.1775e-09 | -3.7976e-07 | 3.1579e-07 | 3.382e-09 | -7.2968e-07 | -7.6457e-07 | -2.7201e-09 | 5.7995e-07 | 6.1546e-07 | -92.3101 | -92.2979 | -92.2979 | 87.0624 | 87.0777 | 87.0777 | 0.0081085 | 1.8964 | 1.8924 | 0.0081084 | 1.8964 | 1.8924 | -26.3445 | -149.7051 | 149.9153 | -26.3444 | -149.7051 | 149.9153
Line12_13_15 | 1.1865e-06 | 1.1865e-06 | 1.1865e-06 | 0 | 0 | 0 | 2.7401e-07 | 2.7401e-07 | 2.7401e-07 | 0 | 0 | 0 | 9.049e-10 | 2.7991e-07 | -2.4173e-07 | -5.742e-10 | -1.9315e-07 | 1.5464e-07 | 2.0292e-09 | -4.3781e-07 | -4.5874e-07 | -1.3673e-09 | 2.8808e-07 | 3.0963e-07 | -92.3101 | -92.2979 | -92.2979 | 0 | 0 | 0 | 0.0081084 | 1.8964 | 1.8924 | 0.0081084 | 1.8964 | 1.8924 | -26.3444 | -149.7051 | 149.9153 | -26.3444 | -149.7051 | 149.9153
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0163e-10 | 9.3304e-08 | -8.0577e-08 | 2.9066e-11 | -6.5431e-09 | -6.515e-09 | 6.7639e-10 | -1.4594e-07 | -1.5291e-07 | -1.4513e-11 | -3.7903e-09 | 3.8065e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0081084 | 1.8964 | 1.8924 | 0.0081084 | 1.8964 | 1.8924 | -26.3444 | -149.7051 | 149.9153 | -26.3444 | -149.7051 | 149.9153
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0326e-10 | 1.8661e-07 | -1.6115e-07 | -2.7256e-10 | -9.9847e-08 | 7.4062e-08 | 1.3528e-09 | -2.9187e-07 | -3.0583e-07 | -6.909e-10 | 1.4215e-07 | 1.5672e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0081084 | 1.8964 | 1.8924 | 0.0081084 | 1.8964 | 1.8924 | -26.3444 | -149.7051 | 149.9153 | -26.3444 | -149.7051 | 149.9153
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0163e-10 | 9.3304e-08 | -8.0577e-08 | 2.9066e-11 | -6.5431e-09 | -6.515e-09 | 6.7638e-10 | -1.4594e-07 | -1.5291e-07 | -1.4513e-11 | -3.7903e-09 | 3.8065e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0081084 | 1.8964 | 1.8924 | 0.0081083 | 1.8964 | 1.8924 | -26.3444 | -149.7051 | 149.9153 | -26.3444 | -149.7051 | 149.9153
Line16_4_18 | 0.050249 | 0 | 0 | 0.050249 | 0 | 0 | 0.011605 | 0 | 0 | 0.011604 | 0 | 0 | 2.1041e-05 | 9.349e-08 | -8.0571e-08 | -1.6094e-14 | -6.5311e-09 | -6.498e-09 | 4.2083e-05 | -1.4598e-07 | -1.5304e-07 | 2.4332e-14 | -3.7838e-09 | 3.8029e-09 | -89.7796 | 0 | 0 | 90.2204 | 0 | 0 | 0.0040544 | 1.896 | 1.8916 | 0 | 1.8955 | 1.8908 | -26.3446 | -149.6846 | 149.9137 | 0 | -149.6642 | 149.9121
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0165e-10 | 9.3304e-08 | -8.0577e-08 | 2.9068e-11 | -6.5431e-09 | -6.515e-09 | 6.7642e-10 | -1.4594e-07 | -1.5291e-07 | -1.4514e-11 | -3.7903e-09 | 3.8065e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0081089 | 1.8964 | 1.8924 | 0.0081089 | 1.8964 | 1.8924 | -26.3446 | -149.7051 | 149.9153 | -26.3446 | -149.7051 | 149.9153
Line1_1_3 | 3.164e-06 | 3.164e-06 | 3.164e-06 | 2.7693e-06 | 2.7693e-06 | 2.7693e-06 | 7.3069e-07 | 7.307e-07 | 7.307e-07 | 6.3954e-07 | 6.3955e-07 | 6.3955e-07 | 2.4132e-09 | 7.4643e-07 | -6.4462e-07 | -2.0825e-09 | -6.5967e-07 | 5.5752e-07 | 5.4114e-09 | -1.1675e-06 | -1.2233e-06 | -4.7494e-09 | 1.0178e-06 | 1.0742e-06 | -92.3101 | -92.2979 | -92.2979 | 87.3312 | 87.3452 | 87.3452 | 0.0081089 | 1.8964 | 1.8924 | 0.0081087 | 1.8964 | 1.8924 | -26.3446 | -149.7051 | 149.9153 | -26.3446 | -149.7051 | 149.9153
Line2_1_4 | 0.05025 | 0 | 0 | 0.050249 | 0 | 0 | 0.011605 | 0 | 0 | 0.011605 | 0 | 0 | 4.2083e-05 | 1.8681e-07 | -1.6119e-07 | -2.1041e-05 | -1.0003e-07 | 7.4064e-08 | 8.4166e-05 | -2.9203e-07 | -3.0608e-07 | -4.2083e-05 | 1.422e-07 | 1.5684e-07 | -89.7796 | 0 | 0 | 90.2204 | 0 | 0 | 0.0081089 | 1.8964 | 1.8924 | 0.0040544 | 1.896 | 1.8916 | -26.3446 | -149.7051 | 149.9153 | -26.3446 | -149.6846 | 149.9137
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.033e-10 | 1.8661e-07 | -1.6115e-07 | -2.7258e-10 | -9.9847e-08 | 7.4062e-08 | 1.3529e-09 | -2.9187e-07 | -3.0583e-07 | -6.9094e-10 | 1.4215e-07 | 1.5672e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0081089 | 1.8964 | 1.8924 | 0.0081089 | 1.8964 | 1.8924 | -26.3446 | -149.7051 | 149.9153 | -26.3446 | -149.7051 | 149.9153
Line4_2_6 | 1.9775e-06 | 1.9775e-06 | 1.9775e-06 | 1.5828e-06 | 1.5829e-06 | 1.5829e-06 | 4.5668e-07 | 4.5669e-07 | 4.5669e-07 | 3.6554e-07 | 3.6555e-07 | 3.6555e-07 | 1.5082e-09 | 4.6652e-07 | -4.0288e-07 | -1.1775e-09 | -3.7976e-07 | 3.1579e-07 | 3.3821e-09 | -7.2968e-07 | -7.6457e-07 | -2.7202e-09 | 5.7995e-07 | 6.1546e-07 | -92.3101 | -92.2979 | -92.2979 | 87.0624 | 87.0777 | 87.0777 | 0.0081088 | 1.8964 | 1.8924 | 0.0081087 | 1.8964 | 1.8924 | -26.3446 | -149.7051 | 149.9153 | -26.3445 | -149.7051 | 149.9153
Line5_6_7 | 1.582e-06 | 1.582e-06 | 1.582e-06 | 1.1874e-06 | 1.1874e-06 | 1.1874e-06 | 3.6535e-07 | 3.6535e-07 | 3.6535e-07 | 2.7421e-07 | 2.7422e-07 | 2.7422e-07 | 1.2066e-09 | 3.7322e-07 | -3.2231e-07 | -8.7586e-10 | -2.8646e-07 | 2.3522e-07 | 2.7056e-09 | -5.8374e-07 | -6.1165e-07 | -2.0437e-09 | 4.3402e-07 | 4.6255e-07 | -92.3101 | -92.2979 | -92.2979 | 86.8534 | 86.8697 | 86.8697 | 0.0081087 | 1.8964 | 1.8924 | 0.0081086 | 1.8964 | 1.8924 | -26.3445 | -149.7051 | 149.9153 | -26.3445 | -149.7051 | 149.9153
Line6_7_8 | 1.1865e-06 | 1.1865e-06 | 1.1865e-06 | 0 | 0 | 0 | 2.7401e-07 | 2.7401e-07 | 2.7401e-07 | 0 | 0 | 0 | 9.0492e-10 | 2.7991e-07 | -2.4173e-07 | -5.7421e-10 | -1.9315e-07 | 1.5464e-07 | 2.0292e-09 | -4.3781e-07 | -4.5874e-07 | -1.3673e-09 | 2.8808e-07 | 3.0963e-07 | -92.3101 | -92.2979 | -92.2979 | 0 | 0 | 0 | 0.0081086 | 1.8964 | 1.8924 | 0.0081086 | 1.8964 | 1.8924 | -26.3445 | -149.7051 | 149.9153 | -26.3445 | -149.7051 | 149.9153
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0164e-10 | 9.3304e-08 | -8.0577e-08 | 2.9067e-11 | -6.5431e-09 | -6.515e-09 | 6.764e-10 | -1.4594e-07 | -1.5291e-07 | -1.4513e-11 | -3.7903e-09 | 3.8065e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0081086 | 1.8964 | 1.8924 | 0.0081086 | 1.8964 | 1.8924 | -26.3445 | -149.7051 | 149.9153 | -26.3445 | -149.7051 | 149.9153
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0164e-10 | 9.3304e-08 | -8.0577e-08 | 2.9067e-11 | -6.5431e-09 | -6.515e-09 | 6.764e-10 | -1.4594e-07 | -1.5291e-07 | -1.4513e-11 | -3.7903e-09 | 3.8065e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0081086 | 1.8964 | 1.8924 | 0.0081086 | 1.8964 | 1.8924 | -26.3445 | -149.7051 | 149.9153 | -26.3445 | -149.7051 | 149.9153
Line9_3_11 | 2.7685e-06 | 2.7685e-06 | 2.7685e-06 | 2.3738e-06 | 2.3738e-06 | 2.3738e-06 | 6.3936e-07 | 6.3936e-07 | 6.3936e-07 | 5.4821e-07 | 5.4821e-07 | 5.4821e-07 | 2.1115e-09 | 6.5313e-07 | -5.6404e-07 | -1.7808e-09 | -5.6637e-07 | 4.7695e-07 | 4.7349e-09 | -1.0216e-06 | -1.0704e-06 | -4.0729e-09 | 8.7183e-07 | 9.2129e-07 | -92.3101 | -92.2979 | -92.2979 | 87.2715 | 87.2857 | 87.2857 | 0.0081087 | 1.8964 | 1.8924 | 0.0081086 | 1.8964 | 1.8924 | -26.3446 | -149.7051 | 149.9153 | -26.3445 | -149.7051 | 149.9153

## LG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 1.019e-06 | 1.019e-06 | 1.019e-06 | 0 | 0 | 0 | 2.3532e-07 | 2.3532e-07 | 2.3532e-07 | 0 | 0 | 0 | 1.0531e-07 | 1.5001e-07 | -2.4093e-07 | -8.695e-08 | -1.2731e-07 | 1.9987e-07 | 1.1543e-07 | -3.0972e-07 | -1.3557e-07 | -9.6997e-08 | 2.5711e-07 | 1.1477e-07 | -66.0008 | -65.9892 | -65.9892 | 0 | 0 | 0 | 0.66399 | 1.4624 | 1.1748 | 0.66399 | 1.4624 | 1.1748 | -18.3763 | -130.1461 | 143.3771 | -18.3763 | -130.1461 | 143.3771
Line10_11_12 | 1.019e-06 | 1.019e-06 | 1.019e-06 | 0 | 0 | 0 | 2.3532e-07 | 2.3532e-07 | 2.3532e-07 | 0 | 0 | 0 | 1.0531e-07 | 1.5001e-07 | -2.4093e-07 | -8.695e-08 | -1.2731e-07 | 1.9987e-07 | 1.1543e-07 | -3.0972e-07 | -1.3557e-07 | -9.6997e-08 | 2.5711e-07 | 1.1477e-07 | -66.0008 | -65.9892 | -65.9892 | 0 | 0 | 0 | 0.66399 | 1.4624 | 1.1748 | 0.66399 | 1.4624 | 1.1748 | -18.3763 | -130.1461 | 143.3771 | -18.3763 | -130.1461 | 143.3771
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.7759e-08 | 1.2501e-07 | -2.0077e-07 | -6.9398e-08 | -1.0231e-07 | 1.5971e-07 | 9.6191e-08 | -2.581e-07 | -1.1298e-07 | -7.7759e-08 | 2.0549e-07 | 9.2175e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0.66399 | 1.4624 | 1.1748 | 0.66399 | 1.4624 | 1.1748 | -18.3763 | -130.1461 | 143.3771 | -18.3763 | -130.1461 | 143.3771
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2655e-08 | 7.5005e-08 | -1.2046e-07 | -3.4294e-08 | -5.2303e-08 | 7.9401e-08 | 5.7715e-08 | -1.5486e-07 | -6.7785e-08 | -3.9282e-08 | 1.0225e-07 | 4.6985e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0.66399 | 1.4624 | 1.1748 | 0.66399 | 1.4624 | 1.1748 | -18.3763 | -130.1461 | 143.3771 | -18.3763 | -130.1461 | 143.3771
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7552e-08 | 2.5002e-08 | -4.0155e-08 | 8.0944e-10 | -2.2992e-09 | -9.0875e-10 | 1.9238e-08 | -5.1619e-08 | -2.2595e-08 | -8.059e-10 | -9.918e-10 | 1.7946e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.66399 | 1.4624 | 1.1748 | 0.66399 | 1.4624 | 1.1748 | -18.3763 | -130.1461 | 143.3771 | -18.3763 | -130.1461 | 143.3771
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5104e-08 | 5.0003e-08 | -8.031e-08 | -1.6742e-08 | -2.7301e-08 | 3.9246e-08 | 3.8476e-08 | -1.0324e-07 | -4.519e-08 | -2.0044e-08 | 5.0628e-08 | 2.439e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0.66399 | 1.4624 | 1.1748 | 0.66399 | 1.4624 | 1.1748 | -18.3763 | -130.1461 | 143.3771 | -18.3763 | -130.1461 | 143.3771
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7552e-08 | 2.5002e-08 | -4.0155e-08 | 8.0944e-10 | -2.2992e-09 | -9.0875e-10 | 1.9238e-08 | -5.1619e-08 | -2.2595e-08 | -8.059e-10 | -9.918e-10 | 1.7946e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.66399 | 1.4624 | 1.1748 | 0.66399 | 1.4624 | 1.1748 | -18.3763 | -130.1461 | 143.3771 | -18.3763 | -130.1461 | 143.3771
Line16_4_18 | 0.021578 | 0 | 0 | 0.021578 | 0 | 0 | 0.0049832 | 0 | 0 | 0.0049832 | 0 | 0 | 0.0023319 | 2.5054e-08 | -4.0182e-08 | -0.002328 | -2.2958e-09 | -9.0527e-10 | 0.0023358 | -5.1651e-08 | -2.2622e-08 | -0.002328 | -9.8948e-10 | 1.7923e-09 | -63.4713 | 0 | 0 | 116.5287 | 0 | 0 | 0.66233 | 1.4622 | 1.1745 | 0.66068 | 1.4619 | 1.1742 | -18.4236 | -130.1357 | 143.367 | -18.4713 | -130.1252 | 143.3569
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7552e-08 | 2.5002e-08 | -4.0155e-08 | 8.0944e-10 | -2.2992e-09 | -9.0875e-10 | 1.9238e-08 | -5.1619e-08 | -2.2595e-08 | -8.059e-10 | -9.918e-10 | 1.7946e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.66399 | 1.4624 | 1.1748 | 0.66399 | 1.4624 | 1.1748 | -18.3763 | -130.1461 | 143.3771 | -18.3763 | -130.1461 | 143.3771
Line1_1_3 | 1.3586e-06 | 1.3586e-06 | 1.3586e-06 | 1.1892e-06 | 1.1892e-06 | 1.1892e-06 | 3.1376e-07 | 3.1377e-07 | 3.1377e-07 | 2.7462e-07 | 2.7463e-07 | 2.7463e-07 | 1.4041e-07 | 2.0001e-07 | -3.2124e-07 | -1.2205e-07 | -1.7731e-07 | 2.8018e-07 | 1.5391e-07 | -4.1296e-07 | -1.8076e-07 | -1.3547e-07 | 3.6034e-07 | 1.5996e-07 | -66.0008 | -65.9892 | -65.9892 | 113.6406 | 113.6539 | 113.6539 | 0.66399 | 1.4624 | 1.1748 | 0.66399 | 1.4624 | 1.1748 | -18.3763 | -130.1461 | 143.3771 | -18.3763 | -130.1461 | 143.3771
Line2_1_4 | 0.021578 | 0 | 0 | 0.021578 | 0 | 0 | 0.0049833 | 0 | 0 | 0.0049832 | 0 | 0 | 0.0023358 | 5.0065e-08 | -8.0354e-08 | -0.0023319 | -2.7351e-08 | 3.9275e-08 | 0.0023436 | -1.033e-07 | -4.5242e-08 | -0.0023358 | 5.066e-08 | 2.4416e-08 | -63.4713 | 0 | 0 | 116.5287 | 0 | 0 | 0.66399 | 1.4624 | 1.1748 | 0.66233 | 1.4622 | 1.1745 | -18.3763 | -130.1461 | 143.3771 | -18.4236 | -130.1357 | 143.367
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5104e-08 | 5.0003e-08 | -8.031e-08 | -1.6742e-08 | -2.7301e-08 | 3.9246e-08 | 3.8476e-08 | -1.0324e-07 | -4.519e-08 | -2.0044e-08 | 5.0628e-08 | 2.439e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0.66399 | 1.4624 | 1.1748 | 0.66399 | 1.4624 | 1.1748 | -18.3763 | -130.1461 | 143.3771 | -18.3763 | -130.1461 | 143.3771
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.7759e-08 | 1.2501e-07 | -2.0077e-07 | -6.9398e-08 | -1.0231e-07 | 1.5971e-07 | 9.6191e-08 | -2.581e-07 | -1.1298e-07 | -7.7759e-08 | 2.0549e-07 | 9.2175e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0.66399 | 1.4624 | 1.1748 | 0.66399 | 1.4624 | 1.1748 | -18.3763 | -130.1461 | 143.3771 | -18.3763 | -130.1461 | 143.3771
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.0207e-08 | 1.0001e-07 | -1.6062e-07 | -5.1846e-08 | -7.7304e-08 | 1.1956e-07 | 7.6953e-08 | -2.0648e-07 | -9.038e-08 | -5.8521e-08 | 1.5387e-07 | 6.958e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0.66399 | 1.4624 | 1.1748 | 0.66399 | 1.4624 | 1.1748 | -18.3763 | -130.1461 | 143.3771 | -18.3763 | -130.1461 | 143.3771
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2655e-08 | 7.5005e-08 | -1.2046e-07 | -3.4294e-08 | -5.2303e-08 | 7.9401e-08 | 5.7715e-08 | -1.5486e-07 | -6.7785e-08 | -3.9282e-08 | 1.0225e-07 | 4.6985e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0.66399 | 1.4624 | 1.1748 | 0.66399 | 1.4624 | 1.1748 | -18.3763 | -130.1461 | 143.3771 | -18.3763 | -130.1461 | 143.3771
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7552e-08 | 2.5002e-08 | -4.0155e-08 | 8.0944e-10 | -2.2992e-09 | -9.0875e-10 | 1.9238e-08 | -5.1619e-08 | -2.2595e-08 | -8.059e-10 | -9.918e-10 | 1.7946e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.66399 | 1.4624 | 1.1748 | 0.66399 | 1.4624 | 1.1748 | -18.3763 | -130.1461 | 143.3771 | -18.3763 | -130.1461 | 143.3771
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7552e-08 | 2.5002e-08 | -4.0155e-08 | 8.0944e-10 | -2.2992e-09 | -9.0875e-10 | 1.9238e-08 | -5.1619e-08 | -2.2595e-08 | -8.059e-10 | -9.918e-10 | 1.7946e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.66399 | 1.4624 | 1.1748 | 0.66399 | 1.4624 | 1.1748 | -18.3763 | -130.1461 | 143.3771 | -18.3763 | -130.1461 | 143.3771
Line9_3_11 | 1.1888e-06 | 1.1888e-06 | 1.1888e-06 | 1.0193e-06 | 1.0193e-06 | 1.0193e-06 | 2.7454e-07 | 2.7454e-07 | 2.7454e-07 | 2.354e-07 | 2.3541e-07 | 2.3541e-07 | 1.2286e-07 | 1.7501e-07 | -2.8108e-07 | -1.045e-07 | -1.5231e-07 | 2.4002e-07 | 1.3467e-07 | -3.6134e-07 | -1.5817e-07 | -1.1624e-07 | 3.0872e-07 | 1.3737e-07 | -66.0008 | -65.9892 | -65.9892 | 113.5809 | 113.5945 | 113.5945 | 0.66399 | 1.4624 | 1.1748 | 0.66399 | 1.4624 | 1.1748 | -18.3763 | -130.1461 | 143.3771 | -18.3763 | -130.1461 | 143.3771

## LG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 1.0675e-06 | 1.0675e-06 | 1.0675e-06 | 0 | 0 | 0 | 2.4652e-07 | 2.4652e-07 | 2.4652e-07 | 0 | 0 | 0 | 1.1556e-07 | 1.6464e-07 | -2.6441e-07 | -9.5414e-08 | -1.3972e-07 | 2.1934e-07 | 1.2667e-07 | -3.3988e-07 | -1.4878e-07 | -1.0644e-07 | 2.8215e-07 | 1.2595e-07 | -66.0034 | -65.9912 | -65.9912 | 0 | 0 | 0 | 0.69555 | 1.532 | 1.2307 | 0.69555 | 1.532 | 1.2307 | -18.3778 | -130.1458 | 143.3745 | -18.3778 | -130.1458 | 143.3745
Line10_11_12 | 1.0675e-06 | 1.0675e-06 | 1.0675e-06 | 0 | 0 | 0 | 2.4652e-07 | 2.4652e-07 | 2.4652e-07 | 0 | 0 | 0 | 1.1556e-07 | 1.6464e-07 | -2.6441e-07 | -9.5414e-08 | -1.3972e-07 | 2.1934e-07 | 1.2667e-07 | -3.3988e-07 | -1.4878e-07 | -1.0644e-07 | 2.8215e-07 | 1.2595e-07 | -66.0034 | -65.9912 | -65.9912 | 0 | 0 | 0 | 0.69555 | 1.532 | 1.2307 | 0.69555 | 1.532 | 1.2307 | -18.3778 | -130.1458 | 143.3745 | -18.3778 | -130.1458 | 143.3745
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.6303e-08 | 1.372e-07 | -2.2034e-07 | -7.6154e-08 | -1.1228e-07 | 1.7528e-07 | 1.0556e-07 | -2.8324e-07 | -1.2398e-07 | -8.5332e-08 | 2.255e-07 | 1.0116e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0.69555 | 1.532 | 1.2307 | 0.69555 | 1.532 | 1.2307 | -18.3778 | -130.1458 | 143.3745 | -18.3778 | -130.1458 | 143.3745
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.7782e-08 | 8.2319e-08 | -1.322e-07 | -3.7633e-08 | -5.7402e-08 | 8.7139e-08 | 6.3336e-08 | -1.6994e-07 | -7.4389e-08 | -4.3108e-08 | 1.1221e-07 | 5.1562e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0.69555 | 1.532 | 1.2307 | 0.69555 | 1.532 | 1.2307 | -18.3778 | -130.1458 | 143.3745 | -18.3778 | -130.1458 | 143.3745
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9261e-08 | 2.744e-08 | -4.4068e-08 | 8.8841e-10 | -2.523e-09 | -9.972e-10 | 2.1112e-08 | -5.6647e-08 | -2.4796e-08 | -8.8448e-10 | -1.0884e-09 | 1.9694e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.69555 | 1.532 | 1.2307 | 0.69555 | 1.532 | 1.2307 | -18.3778 | -130.1458 | 143.3745 | -18.3778 | -130.1458 | 143.3745
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8521e-08 | 5.4879e-08 | -8.8137e-08 | -1.8372e-08 | -2.9963e-08 | 4.3071e-08 | 4.2224e-08 | -1.1329e-07 | -4.9593e-08 | -2.1996e-08 | 5.5559e-08 | 2.6766e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0.69555 | 1.532 | 1.2307 | 0.69555 | 1.532 | 1.2307 | -18.3778 | -130.1458 | 143.3745 | -18.3778 | -130.1458 | 143.3745
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9261e-08 | 2.744e-08 | -4.4068e-08 | 8.8841e-10 | -2.523e-09 | -9.972e-10 | 2.1112e-08 | -5.6647e-08 | -2.4796e-08 | -8.8448e-10 | -1.0884e-09 | 1.9694e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.69555 | 1.532 | 1.2307 | 0.69555 | 1.532 | 1.2307 | -18.3778 | -130.1458 | 143.3745 | -18.3778 | -130.1458 | 143.3745
Line16_4_18 | 0.022604 | 0 | 0 | 0.022604 | 0 | 0 | 0.0052201 | 0 | 0 | 0.0052201 | 0 | 0 | 0.0025589 | 2.7497e-08 | -4.4098e-08 | -0.0025546 | -2.5192e-09 | -9.9339e-10 | 0.0025631 | -5.6682e-08 | -2.4826e-08 | -0.0025546 | -1.0859e-09 | 1.9668e-09 | -63.4728 | 0 | 0 | 116.5272 | 0 | 0 | 0.69382 | 1.5317 | 1.2304 | 0.69209 | 1.5315 | 1.2301 | -18.4251 | -130.1354 | 143.3643 | -18.4728 | -130.1249 | 143.3542
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9261e-08 | 2.744e-08 | -4.4068e-08 | 8.8841e-10 | -2.523e-09 | -9.972e-10 | 2.1112e-08 | -5.6647e-08 | -2.4796e-08 | -8.8449e-10 | -1.0884e-09 | 1.9694e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.69555 | 1.532 | 1.2307 | 0.69555 | 1.532 | 1.2307 | -18.3778 | -130.1458 | 143.3745 | -18.3778 | -130.1458 | 143.3745
Line1_1_3 | 1.4233e-06 | 1.4233e-06 | 1.4233e-06 | 1.2457e-06 | 1.2457e-06 | 1.2457e-06 | 3.2869e-07 | 3.2869e-07 | 3.2869e-07 | 2.8769e-07 | 2.8769e-07 | 2.8769e-07 | 1.5408e-07 | 2.1952e-07 | -3.5255e-07 | -1.3394e-07 | -1.946e-07 | 3.0748e-07 | 1.689e-07 | -4.5318e-07 | -1.9837e-07 | -1.4867e-07 | 3.9544e-07 | 1.7554e-07 | -66.0034 | -65.9912 | -65.9912 | 113.638 | 113.6519 | 113.6519 | 0.69555 | 1.532 | 1.2307 | 0.69555 | 1.532 | 1.2307 | -18.3778 | -130.1458 | 143.3745 | -18.3778 | -130.1458 | 143.3745
Line2_1_4 | 0.022604 | 0 | 0 | 0.022604 | 0 | 0 | 0.0052202 | 0 | 0 | 0.0052201 | 0 | 0 | 0.0025632 | 5.4947e-08 | -8.8185e-08 | -0.0025589 | -3.0018e-08 | 4.3103e-08 | 0.0025717 | -1.1336e-07 | -4.965e-08 | -0.0025631 | 5.5594e-08 | 2.6794e-08 | -63.4728 | 0 | 0 | 116.5272 | 0 | 0 | 0.69555 | 1.532 | 1.2307 | 0.69382 | 1.5317 | 1.2304 | -18.3778 | -130.1458 | 143.3745 | -18.4251 | -130.1354 | 143.3643
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8521e-08 | 5.4879e-08 | -8.8137e-08 | -1.8372e-08 | -2.9963e-08 | 4.3071e-08 | 4.2224e-08 | -1.1329e-07 | -4.9593e-08 | -2.1996e-08 | 5.5559e-08 | 2.6766e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0.69555 | 1.532 | 1.2307 | 0.69555 | 1.532 | 1.2307 | -18.3778 | -130.1458 | 143.3745 | -18.3778 | -130.1458 | 143.3745
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.6303e-08 | 1.372e-07 | -2.2034e-07 | -7.6154e-08 | -1.1228e-07 | 1.7528e-07 | 1.0556e-07 | -2.8323e-07 | -1.2398e-07 | -8.5332e-08 | 2.255e-07 | 1.0116e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0.69555 | 1.532 | 1.2307 | 0.69555 | 1.532 | 1.2307 | -18.3778 | -130.1458 | 143.3745 | -18.3778 | -130.1458 | 143.3745
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7042e-08 | 1.0976e-07 | -1.7627e-07 | -5.6893e-08 | -8.4842e-08 | 1.3121e-07 | 8.4448e-08 | -2.2659e-07 | -9.9186e-08 | -6.422e-08 | 1.6885e-07 | 7.6359e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0.69555 | 1.532 | 1.2307 | 0.69555 | 1.532 | 1.2307 | -18.3778 | -130.1458 | 143.3745 | -18.3778 | -130.1458 | 143.3745
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.7782e-08 | 8.2319e-08 | -1.322e-07 | -3.7633e-08 | -5.7402e-08 | 8.7139e-08 | 6.3336e-08 | -1.6994e-07 | -7.4389e-08 | -4.3108e-08 | 1.1221e-07 | 5.1562e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0.69555 | 1.532 | 1.2307 | 0.69555 | 1.532 | 1.2307 | -18.3778 | -130.1458 | 143.3745 | -18.3778 | -130.1458 | 143.3745
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9261e-08 | 2.744e-08 | -4.4068e-08 | 8.8841e-10 | -2.523e-09 | -9.972e-10 | 2.1112e-08 | -5.6647e-08 | -2.4796e-08 | -8.8448e-10 | -1.0884e-09 | 1.9694e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.69555 | 1.532 | 1.2307 | 0.69555 | 1.532 | 1.2307 | -18.3778 | -130.1458 | 143.3745 | -18.3778 | -130.1458 | 143.3745
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9261e-08 | 2.744e-08 | -4.4068e-08 | 8.8841e-10 | -2.523e-09 | -9.972e-10 | 2.1112e-08 | -5.6647e-08 | -2.4796e-08 | -8.8449e-10 | -1.0884e-09 | 1.9694e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.69555 | 1.532 | 1.2307 | 0.69555 | 1.532 | 1.2307 | -18.3778 | -130.1458 | 143.3745 | -18.3778 | -130.1458 | 143.3745
Line9_3_11 | 1.2454e-06 | 1.2454e-06 | 1.2454e-06 | 1.0678e-06 | 1.0678e-06 | 1.0678e-06 | 2.876e-07 | 2.8761e-07 | 2.8761e-07 | 2.466e-07 | 2.466e-07 | 2.466e-07 | 1.3482e-07 | 1.9208e-07 | -3.0848e-07 | -1.1467e-07 | -1.6716e-07 | 2.6341e-07 | 1.4778e-07 | -3.9653e-07 | -1.7357e-07 | -1.2756e-07 | 3.3879e-07 | 1.5075e-07 | -66.0034 | -65.9912 | -65.9912 | 113.5783 | 113.5925 | 113.5925 | 0.69555 | 1.532 | 1.2307 | 0.69555 | 1.532 | 1.2307 | -18.3778 | -130.1458 | 143.3745 | -18.3778 | -130.1458 | 143.3745

## LG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 2.0494e-06 | 2.0494e-06 | 2.0494e-06 | 1.7086e-06 | 1.7086e-06 | 1.7086e-06 | 4.7329e-07 | 4.733e-07 | 4.733e-07 | 3.9458e-07 | 3.9458e-07 | 3.9458e-07 | 2.7124e-09 | 4.1692e-07 | -3.6133e-07 | -2.2386e-09 | -3.5233e-07 | 2.9626e-07 | 3.0874e-09 | -6.5431e-07 | -6.8318e-07 | -2.5936e-09 | 5.4244e-07 | 5.7216e-07 | -92.1364 | -92.1243 | -92.1243 | 87.3616 | 87.3761 | 87.3761 | 0.0086831 | 1.6393 | 1.6329 | 0.008683 | 1.6393 | 1.6329 | -43.4369 | -149.6193 | 150.0018 | -43.4368 | -149.6193 | 150.0018
Line10_11_12 | 2.0494e-06 | 2.0494e-06 | 2.0494e-06 | 1.7086e-06 | 1.7086e-06 | 1.7086e-06 | 4.7329e-07 | 4.733e-07 | 4.733e-07 | 3.9458e-07 | 3.9458e-07 | 3.9458e-07 | 2.7123e-09 | 4.1692e-07 | -3.6133e-07 | -2.2385e-09 | -3.5233e-07 | 2.9626e-07 | 3.0873e-09 | -6.5431e-07 | -6.8318e-07 | -2.5935e-09 | 5.4244e-07 | 5.7216e-07 | -92.1364 | -92.1243 | -92.1243 | 87.3616 | 87.3761 | 87.3761 | 0.0086828 | 1.6393 | 1.6329 | 0.0086827 | 1.6393 | 1.6329 | -43.4368 | -149.6193 | 150.0018 | -43.4367 | -149.6193 | 150.0018
Line11_12_13 | 1.7079e-06 | 1.7079e-06 | 1.7079e-06 | 1.367e-06 | 1.367e-06 | 1.367e-06 | 3.9441e-07 | 3.9441e-07 | 3.9441e-07 | 3.157e-07 | 3.157e-07 | 3.157e-07 | 2.2602e-09 | 3.4744e-07 | -3.0111e-07 | -1.7865e-09 | -2.8284e-07 | 2.3603e-07 | 2.5727e-09 | -5.4526e-07 | -5.6932e-07 | -2.079e-09 | 4.3339e-07 | 4.583e-07 | -92.1364 | -92.1243 | -92.1243 | 87.2362 | 87.2513 | 87.2513 | 0.0086827 | 1.6393 | 1.6329 | 0.0086826 | 1.6393 | 1.6329 | -43.4367 | -149.6193 | 150.0018 | -43.4367 | -149.6193 | 150.0018
Line12_13_15 | 1.0247e-06 | 1.0247e-06 | 1.0247e-06 | 0 | 0 | 0 | 2.3665e-07 | 2.3665e-07 | 2.3665e-07 | 0 | 0 | 0 | 1.3561e-09 | 2.0846e-07 | -1.8066e-07 | -8.8239e-10 | -1.4386e-07 | 1.1559e-07 | 1.5436e-09 | -3.2716e-07 | -3.4159e-07 | -1.0499e-09 | 2.1528e-07 | 2.3057e-07 | -92.1364 | -92.1243 | -92.1243 | 0 | 0 | 0 | 0.0086826 | 1.6393 | 1.6329 | 0.0086826 | 1.6393 | 1.6329 | -43.4367 | -149.6193 | 150.0018 | -43.4367 | -149.6193 | 150.0018
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5204e-10 | 6.9487e-08 | -6.0221e-08 | 2.1685e-11 | -4.889e-09 | -4.8509e-09 | 5.1454e-10 | -1.0905e-07 | -1.1386e-07 | -2.0795e-11 | -2.8221e-09 | 2.8441e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0086826 | 1.6393 | 1.6329 | 0.0086826 | 1.6393 | 1.6329 | -43.4367 | -149.6193 | 150.0018 | -43.4367 | -149.6193 | 150.0018
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0408e-10 | 1.3897e-07 | -1.2044e-07 | -4.3035e-10 | -7.4376e-08 | 5.537e-08 | 1.0291e-09 | -2.181e-07 | -2.2773e-07 | -5.3533e-10 | 1.0623e-07 | 1.1671e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0086826 | 1.6393 | 1.6329 | 0.0086825 | 1.6393 | 1.6329 | -43.4367 | -149.6193 | 150.0018 | -43.4367 | -149.6193 | 150.0018
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5204e-10 | 6.9487e-08 | -6.0221e-08 | 2.1685e-11 | -4.889e-09 | -4.8509e-09 | 5.1454e-10 | -1.0905e-07 | -1.1386e-07 | -2.0794e-11 | -2.8221e-09 | 2.8441e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0086825 | 1.6393 | 1.6329 | 0.0086825 | 1.6393 | 1.6329 | -43.4367 | -149.6193 | 150.0018 | -43.4367 | -149.6193 | 150.0018
Line16_4_18 | 0.043398 | 0 | 0 | 0.043397 | 0 | 0 | 0.010022 | 0 | 0 | 0.010022 | 0 | 0 | 3.0133e-05 | 6.9701e-08 | -6.0145e-08 | 9.1835e-15 | -4.8818e-09 | -4.8365e-09 | 3.1389e-05 | -1.0906e-07 | -1.1399e-07 | 4.2197e-15 | -2.8162e-09 | 2.8424e-09 | -89.606 | 0 | 0 | 90.394 | 0 | 0 | 0.0043415 | 1.639 | 1.6321 | 0 | 1.6388 | 1.6312 | -43.4369 | -149.5902 | 150.0089 | 0 | -149.561 | 150.016
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5207e-10 | 6.9487e-08 | -6.0221e-08 | 2.1686e-11 | -4.889e-09 | -4.8509e-09 | 5.1457e-10 | -1.0905e-07 | -1.1386e-07 | -2.0796e-11 | -2.8221e-09 | 2.8441e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0086831 | 1.6393 | 1.6329 | 0.0086831 | 1.6393 | 1.6329 | -43.4369 | -149.6193 | 150.0018 | -43.4368 | -149.6193 | 150.0018
Line1_1_3 | 2.7326e-06 | 2.7326e-06 | 2.7326e-06 | 2.3917e-06 | 2.3917e-06 | 2.3917e-06 | 6.3106e-07 | 6.3106e-07 | 6.3106e-07 | 5.5234e-07 | 5.5234e-07 | 5.5234e-07 | 3.6165e-09 | 5.559e-07 | -4.8177e-07 | -3.1427e-09 | -4.913e-07 | 4.167e-07 | 4.1166e-09 | -8.7242e-07 | -9.1091e-07 | -3.6227e-09 | 7.6054e-07 | 7.9989e-07 | -92.1364 | -92.1243 | -92.1243 | 87.505 | 87.5188 | 87.5188 | 0.0086831 | 1.6393 | 1.6329 | 0.0086829 | 1.6393 | 1.6329 | -43.4369 | -149.6193 | 150.0018 | -43.4368 | -149.6193 | 150.0018
Line2_1_4 | 0.043398 | 0 | 0 | 0.043398 | 0 | 0 | 0.010022 | 0 | 0 | 0.010022 | 0 | 0 | 6.0267e-05 | 1.392e-07 | -1.204e-07 | -3.0133e-05 | -7.4587e-08 | 5.5301e-08 | 6.2779e-05 | -2.1819e-07 | -2.2796e-07 | -3.1389e-05 | 1.0624e-07 | 1.1683e-07 | -89.606 | 0 | 0 | 90.394 | 0 | 0 | 0.0086831 | 1.6393 | 1.6329 | 0.0043415 | 1.639 | 1.6321 | -43.4369 | -149.6193 | 150.0018 | -43.4369 | -149.5902 | 150.0089
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0414e-10 | 1.3897e-07 | -1.2044e-07 | -4.3038e-10 | -7.4376e-08 | 5.537e-08 | 1.0291e-09 | -2.181e-07 | -2.2773e-07 | -5.3536e-10 | 1.0623e-07 | 1.1671e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0086831 | 1.6393 | 1.6329 | 0.0086831 | 1.6393 | 1.6329 | -43.4369 | -149.6193 | 150.0018 | -43.4369 | -149.6193 | 150.0018
Line4_2_6 | 1.7079e-06 | 1.7079e-06 | 1.7079e-06 | 1.367e-06 | 1.367e-06 | 1.367e-06 | 3.9441e-07 | 3.9441e-07 | 3.9441e-07 | 3.157e-07 | 3.157e-07 | 3.157e-07 | 2.2603e-09 | 3.4744e-07 | -3.0111e-07 | -1.7865e-09 | -2.8284e-07 | 2.3603e-07 | 2.5728e-09 | -5.4526e-07 | -5.6932e-07 | -2.079e-09 | 4.3339e-07 | 4.583e-07 | -92.1364 | -92.1243 | -92.1243 | 87.2362 | 87.2513 | 87.2513 | 0.008683 | 1.6393 | 1.6329 | 0.0086829 | 1.6393 | 1.6329 | -43.4368 | -149.6193 | 150.0018 | -43.4368 | -149.6193 | 150.0018
Line5_6_7 | 1.3663e-06 | 1.3663e-06 | 1.3663e-06 | 1.0255e-06 | 1.0255e-06 | 1.0255e-06 | 3.1553e-07 | 3.1553e-07 | 3.1553e-07 | 2.3682e-07 | 2.3682e-07 | 2.3682e-07 | 1.8082e-09 | 2.7795e-07 | -2.4088e-07 | -1.3345e-09 | -2.1335e-07 | 1.7581e-07 | 2.0582e-09 | -4.3621e-07 | -4.5545e-07 | -1.5645e-09 | 3.2434e-07 | 3.4444e-07 | -92.1364 | -92.1243 | -92.1243 | 87.0272 | 87.0433 | 87.0433 | 0.0086829 | 1.6393 | 1.6329 | 0.0086828 | 1.6393 | 1.6329 | -43.4368 | -149.6193 | 150.0018 | -43.4368 | -149.6193 | 150.0018
Line6_7_8 | 1.0247e-06 | 1.0247e-06 | 1.0247e-06 | 0 | 0 | 0 | 2.3665e-07 | 2.3665e-07 | 2.3665e-07 | 0 | 0 | 0 | 1.3562e-09 | 2.0846e-07 | -1.8066e-07 | -8.8241e-10 | -1.4386e-07 | 1.1559e-07 | 1.5437e-09 | -3.2716e-07 | -3.4159e-07 | -1.0499e-09 | 2.1528e-07 | 2.3057e-07 | -92.1364 | -92.1243 | -92.1243 | 0 | 0 | 0 | 0.0086828 | 1.6393 | 1.6329 | 0.0086828 | 1.6393 | 1.6329 | -43.4368 | -149.6193 | 150.0018 | -43.4368 | -149.6193 | 150.0018
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5205e-10 | 6.9487e-08 | -6.0221e-08 | 2.1685e-11 | -4.889e-09 | -4.8509e-09 | 5.1455e-10 | -1.0905e-07 | -1.1386e-07 | -2.0795e-11 | -2.8221e-09 | 2.8441e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0086828 | 1.6393 | 1.6329 | 0.0086828 | 1.6393 | 1.6329 | -43.4368 | -149.6193 | 150.0018 | -43.4367 | -149.6193 | 150.0018
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5205e-10 | 6.9487e-08 | -6.0221e-08 | 2.1685e-11 | -4.889e-09 | -4.8509e-09 | 5.1455e-10 | -1.0905e-07 | -1.1386e-07 | -2.0795e-11 | -2.8221e-09 | 2.8441e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0086828 | 1.6393 | 1.6329 | 0.0086828 | 1.6393 | 1.6329 | -43.4368 | -149.6193 | 150.0018 | -43.4367 | -149.6193 | 150.0018
Line9_3_11 | 2.391e-06 | 2.391e-06 | 2.391e-06 | 2.0501e-06 | 2.0501e-06 | 2.0501e-06 | 5.5218e-07 | 5.5218e-07 | 5.5218e-07 | 4.7346e-07 | 4.7346e-07 | 4.7346e-07 | 3.1644e-09 | 4.8641e-07 | -4.2155e-07 | -2.6906e-09 | -4.2181e-07 | 3.5648e-07 | 3.6019e-09 | -7.6337e-07 | -7.9705e-07 | -3.1081e-09 | 6.5149e-07 | 6.8603e-07 | -92.1364 | -92.1243 | -92.1243 | 87.4452 | 87.4594 | 87.4594 | 0.0086829 | 1.6393 | 1.6329 | 0.0086828 | 1.6393 | 1.6329 | -43.4368 | -149.6193 | 150.0018 | -43.4368 | -149.6193 | 150.0018

## LG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 1.9416e-06 | 1.9416e-06 | 1.9416e-06 | 1.6186e-06 | 1.6187e-06 | 1.6187e-06 | 4.4838e-07 | 4.4839e-07 | 4.4839e-07 | 3.7381e-07 | 3.7381e-07 | 3.7381e-07 | 2.4344e-09 | 3.7419e-07 | -3.2429e-07 | -2.0092e-09 | -3.1621e-07 | 2.6589e-07 | 2.771e-09 | -5.8725e-07 | -6.1316e-07 | -2.3278e-09 | 4.8684e-07 | 5.1352e-07 | -92.1364 | -92.1243 | -92.1243 | 87.3616 | 87.3761 | 87.3761 | 0.0082261 | 1.553 | 1.547 | 0.008226 | 1.553 | 1.547 | -43.4369 | -149.6193 | 150.0018 | -43.4368 | -149.6193 | 150.0018
Line10_11_12 | 1.9416e-06 | 1.9416e-06 | 1.9416e-06 | 1.6186e-06 | 1.6187e-06 | 1.6187e-06 | 4.4838e-07 | 4.4839e-07 | 4.4839e-07 | 3.7381e-07 | 3.7381e-07 | 3.7381e-07 | 2.4343e-09 | 3.7419e-07 | -3.2429e-07 | -2.0091e-09 | -3.1622e-07 | 2.6589e-07 | 2.7709e-09 | -5.8725e-07 | -6.1316e-07 | -2.3277e-09 | 4.8684e-07 | 5.1352e-07 | -92.1364 | -92.1243 | -92.1243 | 87.3616 | 87.3761 | 87.3761 | 0.0082258 | 1.553 | 1.547 | 0.0082257 | 1.553 | 1.547 | -43.4368 | -149.6193 | 150.0018 | -43.4367 | -149.6193 | 150.0018
Line11_12_13 | 1.618e-06 | 1.618e-06 | 1.618e-06 | 1.2951e-06 | 1.2951e-06 | 1.2951e-06 | 3.7365e-07 | 3.7366e-07 | 3.7366e-07 | 2.9908e-07 | 2.9909e-07 | 2.9909e-07 | 2.0286e-09 | 3.1183e-07 | -2.7024e-07 | -1.6034e-09 | -2.5385e-07 | 2.1184e-07 | 2.309e-09 | -4.8938e-07 | -5.1097e-07 | -1.8659e-09 | 3.8897e-07 | 4.1133e-07 | -92.1364 | -92.1243 | -92.1243 | 87.2362 | 87.2513 | 87.2513 | 0.0082257 | 1.553 | 1.547 | 0.0082256 | 1.553 | 1.547 | -43.4367 | -149.6193 | 150.0018 | -43.4367 | -149.6193 | 150.0018
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2171e-09 | 1.871e-07 | -1.6215e-07 | -7.9195e-10 | -1.2912e-07 | 1.0374e-07 | 1.3854e-09 | -2.9363e-07 | -3.0658e-07 | -9.4227e-10 | 1.9322e-07 | 2.0694e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0082256 | 1.553 | 1.547 | 0.0082256 | 1.553 | 1.547 | -43.4367 | -149.6193 | 150.0018 | -43.4367 | -149.6193 | 150.0018
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0571e-10 | 6.2365e-08 | -5.4049e-08 | 1.9462e-11 | -4.3879e-09 | -4.3537e-09 | 4.618e-10 | -9.7875e-08 | -1.0219e-07 | -1.8663e-11 | -2.5329e-09 | 2.5526e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0082256 | 1.553 | 1.547 | 0.0082256 | 1.553 | 1.547 | -43.4367 | -149.6193 | 150.0018 | -43.4367 | -149.6193 | 150.0018
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.1141e-10 | 1.2473e-07 | -1.081e-07 | -3.8624e-10 | -6.6753e-08 | 4.9695e-08 | 9.236e-10 | -1.9575e-07 | -2.0439e-07 | -4.8046e-10 | 9.5342e-08 | 1.0475e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0082256 | 1.553 | 1.547 | 0.0082255 | 1.553 | 1.547 | -43.4367 | -149.6193 | 150.0018 | -43.4367 | -149.6193 | 150.0018
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0571e-10 | 6.2365e-08 | -5.4049e-08 | 1.9462e-11 | -4.3879e-09 | -4.3537e-09 | 4.618e-10 | -9.7875e-08 | -1.0219e-07 | -1.8663e-11 | -2.5329e-09 | 2.5526e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0082255 | 1.553 | 1.547 | 0.0082255 | 1.553 | 1.547 | -43.4367 | -149.6193 | 150.0018 | -43.4367 | -149.6193 | 150.0018
Line16_4_18 | 0.041113 | 0 | 0 | 0.041113 | 0 | 0 | 0.0094947 | 0 | 0 | 0.0094947 | 0 | 0 | 2.7045e-05 | 6.2558e-08 | -5.398e-08 | 8.2426e-15 | -4.3814e-09 | -4.3408e-09 | 2.8172e-05 | -9.7883e-08 | -1.023e-07 | 3.7825e-15 | -2.5276e-09 | 2.5511e-09 | -89.606 | 0 | 0 | 90.394 | 0 | 0 | 0.004113 | 1.5528 | 1.5462 | 0 | 1.5525 | 1.5454 | -43.4369 | -149.5902 | 150.0089 | 0 | -149.561 | 150.016
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0573e-10 | 6.2365e-08 | -5.4049e-08 | 1.9463e-11 | -4.3879e-09 | -4.3537e-09 | 4.6183e-10 | -9.7875e-08 | -1.0219e-07 | -1.8664e-11 | -2.5329e-09 | 2.5526e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0082261 | 1.553 | 1.547 | 0.0082261 | 1.553 | 1.547 | -43.4369 | -149.6193 | 150.0018 | -43.4368 | -149.6193 | 150.0018
Line1_1_3 | 2.5887e-06 | 2.5888e-06 | 2.5888e-06 | 2.2658e-06 | 2.2658e-06 | 2.2658e-06 | 5.9784e-07 | 5.9785e-07 | 5.9785e-07 | 5.2327e-07 | 5.2327e-07 | 5.2327e-07 | 3.2459e-09 | 4.9892e-07 | -4.3239e-07 | -2.8206e-09 | -4.4095e-07 | 3.7399e-07 | 3.6946e-09 | -7.83e-07 | -8.1755e-07 | -3.2514e-09 | 6.8259e-07 | 7.1791e-07 | -92.1364 | -92.1243 | -92.1243 | 87.505 | 87.5188 | 87.5188 | 0.0082261 | 1.553 | 1.547 | 0.0082259 | 1.553 | 1.547 | -43.4369 | -149.6193 | 150.0018 | -43.4368 | -149.6193 | 150.0018
Line2_1_4 | 0.041114 | 0 | 0 | 0.041113 | 0 | 0 | 0.0094948 | 0 | 0 | 0.0094947 | 0 | 0 | 5.409e-05 | 1.2493e-07 | -1.0806e-07 | -2.7045e-05 | -6.6942e-08 | 4.9633e-08 | 5.6344e-05 | -1.9582e-07 | -2.046e-07 | -2.8172e-05 | 9.5353e-08 | 1.0486e-07 | -89.606 | 0 | 0 | 90.394 | 0 | 0 | 0.0082261 | 1.553 | 1.547 | 0.004113 | 1.5528 | 1.5462 | -43.4369 | -149.6193 | 150.0018 | -43.4369 | -149.5902 | 150.0089
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.1147e-10 | 1.2473e-07 | -1.081e-07 | -3.8627e-10 | -6.6753e-08 | 4.9695e-08 | 9.2366e-10 | -1.9575e-07 | -2.0439e-07 | -4.8049e-10 | 9.5342e-08 | 1.0475e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0082261 | 1.553 | 1.547 | 0.0082261 | 1.553 | 1.547 | -43.4369 | -149.6193 | 150.0018 | -43.4369 | -149.6193 | 150.0018
Line4_2_6 | 1.618e-06 | 1.618e-06 | 1.618e-06 | 1.2951e-06 | 1.2951e-06 | 1.2951e-06 | 3.7365e-07 | 3.7366e-07 | 3.7366e-07 | 2.9908e-07 | 2.9909e-07 | 2.9909e-07 | 2.0286e-09 | 3.1183e-07 | -2.7024e-07 | -1.6034e-09 | -2.5385e-07 | 2.1184e-07 | 2.3091e-09 | -4.8938e-07 | -5.1097e-07 | -1.8659e-09 | 3.8897e-07 | 4.1133e-07 | -92.1364 | -92.1243 | -92.1243 | 87.2362 | 87.2513 | 87.2513 | 0.008226 | 1.553 | 1.547 | 0.0082259 | 1.553 | 1.547 | -43.4368 | -149.6193 | 150.0018 | -43.4368 | -149.6193 | 150.0018
Line5_6_7 | 1.2944e-06 | 1.2944e-06 | 1.2944e-06 | 0 | 0 | 0 | 2.9892e-07 | 2.9892e-07 | 2.9892e-07 | 0 | 0 | 0 | 1.6229e-09 | 2.4946e-07 | -2.162e-07 | -1.1977e-09 | -1.9148e-07 | 1.5779e-07 | 1.8473e-09 | -3.915e-07 | -4.0877e-07 | -1.4041e-09 | 2.9109e-07 | 3.0913e-07 | -92.1364 | -92.1243 | -92.1243 | 0 | 0 | 0 | 0.0082259 | 1.553 | 1.547 | 0.0082258 | 1.553 | 1.547 | -43.4368 | -149.6193 | 150.0018 | -43.4368 | -149.6193 | 150.0018
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2172e-09 | 1.871e-07 | -1.6215e-07 | -7.9197e-10 | -1.2912e-07 | 1.0374e-07 | 1.3854e-09 | -2.9363e-07 | -3.0658e-07 | -9.4229e-10 | 1.9322e-07 | 2.0694e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0082258 | 1.553 | 1.547 | 0.0082258 | 1.553 | 1.547 | -43.4368 | -149.6193 | 150.0018 | -43.4368 | -149.6193 | 150.0018
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0572e-10 | 6.2365e-08 | -5.4049e-08 | 1.9463e-11 | -4.3879e-09 | -4.3537e-09 | 4.6181e-10 | -9.7875e-08 | -1.0219e-07 | -1.8664e-11 | -2.5329e-09 | 2.5526e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0082258 | 1.553 | 1.547 | 0.0082258 | 1.553 | 1.547 | -43.4368 | -149.6193 | 150.0018 | -43.4367 | -149.6193 | 150.0018
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0572e-10 | 6.2365e-08 | -5.4049e-08 | 1.9463e-11 | -4.3879e-09 | -4.3537e-09 | 4.6181e-10 | -9.7875e-08 | -1.0219e-07 | -1.8664e-11 | -2.5329e-09 | 2.5526e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0082258 | 1.553 | 1.547 | 0.0082258 | 1.553 | 1.547 | -43.4368 | -149.6193 | 150.0018 | -43.4367 | -149.6193 | 150.0018
Line9_3_11 | 2.2652e-06 | 2.2652e-06 | 2.2652e-06 | 1.9422e-06 | 1.9422e-06 | 1.9422e-06 | 5.2311e-07 | 5.2312e-07 | 5.2312e-07 | 4.4854e-07 | 4.4854e-07 | 4.4854e-07 | 2.8401e-09 | 4.3656e-07 | -3.7834e-07 | -2.4149e-09 | -3.7858e-07 | 3.1994e-07 | 3.2328e-09 | -6.8513e-07 | -7.1535e-07 | -2.7896e-09 | 5.8472e-07 | 6.1571e-07 | -92.1364 | -92.1243 | -92.1243 | 87.4452 | 87.4594 | 87.4594 | 0.0082259 | 1.553 | 1.547 | 0.0082258 | 1.553 | 1.547 | -43.4368 | -149.6193 | 150.0018 | -43.4368 | -149.6193 | 150.0018

## LG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.6367e-08 | 1.2252e-07 | -1.9712e-07 | -7.1311e-08 | -1.0398e-07 | 1.6353e-07 | 9.4379e-08 | -2.5345e-07 | -1.106e-07 | -7.931e-08 | 2.104e-07 | 9.3637e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0.60126 | 1.323 | 1.0623 | 0.60126 | 1.323 | 1.0623 | -18.395 | -130.1209 | 143.3751 | -18.395 | -130.1209 | 143.3751
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.6367e-08 | 1.2252e-07 | -1.9712e-07 | -7.1311e-08 | -1.0398e-07 | 1.6353e-07 | 9.4379e-08 | -2.5345e-07 | -1.106e-07 | -7.931e-08 | 2.104e-07 | 9.3637e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0.60126 | 1.323 | 1.0623 | 0.60126 | 1.323 | 1.0623 | -18.395 | -130.1209 | 143.3751 | -18.395 | -130.1209 | 143.3751
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.1973e-08 | 1.021e-07 | -1.6427e-07 | -5.6916e-08 | -8.3562e-08 | 1.3067e-07 | 7.8649e-08 | -2.1121e-07 | -9.2169e-08 | -6.358e-08 | 1.6815e-07 | 7.5203e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0.60126 | 1.323 | 1.0623 | 0.60126 | 1.323 | 1.0623 | -18.395 | -130.1209 | 143.3751 | -18.395 | -130.1209 | 143.3751
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3184e-08 | 6.1261e-08 | -9.8562e-08 | -2.8127e-08 | -4.2722e-08 | 6.4967e-08 | 4.7189e-08 | -1.2672e-07 | -5.5301e-08 | -3.2121e-08 | 8.3672e-08 | 3.8336e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0.60126 | 1.323 | 1.0623 | 0.60126 | 1.323 | 1.0623 | -18.395 | -130.1209 | 143.3751 | -18.395 | -130.1209 | 143.3751
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4395e-08 | 2.042e-08 | -3.2854e-08 | 6.6182e-10 | -1.8813e-09 | -7.4116e-10 | 1.573e-08 | -4.2241e-08 | -1.8434e-08 | -6.6092e-10 | -8.0985e-10 | 1.4681e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.60126 | 1.323 | 1.0623 | 0.60126 | 1.323 | 1.0623 | -18.395 | -130.1209 | 143.3751 | -18.395 | -130.1209 | 143.3751
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8789e-08 | 4.084e-08 | -6.5708e-08 | -1.3733e-08 | -2.2302e-08 | 3.2113e-08 | 3.146e-08 | -8.4482e-08 | -3.6868e-08 | -1.6391e-08 | 4.1431e-08 | 1.9902e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0.60126 | 1.323 | 1.0623 | 0.60126 | 1.323 | 1.0623 | -18.395 | -130.1209 | 143.3751 | -18.395 | -130.1209 | 143.3751
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4395e-08 | 2.042e-08 | -3.2854e-08 | 6.6182e-10 | -1.8813e-09 | -7.4116e-10 | 1.573e-08 | -4.2241e-08 | -1.8434e-08 | -6.6092e-10 | -8.0985e-10 | 1.4681e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.60126 | 1.323 | 1.0623 | 0.60126 | 1.323 | 1.0623 | -18.395 | -130.1209 | 143.3751 | -18.395 | -130.121 | 143.3751
Line16_4_18 | 0.01951 | 0 | 0 | 0.01951 | 0 | 0 | 0.0045056 | 0 | 0 | 0.0045055 | 0 | 0 | 0.0019092 | 2.0488e-08 | -3.2865e-08 | -0.0019031 | -1.879e-09 | -7.3742e-10 | 0.0019095 | -4.2259e-08 | -1.8472e-08 | -0.0019031 | -8.0719e-10 | 1.4663e-09 | -63.4026 | 0 | 0 | 116.5974 | 0 | 0 | 0.59931 | 1.3229 | 1.0619 | 0.59736 | 1.3227 | 1.0616 | -18.3988 | -130.1054 | 143.3681 | -18.4026 | -130.0898 | 143.3611
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4395e-08 | 2.042e-08 | -3.2854e-08 | 6.6182e-10 | -1.8813e-09 | -7.4116e-10 | 1.573e-08 | -4.2241e-08 | -1.8434e-08 | -6.6092e-10 | -8.0985e-10 | 1.4681e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.60126 | 1.323 | 1.0623 | 0.60126 | 1.323 | 1.0623 | -18.395 | -130.1209 | 143.3751 | -18.395 | -130.1209 | 143.3751
Line1_1_3 | 1.2284e-06 | 1.2285e-06 | 1.2285e-06 | 1.0752e-06 | 1.0752e-06 | 1.0752e-06 | 2.837e-07 | 2.837e-07 | 2.837e-07 | 2.4831e-07 | 2.4831e-07 | 2.4831e-07 | 1.1516e-07 | 1.6336e-07 | -2.6283e-07 | -1.001e-07 | -1.4482e-07 | 2.2924e-07 | 1.2584e-07 | -3.3793e-07 | -1.4747e-07 | -1.1077e-07 | 2.9488e-07 | 1.305e-07 | -65.9331 | -65.921 | -65.921 | 113.7083 | 113.7222 | 113.7222 | 0.60126 | 1.323 | 1.0623 | 0.60126 | 1.323 | 1.0623 | -18.395 | -130.1209 | 143.3751 | -18.395 | -130.1209 | 143.3751
Line2_1_4 | 0.01951 | 0 | 0 | 0.01951 | 0 | 0 | 0.0045056 | 0 | 0 | 0.0045056 | 0 | 0 | 0.0019153 | 4.0918e-08 | -6.5735e-08 | -0.0019092 | -2.2368e-08 | 3.2126e-08 | 0.0019158 | -8.4521e-08 | -3.6932e-08 | -0.0019095 | 4.1451e-08 | 1.9939e-08 | -63.4027 | 0 | 0 | 116.5973 | 0 | 0 | 0.60126 | 1.323 | 1.0623 | 0.59931 | 1.3229 | 1.0619 | -18.395 | -130.1209 | 143.3751 | -18.3988 | -130.1054 | 143.3681
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8789e-08 | 4.084e-08 | -6.5708e-08 | -1.3733e-08 | -2.2301e-08 | 3.2113e-08 | 3.146e-08 | -8.4482e-08 | -3.6868e-08 | -1.6391e-08 | 4.1431e-08 | 1.9902e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0.60126 | 1.323 | 1.0623 | 0.60126 | 1.323 | 1.0623 | -18.395 | -130.1209 | 143.3751 | -18.395 | -130.1209 | 143.3751
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.1973e-08 | 1.021e-07 | -1.6427e-07 | -5.6916e-08 | -8.3562e-08 | 1.3067e-07 | 7.8649e-08 | -2.1121e-07 | -9.2169e-08 | -6.358e-08 | 1.6815e-07 | 7.5203e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0.60126 | 1.323 | 1.0623 | 0.60126 | 1.323 | 1.0623 | -18.395 | -130.1209 | 143.3751 | -18.395 | -130.1209 | 143.3751
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.7578e-08 | 8.1681e-08 | -1.3142e-07 | -4.2522e-08 | -6.3142e-08 | 9.7821e-08 | 6.2919e-08 | -1.6896e-07 | -7.3735e-08 | -4.785e-08 | 1.2591e-07 | 5.677e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0.60126 | 1.323 | 1.0623 | 0.60126 | 1.323 | 1.0623 | -18.395 | -130.1209 | 143.3751 | -18.395 | -130.1209 | 143.3751
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3184e-08 | 6.1261e-08 | -9.8562e-08 | -2.8127e-08 | -4.2722e-08 | 6.4967e-08 | 4.7189e-08 | -1.2672e-07 | -5.5301e-08 | -3.2121e-08 | 8.3672e-08 | 3.8336e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0.60126 | 1.323 | 1.0623 | 0.60126 | 1.323 | 1.0623 | -18.395 | -130.1209 | 143.3751 | -18.395 | -130.1209 | 143.3751
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4395e-08 | 2.042e-08 | -3.2854e-08 | 6.6182e-10 | -1.8813e-09 | -7.4116e-10 | 1.573e-08 | -4.2241e-08 | -1.8434e-08 | -6.6092e-10 | -8.0985e-10 | 1.4681e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.60126 | 1.323 | 1.0623 | 0.60126 | 1.323 | 1.0623 | -18.395 | -130.1209 | 143.3751 | -18.395 | -130.1209 | 143.3751
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4395e-08 | 2.042e-08 | -3.2854e-08 | 6.6182e-10 | -1.8813e-09 | -7.4116e-10 | 1.573e-08 | -4.2241e-08 | -1.8434e-08 | -6.6092e-10 | -8.0985e-10 | 1.4681e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.60126 | 1.323 | 1.0623 | 0.60126 | 1.323 | 1.0623 | -18.395 | -130.1209 | 143.3751 | -18.395 | -130.1209 | 143.3751
Line9_3_11 | 1.0749e-06 | 1.0749e-06 | 1.0749e-06 | 0 | 0 | 0 | 2.4824e-07 | 2.4824e-07 | 2.4824e-07 | 0 | 0 | 0 | 1.0076e-07 | 1.4294e-07 | -2.2998e-07 | -8.5705e-08 | -1.244e-07 | 1.9638e-07 | 1.1011e-07 | -2.9569e-07 | -1.2904e-07 | -9.504e-08 | 2.5264e-07 | 1.1207e-07 | -65.9331 | -65.921 | -65.921 | 0 | 0 | 0 | 0.60126 | 1.323 | 1.0623 | 0.60126 | 1.323 | 1.0623 | -18.395 | -130.1209 | 143.3751 | -18.395 | -130.1209 | 143.3751

## LG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7515e-08 | 1.0996e-07 | -1.7692e-07 | -6.4002e-08 | -9.3325e-08 | 1.4677e-07 | 8.4706e-08 | -2.2747e-07 | -9.9267e-08 | -7.1181e-08 | 1.8883e-07 | 8.404e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56961 | 1.2534 | 1.0064 | 0.56961 | 1.2534 | 1.0064 | -18.395 | -130.1209 | 143.3751 | -18.395 | -130.1209 | 143.3751
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7515e-08 | 1.0996e-07 | -1.7692e-07 | -6.4002e-08 | -9.3325e-08 | 1.4677e-07 | 8.4706e-08 | -2.2747e-07 | -9.9267e-08 | -7.1181e-08 | 1.8883e-07 | 8.404e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56961 | 1.2534 | 1.0064 | 0.56961 | 1.2534 | 1.0064 | -18.395 | -130.1209 | 143.3751 | -18.395 | -130.1209 | 143.3751
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.4596e-08 | 9.1636e-08 | -1.4743e-07 | -5.1083e-08 | -7.4998e-08 | 1.1728e-07 | 7.0588e-08 | -1.8956e-07 | -8.2722e-08 | -5.7064e-08 | 1.5092e-07 | 6.7496e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56961 | 1.2534 | 1.0064 | 0.56961 | 1.2534 | 1.0064 | -18.395 | -130.1209 | 143.3751 | -18.395 | -130.1209 | 143.3751
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8758e-08 | 5.4982e-08 | -8.846e-08 | -2.5244e-08 | -3.8343e-08 | 5.8308e-08 | 4.2353e-08 | -1.1374e-07 | -4.9633e-08 | -2.8828e-08 | 7.5097e-08 | 3.4407e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56961 | 1.2534 | 1.0064 | 0.56961 | 1.2534 | 1.0064 | -18.395 | -130.1209 | 143.3751 | -18.395 | -130.1209 | 143.3751
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2919e-08 | 1.8327e-08 | -2.9487e-08 | 5.9399e-10 | -1.6885e-09 | -6.652e-10 | 1.4118e-08 | -3.7912e-08 | -1.6544e-08 | -5.9318e-10 | -7.2684e-10 | 1.3176e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56961 | 1.2534 | 1.0064 | 0.56961 | 1.2534 | 1.0064 | -18.395 | -130.1209 | 143.3751 | -18.395 | -130.1209 | 143.3751
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5838e-08 | 3.6655e-08 | -5.8973e-08 | -1.2325e-08 | -2.0016e-08 | 2.8822e-08 | 2.8235e-08 | -7.5823e-08 | -3.3089e-08 | -1.4711e-08 | 3.7185e-08 | 1.7862e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56961 | 1.2534 | 1.0064 | 0.56961 | 1.2534 | 1.0064 | -18.395 | -130.1209 | 143.3751 | -18.395 | -130.1209 | 143.3751
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2919e-08 | 1.8327e-08 | -2.9487e-08 | 5.9399e-10 | -1.6885e-09 | -6.652e-10 | 1.4118e-08 | -3.7912e-08 | -1.6544e-08 | -5.9318e-10 | -7.2684e-10 | 1.3176e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56961 | 1.2534 | 1.0064 | 0.56961 | 1.2534 | 1.0064 | -18.395 | -130.1209 | 143.3751 | -18.395 | -130.121 | 143.3751
Line16_4_18 | 0.018483 | 0 | 0 | 0.018483 | 0 | 0 | 0.0042684 | 0 | 0 | 0.0042684 | 0 | 0 | 0.0017135 | 1.8388e-08 | -2.9497e-08 | -0.0017081 | -1.6864e-09 | -6.6184e-10 | 0.0017138 | -3.7928e-08 | -1.6578e-08 | -0.0017081 | -7.2446e-10 | 1.316e-09 | -63.4026 | 0 | 0 | 116.5974 | 0 | 0 | 0.56777 | 1.2533 | 1.006 | 0.56592 | 1.2531 | 1.0057 | -18.3988 | -130.1054 | 143.3681 | -18.4026 | -130.0898 | 143.3611
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2919e-08 | 1.8327e-08 | -2.9487e-08 | 5.9399e-10 | -1.6885e-09 | -6.6519e-10 | 1.4118e-08 | -3.7912e-08 | -1.6544e-08 | -5.9318e-10 | -7.2684e-10 | 1.3176e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56961 | 1.2534 | 1.0064 | 0.56961 | 1.2534 | 1.0064 | -18.395 | -130.1209 | 143.3751 | -18.395 | -130.1209 | 143.3751
Line1_1_3 | 1.1638e-06 | 1.1638e-06 | 1.1638e-06 | 1.0186e-06 | 1.0186e-06 | 1.0186e-06 | 2.6877e-07 | 2.6877e-07 | 2.6877e-07 | 2.3524e-07 | 2.3524e-07 | 2.3524e-07 | 1.0335e-07 | 1.4662e-07 | -2.3589e-07 | -8.984e-08 | -1.2998e-07 | 2.0574e-07 | 1.1294e-07 | -3.0329e-07 | -1.3236e-07 | -9.9416e-08 | 2.6466e-07 | 1.1713e-07 | -65.9331 | -65.921 | -65.921 | 113.7083 | 113.7222 | 113.7222 | 0.56961 | 1.2534 | 1.0064 | 0.56961 | 1.2534 | 1.0064 | -18.395 | -130.1209 | 143.3751 | -18.395 | -130.1209 | 143.3751
Line2_1_4 | 0.018483 | 0 | 0 | 0.018483 | 0 | 0 | 0.0042685 | 0 | 0 | 0.0042684 | 0 | 0 | 0.001719 | 3.6724e-08 | -5.8998e-08 | -0.0017135 | -2.0075e-08 | 2.8833e-08 | 0.0017195 | -7.5858e-08 | -3.3146e-08 | -0.0017138 | 3.7203e-08 | 1.7895e-08 | -63.4027 | 0 | 0 | 116.5973 | 0 | 0 | 0.56961 | 1.2534 | 1.0064 | 0.56777 | 1.2533 | 1.006 | -18.395 | -130.1209 | 143.3751 | -18.3988 | -130.1054 | 143.3681
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5838e-08 | 3.6654e-08 | -5.8973e-08 | -1.2325e-08 | -2.0016e-08 | 2.8822e-08 | 2.8235e-08 | -7.5823e-08 | -3.3089e-08 | -1.4711e-08 | 3.7185e-08 | 1.7862e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56961 | 1.2534 | 1.0064 | 0.56961 | 1.2534 | 1.0064 | -18.395 | -130.1209 | 143.3751 | -18.395 | -130.1209 | 143.3751
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.4596e-08 | 9.1636e-08 | -1.4743e-07 | -5.1083e-08 | -7.4997e-08 | 1.1728e-07 | 7.0588e-08 | -1.8956e-07 | -8.2722e-08 | -5.7064e-08 | 1.5092e-07 | 6.7496e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56961 | 1.2534 | 1.0064 | 0.56961 | 1.2534 | 1.0064 | -18.395 | -130.1209 | 143.3751 | -18.395 | -130.1209 | 143.3751
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.1677e-08 | 7.3309e-08 | -1.1795e-07 | -3.8164e-08 | -5.667e-08 | 8.7795e-08 | 5.647e-08 | -1.5165e-07 | -6.6178e-08 | -4.2946e-08 | 1.1301e-07 | 5.0951e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56961 | 1.2534 | 1.0064 | 0.56961 | 1.2534 | 1.0064 | -18.395 | -130.1209 | 143.3751 | -18.395 | -130.1209 | 143.3751
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8758e-08 | 5.4982e-08 | -8.846e-08 | -2.5244e-08 | -3.8343e-08 | 5.8308e-08 | 4.2353e-08 | -1.1374e-07 | -4.9633e-08 | -2.8828e-08 | 7.5097e-08 | 3.4407e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56961 | 1.2534 | 1.0064 | 0.56961 | 1.2534 | 1.0064 | -18.395 | -130.1209 | 143.3751 | -18.395 | -130.1209 | 143.3751
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2919e-08 | 1.8327e-08 | -2.9487e-08 | 5.9399e-10 | -1.6885e-09 | -6.6519e-10 | 1.4118e-08 | -3.7912e-08 | -1.6544e-08 | -5.9318e-10 | -7.2684e-10 | 1.3176e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56961 | 1.2534 | 1.0064 | 0.56961 | 1.2534 | 1.0064 | -18.395 | -130.1209 | 143.3751 | -18.395 | -130.1209 | 143.3751
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2919e-08 | 1.8327e-08 | -2.9487e-08 | 5.9399e-10 | -1.6885e-09 | -6.6519e-10 | 1.4118e-08 | -3.7912e-08 | -1.6544e-08 | -5.9318e-10 | -7.2684e-10 | 1.3176e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56961 | 1.2534 | 1.0064 | 0.56961 | 1.2534 | 1.0064 | -18.395 | -130.1209 | 143.3751 | -18.395 | -130.1209 | 143.3751
Line9_3_11 | 1.0183e-06 | 1.0183e-06 | 1.0183e-06 | 0 | 0 | 0 | 2.3517e-07 | 2.3517e-07 | 2.3517e-07 | 0 | 0 | 0 | 9.0434e-08 | 1.2829e-07 | -2.0641e-07 | -7.6921e-08 | -1.1165e-07 | 1.7626e-07 | 9.8823e-08 | -2.6538e-07 | -1.1581e-07 | -8.5299e-08 | 2.2674e-07 | 1.0058e-07 | -65.9331 | -65.921 | -65.921 | 0 | 0 | 0 | 0.56961 | 1.2534 | 1.0064 | 0.56961 | 1.2534 | 1.0064 | -18.395 | -130.1209 | 143.3751 | -18.395 | -130.1209 | 143.3751

## LLG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 1.1399e-06 | 1.1688e-06 | 1.111e-06 | 0 | 0 | 0 | 2.6324e-07 | 2.6991e-07 | 2.5658e-07 | 0 | 0 | 0 | 1.7705e-08 | -1.6315e-07 | 1.5562e-07 | -1.7766e-08 | 1.3677e-07 | -1.2918e-07 | -4.1354e-07 | 1.5873e-08 | -1.1983e-08 | 3.4462e-07 | -1.2335e-08 | 8.5675e-09 | 87.5775 | 87.9985 | 87.1226 | 0 | 0 | 0 | 1.5724 | 0.6073 | 0.60832 | 1.5724 | 0.6073 | 0.60832 | 0.028933 | -97.5583 | 82.7194 | 0.028932 | -97.5583 | 82.7194
Line10_11_12 | 1.1399e-06 | 1.1688e-06 | 1.111e-06 | 0 | 0 | 0 | 2.6324e-07 | 2.6991e-07 | 2.5658e-07 | 0 | 0 | 0 | 1.7705e-08 | -1.6315e-07 | 1.5562e-07 | -1.7766e-08 | 1.3677e-07 | -1.2918e-07 | -4.1354e-07 | 1.5873e-08 | -1.1983e-08 | 3.4462e-07 | -1.2335e-08 | 8.5675e-09 | 87.5775 | 87.9985 | 87.1226 | 0 | 0 | 0 | 1.5724 | 0.6073 | 0.60832 | 1.5724 | 0.6073 | 0.60832 | 0.028931 | -97.5583 | 82.7194 | 0.02893 | -97.5583 | 82.7194
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4754e-08 | -1.3596e-07 | 1.2969e-07 | -1.4815e-08 | 1.0958e-07 | -1.0324e-07 | -3.4462e-07 | 1.3227e-08 | -9.9861e-09 | 2.757e-07 | -9.6892e-09 | 6.5703e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5724 | 0.6073 | 0.60832 | 1.5724 | 0.6073 | 0.60832 | 0.02893 | -97.5583 | 82.7194 | 0.028929 | -97.5583 | 82.7194
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.8524e-09 | -8.1575e-08 | 7.7812e-08 | -8.9134e-09 | 5.5192e-08 | -5.1368e-08 | -2.0677e-07 | 7.9363e-09 | -5.9917e-09 | 1.3785e-07 | -4.3983e-09 | 2.5758e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5724 | 0.6073 | 0.60832 | 1.5724 | 0.6073 | 0.60832 | 0.028929 | -97.5583 | 82.7194 | 0.028929 | -97.5583 | 82.7194
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9508e-09 | -2.7192e-08 | 2.5937e-08 | -3.0118e-09 | 8.0872e-10 | 5.0664e-10 | -6.8924e-08 | 2.6454e-09 | -1.9972e-09 | 3.0576e-12 | 8.9256e-10 | -1.4186e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5724 | 0.6073 | 0.60832 | 1.5724 | 0.6073 | 0.60832 | 0.028929 | -97.5583 | 82.7194 | 0.028929 | -97.5583 | 82.7194
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.9016e-09 | -5.4383e-08 | 5.1875e-08 | -5.9626e-09 | 2.8e-08 | -2.5431e-08 | -1.3785e-07 | 5.2909e-09 | -3.9945e-09 | 6.8927e-08 | -1.7529e-09 | 5.7861e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5724 | 0.6073 | 0.60832 | 1.5724 | 0.6073 | 0.60832 | 0.028929 | -97.5583 | 82.7194 | 0.028929 | -97.5582 | 82.7194
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9508e-09 | -2.7192e-08 | 2.5937e-08 | -3.0118e-09 | 8.0872e-10 | 5.0664e-10 | -6.8924e-08 | 2.6454e-09 | -1.9972e-09 | 3.0568e-12 | 8.9256e-10 | -1.4186e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5724 | 0.6073 | 0.60832 | 1.5724 | 0.6073 | 0.60832 | 0.028929 | -97.5582 | 82.7194 | 0.028929 | -97.5582 | 82.7194
Line16_4_18 | 0 | 3.1348 | 3.1427 | 0 | 3.1348 | 3.1427 | 0 | 0.72395 | 0.72577 | 0 | 0.72395 | 0.72577 | 2.9881e-09 | 0.098071 | 0.098961 | -3.0065e-09 | 6.3859e-13 | -5.0569e-13 | -6.8979e-08 | 0.19674 | 0.19733 | 4.3939e-12 | 4.8669e-13 | -4.506e-13 | 0 | -161.0628 | 19.3537 | 0 | 18.9372 | -160.6463 | 1.572 | 0.30365 | 0.30416 | 1.5717 | 0 | 0 | 0.035267 | -97.5583 | 82.7194 | 0.041604 | 0 | 0
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9508e-09 | -2.7192e-08 | 2.5937e-08 | -3.0118e-09 | 8.0872e-10 | 5.0664e-10 | -6.8924e-08 | 2.6455e-09 | -1.9972e-09 | 3.0572e-12 | 8.9256e-10 | -1.4186e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5724 | 0.6073 | 0.60832 | 1.5724 | 0.6073 | 0.60832 | 0.028933 | -97.5583 | 82.7194 | 0.028933 | -97.5583 | 82.7194
Line1_1_3 | 1.5198e-06 | 1.5584e-06 | 1.4814e-06 | 1.3302e-06 | 1.3687e-06 | 1.2919e-06 | 3.5099e-07 | 3.5989e-07 | 3.4211e-07 | 3.0721e-07 | 3.1609e-07 | 2.9835e-07 | 2.3606e-08 | -2.1753e-07 | 2.075e-07 | -2.3667e-08 | 1.9115e-07 | -1.8105e-07 | -5.5139e-07 | 2.1164e-08 | -1.5978e-08 | 4.8247e-07 | -1.7626e-08 | 1.2562e-08 | 87.5775 | 87.9985 | 87.1226 | -92.7794 | -92.29 | -93.3117 | 1.5724 | 0.6073 | 0.60832 | 1.5724 | 0.6073 | 0.60832 | 0.028933 | -97.5583 | 82.7194 | 0.028932 | -97.5583 | 82.7194
Line2_1_4 | 0 | 3.1348 | 3.1427 | 0 | 3.1348 | 3.1427 | 0 | 0.72395 | 0.72577 | 0 | 0.72395 | 0.72577 | 5.9413e-09 | 0.19614 | 0.19792 | -5.9972e-09 | -0.098071 | -0.098961 | -1.3794e-07 | 0.39348 | 0.39465 | 6.8983e-08 | -0.19674 | -0.19733 | 0 | -161.0628 | 19.3537 | 0 | 18.9372 | -160.6463 | 1.5724 | 0.6073 | 0.60832 | 1.572 | 0.30365 | 0.30416 | 0.028933 | -97.5583 | 82.7194 | 0.035267 | -97.5583 | 82.7194
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.9015e-09 | -5.4383e-08 | 5.1875e-08 | -5.9626e-09 | 2.8e-08 | -2.5431e-08 | -1.3785e-07 | 5.2909e-09 | -3.9944e-09 | 6.8927e-08 | -1.7529e-09 | 5.7861e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5724 | 0.6073 | 0.60832 | 1.5724 | 0.6073 | 0.60832 | 0.028933 | -97.5583 | 82.7194 | 0.028933 | -97.5583 | 82.7194
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4754e-08 | -1.3596e-07 | 1.2969e-07 | -1.4815e-08 | 1.0958e-07 | -1.0324e-07 | -3.4462e-07 | 1.3227e-08 | -9.9861e-09 | 2.757e-07 | -9.6892e-09 | 6.5703e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5724 | 0.6073 | 0.60832 | 1.5724 | 0.6073 | 0.60832 | 0.028932 | -97.5583 | 82.7194 | 0.028932 | -97.5583 | 82.7194
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1803e-08 | -1.0877e-07 | 1.0375e-07 | -1.1864e-08 | 8.2384e-08 | -7.7305e-08 | -2.7569e-07 | 1.0582e-08 | -7.9889e-09 | 2.0677e-07 | -7.0438e-09 | 4.5731e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5724 | 0.6073 | 0.60832 | 1.5724 | 0.6073 | 0.60832 | 0.028932 | -97.5583 | 82.7194 | 0.028931 | -97.5583 | 82.7194
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.8523e-09 | -8.1575e-08 | 7.7812e-08 | -8.9134e-09 | 5.5192e-08 | -5.1368e-08 | -2.0677e-07 | 7.9364e-09 | -5.9917e-09 | 1.3785e-07 | -4.3983e-09 | 2.5758e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5724 | 0.6073 | 0.60832 | 1.5724 | 0.6073 | 0.60832 | 0.028931 | -97.5583 | 82.7194 | 0.028931 | -97.5583 | 82.7194
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9508e-09 | -2.7192e-08 | 2.5937e-08 | -3.0118e-09 | 8.0872e-10 | 5.0664e-10 | -6.8924e-08 | 2.6455e-09 | -1.9972e-09 | 3.0573e-12 | 8.9256e-10 | -1.4186e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5724 | 0.6073 | 0.60832 | 1.5724 | 0.6073 | 0.60832 | 0.028931 | -97.5583 | 82.7194 | 0.028931 | -97.5583 | 82.7194
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9508e-09 | -2.7192e-08 | 2.5937e-08 | -3.0118e-09 | 8.0872e-10 | 5.0664e-10 | -6.8924e-08 | 2.6455e-09 | -1.9972e-09 | 3.0578e-12 | 8.9256e-10 | -1.4186e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5724 | 0.6073 | 0.60832 | 1.5724 | 0.6073 | 0.60832 | 0.028931 | -97.5583 | 82.7194 | 0.028931 | -97.5583 | 82.7194
Line9_3_11 | 1.3299e-06 | 1.3636e-06 | 1.2962e-06 | 1.1403e-06 | 1.1739e-06 | 1.1067e-06 | 3.0712e-07 | 3.149e-07 | 2.9935e-07 | 2.6333e-07 | 2.711e-07 | 2.5558e-07 | 2.0655e-08 | -1.9034e-07 | 1.8156e-07 | -2.0717e-08 | 1.6396e-07 | -1.5512e-07 | -4.8246e-07 | 1.8518e-08 | -1.3981e-08 | 4.1354e-07 | -1.498e-08 | 1.0565e-08 | 87.5775 | 87.9985 | 87.1226 | -92.8389 | -92.3379 | -93.3843 | 1.5724 | 0.6073 | 0.60832 | 1.5724 | 0.6073 | 0.60832 | 0.028932 | -97.5583 | 82.7194 | 0.028931 | -97.5583 | 82.7194

## LLG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 1.1941e-06 | 1.2253e-06 | 1.1629e-06 | 0 | 1.0267e-06 | 0 | 2.7577e-07 | 2.8298e-07 | 2.6857e-07 | 0 | 2.371e-07 | 0 | 1.9428e-08 | -1.7631e-07 | 1.6792e-07 | -1.9495e-08 | 1.4782e-07 | -1.3937e-07 | -4.5383e-07 | 1.7897e-08 | -1.3578e-08 | 3.782e-07 | -1.396e-08 | 9.7748e-09 | 87.5778 | 88.0056 | 87.1146 | 0 | -92.3961 | 0 | 1.6472 | 0.62624 | 0.62729 | 1.6472 | 0.62624 | 0.62729 | 0.029102 | -97.7908 | 82.4916 | 0.029101 | -97.7908 | 82.4916
Line10_11_12 | 1.1941e-06 | 1.2253e-06 | 1.1629e-06 | 0 | 1.0267e-06 | 0 | 2.7577e-07 | 2.8298e-07 | 2.6857e-07 | 0 | 2.371e-07 | 0 | 1.9428e-08 | -1.7631e-07 | 1.6792e-07 | -1.9495e-08 | 1.4782e-07 | -1.3937e-07 | -4.5383e-07 | 1.7897e-08 | -1.3578e-08 | 3.782e-07 | -1.396e-08 | 9.7748e-09 | 87.5778 | 88.0056 | 87.1146 | 0 | -92.3961 | 0 | 1.6472 | 0.62624 | 0.62729 | 1.6472 | 0.62624 | 0.62729 | 0.0291 | -97.7908 | 82.4916 | 0.029099 | -97.7908 | 82.4916
Line11_12_13 | 0 | 1.0211e-06 | 0 | 0 | 0 | 0 | 0 | 2.3582e-07 | 0 | 0 | 0 | 0 | 1.619e-08 | -1.4692e-07 | 1.3993e-07 | -1.6257e-08 | 1.1844e-07 | -1.1138e-07 | -3.7819e-07 | 1.4914e-08 | -1.1315e-08 | 3.0256e-07 | -1.0977e-08 | 7.5117e-09 | 0 | 88.0056 | 0 | 0 | 0 | 0 | 1.6472 | 0.62624 | 0.62729 | 1.6472 | 0.62624 | 0.62729 | 0.029099 | -97.7908 | 82.4916 | 0.029098 | -97.7908 | 82.4916
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.7141e-09 | -8.8154e-08 | 8.3961e-08 | -9.7811e-09 | 5.967e-08 | -5.541e-08 | -2.2692e-07 | 8.9487e-09 | -6.7892e-09 | 1.5128e-07 | -5.0111e-09 | 2.9856e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6472 | 0.62624 | 0.62729 | 1.6472 | 0.62624 | 0.62729 | 0.029098 | -97.7908 | 82.4916 | 0.029098 | -97.7908 | 82.4916
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.238e-09 | -2.9385e-08 | 2.7987e-08 | -3.305e-09 | 9.0047e-10 | 5.6421e-10 | -7.5639e-08 | 2.9829e-09 | -2.2631e-09 | 3.375e-12 | 9.5473e-10 | -1.5405e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6472 | 0.62624 | 0.62729 | 1.6472 | 0.62624 | 0.62729 | 0.029098 | -97.7908 | 82.4916 | 0.029098 | -97.7908 | 82.4916
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.4761e-09 | -5.8769e-08 | 5.5974e-08 | -6.543e-09 | 3.0285e-08 | -2.7423e-08 | -1.5128e-07 | 5.9658e-09 | -4.5261e-09 | 7.5642e-08 | -2.0282e-09 | 7.2256e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6472 | 0.62624 | 0.62729 | 1.6472 | 0.62624 | 0.62729 | 0.029098 | -97.7908 | 82.4916 | 0.029097 | -97.7908 | 82.4916
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.238e-09 | -2.9385e-08 | 2.7987e-08 | -3.305e-09 | 9.0047e-10 | 5.6421e-10 | -7.5639e-08 | 2.9829e-09 | -2.2631e-09 | 3.3736e-12 | 9.5473e-10 | -1.5405e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6472 | 0.62624 | 0.62729 | 1.6472 | 0.62624 | 0.62729 | 0.029097 | -97.7908 | 82.4916 | 0.029097 | -97.7908 | 82.4916
Line16_4_18 | 0 | 3.2325 | 3.2407 | 0 | 3.2325 | 3.2407 | 0 | 0.74652 | 0.7484 | 0 | 0.74652 | 0.7484 | 3.2789e-09 | 0.10428 | 0.10523 | -3.2991e-09 | 8.5851e-13 | -6.8621e-13 | -7.5699e-08 | 0.2092 | 0.20982 | 4.8417e-12 | 1.2262e-13 | -1.2698e-13 | 0 | -161.2965 | 19.1271 | 0 | 18.7035 | -160.8729 | 1.6468 | 0.31312 | 0.31364 | 1.6465 | 0 | 0 | 0.035436 | -97.7908 | 82.4916 | 0.041772 | 0 | 0
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.238e-09 | -2.9385e-08 | 2.7987e-08 | -3.305e-09 | 9.0047e-10 | 5.6421e-10 | -7.5639e-08 | 2.9829e-09 | -2.2631e-09 | 3.3747e-12 | 9.5473e-10 | -1.5405e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6472 | 0.62624 | 0.62729 | 1.6472 | 0.62624 | 0.62729 | 0.029102 | -97.7908 | 82.4916 | 0.029102 | -97.7908 | 82.4916
Line1_1_3 | 1.5921e-06 | 1.6338e-06 | 1.5506e-06 | 1.3935e-06 | 1.4351e-06 | 1.3521e-06 | 3.6769e-07 | 3.7731e-07 | 3.5809e-07 | 3.2182e-07 | 3.3143e-07 | 3.1224e-07 | 2.5904e-08 | -2.3508e-07 | 2.239e-07 | -2.5971e-08 | 2.0659e-07 | -1.9534e-07 | -6.0511e-07 | 2.3863e-08 | -1.8104e-08 | 5.2947e-07 | -1.9926e-08 | 1.4301e-08 | 87.5778 | 88.0056 | 87.1146 | -92.7791 | -92.2818 | -93.3213 | 1.6472 | 0.62624 | 0.62729 | 1.6472 | 0.62624 | 0.62729 | 0.029102 | -97.7908 | 82.4916 | 0.029101 | -97.7908 | 82.4916
Line2_1_4 | 0 | 3.2325 | 3.2407 | 0 | 3.2325 | 3.2407 | 0 | 0.74652 | 0.7484 | 0 | 0.74652 | 0.7484 | 6.5197e-09 | 0.20855 | 0.21047 | -6.581e-09 | -0.10428 | -0.10523 | -1.5138e-07 | 0.4184 | 0.41964 | 7.5703e-08 | -0.2092 | -0.20982 | 0 | -161.2965 | 19.1272 | 0 | 18.7035 | -160.8729 | 1.6472 | 0.62624 | 0.62729 | 1.6468 | 0.31312 | 0.31364 | 0.029102 | -97.7908 | 82.4916 | 0.035436 | -97.7908 | 82.4916
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.476e-09 | -5.8769e-08 | 5.5974e-08 | -6.543e-09 | 3.0285e-08 | -2.7423e-08 | -1.5128e-07 | 5.9658e-09 | -4.5261e-09 | 7.5642e-08 | -2.0282e-09 | 7.2256e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6472 | 0.62624 | 0.62729 | 1.6472 | 0.62624 | 0.62729 | 0.029102 | -97.7908 | 82.4916 | 0.029102 | -97.7908 | 82.4916
Line4_2_6 | 0 | 1.0211e-06 | 0 | 0 | 0 | 0 | 0 | 2.3582e-07 | 0 | 0 | 0 | 0 | 1.619e-08 | -1.4692e-07 | 1.3993e-07 | -1.6257e-08 | 1.1844e-07 | -1.1138e-07 | -3.7819e-07 | 1.4915e-08 | -1.1315e-08 | 3.0256e-07 | -1.0977e-08 | 7.5117e-09 | 0 | 88.0056 | 0 | 0 | 0 | 0 | 1.6472 | 0.62624 | 0.62729 | 1.6472 | 0.62624 | 0.62729 | 0.029101 | -97.7908 | 82.4916 | 0.0291 | -97.7908 | 82.4916
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2952e-08 | -1.1754e-07 | 1.1195e-07 | -1.3019e-08 | 8.9054e-08 | -8.3396e-08 | -3.0255e-07 | 1.1932e-08 | -9.0522e-09 | 2.2692e-07 | -7.994e-09 | 5.2487e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6472 | 0.62624 | 0.62729 | 1.6472 | 0.62624 | 0.62729 | 0.0291 | -97.7908 | 82.4916 | 0.0291 | -97.7908 | 82.4916
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.7141e-09 | -8.8154e-08 | 8.3961e-08 | -9.7811e-09 | 5.967e-08 | -5.541e-08 | -2.2692e-07 | 8.9487e-09 | -6.7892e-09 | 1.5128e-07 | -5.0111e-09 | 2.9856e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6472 | 0.62624 | 0.62729 | 1.6472 | 0.62624 | 0.62729 | 0.0291 | -97.7908 | 82.4916 | 0.029099 | -97.7908 | 82.4916
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.238e-09 | -2.9385e-08 | 2.7987e-08 | -3.305e-09 | 9.0047e-10 | 5.6421e-10 | -7.5639e-08 | 2.9829e-09 | -2.2631e-09 | 3.3748e-12 | 9.5473e-10 | -1.5405e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6472 | 0.62624 | 0.62729 | 1.6472 | 0.62624 | 0.62729 | 0.029099 | -97.7908 | 82.4916 | 0.029099 | -97.7908 | 82.4916
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.238e-09 | -2.9385e-08 | 2.7987e-08 | -3.305e-09 | 9.0047e-10 | 5.6421e-10 | -7.5639e-08 | 2.9829e-09 | -2.2631e-09 | 3.3752e-12 | 9.5473e-10 | -1.5405e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6472 | 0.62624 | 0.62729 | 1.6472 | 0.62624 | 0.62729 | 0.029099 | -97.7908 | 82.4916 | 0.029099 | -97.7908 | 82.4916
Line9_3_11 | 1.3931e-06 | 1.4296e-06 | 1.3568e-06 | 1.1945e-06 | 1.2309e-06 | 1.1582e-06 | 3.2173e-07 | 3.3015e-07 | 3.1333e-07 | 2.7586e-07 | 2.8426e-07 | 2.6748e-07 | 2.2666e-08 | -2.0569e-07 | 1.9591e-07 | -2.2733e-08 | 1.7721e-07 | -1.6736e-07 | -5.2947e-07 | 2.088e-08 | -1.5841e-08 | 4.5383e-07 | -1.6943e-08 | 1.2038e-08 | 87.5778 | 88.0056 | 87.1146 | -92.8385 | -92.3294 | -93.3942 | 1.6472 | 0.62624 | 0.62729 | 1.6472 | 0.62624 | 0.62729 | 0.029101 | -97.7908 | 82.4916 | 0.0291 | -97.7908 | 82.4916

## LLG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.5612e-08 | -1.1896e-07 | 1.7172e-07 | 3.64e-08 | 9.9696e-08 | -1.4324e-07 | -2.2348e-07 | 7.076e-08 | -1.2813e-08 | 1.8663e-07 | -5.813e-08 | 9.4246e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3679 | 0.82985 | 1.0331 | 1.3679 | 0.82985 | 1.0331 | 4.3862 | -104.8188 | 101.6395 | 4.3862 | -104.8188 | 101.6395
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.5612e-08 | -1.1896e-07 | 1.7172e-07 | 3.64e-08 | 9.9696e-08 | -1.4324e-07 | -2.2348e-07 | 7.076e-08 | -1.2813e-08 | 1.8663e-07 | -5.813e-08 | 9.4246e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3679 | 0.82985 | 1.0331 | 1.3679 | 0.82985 | 1.0331 | 4.3862 | -104.8188 | 101.6395 | 4.3862 | -104.8188 | 101.6395
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.801e-08 | -9.9137e-08 | 1.431e-07 | 2.8798e-08 | 7.9868e-08 | -1.1462e-07 | -1.8623e-07 | 5.8966e-08 | -1.0678e-08 | 1.4939e-07 | -4.6336e-08 | 7.2891e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3679 | 0.82985 | 1.0331 | 1.3679 | 0.82985 | 1.0331 | 4.3862 | -104.8188 | 101.6395 | 4.3862 | -104.8188 | 101.6395
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.2806e-08 | -5.9482e-08 | 8.5859e-08 | 1.3594e-08 | 4.0213e-08 | -5.7378e-08 | -1.1174e-07 | 3.538e-08 | -6.4065e-09 | 7.4896e-08 | -2.275e-08 | 3.0181e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3679 | 0.82985 | 1.0331 | 1.3679 | 0.82985 | 1.0331 | 4.3862 | -104.8188 | 101.6395 | 4.3862 | -104.8188 | 101.6395
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.602e-09 | -1.9827e-08 | 2.862e-08 | -1.61e-09 | 5.5836e-10 | -1.3844e-10 | -3.7246e-08 | 1.1793e-08 | -2.1355e-09 | 4.0277e-10 | 8.3667e-10 | -1.2529e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3679 | 0.82985 | 1.0331 | 1.3679 | 0.82985 | 1.0331 | 4.3862 | -104.8188 | 101.6395 | 4.3862 | -104.8188 | 101.6395
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.5204e-08 | -3.9655e-08 | 5.7239e-08 | 5.992e-09 | 2.0386e-08 | -2.8758e-08 | -7.4493e-08 | 2.3587e-08 | -4.271e-09 | 3.7649e-08 | -1.0957e-08 | 8.8264e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3679 | 0.82985 | 1.0331 | 1.3679 | 0.82985 | 1.0331 | 4.3862 | -104.8188 | 101.6395 | 4.3862 | -104.8188 | 101.6395
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.602e-09 | -1.9827e-08 | 2.862e-08 | -1.61e-09 | 5.5836e-10 | -1.3844e-10 | -3.7246e-08 | 1.1793e-08 | -2.1355e-09 | 4.0277e-10 | 8.3667e-10 | -1.2529e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3679 | 0.82985 | 1.0331 | 1.3679 | 0.82985 | 1.0331 | 4.3862 | -104.8188 | 101.6395 | 4.3862 | -104.8188 | 101.6395
Line16_4_18 | 0 | 0.026943 | 0.033545 | 0 | 0.026943 | 0.033545 | 0 | 0.0062222 | 0.0077469 | 0 | 0.0062222 | 0.0077468 | -7.5924e-09 | 0.0036357 | 0.0056384 | -1.6071e-09 | -0.0036297 | -0.0056263 | -3.7282e-08 | 0.0036451 | 0.005647 | 4.0304e-10 | -0.0036297 | -0.0056263 | 0 | -149.9668 | 56.5515 | 0 | 30.0335 | -123.4486 | 1.3677 | 0.82741 | 1.0301 | 1.3674 | 0.82496 | 1.0271 | 4.3884 | -104.8924 | 101.5956 | 4.3907 | -104.9665 | 101.5514
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.602e-09 | -1.9827e-08 | 2.862e-08 | -1.61e-09 | 5.5836e-10 | -1.3843e-10 | -3.7246e-08 | 1.1793e-08 | -2.1355e-09 | 4.0277e-10 | 8.3667e-10 | -1.2529e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3679 | 0.82985 | 1.0331 | 1.3679 | 0.82985 | 1.0331 | 4.3862 | -104.8188 | 101.6395 | 4.3862 | -104.8188 | 101.6395
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.0816e-08 | -1.5862e-07 | 2.2896e-07 | 5.1604e-08 | 1.3935e-07 | -2.0048e-07 | -2.9797e-07 | 9.4346e-08 | -1.7084e-08 | 2.6113e-07 | -8.1716e-08 | 1.3696e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3679 | 0.82985 | 1.0331 | 1.3679 | 0.82985 | 1.0331 | 4.3862 | -104.8188 | 101.6395 | 4.3862 | -104.8188 | 101.6395
Line2_1_4 | 0 | 0.026943 | 0.033545 | 0 | 0.026943 | 0.033545 | 0 | 0.0062222 | 0.0077469 | 0 | 0.0062222 | 0.0077469 | -1.5195e-08 | 0.0036417 | 0.0056505 | 5.9839e-09 | -0.0036357 | -0.0056384 | -7.4549e-08 | 0.0036606 | 0.0056678 | 3.7685e-08 | -0.0036451 | -0.0056471 | 0 | -149.967 | 56.5517 | 0 | 30.0332 | -123.4485 | 1.3679 | 0.82985 | 1.0331 | 1.3677 | 0.82741 | 1.0301 | 4.3862 | -104.8188 | 101.6395 | 4.3884 | -104.8924 | 101.5956
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.5204e-08 | -3.9655e-08 | 5.7239e-08 | 5.992e-09 | 2.0386e-08 | -2.8758e-08 | -7.4493e-08 | 2.3587e-08 | -4.271e-09 | 3.7649e-08 | -1.0957e-08 | 8.8264e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3679 | 0.82985 | 1.0331 | 1.3679 | 0.82985 | 1.0331 | 4.3862 | -104.8188 | 101.6395 | 4.3862 | -104.8188 | 101.6395
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.801e-08 | -9.9137e-08 | 1.431e-07 | 2.8798e-08 | 7.9868e-08 | -1.1462e-07 | -1.8623e-07 | 5.8966e-08 | -1.0678e-08 | 1.4939e-07 | -4.6336e-08 | 7.2891e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3679 | 0.82985 | 1.0331 | 1.3679 | 0.82985 | 1.0331 | 4.3862 | -104.8188 | 101.6395 | 4.3862 | -104.8188 | 101.6395
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.0408e-08 | -7.931e-08 | 1.1448e-07 | 2.1196e-08 | 6.0041e-08 | -8.5997e-08 | -1.4899e-07 | 4.7173e-08 | -8.542e-09 | 1.1214e-07 | -3.4543e-08 | 5.1536e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3679 | 0.82985 | 1.0331 | 1.3679 | 0.82985 | 1.0331 | 4.3862 | -104.8188 | 101.6395 | 4.3862 | -104.8188 | 101.6395
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.2806e-08 | -5.9482e-08 | 8.5859e-08 | 1.3594e-08 | 4.0213e-08 | -5.7378e-08 | -1.1174e-07 | 3.538e-08 | -6.4065e-09 | 7.4896e-08 | -2.275e-08 | 3.0181e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3679 | 0.82985 | 1.0331 | 1.3679 | 0.82985 | 1.0331 | 4.3862 | -104.8188 | 101.6395 | 4.3862 | -104.8188 | 101.6395
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.602e-09 | -1.9827e-08 | 2.862e-08 | -1.61e-09 | 5.5836e-10 | -1.3843e-10 | -3.7246e-08 | 1.1793e-08 | -2.1355e-09 | 4.0277e-10 | 8.3667e-10 | -1.2529e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3679 | 0.82985 | 1.0331 | 1.3679 | 0.82985 | 1.0331 | 4.3862 | -104.8188 | 101.6395 | 4.3862 | -104.8188 | 101.6395
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.602e-09 | -1.9827e-08 | 2.862e-08 | -1.61e-09 | 5.5836e-10 | -1.3844e-10 | -3.7246e-08 | 1.1793e-08 | -2.1355e-09 | 4.0277e-10 | 8.3667e-10 | -1.2529e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3679 | 0.82985 | 1.0331 | 1.3679 | 0.82985 | 1.0331 | 4.3862 | -104.8188 | 101.6395 | 4.3862 | -104.8188 | 101.6395
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.3214e-08 | -1.3879e-07 | 2.0034e-07 | 4.4002e-08 | 1.1952e-07 | -1.7186e-07 | -2.6072e-07 | 8.2553e-08 | -1.4949e-08 | 2.2388e-07 | -6.9923e-08 | 1.156e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3679 | 0.82985 | 1.0331 | 1.3679 | 0.82985 | 1.0331 | 4.3862 | -104.8188 | 101.6395 | 4.3862 | -104.8188 | 101.6395

## LLG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.0056e-08 | -1.3054e-07 | 1.8843e-07 | 3.9947e-08 | 1.094e-07 | -1.5718e-07 | -2.4526e-07 | 7.7667e-08 | -1.4069e-08 | 2.0483e-07 | -6.3805e-08 | 1.0349e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 1.433 | 0.86929 | 1.0822 | 1.433 | 0.86929 | 1.0822 | 4.3857 | -104.8259 | 101.6353 | 4.3857 | -104.8259 | 101.6353
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.0056e-08 | -1.3054e-07 | 1.8843e-07 | 3.9947e-08 | 1.094e-07 | -1.5718e-07 | -2.4526e-07 | 7.7667e-08 | -1.4069e-08 | 2.0483e-07 | -6.3805e-08 | 1.0349e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 1.433 | 0.86929 | 1.0822 | 1.433 | 0.86929 | 1.0822 | 4.3857 | -104.8259 | 101.6353 | 4.3857 | -104.8259 | 101.6353
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.1714e-08 | -1.0879e-07 | 1.5703e-07 | 3.1604e-08 | 8.7642e-08 | -1.2577e-07 | -2.0438e-07 | 6.4722e-08 | -1.1724e-08 | 1.6395e-07 | -5.086e-08 | 8.0042e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.433 | 0.86929 | 1.0822 | 1.433 | 0.86929 | 1.0822 | 4.3857 | -104.8259 | 101.6353 | 4.3857 | -104.8259 | 101.6353
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5028e-08 | -6.5272e-08 | 9.4216e-08 | 1.4919e-08 | 4.4128e-08 | -6.2962e-08 | -1.2263e-07 | 3.8833e-08 | -7.0345e-09 | 8.2196e-08 | -2.4971e-08 | 3.3145e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.433 | 0.86929 | 1.0822 | 1.433 | 0.86929 | 1.0822 | 4.3857 | -104.8259 | 101.6353 | 4.3857 | -104.8259 | 101.6353
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.3427e-09 | -2.1757e-08 | 3.1405e-08 | -1.7668e-09 | 6.1313e-10 | -1.5148e-10 | -4.0877e-08 | 1.2944e-08 | -2.3448e-09 | 4.4199e-10 | 9.1774e-10 | -1.3752e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.433 | 0.86929 | 1.0822 | 1.433 | 0.86929 | 1.0822 | 4.3857 | -104.8259 | 101.6353 | 4.3857 | -104.8259 | 101.6353
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.6685e-08 | -4.3515e-08 | 6.281e-08 | 6.5759e-09 | 2.237e-08 | -3.1557e-08 | -8.1754e-08 | 2.5889e-08 | -4.6897e-09 | 4.1319e-08 | -1.2027e-08 | 9.6968e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.433 | 0.86929 | 1.0822 | 1.433 | 0.86929 | 1.0822 | 4.3857 | -104.8259 | 101.6353 | 4.3857 | -104.8259 | 101.6353
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.3427e-09 | -2.1757e-08 | 3.1405e-08 | -1.7668e-09 | 6.1313e-10 | -1.5148e-10 | -4.0877e-08 | 1.2944e-08 | -2.3448e-09 | 4.4199e-10 | 9.1774e-10 | -1.3752e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.433 | 0.86929 | 1.0822 | 1.433 | 0.86929 | 1.0822 | 4.3857 | -104.8259 | 101.6353 | 4.3857 | -104.8259 | 101.6353
Line16_4_18 | 0 | 0.028223 | 0.035138 | 0 | 0.028223 | 0.035138 | 0 | 0.0065179 | 0.0081147 | 0 | 0.0065179 | 0.0081147 | -8.3322e-09 | 0.0039894 | 0.0061866 | -1.7636e-09 | -0.0039828 | -0.0061733 | -4.0916e-08 | 0.0039998 | 0.0061961 | 4.4229e-10 | -0.0039828 | -0.0061733 | 0 | -149.9739 | 56.5473 | 0 | 30.0263 | -123.4528 | 1.4328 | 0.86672 | 1.079 | 1.4325 | 0.86416 | 1.0759 | 4.388 | -104.8996 | 101.5914 | 4.3902 | -104.9737 | 101.5472
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.3427e-09 | -2.1757e-08 | 3.1405e-08 | -1.7668e-09 | 6.1313e-10 | -1.5148e-10 | -4.0877e-08 | 1.2944e-08 | -2.3448e-09 | 4.4199e-10 | 9.1774e-10 | -1.3752e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.433 | 0.86929 | 1.0822 | 1.433 | 0.86929 | 1.0822 | 4.3857 | -104.8259 | 101.6353 | 4.3857 | -104.8259 | 101.6353
Line1_1_3 | 1.0085e-06 | 1.0089e-06 | 1.0081e-06 | 0 | 0 | 0 | 2.329e-07 | 2.3299e-07 | 2.3281e-07 | 0 | 0 | 0 | -6.6742e-08 | -1.7406e-07 | 2.5124e-07 | 5.6632e-08 | 1.5291e-07 | -2.1999e-07 | -3.2702e-07 | 1.0356e-07 | -1.8759e-08 | 2.8658e-07 | -8.9694e-08 | 1.5039e-08 | 105.921 | 105.9245 | 105.9053 | 0 | 0 | 0 | 1.433 | 0.86929 | 1.0822 | 1.433 | 0.86929 | 1.0822 | 4.3857 | -104.8259 | 101.6353 | 4.3857 | -104.8259 | 101.6353
Line2_1_4 | 0 | 0.028223 | 0.035138 | 0 | 0.028223 | 0.035138 | 0 | 0.0065179 | 0.0081148 | 0 | 0.0065179 | 0.0081147 | -1.6676e-08 | 0.003996 | 0.0061999 | 6.567e-09 | -0.0039894 | -0.0061866 | -8.1815e-08 | 0.0040168 | 0.0062189 | 4.1358e-08 | -0.0039998 | -0.0061961 | 0 | -149.9742 | 56.5475 | 0 | 30.0261 | -123.4527 | 1.433 | 0.86929 | 1.0822 | 1.4328 | 0.86672 | 1.079 | 4.3857 | -104.8259 | 101.6353 | 4.388 | -104.8996 | 101.5914
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.6685e-08 | -4.3515e-08 | 6.281e-08 | 6.5759e-09 | 2.237e-08 | -3.1557e-08 | -8.1754e-08 | 2.5889e-08 | -4.6897e-09 | 4.1319e-08 | -1.2027e-08 | 9.6968e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.433 | 0.86929 | 1.0822 | 1.433 | 0.86929 | 1.0822 | 4.3857 | -104.8259 | 101.6353 | 4.3857 | -104.8259 | 101.6353
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.1714e-08 | -1.0879e-07 | 1.5703e-07 | 3.1604e-08 | 8.7642e-08 | -1.2577e-07 | -2.0438e-07 | 6.4722e-08 | -1.1724e-08 | 1.6395e-07 | -5.086e-08 | 8.0042e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.433 | 0.86929 | 1.0822 | 1.433 | 0.86929 | 1.0822 | 4.3857 | -104.8259 | 101.6353 | 4.3857 | -104.8259 | 101.6353
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.3371e-08 | -8.7029e-08 | 1.2562e-07 | 2.3261e-08 | 6.5885e-08 | -9.4367e-08 | -1.6351e-07 | 5.1778e-08 | -9.3793e-09 | 1.2307e-07 | -3.7916e-08 | 5.6594e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.433 | 0.86929 | 1.0822 | 1.433 | 0.86929 | 1.0822 | 4.3857 | -104.8259 | 101.6353 | 4.3857 | -104.8259 | 101.6353
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5028e-08 | -6.5272e-08 | 9.4216e-08 | 1.4919e-08 | 4.4128e-08 | -6.2962e-08 | -1.2263e-07 | 3.8833e-08 | -7.0345e-09 | 8.2196e-08 | -2.4971e-08 | 3.3145e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.433 | 0.86929 | 1.0822 | 1.433 | 0.86929 | 1.0822 | 4.3857 | -104.8259 | 101.6353 | 4.3857 | -104.8259 | 101.6353
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.3427e-09 | -2.1757e-08 | 3.1405e-08 | -1.7668e-09 | 6.1313e-10 | -1.5148e-10 | -4.0877e-08 | 1.2944e-08 | -2.3448e-09 | 4.4199e-10 | 9.1774e-10 | -1.3752e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.433 | 0.86929 | 1.0822 | 1.433 | 0.86929 | 1.0822 | 4.3857 | -104.8259 | 101.6353 | 4.3857 | -104.8259 | 101.6353
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.3427e-09 | -2.1757e-08 | 3.1405e-08 | -1.7668e-09 | 6.1313e-10 | -1.5148e-10 | -4.0877e-08 | 1.2944e-08 | -2.3448e-09 | 4.4199e-10 | 9.1774e-10 | -1.3752e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.433 | 0.86929 | 1.0822 | 1.433 | 0.86929 | 1.0822 | 4.3857 | -104.8259 | 101.6353 | 4.3857 | -104.8259 | 101.6353
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.8399e-08 | -1.523e-07 | 2.1984e-07 | 4.829e-08 | 1.3116e-07 | -1.8858e-07 | -2.8614e-07 | 9.0611e-08 | -1.6414e-08 | 2.457e-07 | -7.6749e-08 | 1.2694e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 1.433 | 0.86929 | 1.0822 | 1.433 | 0.86929 | 1.0822 | 4.3857 | -104.8259 | 101.6353 | 4.3857 | -104.8259 | 101.6353

## LLG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 1.0313e-06 | 1.0531e-06 | 1.0096e-06 | 0 | 0 | 0 | 2.3816e-07 | 2.4319e-07 | 2.3317e-07 | 0 | 0 | 0 | 1.4215e-08 | -1.439e-07 | 1.3905e-07 | -1.4311e-08 | 1.2058e-07 | -1.1563e-07 | -3.3851e-07 | 2.5535e-08 | -2.0527e-08 | 2.821e-07 | -2.0623e-08 | 1.5716e-08 | 87.6477 | 88.3183 | 86.9359 | 0 | 0 | 0 | 1.4226 | 0.60096 | 0.60282 | 1.4226 | 0.60096 | 0.60282 | 0.052314 | -101.7438 | 78.5382 | 0.052313 | -101.7438 | 78.5382
Line10_11_12 | 1.0313e-06 | 1.0531e-06 | 1.0096e-06 | 0 | 0 | 0 | 2.3816e-07 | 2.4319e-07 | 2.3317e-07 | 0 | 0 | 0 | 1.4215e-08 | -1.439e-07 | 1.3905e-07 | -1.4311e-08 | 1.2058e-07 | -1.1563e-07 | -3.3851e-07 | 2.5535e-08 | -2.0527e-08 | 2.821e-07 | -2.0623e-08 | 1.5716e-08 | 87.6477 | 88.3183 | 86.9359 | 0 | 0 | 0 | 1.4226 | 0.60096 | 0.60282 | 1.4226 | 0.60096 | 0.60282 | 0.05231 | -101.7438 | 78.5382 | 0.052308 | -101.7438 | 78.5382
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1846e-08 | -1.1992e-07 | 1.1587e-07 | -1.1942e-08 | 9.6599e-08 | -9.2459e-08 | -2.8209e-07 | 2.1279e-08 | -1.7106e-08 | 2.2568e-07 | -1.6367e-08 | 1.2295e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4226 | 0.60096 | 0.60282 | 1.4226 | 0.60096 | 0.60282 | 0.052308 | -101.7438 | 78.5382 | 0.052307 | -101.7438 | 78.5382
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.1076e-09 | -7.1952e-08 | 6.9525e-08 | -7.2035e-09 | 4.8632e-08 | -4.6109e-08 | -1.6926e-07 | 1.2767e-08 | -1.0264e-08 | 1.1284e-07 | -7.8558e-09 | 5.4521e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4226 | 0.60096 | 0.60282 | 1.4226 | 0.60096 | 0.60282 | 0.052307 | -101.7438 | 78.5382 | 0.052306 | -101.7438 | 78.5382
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3692e-09 | -2.3984e-08 | 2.3175e-08 | -2.4652e-09 | 6.6374e-10 | 2.4117e-10 | -5.6419e-08 | 4.2558e-09 | -3.4212e-09 | 4.524e-12 | 6.5578e-10 | -1.3903e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4226 | 0.60096 | 0.60282 | 1.4226 | 0.60096 | 0.60282 | 0.052307 | -101.7438 | 78.5382 | 0.052307 | -101.7438 | 78.5382
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7384e-09 | -4.7968e-08 | 4.635e-08 | -4.8344e-09 | 2.4648e-08 | -2.2934e-08 | -1.1284e-07 | 8.5116e-09 | -6.8425e-09 | 5.6423e-08 | -3.6e-09 | 2.0309e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4226 | 0.60096 | 0.60282 | 1.4226 | 0.60096 | 0.60282 | 0.052306 | -101.7438 | 78.5382 | 0.052306 | -101.7438 | 78.5382
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3692e-09 | -2.3984e-08 | 2.3175e-08 | -2.4652e-09 | 6.6374e-10 | 2.4117e-10 | -5.6419e-08 | 4.2558e-09 | -3.4212e-09 | 4.524e-12 | 6.5578e-10 | -1.3903e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4226 | 0.60096 | 0.60282 | 1.4226 | 0.60096 | 0.60282 | 0.052306 | -101.7438 | 78.5382 | 0.052306 | -101.7438 | 78.5382
Line16_4_18 | 0 | 2.5011 | 2.5126 | 0 | 2.5011 | 2.5126 | 0 | 0.57759 | 0.58027 | 0 | 0.57759 | 0.58027 | 2.4313e-09 | 0.12004 | 0.12128 | -2.4608e-09 | -1.2789e-14 | 2.3342e-15 | -5.6465e-08 | 0.12535 | 0.12602 | 6.6266e-12 | -3.3899e-13 | 3.2897e-13 | 0 | -147.9837 | 32.4393 | 0 | 32.0163 | -147.5607 | 1.4223 | 0.30048 | 0.30141 | 1.422 | 0 | 0 | 0.064478 | -101.7438 | 78.5382 | 0.076648 | 0 | 0
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3692e-09 | -2.3984e-08 | 2.3175e-08 | -2.4651e-09 | 6.6374e-10 | 2.4117e-10 | -5.6419e-08 | 4.2558e-09 | -3.4212e-09 | 4.5245e-12 | 6.5578e-10 | -1.3903e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4226 | 0.60096 | 0.60282 | 1.4226 | 0.60096 | 0.60282 | 0.052314 | -101.7438 | 78.5382 | 0.052314 | -101.7438 | 78.5382
Line1_1_3 | 1.375e-06 | 1.4041e-06 | 1.3462e-06 | 1.2035e-06 | 1.2325e-06 | 1.1748e-06 | 3.1755e-07 | 3.2426e-07 | 3.1089e-07 | 2.7794e-07 | 2.8463e-07 | 2.713e-07 | 1.8954e-08 | -1.9187e-07 | 1.854e-07 | -1.905e-08 | 1.6855e-07 | -1.6198e-07 | -4.5135e-07 | 3.4046e-08 | -2.737e-08 | 3.9494e-07 | -2.9135e-08 | 2.2558e-08 | 87.6477 | 88.3183 | 86.9359 | -92.7092 | -91.9368 | -93.5336 | 1.4226 | 0.60096 | 0.60282 | 1.4226 | 0.60096 | 0.60282 | 0.052314 | -101.7438 | 78.5382 | 0.052312 | -101.7438 | 78.5382
Line2_1_4 | 0 | 2.5011 | 2.5126 | 0 | 2.5011 | 2.5126 | 0 | 0.57759 | 0.58027 | 0 | 0.57759 | 0.58027 | 4.8054e-09 | 0.24008 | 0.24256 | -4.8943e-09 | -0.12004 | -0.12128 | -1.1292e-07 | 0.2507 | 0.25204 | 5.6471e-08 | -0.12535 | -0.12602 | 0 | -147.9837 | 32.4393 | 0 | 32.0163 | -147.5607 | 1.4226 | 0.60096 | 0.60282 | 1.4223 | 0.30048 | 0.30141 | 0.052314 | -101.7438 | 78.5382 | 0.064478 | -101.7438 | 78.5382
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7384e-09 | -4.7968e-08 | 4.635e-08 | -4.8343e-09 | 2.4648e-08 | -2.2934e-08 | -1.1284e-07 | 8.5116e-09 | -6.8425e-09 | 5.6423e-08 | -3.6e-09 | 2.0309e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4226 | 0.60096 | 0.60282 | 1.4226 | 0.60096 | 0.60282 | 0.052314 | -101.7438 | 78.5382 | 0.052314 | -101.7438 | 78.5382
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1846e-08 | -1.1992e-07 | 1.1587e-07 | -1.1942e-08 | 9.6599e-08 | -9.2459e-08 | -2.8209e-07 | 2.1279e-08 | -1.7106e-08 | 2.2568e-07 | -1.6367e-08 | 1.2295e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4226 | 0.60096 | 0.60282 | 1.4226 | 0.60096 | 0.60282 | 0.052313 | -101.7438 | 78.5382 | 0.052311 | -101.7438 | 78.5382
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.4768e-09 | -9.5936e-08 | 9.27e-08 | -9.5727e-09 | 7.2615e-08 | -6.9284e-08 | -2.2567e-07 | 1.7023e-08 | -1.3685e-08 | 1.6926e-07 | -1.2112e-08 | 8.8734e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4226 | 0.60096 | 0.60282 | 1.4226 | 0.60096 | 0.60282 | 0.052311 | -101.7438 | 78.5382 | 0.05231 | -101.7438 | 78.5382
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.1076e-09 | -7.1952e-08 | 6.9525e-08 | -7.2035e-09 | 4.8632e-08 | -4.6109e-08 | -1.6926e-07 | 1.2767e-08 | -1.0264e-08 | 1.1284e-07 | -7.8558e-09 | 5.4521e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4226 | 0.60096 | 0.60282 | 1.4226 | 0.60096 | 0.60282 | 0.05231 | -101.7438 | 78.5382 | 0.052309 | -101.7438 | 78.5382
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3692e-09 | -2.3984e-08 | 2.3175e-08 | -2.4652e-09 | 6.6374e-10 | 2.4117e-10 | -5.6419e-08 | 4.2558e-09 | -3.4212e-09 | 4.5244e-12 | 6.5578e-10 | -1.3903e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4226 | 0.60096 | 0.60282 | 1.4226 | 0.60096 | 0.60282 | 0.052309 | -101.7438 | 78.5382 | 0.052309 | -101.7438 | 78.5382
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3692e-09 | -2.3984e-08 | 2.3175e-08 | -2.4651e-09 | 6.6374e-10 | 2.4117e-10 | -5.6419e-08 | 4.2558e-09 | -3.4212e-09 | 4.5249e-12 | 6.5578e-10 | -1.3903e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4226 | 0.60096 | 0.60282 | 1.4226 | 0.60096 | 0.60282 | 0.052309 | -101.7438 | 78.5382 | 0.052309 | -101.7438 | 78.5382
Line9_3_11 | 1.2032e-06 | 1.2286e-06 | 1.1779e-06 | 1.0316e-06 | 1.057e-06 | 1.0065e-06 | 2.7786e-07 | 2.8373e-07 | 2.7203e-07 | 2.3825e-07 | 2.4409e-07 | 2.3244e-07 | 1.6584e-08 | -1.6789e-07 | 1.6222e-07 | -1.668e-08 | 1.4457e-07 | -1.3881e-07 | -3.9493e-07 | 2.9791e-08 | -2.3949e-08 | 3.3852e-07 | -2.4879e-08 | 1.9137e-08 | 87.6477 | 88.3183 | 86.9359 | -92.7686 | -91.9792 | -93.6121 | 1.4226 | 0.60096 | 0.60282 | 1.4226 | 0.60096 | 0.60282 | 0.052312 | -101.7438 | 78.5382 | 0.05231 | -101.7438 | 78.5382

## LLG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2758e-08 | -1.2915e-07 | 1.248e-07 | -1.2844e-08 | 1.0822e-07 | -1.0378e-07 | -3.0382e-07 | 2.2918e-08 | -1.8423e-08 | 2.5319e-07 | -1.851e-08 | 1.4105e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3477 | 0.56933 | 0.57109 | 1.3477 | 0.56933 | 0.57109 | 0.052314 | -101.7438 | 78.5382 | 0.052313 | -101.7438 | 78.5382
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2758e-08 | -1.2915e-07 | 1.248e-07 | -1.2844e-08 | 1.0822e-07 | -1.0378e-07 | -3.0382e-07 | 2.2918e-08 | -1.8423e-08 | 2.5319e-07 | -1.8509e-08 | 1.4105e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3477 | 0.56933 | 0.57109 | 1.3477 | 0.56933 | 0.57109 | 0.05231 | -101.7438 | 78.5382 | 0.052308 | -101.7438 | 78.5382
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0632e-08 | -1.0763e-07 | 1.04e-07 | -1.0718e-08 | 8.6699e-08 | -8.2982e-08 | -2.5318e-07 | 1.9098e-08 | -1.5353e-08 | 2.0255e-07 | -1.469e-08 | 1.1034e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3477 | 0.56933 | 0.57109 | 1.3477 | 0.56933 | 0.57109 | 0.052308 | -101.7438 | 78.5382 | 0.052307 | -101.7438 | 78.5382
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.3791e-09 | -6.4577e-08 | 6.2399e-08 | -6.4652e-09 | 4.3647e-08 | -4.1383e-08 | -1.5191e-07 | 1.1459e-08 | -9.2117e-09 | 1.0128e-07 | -7.0507e-09 | 4.8933e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3477 | 0.56933 | 0.57109 | 1.3477 | 0.56933 | 0.57109 | 0.052307 | -101.7438 | 78.5382 | 0.052306 | -101.7438 | 78.5382
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1264e-09 | -2.1526e-08 | 2.08e-08 | -2.2125e-09 | 5.9571e-10 | 2.1645e-10 | -5.0636e-08 | 3.8196e-09 | -3.0706e-09 | 4.0604e-12 | 5.8857e-10 | -1.2478e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3477 | 0.56933 | 0.57109 | 1.3477 | 0.56933 | 0.57109 | 0.052307 | -101.7438 | 78.5382 | 0.052307 | -101.7438 | 78.5382
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2527e-09 | -4.3051e-08 | 4.1599e-08 | -4.3389e-09 | 2.2121e-08 | -2.0583e-08 | -1.0127e-07 | 7.6392e-09 | -6.1412e-09 | 5.064e-08 | -3.231e-09 | 1.8227e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3477 | 0.56933 | 0.57109 | 1.3477 | 0.56933 | 0.57109 | 0.052306 | -101.7438 | 78.5382 | 0.052306 | -101.7438 | 78.5382
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1264e-09 | -2.1526e-08 | 2.08e-08 | -2.2125e-09 | 5.9571e-10 | 2.1645e-10 | -5.0636e-08 | 3.8196e-09 | -3.0706e-09 | 4.0602e-12 | 5.8857e-10 | -1.2478e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3477 | 0.56933 | 0.57109 | 1.3477 | 0.56933 | 0.57109 | 0.052306 | -101.7438 | 78.5382 | 0.052306 | -101.7438 | 78.5382
Line16_4_18 | 0 | 2.3694 | 2.3804 | 0 | 2.3694 | 2.3804 | 0 | 0.54719 | 0.54973 | 0 | 0.54719 | 0.54973 | 2.1821e-09 | 0.10774 | 0.10885 | -2.2086e-09 | -8.1493e-15 | -1.2015e-15 | -5.0678e-08 | 0.1125 | 0.11311 | 5.9469e-12 | -2.8788e-13 | 2.7875e-13 | 0 | -147.9837 | 32.4393 | 0 | 32.0163 | -147.5607 | 1.3474 | 0.28467 | 0.28555 | 1.3471 | 0 | 0 | 0.064478 | -101.7438 | 78.5382 | 0.076648 | 0 | 0
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1264e-09 | -2.1526e-08 | 2.08e-08 | -2.2125e-09 | 5.9572e-10 | 2.1645e-10 | -5.0636e-08 | 3.8196e-09 | -3.0706e-09 | 4.0613e-12 | 5.8857e-10 | -1.2478e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3477 | 0.56933 | 0.57109 | 1.3477 | 0.56933 | 0.57109 | 0.052314 | -101.7438 | 78.5382 | 0.052314 | -101.7438 | 78.5382
Line1_1_3 | 1.3027e-06 | 1.3302e-06 | 1.2753e-06 | 1.1402e-06 | 1.1676e-06 | 1.1129e-06 | 3.0084e-07 | 3.0719e-07 | 2.9452e-07 | 2.6331e-07 | 2.6965e-07 | 2.5702e-07 | 1.7011e-08 | -1.7221e-07 | 1.664e-07 | -1.7097e-08 | 1.5128e-07 | -1.4538e-07 | -4.0509e-07 | 3.0557e-08 | -2.4565e-08 | 3.5446e-07 | -2.6149e-08 | 2.0246e-08 | 87.6477 | 88.3183 | 86.9359 | -92.7092 | -91.9368 | -93.5336 | 1.3477 | 0.56933 | 0.57109 | 1.3477 | 0.56933 | 0.57109 | 0.052314 | -101.7438 | 78.5382 | 0.052312 | -101.7438 | 78.5382
Line2_1_4 | 0 | 2.3694 | 2.3804 | 0 | 2.3694 | 2.3804 | 0 | 0.54719 | 0.54973 | 0 | 0.54719 | 0.54973 | 4.3129e-09 | 0.21547 | 0.2177 | -4.3926e-09 | -0.10774 | -0.10885 | -1.0134e-07 | 0.225 | 0.22621 | 5.0683e-08 | -0.1125 | -0.11311 | 0 | -147.9837 | 32.4393 | 0 | 32.0163 | -147.5607 | 1.3477 | 0.56933 | 0.57109 | 1.3474 | 0.28467 | 0.28555 | 0.052314 | -101.7438 | 78.5382 | 0.064478 | -101.7438 | 78.5382
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2527e-09 | -4.3051e-08 | 4.1599e-08 | -4.3388e-09 | 2.2121e-08 | -2.0583e-08 | -1.0127e-07 | 7.6392e-09 | -6.1412e-09 | 5.064e-08 | -3.2311e-09 | 1.8227e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3477 | 0.56933 | 0.57109 | 1.3477 | 0.56933 | 0.57109 | 0.052314 | -101.7438 | 78.5382 | 0.052314 | -101.7438 | 78.5382
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0632e-08 | -1.0763e-07 | 1.04e-07 | -1.0718e-08 | 8.6699e-08 | -8.2982e-08 | -2.5318e-07 | 1.9098e-08 | -1.5353e-08 | 2.0255e-07 | -1.469e-08 | 1.1034e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3477 | 0.56933 | 0.57109 | 1.3477 | 0.56933 | 0.57109 | 0.052313 | -101.7438 | 78.5382 | 0.052311 | -101.7438 | 78.5382
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.5055e-09 | -8.6103e-08 | 8.3199e-08 | -8.5916e-09 | 6.5173e-08 | -6.2183e-08 | -2.0254e-07 | 1.5278e-08 | -1.2282e-08 | 1.5191e-07 | -1.087e-08 | 7.9639e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3477 | 0.56933 | 0.57109 | 1.3477 | 0.56933 | 0.57109 | 0.052311 | -101.7438 | 78.5382 | 0.05231 | -101.7438 | 78.5382
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.3791e-09 | -6.4577e-08 | 6.2399e-08 | -6.4652e-09 | 4.3647e-08 | -4.1383e-08 | -1.5191e-07 | 1.1459e-08 | -9.2117e-09 | 1.0128e-07 | -7.0507e-09 | 4.8933e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3477 | 0.56933 | 0.57109 | 1.3477 | 0.56933 | 0.57109 | 0.05231 | -101.7438 | 78.5382 | 0.052309 | -101.7438 | 78.5382
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1264e-09 | -2.1526e-08 | 2.08e-08 | -2.2125e-09 | 5.9571e-10 | 2.1645e-10 | -5.0636e-08 | 3.8196e-09 | -3.0706e-09 | 4.0605e-12 | 5.8857e-10 | -1.2478e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3477 | 0.56933 | 0.57109 | 1.3477 | 0.56933 | 0.57109 | 0.052309 | -101.7438 | 78.5382 | 0.052309 | -101.7438 | 78.5382
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1264e-09 | -2.1526e-08 | 2.08e-08 | -2.2125e-09 | 5.9571e-10 | 2.1645e-10 | -5.0636e-08 | 3.8196e-09 | -3.0706e-09 | 4.0609e-12 | 5.8857e-10 | -1.2478e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3477 | 0.56933 | 0.57109 | 1.3477 | 0.56933 | 0.57109 | 0.052309 | -101.7438 | 78.5382 | 0.052309 | -101.7438 | 78.5382
Line9_3_11 | 1.1398e-06 | 1.1639e-06 | 1.1159e-06 | 0 | 1.0013e-06 | 0 | 2.6323e-07 | 2.6879e-07 | 2.5771e-07 | 0 | 2.3125e-07 | 0 | 1.4885e-08 | -1.5068e-07 | 1.456e-07 | -1.4971e-08 | 1.2975e-07 | -1.2458e-07 | -3.5445e-07 | 2.6737e-08 | -2.1494e-08 | 3.0382e-07 | -2.2329e-08 | 1.7176e-08 | 87.6477 | 88.3183 | 86.9359 | 0 | -91.9792 | 0 | 1.3477 | 0.56933 | 0.57109 | 1.3477 | 0.56933 | 0.57109 | 0.052312 | -101.7438 | 78.5382 | 0.05231 | -101.7438 | 78.5382

## LLG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.7428e-08 | -9.7273e-08 | 1.4054e-07 | 2.9873e-08 | 8.1519e-08 | -1.1723e-07 | -1.8285e-07 | 5.7998e-08 | -1.0581e-08 | 1.527e-07 | -4.7648e-08 | 7.792e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2375 | 0.75062 | 0.93482 | 1.2375 | 0.75062 | 0.93482 | 4.3949 | -104.8385 | 101.642 | 4.3949 | -104.8385 | 101.642
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.7428e-08 | -9.7273e-08 | 1.4054e-07 | 2.9873e-08 | 8.1519e-08 | -1.1723e-07 | -1.8285e-07 | 5.7998e-08 | -1.0581e-08 | 1.527e-07 | -4.7648e-08 | 7.792e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2375 | 0.75062 | 0.93482 | 1.2375 | 0.75062 | 0.93482 | 4.3948 | -104.8385 | 101.642 | 4.3948 | -104.8385 | 101.642
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.119e-08 | -8.1061e-08 | 1.1712e-07 | 2.3635e-08 | 6.5306e-08 | -9.3807e-08 | -1.5237e-07 | 4.8332e-08 | -8.8176e-09 | 1.2223e-07 | -3.7982e-08 | 6.0285e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2375 | 0.75062 | 0.93482 | 1.2375 | 0.75062 | 0.93482 | 4.3948 | -104.8385 | 101.642 | 4.3948 | -104.8385 | 101.642
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.8714e-08 | -4.8637e-08 | 7.027e-08 | 1.1159e-08 | 3.2882e-08 | -4.696e-08 | -9.1425e-08 | 2.8999e-08 | -5.2906e-09 | 6.128e-08 | -1.8649e-08 | 2.5015e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2375 | 0.75062 | 0.93482 | 1.2375 | 0.75062 | 0.93482 | 4.3948 | -104.8385 | 101.642 | 4.3948 | -104.8385 | 101.642
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.238e-09 | -1.6212e-08 | 2.3423e-08 | -1.3172e-09 | 4.5773e-10 | -1.137e-10 | -3.0475e-08 | 9.6664e-09 | -1.7635e-09 | 3.3032e-10 | 6.8384e-10 | -1.0256e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2375 | 0.75062 | 0.93482 | 1.2375 | 0.75062 | 0.93482 | 4.3948 | -104.8385 | 101.642 | 4.3948 | -104.8385 | 101.642
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.2476e-08 | -3.2424e-08 | 4.6847e-08 | 4.9208e-09 | 1.667e-08 | -2.3537e-08 | -6.095e-08 | 1.9333e-08 | -3.527e-09 | 3.0805e-08 | -8.9825e-09 | 7.3793e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2375 | 0.75062 | 0.93482 | 1.2375 | 0.75062 | 0.93482 | 4.3948 | -104.8385 | 101.642 | 4.3948 | -104.8385 | 101.642
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.238e-09 | -1.6212e-08 | 2.3423e-08 | -1.3172e-09 | 4.5773e-10 | -1.137e-10 | -3.0475e-08 | 9.6664e-09 | -1.7635e-09 | 3.3032e-10 | 6.8384e-10 | -1.0256e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2375 | 0.75062 | 0.93482 | 1.2375 | 0.75062 | 0.93482 | 4.3948 | -104.8385 | 101.642 | 4.3948 | -104.8385 | 101.642
Line16_4_18 | 0 | 0.024321 | 0.030305 | 0 | 0.024321 | 0.030305 | 0 | 0.0056168 | 0.0069985 | 0 | 0.0056168 | 0.0069985 | -6.2143e-09 | 0.0029681 | 0.0046097 | -1.3146e-09 | -0.0029576 | -0.0045918 | -3.0508e-08 | 0.0029707 | 0.0046083 | 3.3115e-10 | -0.0029576 | -0.0045918 | 0 | -149.8894 | 56.6601 | 0 | 30.1108 | -123.34 | 1.2373 | 0.74765 | 0.93135 | 1.237 | 0.74468 | 0.92788 | 4.4012 | -104.8637 | 101.651 | 4.4076 | -104.8892 | 101.66
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.238e-09 | -1.6212e-08 | 2.3423e-08 | -1.3172e-09 | 4.5773e-10 | -1.137e-10 | -3.0475e-08 | 9.6664e-09 | -1.7635e-09 | 3.3032e-10 | 6.8384e-10 | -1.0256e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2375 | 0.75062 | 0.93482 | 1.2375 | 0.75062 | 0.93482 | 4.3949 | -104.8385 | 101.642 | 4.3949 | -104.8385 | 101.642
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.9904e-08 | -1.297e-07 | 1.8739e-07 | 4.2349e-08 | 1.1394e-07 | -1.6408e-07 | -2.438e-07 | 7.7331e-08 | -1.4108e-08 | 2.1365e-07 | -6.6981e-08 | 1.1319e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2375 | 0.75062 | 0.93482 | 1.2375 | 0.75062 | 0.93482 | 4.3949 | -104.8385 | 101.642 | 4.3949 | -104.8385 | 101.642
Line2_1_4 | 0 | 0.024321 | 0.030305 | 0 | 0.024321 | 0.030305 | 0 | 0.0056168 | 0.0069986 | 0 | 0.0056168 | 0.0069985 | -1.2451e-08 | 0.0029785 | 0.0046277 | 4.8984e-09 | -0.0029681 | -0.0046097 | -6.1001e-08 | 0.0029839 | 0.0046247 | 3.0839e-08 | -0.0029707 | -0.0046083 | 0 | -149.8897 | 56.6603 | 0 | 30.1106 | -123.3399 | 1.2375 | 0.75062 | 0.93482 | 1.2373 | 0.74765 | 0.93135 | 4.3949 | -104.8385 | 101.642 | 4.4012 | -104.8637 | 101.651
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.2476e-08 | -3.2424e-08 | 4.6847e-08 | 4.9208e-09 | 1.667e-08 | -2.3537e-08 | -6.095e-08 | 1.9333e-08 | -3.527e-09 | 3.0805e-08 | -8.9825e-09 | 7.3794e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2375 | 0.75062 | 0.93482 | 1.2375 | 0.75062 | 0.93482 | 4.3949 | -104.8385 | 101.642 | 4.3949 | -104.8385 | 101.642
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.119e-08 | -8.1061e-08 | 1.1712e-07 | 2.3635e-08 | 6.5306e-08 | -9.3807e-08 | -1.5237e-07 | 4.8332e-08 | -8.8176e-09 | 1.2223e-07 | -3.7982e-08 | 6.0285e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2375 | 0.75062 | 0.93482 | 1.2375 | 0.75062 | 0.93482 | 4.3949 | -104.8385 | 101.642 | 4.3949 | -104.8385 | 101.642
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.4952e-08 | -6.4849e-08 | 9.3694e-08 | 1.7397e-08 | 4.9094e-08 | -7.0384e-08 | -1.219e-07 | 3.8666e-08 | -7.0541e-09 | 9.1755e-08 | -2.8315e-08 | 4.265e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2375 | 0.75062 | 0.93482 | 1.2375 | 0.75062 | 0.93482 | 4.3949 | -104.8385 | 101.642 | 4.3948 | -104.8385 | 101.642
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.8714e-08 | -4.8637e-08 | 7.027e-08 | 1.1159e-08 | 3.2882e-08 | -4.696e-08 | -9.1425e-08 | 2.8999e-08 | -5.2906e-09 | 6.128e-08 | -1.8649e-08 | 2.5015e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2375 | 0.75062 | 0.93482 | 1.2375 | 0.75062 | 0.93482 | 4.3948 | -104.8385 | 101.642 | 4.3948 | -104.8385 | 101.642
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.238e-09 | -1.6212e-08 | 2.3423e-08 | -1.3172e-09 | 4.5773e-10 | -1.137e-10 | -3.0475e-08 | 9.6664e-09 | -1.7635e-09 | 3.3032e-10 | 6.8384e-10 | -1.0256e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2375 | 0.75062 | 0.93482 | 1.2375 | 0.75062 | 0.93482 | 4.3948 | -104.8385 | 101.642 | 4.3948 | -104.8385 | 101.642
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.238e-09 | -1.6212e-08 | 2.3423e-08 | -1.3172e-09 | 4.5773e-10 | -1.137e-10 | -3.0475e-08 | 9.6664e-09 | -1.7635e-09 | 3.3032e-10 | 6.8384e-10 | -1.0256e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2375 | 0.75062 | 0.93482 | 1.2375 | 0.75062 | 0.93482 | 4.3948 | -104.8385 | 101.642 | 4.3948 | -104.8385 | 101.642
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.3666e-08 | -1.1349e-07 | 1.6396e-07 | 3.6111e-08 | 9.7731e-08 | -1.4065e-07 | -2.1332e-07 | 6.7665e-08 | -1.2345e-08 | 1.8318e-07 | -5.7314e-08 | 9.5555e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2375 | 0.75062 | 0.93482 | 1.2375 | 0.75062 | 0.93482 | 4.3949 | -104.8385 | 101.642 | 4.3948 | -104.8385 | 101.642

## LLG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.3592e-08 | -8.7303e-08 | 1.2614e-07 | 2.6811e-08 | 7.3164e-08 | -1.0522e-07 | -1.6411e-07 | 5.2054e-08 | -9.4966e-09 | 1.3705e-07 | -4.2764e-08 | 6.9934e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1724 | 0.71112 | 0.88562 | 1.1724 | 0.71112 | 0.88562 | 4.3949 | -104.8385 | 101.642 | 4.3949 | -104.8385 | 101.642
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.3592e-08 | -8.7303e-08 | 1.2614e-07 | 2.6811e-08 | 7.3164e-08 | -1.0522e-07 | -1.6411e-07 | 5.2054e-08 | -9.4966e-09 | 1.3705e-07 | -4.2764e-08 | 6.9934e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1724 | 0.71112 | 0.88562 | 1.1724 | 0.71112 | 0.88562 | 4.3948 | -104.8385 | 101.642 | 4.3948 | -104.8385 | 101.642
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.7993e-08 | -7.2753e-08 | 1.0511e-07 | 2.1213e-08 | 5.8613e-08 | -8.4193e-08 | -1.3676e-07 | 4.3378e-08 | -7.9139e-09 | 1.097e-07 | -3.4089e-08 | 5.4106e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1724 | 0.71112 | 0.88562 | 1.1724 | 0.71112 | 0.88562 | 4.3948 | -104.8385 | 101.642 | 4.3948 | -104.8385 | 101.642
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.6796e-08 | -4.3652e-08 | 6.3068e-08 | 1.0015e-08 | 2.9512e-08 | -4.2147e-08 | -8.2054e-08 | 2.6027e-08 | -4.7483e-09 | 5.4999e-08 | -1.6738e-08 | 2.2451e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1724 | 0.71112 | 0.88562 | 1.1724 | 0.71112 | 0.88562 | 4.3948 | -104.8385 | 101.642 | 4.3948 | -104.8385 | 101.642
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.5987e-09 | -1.4551e-08 | 2.1023e-08 | -1.1822e-09 | 4.1082e-10 | -1.0205e-10 | -2.7351e-08 | 8.6756e-09 | -1.5828e-09 | 2.9646e-10 | 6.1375e-10 | -9.2047e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1724 | 0.71112 | 0.88562 | 1.1724 | 0.71112 | 0.88562 | 4.3948 | -104.8385 | 101.642 | 4.3948 | -104.8385 | 101.642
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.1197e-08 | -2.9101e-08 | 4.2045e-08 | 4.4165e-09 | 1.4961e-08 | -2.1125e-08 | -5.4703e-08 | 1.7351e-08 | -3.1655e-09 | 2.7648e-08 | -8.0619e-09 | 6.623e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1724 | 0.71112 | 0.88562 | 1.1724 | 0.71112 | 0.88562 | 4.3948 | -104.8385 | 101.642 | 4.3948 | -104.8385 | 101.642
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.5987e-09 | -1.4551e-08 | 2.1023e-08 | -1.1822e-09 | 4.1082e-10 | -1.0205e-10 | -2.7351e-08 | 8.6756e-09 | -1.5828e-09 | 2.9646e-10 | 6.1375e-10 | -9.2047e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1724 | 0.71112 | 0.88562 | 1.1724 | 0.71112 | 0.88562 | 4.3948 | -104.8385 | 101.642 | 4.3948 | -104.8385 | 101.642
Line16_4_18 | 0 | 0.023041 | 0.02871 | 0 | 0.023041 | 0.02871 | 0 | 0.0053211 | 0.0066302 | 0 | 0.0053211 | 0.0066302 | -5.5774e-09 | 0.0026639 | 0.0041373 | -1.1798e-09 | -0.0026545 | -0.0041212 | -2.7381e-08 | 0.0026663 | 0.0041359 | 2.9721e-10 | -0.0026545 | -0.0041212 | 0 | -149.8894 | 56.6601 | 0 | 30.1108 | -123.34 | 1.1721 | 0.7083 | 0.88233 | 1.1719 | 0.70549 | 0.87905 | 4.4012 | -104.8637 | 101.651 | 4.4076 | -104.8892 | 101.66
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.5987e-09 | -1.4551e-08 | 2.1023e-08 | -1.1822e-09 | 4.1082e-10 | -1.0205e-10 | -2.7351e-08 | 8.6756e-09 | -1.5828e-09 | 2.9646e-10 | 6.1375e-10 | -9.2047e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1724 | 0.71112 | 0.88562 | 1.1724 | 0.71112 | 0.88562 | 4.3949 | -104.8385 | 101.642 | 4.3949 | -104.8385 | 101.642
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.4789e-08 | -1.164e-07 | 1.6818e-07 | 3.8009e-08 | 1.0226e-07 | -1.4726e-07 | -2.1881e-07 | 6.9405e-08 | -1.2662e-08 | 1.9176e-07 | -6.0116e-08 | 1.0159e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1724 | 0.71112 | 0.88562 | 1.1724 | 0.71112 | 0.88562 | 4.3949 | -104.8385 | 101.642 | 4.3949 | -104.8385 | 101.642
Line2_1_4 | 0 | 0.023041 | 0.02871 | 0 | 0.023041 | 0.02871 | 0 | 0.0053211 | 0.0066302 | 0 | 0.0053211 | 0.0066302 | -1.1175e-08 | 0.0026733 | 0.0041534 | 4.3963e-09 | -0.0026639 | -0.0041373 | -5.4749e-08 | 0.002678 | 0.0041507 | 2.7678e-08 | -0.0026663 | -0.0041359 | 0 | -149.8897 | 56.6603 | 0 | 30.1106 | -123.3399 | 1.1724 | 0.71112 | 0.88562 | 1.1721 | 0.7083 | 0.88233 | 4.3949 | -104.8385 | 101.642 | 4.4012 | -104.8637 | 101.651
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.1197e-08 | -2.9101e-08 | 4.2045e-08 | 4.4165e-09 | 1.4961e-08 | -2.1125e-08 | -5.4703e-08 | 1.7351e-08 | -3.1656e-09 | 2.7648e-08 | -8.0619e-09 | 6.6231e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1724 | 0.71112 | 0.88562 | 1.1724 | 0.71112 | 0.88562 | 4.3949 | -104.8385 | 101.642 | 4.3949 | -104.8385 | 101.642
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.7993e-08 | -7.2753e-08 | 1.0511e-07 | 2.1213e-08 | 5.8613e-08 | -8.4193e-08 | -1.3676e-07 | 4.3378e-08 | -7.9139e-09 | 1.097e-07 | -3.4089e-08 | 5.4106e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1724 | 0.71112 | 0.88562 | 1.1724 | 0.71112 | 0.88562 | 4.3949 | -104.8385 | 101.642 | 4.3949 | -104.8385 | 101.642
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.2395e-08 | -5.8202e-08 | 8.4091e-08 | 1.5614e-08 | 4.4062e-08 | -6.317e-08 | -1.0941e-07 | 3.4703e-08 | -6.3311e-09 | 8.2351e-08 | -2.5413e-08 | 3.8278e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1724 | 0.71112 | 0.88562 | 1.1724 | 0.71112 | 0.88562 | 4.3949 | -104.8385 | 101.642 | 4.3948 | -104.8385 | 101.642
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.6796e-08 | -4.3652e-08 | 6.3068e-08 | 1.0015e-08 | 2.9512e-08 | -4.2147e-08 | -8.2054e-08 | 2.6027e-08 | -4.7483e-09 | 5.4999e-08 | -1.6738e-08 | 2.2451e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1724 | 0.71112 | 0.88562 | 1.1724 | 0.71112 | 0.88562 | 4.3948 | -104.8385 | 101.642 | 4.3948 | -104.8385 | 101.642
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.5987e-09 | -1.4551e-08 | 2.1023e-08 | -1.1822e-09 | 4.1082e-10 | -1.0205e-10 | -2.7351e-08 | 8.6756e-09 | -1.5828e-09 | 2.9646e-10 | 6.1375e-10 | -9.2047e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1724 | 0.71112 | 0.88562 | 1.1724 | 0.71112 | 0.88562 | 4.3948 | -104.8385 | 101.642 | 4.3948 | -104.8385 | 101.642
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.5987e-09 | -1.4551e-08 | 2.1023e-08 | -1.1822e-09 | 4.1082e-10 | -1.0205e-10 | -2.7351e-08 | 8.6756e-09 | -1.5828e-09 | 2.9646e-10 | 6.1375e-10 | -9.2047e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1724 | 0.71112 | 0.88562 | 1.1724 | 0.71112 | 0.88562 | 4.3948 | -104.8385 | 101.642 | 4.3948 | -104.8385 | 101.642
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.9191e-08 | -1.0185e-07 | 1.4716e-07 | 3.241e-08 | 8.7714e-08 | -1.2624e-07 | -1.9146e-07 | 6.0729e-08 | -1.1079e-08 | 1.644e-07 | -5.144e-08 | 8.5762e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1724 | 0.71112 | 0.88562 | 1.1724 | 0.71112 | 0.88562 | 4.3949 | -104.8385 | 101.642 | 4.3948 | -104.8385 | 101.642