## LLL_max_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 2.1767 | 2.1767 | 0 | 0 | 1.508 | 1.508 | 0.56854 | -0.42641 | 1.1371 | -0.85282 | -67.8829 | 112.1171 | 0.84302 | 0.63226 | -4.4479 | -4.4479
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84302 | 0.84302 | -4.4479 | -4.4479
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84302 | 0.84302 | -4.4479 | -4.4479
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84302 | 0.84302 | -4.4479 | -4.4479
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84302 | 0.84302 | -4.4479 | -4.4479
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84302 | 0.84302 | -4.4479 | -4.4479
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84302 | 0.84302 | -4.4479 | -4.4479
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84302 | 0.84302 | -4.4479 | -4.4479
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84302 | 0.84302 | -4.4479 | -4.4479
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84302 | 0.84302 | -4.4479 | -4.4479
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84302 | 0.84302 | -4.4479 | -4.4479
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84302 | 0.84302 | -4.4479 | -4.4479
Line4_2_6 | 2.1767 | 2.1767 | 0 | 0 | 1.508 | 1.508 | 0.42641 | -0.28427 | 0.85282 | -0.56854 | -67.8829 | 112.1171 | 0.63226 | 0.42151 | -4.4479 | -4.4479
Line5_6_7 | 2.1767 | 2.1767 | 0 | 0 | 1.508 | 1.508 | 0.28427 | -0.14214 | 0.56854 | -0.28427 | -67.8829 | 112.1171 | 0.42151 | 0.21075 | -4.4479 | -4.4479
Line6_7_8 | 2.1767 | 2.1767 | 0 | 4.0311 | 1.508 | 1.508 | 0.14214 | -1e-07 | 0.28427 | -1e-07 | -67.8829 | 112.1171 | 0.21075 | 0 | -4.4479 | 0
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4632e-22 | 0 | 4.2265e-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4632e-22 | 0 | 4.2265e-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84302 | 0.84302 | -4.4479 | -4.4479

## LLL_max_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 2.259 | 2.259 | 0 | 0 | 1.5651 | 1.5651 | 0.61237 | -0.45928 | 1.2247 | -0.91856 | -68.05 | 111.95 | 0.87491 | 0.65618 | -4.615 | -4.615
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87491 | 0.87491 | -4.615 | -4.615
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87491 | 0.87491 | -4.615 | -4.615
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87491 | 0.87491 | -4.615 | -4.615
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87491 | 0.87491 | -4.615 | -4.615
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87491 | 0.87491 | -4.615 | -4.615
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87491 | 0.87491 | -4.615 | -4.615
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87491 | 0.87491 | -4.615 | -4.615
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87491 | 0.87491 | -4.615 | -4.615
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87491 | 0.87491 | -4.615 | -4.615
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87491 | 0.87491 | -4.615 | -4.615
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87491 | 0.87491 | -4.615 | -4.615
Line4_2_6 | 2.259 | 2.259 | 0 | 0 | 1.5651 | 1.5651 | 0.45928 | -0.30619 | 0.91856 | -0.61237 | -68.05 | 111.95 | 0.65618 | 0.43745 | -4.615 | -4.615
Line5_6_7 | 2.259 | 2.259 | 0 | 0 | 1.5651 | 1.5651 | 0.30619 | -0.15309 | 0.61237 | -0.30619 | -68.05 | 111.95 | 0.43745 | 0.21873 | -4.615 | -4.615
Line6_7_8 | 2.259 | 2.259 | 0 | 4.1931 | 1.5651 | 1.5651 | 0.15309 | -1e-07 | 0.30619 | -1e-07 | -68.05 | 111.95 | 0.21873 | 0 | -4.615 | 0
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1499e-21 | 0 | -5.8009e-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1499e-21 | 0 | -5.8009e-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87491 | 0.87491 | -4.615 | -4.615

## LLL_max_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 0.033802 | 0.033802 | 0 | 0 | 0.023418 | 0.023418 | 0.017275 | -0.017241 | 0.017412 | -0.017344 | -45.346 | 134.654 | 1.0474 | 1.0443 | -0.11952 | -0.17563
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.11952 | -0.11952
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.11952 | -0.11952
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.11952 | -0.11952
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.11952 | -0.11952
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.11952 | -0.11952
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.11952 | -0.11952
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.11952 | -0.11952
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.11952 | -0.11952
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.11952 | -0.11952
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.11952 | -0.11952
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.11952 | -0.11952
Line4_2_6 | 0.033802 | 0.033802 | 0 | 0 | 0.023418 | 0.023418 | 0.017241 | -0.017207 | 0.017344 | -0.017275 | -45.346 | 134.654 | 1.0443 | 1.0412 | -0.17563 | -0.23207
Line5_6_7 | 0.033802 | 0.033802 | 0 | 0 | 0.023418 | 0.023418 | 0.017207 | -0.017173 | 0.017275 | -0.017207 | -45.346 | 134.654 | 1.0412 | 1.0381 | -0.23207 | -0.28886
Line6_7_8 | 0.033802 | 0.033802 | 0 | 0.0626 | 0.023418 | 0.023418 | 0.017173 | -0.017138 | 0.017207 | -0.017138 | -45.346 | 134.654 | 1.0381 | 1.035 | -0.28886 | -0.34598
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | -1.7102e-10 | 0 | 7.2182e-11 | 0 | 0 | 0 | 1.035 | 1.035 | -0.34598 | -0.34598
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | -1.7102e-10 | 0 | 7.2182e-11 | 0 | 0 | 0 | 1.035 | 1.035 | -0.34598 | -0.34598
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.11952 | -0.11952

## LLL_max_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 0.035407 | 0.035407 | 0 | 0 | 0.024531 | 0.024531 | 0.018955 | -0.018918 | 0.019106 | -0.019031 | -45.3516 | 134.6484 | 1.0971 | 1.0939 | -0.12515 | -0.18126
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12515 | -0.12515
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12515 | -0.12515
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12515 | -0.12515
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12515 | -0.12515
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12515 | -0.12515
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12515 | -0.12515
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12515 | -0.12515
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12515 | -0.12515
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12515 | -0.12515
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12515 | -0.12515
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12515 | -0.12515
Line4_2_6 | 0.035407 | 0.035407 | 0 | 0 | 0.024531 | 0.024531 | 0.018918 | -0.01888 | 0.019031 | -0.018955 | -45.3516 | 134.6484 | 1.0939 | 1.0906 | -0.18126 | -0.23771
Line5_6_7 | 0.035407 | 0.035407 | 0 | 0 | 0.024531 | 0.024531 | 0.01888 | -0.018842 | 0.018955 | -0.01888 | -45.3516 | 134.6484 | 1.0906 | 1.0874 | -0.23771 | -0.29449
Line6_7_8 | 0.035407 | 0.035407 | 0 | 0.065722 | 0.024531 | 0.024531 | 0.018842 | -0.018805 | 0.01888 | -0.018805 | -45.3516 | 134.6484 | 1.0874 | 1.0841 | -0.29449 | -0.35161
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | -1.8919e-10 | 0 | 8.0501e-11 | 0 | 0 | 0 | 1.0841 | 1.0841 | -0.35161 | -0.35161
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | -1.8919e-10 | 0 | 8.0501e-11 | 0 | 0 | 0 | 1.0841 | 1.0841 | -0.35161 | -0.35161
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12515 | -0.12515

## LLL_min_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 1.6801 | 1.6801 | 0 | 0 | 1.164 | 1.164 | 0.65034 | -0.48775 | 0.67743 | -0.50807 | -52.8727 | 127.1273 | 0.80677 | 0.60508 | -6.7036 | -6.7036
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80677 | 0.80677 | -6.7036 | -6.7036
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80677 | 0.80677 | -6.7036 | -6.7036
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80677 | 0.80677 | -6.7036 | -6.7036
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80677 | 0.80677 | -6.7036 | -6.7036
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80677 | 0.80677 | -6.7036 | -6.7036
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80677 | 0.80677 | -6.7036 | -6.7036
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80677 | 0.80677 | -6.7036 | -6.7036
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80677 | 0.80677 | -6.7036 | -6.7036
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80677 | 0.80677 | -6.7036 | -6.7036
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80677 | 0.80677 | -6.7036 | -6.7036
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80677 | 0.80677 | -6.7036 | -6.7036
Line4_2_6 | 1.6801 | 1.6801 | 0 | 0 | 1.164 | 1.164 | 0.48775 | -0.32517 | 0.50807 | -0.33872 | -52.8727 | 127.1273 | 0.60508 | 0.40338 | -6.7036 | -6.7036
Line5_6_7 | 1.6801 | 1.6801 | 0 | 0 | 1.164 | 1.164 | 0.32517 | -0.16258 | 0.33872 | -0.16936 | -52.8727 | 127.1273 | 0.40338 | 0.20169 | -6.7036 | -6.7036
Line6_7_8 | 1.6801 | 1.6801 | 0 | 2.6638 | 1.164 | 1.164 | 0.16258 | -1e-07 | 0.16936 | -1e-07 | -52.8727 | 127.1273 | 0.20169 | 0 | -6.7036 | 0
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 7.0075e-22 | 0 | 9.1561e-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 7.0075e-22 | 0 | 9.1561e-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80677 | 0.80677 | -6.7036 | -6.7036

## LLL_min_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 1.5916 | 1.5916 | 0 | 0 | 1.1027 | 1.1027 | 0.58368 | -0.43776 | 0.608 | -0.456 | -52.8727 | 127.1273 | 0.76431 | 0.57323 | -6.7036 | -6.7036
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76431 | 0.76431 | -6.7036 | -6.7036
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76431 | 0.76431 | -6.7036 | -6.7036
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76431 | 0.76431 | -6.7036 | -6.7036
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76431 | 0.76431 | -6.7036 | -6.7036
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76431 | 0.76431 | -6.7036 | -6.7036
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76431 | 0.76431 | -6.7036 | -6.7036
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76431 | 0.76431 | -6.7036 | -6.7036
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76431 | 0.76431 | -6.7036 | -6.7036
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76431 | 0.76431 | -6.7036 | -6.7036
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76431 | 0.76431 | -6.7036 | -6.7036
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76431 | 0.76431 | -6.7036 | -6.7036
Line4_2_6 | 1.5916 | 1.5916 | 0 | 0 | 1.1027 | 1.1027 | 0.43776 | -0.29184 | 0.456 | -0.304 | -52.8727 | 127.1273 | 0.57323 | 0.38215 | -6.7036 | -6.7036
Line5_6_7 | 1.5916 | 1.5916 | 0 | 0 | 1.1027 | 1.1027 | 0.29184 | -0.14592 | 0.304 | -0.152 | -52.8727 | 127.1273 | 0.38215 | 0.19108 | -6.7036 | -6.7036
Line6_7_8 | 1.5916 | 1.5916 | 0 | 2.5236 | 1.1027 | 1.1027 | 0.14592 | -1e-07 | 0.152 | -1e-07 | -52.8727 | 127.1273 | 0.19108 | 0 | -6.7036 | 0
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 6.276e-22 | 0 | 8.2153e-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 6.276e-22 | 0 | 8.2153e-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76431 | 0.76431 | -6.7036 | -6.7036

## LLL_min_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 0.030469 | 0.030469 | 0 | 0 | 0.02111 | 0.02111 | 0.01414 | -0.014086 | 0.014149 | -0.014093 | -45.1423 | 134.8577 | 0.94756 | 0.9439 | -0.12428 | -0.12874
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94756 | 0.94756 | -0.12428 | -0.12428
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94756 | 0.94756 | -0.12428 | -0.12428
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94756 | 0.94756 | -0.12428 | -0.12428
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94756 | 0.94756 | -0.12428 | -0.12428
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94756 | 0.94756 | -0.12428 | -0.12428
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94756 | 0.94756 | -0.12428 | -0.12428
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94756 | 0.94756 | -0.12428 | -0.12428
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94756 | 0.94756 | -0.12428 | -0.12428
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94756 | 0.94756 | -0.12428 | -0.12428
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94756 | 0.94756 | -0.12428 | -0.12428
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94756 | 0.94756 | -0.12428 | -0.12428
Line4_2_6 | 0.030469 | 0.030469 | 0 | 0 | 0.02111 | 0.02111 | 0.014086 | -0.014033 | 0.014093 | -0.014037 | -45.1423 | 134.8577 | 0.9439 | 0.94024 | -0.12874 | -0.13323
Line5_6_7 | 0.030469 | 0.030469 | 0 | 0 | 0.02111 | 0.02111 | 0.014033 | -0.013979 | 0.014037 | -0.013981 | -45.1423 | 134.8577 | 0.94024 | 0.93659 | -0.13323 | -0.13776
Line6_7_8 | 0.030469 | 0.030469 | 0 | 0.04831 | 0.02111 | 0.02111 | 0.013979 | -0.013926 | 0.013981 | -0.013926 | -45.1423 | 134.8577 | 0.93659 | 0.93293 | -0.13776 | -0.14233
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | -1.7514e-10 | 0 | 2.4218e-11 | 0 | 0 | 0 | 0.93293 | 0.93293 | -0.14233 | -0.14233
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | -1.7514e-10 | 0 | 2.4218e-11 | 0 | 0 | 0 | 0.93293 | 0.93293 | -0.14233 | -0.14233
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94756 | 0.94756 | -0.12428 | -0.12428

## LLL_min_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 0.028866 | 0.028866 | 0 | 0 | 0.019999 | 0.019999 | 0.01269 | -0.012642 | 0.012698 | -0.012648 | -45.1423 | 134.8577 | 0.89769 | 0.89422 | -0.12428 | -0.12874
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89769 | 0.89769 | -0.12428 | -0.12428
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89769 | 0.89769 | -0.12428 | -0.12428
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89769 | 0.89769 | -0.12428 | -0.12428
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89769 | 0.89769 | -0.12428 | -0.12428
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89769 | 0.89769 | -0.12428 | -0.12428
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89769 | 0.89769 | -0.12428 | -0.12428
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89769 | 0.89769 | -0.12428 | -0.12428
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89769 | 0.89769 | -0.12428 | -0.12428
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89769 | 0.89769 | -0.12428 | -0.12428
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89769 | 0.89769 | -0.12428 | -0.12428
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89769 | 0.89769 | -0.12428 | -0.12428
Line4_2_6 | 0.028866 | 0.028866 | 0 | 0 | 0.019999 | 0.019999 | 0.012642 | -0.012594 | 0.012648 | -0.012598 | -45.1423 | 134.8577 | 0.89422 | 0.89076 | -0.12874 | -0.13323
Line5_6_7 | 0.028866 | 0.028866 | 0 | 0 | 0.019999 | 0.019999 | 0.012594 | -0.012546 | 0.012598 | -0.012548 | -45.1423 | 134.8577 | 0.89076 | 0.88729 | -0.13323 | -0.13776
Line6_7_8 | 0.028866 | 0.028866 | 0 | 0.045767 | 0.019999 | 0.019999 | 0.012546 | -0.012498 | 0.012548 | -0.012498 | -45.1423 | 134.8577 | 0.88729 | 0.88383 | -0.13776 | -0.14233
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | -1.5719e-10 | 0 | 2.1736e-11 | 0 | 0 | 0 | 0.88383 | 0.88383 | -0.14233 | -0.14233
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | -1.5719e-10 | 0 | 2.1736e-11 | 0 | 0 | 0 | 0.88383 | 0.88383 | -0.14233 | -0.14233
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89769 | 0.89769 | -0.12428 | -0.12428

## LL_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 1.885 | 1.885 | 0 | 1.885 | 1.885 | 0 | 0.43533 | 0.43533 | 0 | 0.43533 | 0.43533 | 9.3259e-16 | 0.35387 | -0.069596 | -9.3259e-16 | -0.31833 | 0.10513 | -3.1086e-16 | 0.19822 | 0.37032 | 3.1086e-16 | -0.12715 | -0.29925 | 0 | -157.8829 | 22.1171 | 0 | 22.1171 | -157.8829 | 1.05 | 0.93171 | 0.86555 | 1.05 | 0.78742 | 0.7286 | -1.1514e-11 | -128.6271 | 122.7608 | -1.1529e-11 | -136.1092 | 131.4739
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1086e-16 | -2.1811e-09 | -3.489e-09 | -2.9143e-16 | 2.1811e-09 | 3.489e-09 | 1.9429e-17 | 3.2284e-09 | -9.6307e-10 | -3.8858e-17 | -3.2284e-09 | 9.6307e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.93171 | 0.86555 | 1.05 | 0.93171 | 0.86555 | -1.1527e-11 | -128.6271 | 122.7608 | -1.1532e-11 | -128.6271 | 122.7608
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5258e-16 | -1.8176e-09 | -2.9075e-09 | -2.72e-16 | 1.8176e-09 | 2.9075e-09 | -1.9429e-17 | 2.6904e-09 | -8.0256e-10 | 1.9429e-17 | -2.6904e-09 | 8.0256e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.93171 | 0.86555 | 1.05 | 0.93171 | 0.86555 | -1.1532e-11 | -128.6271 | 122.7608 | -1.1537e-11 | -128.6271 | 122.7608
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5543e-16 | -1.0906e-09 | -1.7445e-09 | -1.5543e-16 | 1.0906e-09 | 1.7445e-09 | 3.8858e-17 | 1.6142e-09 | -4.8153e-10 | -3.8858e-17 | -1.6142e-09 | 4.8153e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.93171 | 0.86555 | 1.05 | 0.93171 | 0.86555 | -1.1537e-11 | -128.6271 | 122.7608 | -1.1539e-11 | -128.6271 | 122.7608
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9429e-17 | -3.6352e-10 | -5.8151e-10 | 3.9122e-30 | 3.6352e-10 | 5.8151e-10 | -1.9429e-17 | 5.3807e-10 | -1.6051e-10 | 1.9429e-17 | -5.3807e-10 | 1.6051e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.93171 | 0.86555 | 1.05 | 0.93171 | 0.86555 | -1.1537e-11 | -128.6271 | 122.7608 | -1.1537e-11 | -128.6271 | 122.7608
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.7145e-17 | -7.2704e-10 | -1.163e-09 | -1.1657e-16 | 7.2704e-10 | 1.163e-09 | 1.9429e-17 | 1.0761e-09 | -3.2102e-10 | 2.3479e-29 | -1.0761e-09 | 3.2102e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.93171 | 0.86555 | 1.05 | 0.93171 | 0.86555 | -1.1539e-11 | -128.6271 | 122.7608 | -1.154e-11 | -128.6271 | 122.7608
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.9429e-17 | -3.6352e-10 | -5.8151e-10 | 1.9429e-17 | 3.6352e-10 | 5.8151e-10 | 3.9131e-30 | 5.3807e-10 | -1.6051e-10 | -3.9132e-30 | -5.3807e-10 | 1.6051e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.93171 | 0.86555 | 1.05 | 0.93171 | 0.86555 | -1.154e-11 | -128.6271 | 122.7608 | -1.154e-11 | -128.6271 | 122.7608
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9047e-30 | -3.6352e-10 | -5.8151e-10 | 1.9429e-17 | 3.6352e-10 | 5.8151e-10 | 1.9429e-17 | 5.3807e-10 | -1.6051e-10 | -3.9048e-30 | -5.3807e-10 | 1.6051e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.93171 | 0.86555 | 1.05 | 0.93171 | 0.86555 | -1.1515e-11 | -128.6271 | 122.7608 | -1.1515e-11 | -128.6271 | 122.7608
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9047e-30 | -3.6352e-10 | -5.8151e-10 | 1.9429e-17 | 3.6352e-10 | 5.8151e-10 | 1.9429e-17 | 5.3807e-10 | -1.6051e-10 | -3.9048e-30 | -5.3807e-10 | 1.6051e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.93171 | 0.86555 | 1.05 | 0.93171 | 0.86555 | -1.1515e-11 | -128.6271 | 122.7608 | -1.1515e-11 | -128.6271 | 122.7608
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0801e-16 | -2.9082e-09 | -4.6521e-09 | -3.8858e-16 | 2.9082e-09 | 4.6521e-09 | 1.1657e-16 | 4.3046e-09 | -1.2841e-09 | -1.36e-16 | -4.3046e-09 | 1.2841e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.93171 | 0.86555 | 1.05 | 0.93171 | 0.86555 | -1.1514e-11 | -128.6271 | 122.7608 | -1.152e-11 | -128.6271 | 122.7608
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.7145e-17 | -7.2704e-10 | -1.163e-09 | -9.7145e-17 | 7.2704e-10 | 1.163e-09 | 1.9429e-17 | 1.0761e-09 | -3.2102e-10 | -3.8858e-17 | -1.0761e-09 | 3.2102e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.93171 | 0.86555 | 1.05 | 0.93171 | 0.86555 | -1.1514e-11 | -128.6271 | 122.7608 | -1.1515e-11 | -128.6271 | 122.7608
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.7145e-17 | -7.2704e-10 | -1.163e-09 | -9.7145e-17 | 7.2704e-10 | 1.163e-09 | 1.9429e-17 | 1.0761e-09 | -3.2102e-10 | -3.8858e-17 | -1.0761e-09 | 3.2102e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.93171 | 0.86555 | 1.05 | 0.93171 | 0.86555 | -1.1514e-11 | -128.6271 | 122.7608 | -1.1515e-11 | -128.6271 | 122.7608
Line4_2_6 | 0 | 1.885 | 1.885 | 0 | 1.885 | 1.885 | 0 | 0.43533 | 0.43533 | 0 | 0.43533 | 0.43533 | 7.7716e-16 | 0.31833 | -0.10513 | -7.7716e-16 | -0.2828 | 0.14066 | -3.8858e-16 | 0.12715 | 0.29925 | 3.8858e-16 | -0.056087 | -0.22819 | 0 | -157.8829 | 22.1171 | 0 | 22.1171 | -157.8829 | 1.05 | 0.78742 | 0.7286 | 1.05 | 0.66227 | 0.61575 | -1.1529e-11 | -136.1092 | 131.4739 | -1.1543e-11 | -146.6652 | 143.7688
Line5_6_7 | 0 | 1.885 | 1.885 | 0 | 1.885 | 1.885 | 0 | 0.43533 | 0.43533 | 0 | 0.43533 | 0.43533 | 6.2172e-16 | 0.2828 | -0.14066 | -5.4401e-16 | -0.24727 | 0.1762 | -3.4972e-16 | 0.056087 | 0.22819 | 3.1086e-16 | 0.014981 | -0.15712 | 0 | -157.8829 | 22.1171 | 0 | 22.1171 | -157.8829 | 1.05 | 0.66227 | 0.61575 | 1.05 | 0.56903 | 0.54229 | -1.1543e-11 | -146.6652 | 143.7688 | -1.1555e-11 | -161.35 | 160.3935
Line6_7_8 | 0 | 1.885 | 1.885 | 0 | 1.885 | 1.885 | 0 | 0.43533 | 0.43533 | 0 | 0.43533 | 0.43533 | 5.4401e-16 | 0.24727 | -0.1762 | -6.2172e-16 | -0.21173 | 0.21173 | -2.72e-16 | -0.014981 | 0.15712 | 2.72e-16 | 0.086049 | -0.086049 | 0 | -157.8829 | 22.1171 | 0 | 22.1171 | -157.8829 | 1.05 | 0.56903 | 0.54229 | 1.05 | 0.525 | 0.525 | -1.1555e-11 | -161.35 | 160.3935 | -1.1566e-11 | -180 | -180
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3315e-16 | 1.1657e-16 | -4.6629e-16 | -2.3315e-16 | 1.9637e-16 | 1.5751e-16 | -1.1657e-16 | 1.7505e-09 | -1.7505e-09 | 7.7716e-17 | -1.7505e-09 | 1.7505e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.525 | 0.525 | 1.05 | 0.525 | 0.525 | -1.1566e-11 | -180 | -180 | -1.1569e-11 | -180 | 180
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5543e-16 | 3.8857e-17 | -3.1086e-16 | -1.5543e-16 | 2.7409e-16 | 2.0837e-18 | -3.8858e-17 | 1.7505e-09 | -1.7505e-09 | 7.7716e-17 | -1.7505e-09 | 1.7505e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.525 | 0.525 | 1.05 | 0.525 | 0.525 | -1.1566e-11 | -180 | -180 | -1.1571e-11 | -180 | 180
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4972e-16 | -2.5447e-09 | -4.0705e-09 | -3.4972e-16 | 2.5447e-09 | 4.0705e-09 | 5.8287e-17 | 3.7665e-09 | -1.1236e-09 | -7.7716e-17 | -3.7665e-09 | 1.1236e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.93171 | 0.86555 | 1.05 | 0.93171 | 0.86555 | -1.152e-11 | -128.6271 | 122.7608 | -1.1527e-11 | -128.6271 | 122.7608

## LL_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 1.9564 | 1.9564 | 0 | 1.9564 | 1.9564 | 0 | 0.4518 | 0.4518 | 0 | 0.4518 | 0.4518 | 1.1805e-15 | 0.38357 | -0.077384 | -1.2212e-15 | -0.3453 | 0.11566 | -1.6283e-16 | 0.2133 | 0.39907 | 1.6283e-16 | -0.13675 | -0.32252 | 0 | -158.05 | 21.95 | 0 | 21.95 | -158.05 | 1.1 | 0.97142 | 0.89974 | 1.1 | 0.82203 | 0.75838 | 6.5894e-13 | -128.9719 | 122.9242 | 6.4126e-13 | -136.444 | 131.678
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6637e-16 | -2.4603e-09 | -3.9356e-09 | -3.8673e-16 | 2.4603e-09 | 3.9356e-09 | 2.0354e-17 | 3.6661e-09 | -1.1108e-09 | -2.0354e-17 | -3.6661e-09 | 1.1108e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.97142 | 0.89974 | 1.1 | 0.97142 | 0.89974 | 6.4472e-13 | -128.9719 | 122.9242 | 6.3897e-13 | -128.9719 | 122.9242
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4425e-16 | -2.0502e-09 | -3.2797e-09 | -2.4425e-16 | 2.0502e-09 | 3.2797e-09 | 2.7239e-30 | 3.0551e-09 | -9.2564e-10 | 2.0354e-17 | -3.0551e-09 | 9.2564e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.97142 | 0.89974 | 1.1 | 0.97142 | 0.89974 | 6.3897e-13 | -128.9719 | 122.9242 | 6.3448e-13 | -128.9719 | 122.9242
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4248e-16 | -1.2301e-09 | -1.9678e-09 | -1.6283e-16 | 1.2301e-09 | 1.9678e-09 | 8.1416e-17 | 1.8331e-09 | -5.5539e-10 | -1.0177e-16 | -1.8331e-09 | 5.5539e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.97142 | 0.89974 | 1.1 | 0.97142 | 0.89974 | 6.3448e-13 | -128.9719 | 122.9242 | 6.3228e-13 | -128.9719 | 122.9242
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.0354e-17 | -4.1005e-10 | -6.5593e-10 | 2.0354e-17 | 4.1005e-10 | 6.5593e-10 | -2.254e-31 | 6.1102e-10 | -1.8513e-10 | 2.2517e-31 | -6.1102e-10 | 1.8513e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.97142 | 0.89974 | 1.1 | 0.97142 | 0.89974 | 6.3448e-13 | -128.9719 | 122.9242 | 6.3384e-13 | -128.9719 | 122.9242
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.1062e-17 | -8.2009e-10 | -1.3119e-09 | -1.0177e-16 | 8.2009e-10 | 1.3119e-09 | 6.7384e-31 | 1.222e-09 | -3.7026e-10 | -2.0354e-17 | -1.222e-09 | 3.7026e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.97142 | 0.89974 | 1.1 | 0.97142 | 0.89974 | 6.3228e-13 | -128.9719 | 122.9242 | 6.3117e-13 | -128.9719 | 122.9242
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0354e-17 | -4.1005e-10 | -6.5593e-10 | 0 | 4.1005e-10 | 6.5593e-10 | 2.2422e-31 | 6.1102e-10 | -1.8513e-10 | 0 | -6.1102e-10 | 1.8513e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.97142 | 0.89974 | 1.1 | 0.97142 | 0.89974 | 6.3117e-13 | -128.9719 | 122.9242 | 6.3081e-13 | -128.9719 | 122.9242
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.0354e-17 | -4.1005e-10 | -6.5593e-10 | -2.3355e-31 | 4.1005e-10 | 6.5593e-10 | -2.0354e-17 | 6.1102e-10 | -1.8513e-10 | 2.0354e-17 | -6.1102e-10 | 1.8513e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.97142 | 0.89974 | 1.1 | 0.97142 | 0.89974 | 6.5781e-13 | -128.9719 | 122.9242 | 6.5745e-13 | -128.9719 | 122.9242
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.0354e-17 | -4.1005e-10 | -6.5593e-10 | -2.3355e-31 | 4.1005e-10 | 6.5593e-10 | -2.0354e-17 | 6.1102e-10 | -1.8513e-10 | 2.0354e-17 | -6.1102e-10 | 1.8513e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.97142 | 0.89974 | 1.1 | 0.97142 | 0.89974 | 6.5781e-13 | -128.9719 | 122.9242 | 6.5745e-13 | -128.9719 | 122.9242
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.6814e-16 | -3.2804e-09 | -5.2475e-09 | -4.885e-16 | 3.2804e-09 | 5.2475e-09 | 1.0177e-16 | 4.8882e-09 | -1.481e-09 | -1.0177e-16 | -4.8882e-09 | 1.481e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.97142 | 0.89974 | 1.1 | 0.97142 | 0.89974 | 6.5894e-13 | -128.9719 | 122.9242 | 6.512e-13 | -128.9719 | 122.9242
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.1062e-17 | -8.2009e-10 | -1.3119e-09 | -6.1062e-17 | 8.2009e-10 | 1.3119e-09 | 4.0708e-17 | 1.222e-09 | -3.7026e-10 | -4.0708e-17 | -1.222e-09 | 3.7026e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.97142 | 0.89974 | 1.1 | 0.97142 | 0.89974 | 6.5894e-13 | -128.9719 | 122.9242 | 6.5781e-13 | -128.9719 | 122.9242
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.1062e-17 | -8.2009e-10 | -1.3119e-09 | -6.1062e-17 | 8.2009e-10 | 1.3119e-09 | 4.0708e-17 | 1.222e-09 | -3.7026e-10 | -4.0708e-17 | -1.222e-09 | 3.7026e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.97142 | 0.89974 | 1.1 | 0.97142 | 0.89974 | 6.5894e-13 | -128.9719 | 122.9242 | 6.5781e-13 | -128.9719 | 122.9242
Line4_2_6 | 0 | 1.9564 | 1.9564 | 0 | 1.9564 | 1.9564 | 0 | 0.4518 | 0.4518 | 0 | 0.4518 | 0.4518 | 1.2212e-15 | 0.3453 | -0.11566 | -1.1398e-15 | -0.30702 | 0.15393 | -1.6283e-16 | 0.13675 | 0.32252 | 1.6283e-16 | -0.060208 | -0.24598 | 0 | -158.05 | 21.95 | 0 | 21.95 | -158.05 | 1.1 | 0.82203 | 0.75838 | 1.1 | 0.6925 | 0.64226 | 6.4126e-13 | -136.444 | 131.678 | 6.2484e-13 | -146.955 | 143.988
Line5_6_7 | 0 | 1.9564 | 1.9564 | 0 | 1.9564 | 1.9564 | 0 | 0.4518 | 0.4518 | 0 | 0.4518 | 0.4518 | 1.2212e-15 | 0.30702 | -0.15393 | -1.3027e-15 | -0.26875 | 0.1922 | -2.4425e-16 | 0.060208 | 0.24598 | 2.8496e-16 | 0.016339 | -0.16943 | 0 | -158.05 | 21.95 | 0 | 21.95 | -158.05 | 1.1 | 0.6925 | 0.64226 | 1.1 | 0.59594 | 0.56711 | 6.2484e-13 | -146.955 | 143.988 | 6.0958e-13 | -161.529 | 160.5532
Line6_7_8 | 0 | 1.9564 | 1.9564 | 0 | 1.9564 | 1.9564 | 0 | 0.4518 | 0.4518 | 0 | 0.4518 | 0.4518 | 6.5133e-16 | 0.26875 | -0.1922 | -6.5133e-16 | -0.23048 | 0.23048 | -8.1416e-17 | -0.016339 | 0.16943 | 8.1416e-17 | 0.092885 | -0.092885 | 0 | -158.05 | 21.95 | 0 | 21.95 | -158.05 | 1.1 | 0.59594 | 0.56711 | 1.1 | 0.55 | 0.55 | 6.0958e-13 | -161.529 | 160.5532 | 6.0094e-13 | 180 | 180
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.5393e-31 | 6.5133e-16 | -3.2567e-16 | -1.6988e-30 | -2.4196e-16 | -3.2338e-16 | -8.1416e-17 | 1.9211e-09 | -1.9211e-09 | 1.6283e-16 | -1.9211e-09 | 1.9211e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.55 | 0.55 | 1.1 | 0.55 | 0.55 | 6.0094e-13 | 180 | 180 | 5.9775e-13 | -180 | 180
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5618e-30 | 6.5133e-16 | -3.2567e-16 | -1.6981e-30 | -2.4196e-16 | -3.2338e-16 | -2.4425e-16 | 1.9211e-09 | -1.9211e-09 | 1.6283e-16 | -1.9211e-09 | 1.9211e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.55 | 0.55 | 1.1 | 0.55 | 0.55 | 6.0094e-13 | 180 | 180 | 5.9753e-13 | -180 | 180
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2744e-16 | -2.8703e-09 | -4.5915e-09 | -4.2744e-16 | 2.8703e-09 | 4.5915e-09 | 8.1416e-17 | 4.2771e-09 | -1.2959e-09 | -6.1062e-17 | -4.2771e-09 | 1.2959e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.97142 | 0.89974 | 1.1 | 0.97142 | 0.89974 | 6.512e-13 | -128.9719 | 122.9242 | 6.4472e-13 | -128.9719 | 122.9242

## LL_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0.057717 | 0.057717 | 0 | 0.057717 | 0.057717 | 0 | 0.013329 | 0.013329 | 0 | 0.013329 | 0.013329 | 2.7929e-17 | 0.013468 | 0.0034547 | -2.6715e-17 | -0.013435 | -0.0034214 | 3.6429e-18 | 0.0037057 | 0.013484 | -3.6429e-18 | -0.0036391 | -0.013417 | 0 | -135.6822 | 44.3178 | 0 | 44.3178 | -135.6822 | 1.05 | 1.048 | 1.0443 | 1.05 | 1.0443 | 1.0388 | -1.46e-13 | -120.2981 | 119.9471 | -1.4641e-13 | -120.5262 | 120.0122
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.2858e-18 | -4.627e-11 | -1.3184e-10 | -6.6787e-18 | 4.627e-11 | 1.3184e-10 | 3.0358e-18 | 1.2595e-10 | 2.226e-11 | -3.0358e-18 | -1.2595e-10 | -2.226e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0443 | 1.05 | 1.048 | 1.0443 | -1.4633e-13 | -120.2981 | 119.9471 | -1.4648e-13 | -120.2981 | 119.9471
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0715e-18 | -3.8558e-11 | -1.0987e-10 | -6.6787e-18 | 3.8558e-11 | 1.0987e-10 | 6.0715e-19 | 1.0496e-10 | 1.855e-11 | -6.0715e-19 | -1.0496e-10 | -1.855e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0443 | 1.05 | 1.048 | 1.0443 | -1.4648e-13 | -120.2981 | 119.9471 | -1.466e-13 | -120.2981 | 119.9471
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9465e-18 | -2.3135e-11 | -6.592e-11 | -3.9465e-18 | 2.3135e-11 | 6.592e-11 | 3.0358e-18 | 6.2976e-11 | 1.113e-11 | -1.8215e-18 | -6.2976e-11 | -1.113e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0443 | 1.05 | 1.048 | 1.0443 | -1.466e-13 | -120.2981 | 119.9471 | -1.4666e-13 | -120.2981 | 119.9471
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.5535e-33 | -7.7116e-12 | -2.1973e-11 | 1.5536e-33 | 7.7116e-12 | 2.1973e-11 | -6.0715e-19 | 2.0992e-11 | 3.71e-12 | 6.0715e-19 | -2.0992e-11 | -3.71e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0443 | 1.05 | 1.048 | 1.0443 | -1.466e-13 | -120.2981 | 119.9471 | -1.4661e-13 | -120.2981 | 119.9471
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7322e-18 | -1.5423e-11 | -4.3946e-11 | -1.5179e-18 | 1.5423e-11 | 4.3946e-11 | 6.0715e-19 | 4.1984e-11 | 7.42e-12 | -6.0715e-19 | -4.1984e-11 | -7.42e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0443 | 1.05 | 1.048 | 1.0443 | -1.4666e-13 | -120.2981 | 119.9471 | -1.4669e-13 | -120.2981 | 119.9471
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.0715e-19 | -7.7116e-12 | -2.1973e-11 | 6.0715e-19 | 7.7116e-12 | 2.1973e-11 | 6.0715e-19 | 2.0992e-11 | 3.71e-12 | -6.0715e-19 | -2.0992e-11 | -3.71e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0443 | 1.05 | 1.048 | 1.0443 | -1.4669e-13 | -120.2981 | 119.9471 | -1.467e-13 | -120.2981 | 119.9471
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0358e-19 | -7.7116e-12 | -2.1973e-11 | -3.0358e-19 | 7.7116e-12 | 2.1973e-11 | -1.2143e-18 | 2.0992e-11 | 3.71e-12 | 1.2143e-18 | -2.0992e-11 | -3.71e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0443 | 1.05 | 1.048 | 1.0443 | -1.4603e-13 | -120.2981 | 119.9471 | -1.4604e-13 | -120.2981 | 119.9471
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0358e-19 | -7.7116e-12 | -2.1973e-11 | -3.0358e-19 | 7.7116e-12 | 2.1973e-11 | -1.2143e-18 | 2.0992e-11 | 3.71e-12 | 1.2143e-18 | -2.0992e-11 | -3.71e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0443 | 1.05 | 1.048 | 1.0443 | -1.4603e-13 | -120.2981 | 119.9471 | -1.4604e-13 | -120.2981 | 119.9471
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.4109e-18 | -6.1693e-11 | -1.7579e-10 | -8.8037e-18 | 6.1693e-11 | 1.7579e-10 | 7.2858e-18 | 1.6794e-10 | 2.968e-11 | -7.2858e-18 | -1.6794e-10 | -2.968e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0443 | 1.05 | 1.048 | 1.0443 | -1.46e-13 | -120.2981 | 119.9471 | -1.4616e-13 | -120.2981 | 119.9471
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5179e-18 | -1.5423e-11 | -4.3946e-11 | -1.5179e-18 | 1.5423e-11 | 4.3946e-11 | 1.8215e-18 | 4.1984e-11 | 7.42e-12 | -1.8215e-18 | -4.1984e-11 | -7.42e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0443 | 1.05 | 1.048 | 1.0443 | -1.46e-13 | -120.2981 | 119.9471 | -1.4603e-13 | -120.2981 | 119.9471
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5179e-18 | -1.5423e-11 | -4.3946e-11 | -1.5179e-18 | 1.5423e-11 | 4.3946e-11 | 1.8215e-18 | 4.1984e-11 | 7.42e-12 | -1.8215e-18 | -4.1984e-11 | -7.42e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0443 | 1.05 | 1.048 | 1.0443 | -1.46e-13 | -120.2981 | 119.9471 | -1.4603e-13 | -120.2981 | 119.9471
Line4_2_6 | 0 | 0.057717 | 0.057717 | 0 | 0.057717 | 0.057717 | 0 | 0.013329 | 0.013329 | 0 | 0.013329 | 0.013329 | 2.55e-17 | 0.013435 | 0.0034214 | -2.55e-17 | -0.013402 | -0.003388 | -2.4286e-18 | 0.0036391 | 0.013417 | 6.537e-32 | -0.0035725 | -0.01335 | 0 | -135.6822 | 44.3178 | 0 | 44.3178 | -135.6822 | 1.05 | 1.0443 | 1.0388 | 1.05 | 1.0405 | 1.0333 | -1.4641e-13 | -120.5262 | 120.0122 | -1.4688e-13 | -120.7558 | 120.078
Line5_6_7 | 0 | 0.057717 | 0.057717 | 0 | 0.057717 | 0.057717 | 0 | 0.013329 | 0.013329 | 0 | 0.013329 | 0.013329 | 2.1858e-17 | 0.013402 | 0.003388 | -2.1858e-17 | -0.013368 | -0.0033547 | -4.8572e-18 | 0.0035725 | 0.01335 | 2.4286e-18 | -0.0035059 | -0.013284 | 0 | -135.6822 | 44.3178 | 0 | 44.3178 | -135.6822 | 1.05 | 1.0405 | 1.0333 | 1.05 | 1.0368 | 1.0279 | -1.4688e-13 | -120.7558 | 120.078 | -1.4726e-13 | -120.9872 | 120.1445
Line6_7_8 | 0 | 0.057717 | 0.057717 | 0 | 0.057717 | 0.057717 | 0 | 0.013329 | 0.013329 | 0 | 0.013329 | 0.013329 | 1.4572e-17 | 0.013368 | 0.0033547 | -1.4572e-17 | -0.013335 | -0.0033214 | -4.8572e-18 | 0.0035059 | 0.013284 | 4.8572e-18 | -0.0034392 | -0.013217 | 0 | -135.6822 | 44.3178 | 0 | 44.3178 | -135.6822 | 1.05 | 1.0368 | 1.0279 | 1.05 | 1.0332 | 1.0224 | -1.4726e-13 | -120.9872 | 120.1445 | -1.4763e-13 | -121.2201 | 120.2117
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.4286e-18 | -6.2856e-11 | -1.0336e-10 | 6.2613e-33 | 6.2856e-11 | 1.0336e-10 | -2.4286e-18 | 8.4699e-11 | -1.4546e-11 | 2.4286e-18 | -8.4699e-11 | 1.4546e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.0332 | 1.0224 | 1.05 | 1.0332 | 1.0224 | -1.4763e-13 | -121.2201 | 120.2117 | -1.4772e-13 | -121.2201 | 120.2117
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8572e-18 | -6.2856e-11 | -1.0336e-10 | -2.4286e-18 | 6.2856e-11 | 1.0336e-10 | -2.4286e-18 | 8.4699e-11 | -1.4546e-11 | 2.4286e-18 | -8.4699e-11 | 1.4546e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.0332 | 1.0224 | 1.05 | 1.0332 | 1.0224 | -1.4763e-13 | -121.2201 | 120.2117 | -1.4776e-13 | -121.2201 | 120.2117
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.4109e-18 | -5.3981e-11 | -1.5381e-10 | -8.8037e-18 | 5.3981e-11 | 1.5381e-10 | 5.4644e-18 | 1.4694e-10 | 2.597e-11 | -5.4644e-18 | -1.4694e-10 | -2.597e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0443 | 1.05 | 1.048 | 1.0443 | -1.4616e-13 | -120.2981 | 119.9471 | -1.4633e-13 | -120.2981 | 119.9471

## LL_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0.060452 | 0.060452 | 0 | 0.060452 | 0.060452 | 0 | 0.013961 | 0.013961 | 0 | 0.013961 | 0.013961 | 3.3075e-17 | 0.014777 | 0.0037874 | -3.3075e-17 | -0.01474 | -0.0037509 | 1.1449e-17 | 0.004065 | 0.014792 | -1.1449e-17 | -0.0039919 | -0.014719 | 0 | -135.6932 | 44.3068 | 0 | 44.3068 | -135.6932 | 1.1 | 1.0978 | 1.0937 | 1.1 | 1.0939 | 1.088 | 1.7345e-13 | -120.3121 | 119.9447 | 1.7306e-13 | -120.5402 | 120.0098
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.5869e-18 | -5.3155e-11 | -1.5146e-10 | -8.5869e-18 | 5.3155e-11 | 1.5146e-10 | 3.1803e-18 | 1.4472e-10 | 2.555e-11 | -3.1803e-18 | -1.4472e-10 | -2.555e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0937 | 1.1 | 1.0978 | 1.0937 | 1.7307e-13 | -120.3121 | 119.9447 | 1.7292e-13 | -120.3121 | 119.9447
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6328e-18 | -4.4296e-11 | -1.2622e-10 | -7.6328e-18 | 4.4296e-11 | 1.2622e-10 | 6.3607e-19 | 1.206e-10 | 2.1292e-11 | -2.5443e-18 | -1.206e-10 | -2.1292e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0937 | 1.1 | 1.0978 | 1.0937 | 1.7292e-13 | -120.3121 | 119.9447 | 1.7279e-13 | -120.3121 | 119.9447
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4525e-18 | -2.6578e-11 | -7.5731e-11 | -5.0885e-18 | 2.6578e-11 | 7.5731e-11 | 3.8164e-18 | 7.2361e-11 | 1.2775e-11 | -3.8164e-18 | -7.2361e-11 | -1.2775e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0937 | 1.1 | 1.0978 | 1.0937 | 1.7279e-13 | -120.3121 | 119.9447 | 1.7273e-13 | -120.3121 | 119.9447
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.3607e-19 | -8.8592e-12 | -2.5244e-11 | 0 | 8.8592e-12 | 2.5244e-11 | 6.3607e-19 | 2.412e-11 | 4.2584e-12 | 0 | -2.412e-11 | -4.2584e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0937 | 1.1 | 1.0978 | 1.0937 | 1.7279e-13 | -120.3121 | 119.9447 | 1.7277e-13 | -120.3121 | 119.9447
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5443e-18 | -1.7718e-11 | -5.0487e-11 | -1.9082e-18 | 1.7718e-11 | 5.0487e-11 | 1.2721e-18 | 4.824e-11 | 8.5168e-12 | -1.2721e-18 | -4.824e-11 | -8.5168e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0937 | 1.1 | 1.0978 | 1.0937 | 1.7273e-13 | -120.3121 | 119.9447 | 1.727e-13 | -120.3121 | 119.9447
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -9.541e-19 | -8.8592e-12 | -2.5244e-11 | 9.541e-19 | 8.8592e-12 | 2.5244e-11 | -6.3607e-19 | 2.412e-11 | 4.2584e-12 | 6.3607e-19 | -2.412e-11 | -4.2584e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0937 | 1.1 | 1.0978 | 1.0937 | 1.727e-13 | -120.3121 | 119.9447 | 1.7268e-13 | -120.3121 | 119.9447
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8503e-33 | -8.8592e-12 | -2.5244e-11 | -3.8499e-33 | 8.8592e-12 | 2.5244e-11 | -1.2721e-18 | 2.412e-11 | 4.2584e-12 | 1.2721e-18 | -2.412e-11 | -4.2584e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0937 | 1.1 | 1.0978 | 1.0937 | 1.7342e-13 | -120.3121 | 119.9447 | 1.734e-13 | -120.3121 | 119.9447
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8503e-33 | -8.8592e-12 | -2.5244e-11 | -3.8499e-33 | 8.8592e-12 | 2.5244e-11 | -1.2721e-18 | 2.412e-11 | 4.2584e-12 | 1.2721e-18 | -2.412e-11 | -4.2584e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0937 | 1.1 | 1.0978 | 1.0937 | 1.7342e-13 | -120.3121 | 119.9447 | 1.734e-13 | -120.3121 | 119.9447
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1449e-17 | -7.0874e-11 | -2.0195e-10 | -1.1449e-17 | 7.0874e-11 | 2.0195e-10 | 8.2688e-18 | 1.9296e-10 | 3.4067e-11 | -8.2688e-18 | -1.9296e-10 | -3.4067e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0937 | 1.1 | 1.0978 | 1.0937 | 1.7345e-13 | -120.3121 | 119.9447 | 1.7324e-13 | -120.3121 | 119.9447
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2262e-18 | -1.7718e-11 | -5.0487e-11 | -1.5902e-18 | 1.7718e-11 | 5.0487e-11 | 1.2721e-18 | 4.824e-11 | 8.5168e-12 | -6.3607e-19 | -4.824e-11 | -8.5168e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0937 | 1.1 | 1.0978 | 1.0937 | 1.7345e-13 | -120.3121 | 119.9447 | 1.7342e-13 | -120.3121 | 119.9447
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2262e-18 | -1.7718e-11 | -5.0487e-11 | -1.5902e-18 | 1.7718e-11 | 5.0487e-11 | 1.2721e-18 | 4.824e-11 | 8.5168e-12 | -6.3607e-19 | -4.824e-11 | -8.5168e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0937 | 1.1 | 1.0978 | 1.0937 | 1.7345e-13 | -120.3121 | 119.9447 | 1.7342e-13 | -120.3121 | 119.9447
Line4_2_6 | 0 | 0.060452 | 0.060452 | 0 | 0.060452 | 0.060452 | 0 | 0.013961 | 0.013961 | 0 | 0.013961 | 0.013961 | 3.0531e-17 | 0.01474 | 0.0037509 | -3.0531e-17 | -0.014704 | -0.0037143 | 7.6328e-18 | 0.0039919 | 0.014719 | -1.0177e-17 | -0.0039188 | -0.014646 | 0 | -135.6932 | 44.3068 | 0 | 44.3068 | -135.6932 | 1.1 | 1.0939 | 1.088 | 1.1 | 1.09 | 1.0823 | 1.7306e-13 | -120.5402 | 120.0098 | 1.7267e-13 | -120.7698 | 120.0757
Line5_6_7 | 0 | 0.060452 | 0.060452 | 0 | 0.060452 | 0.060452 | 0 | 0.013961 | 0.013961 | 0 | 0.013961 | 0.013961 | 3.0531e-17 | 0.014704 | 0.0037143 | -3.3075e-17 | -0.014667 | -0.0036778 | 2.5443e-18 | 0.0039188 | 0.014646 | -2.5443e-18 | -0.0038457 | -0.014572 | 0 | -135.6932 | 44.3068 | 0 | 44.3068 | -135.6932 | 1.1 | 1.09 | 1.0823 | 1.1 | 1.0861 | 1.0765 | 1.7267e-13 | -120.7698 | 120.0757 | 1.7232e-13 | -121.0011 | 120.1422
Line6_7_8 | 0 | 0.060452 | 0.060452 | 0 | 0.060452 | 0.060452 | 0 | 0.013961 | 0.013961 | 0 | 0.013961 | 0.013961 | 1.5266e-17 | 0.014667 | 0.0036778 | -1.2721e-17 | -0.014631 | -0.0036413 | 5.0885e-18 | 0.0038457 | 0.014572 | -2.5443e-18 | -0.0037726 | -0.014499 | 0 | -135.6932 | 44.3068 | 0 | 44.3068 | -135.6932 | 1.1 | 1.0861 | 1.0765 | 1.1 | 1.0823 | 1.0708 | 1.7232e-13 | -121.0011 | 120.1422 | 1.7208e-13 | -121.2341 | 120.2095
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5443e-18 | -6.9334e-11 | -1.1449e-10 | -2.5443e-18 | 6.9334e-11 | 1.1449e-10 | 7.6413e-33 | 9.4011e-11 | -1.5791e-11 | -2.5443e-18 | -9.4011e-11 | 1.5791e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0823 | 1.0708 | 1.1 | 1.0823 | 1.0708 | 1.7208e-13 | -121.2341 | 120.2095 | 1.7199e-13 | -121.2341 | 120.2095
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5443e-18 | -6.9334e-11 | -1.1449e-10 | 2.5443e-18 | 6.9334e-11 | 1.1449e-10 | -7.6413e-33 | 9.4011e-11 | -1.5791e-11 | -5.0885e-18 | -9.4011e-11 | 1.5791e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0823 | 1.0708 | 1.1 | 1.0823 | 1.0708 | 1.7208e-13 | -121.2341 | 120.2095 | 1.7202e-13 | -121.2341 | 120.2095
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0813e-17 | -6.2015e-11 | -1.7671e-10 | -1.1449e-17 | 6.2015e-11 | 1.7671e-10 | 5.0885e-18 | 1.6884e-10 | 2.9809e-11 | -3.8164e-18 | -1.6884e-10 | -2.9809e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0937 | 1.1 | 1.0978 | 1.0937 | 1.7324e-13 | -120.3121 | 119.9447 | 1.7307e-13 | -120.3121 | 119.9447

## LL_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 1.455 | 1.455 | 0 | 1.455 | 1.455 | 0 | 0.33601 | 0.33601 | 0 | 0.33601 | 0.33601 | 3.5157e-17 | 0.28984 | 0.03533 | -7.0314e-17 | -0.24919 | 0.005316 | 1.7579e-17 | 0.073022 | 0.26569 | -1.7579e-17 | -0.030682 | -0.22336 | 0 | -142.8727 | 37.1273 | 0 | 37.1273 | -142.8727 | 0.95 | 0.88953 | 0.79769 | 0.95 | 0.74721 | 0.66491 | 6.0574e-13 | -128.7319 | 119.553 | 6.0689e-13 | -135.8534 | 128.4907
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3184e-17 | -9.6789e-10 | -2.6725e-09 | -4.3946e-18 | 9.6789e-10 | 2.6725e-09 | 7.0314e-17 | 2.8224e-09 | 1.3007e-10 | -7.0314e-17 | -2.8224e-09 | -1.3007e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.88953 | 0.79769 | 0.95 | 0.88953 | 0.79769 | 6.0997e-13 | -128.7319 | 119.553 | 6.1224e-13 | -128.7319 | 119.553
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.0762e-17 | -8.0657e-10 | -2.2271e-09 | 3.0762e-17 | 8.0657e-10 | 2.2271e-09 | 7.0314e-17 | 2.352e-09 | 1.0839e-10 | -7.0314e-17 | -2.352e-09 | -1.0839e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.88953 | 0.79769 | 0.95 | 0.88953 | 0.79769 | 6.1224e-13 | -128.7319 | 119.553 | 6.1433e-13 | -128.7319 | 119.553
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.7893e-18 | -4.8394e-10 | -1.3362e-09 | 3.7756e-31 | 4.8394e-10 | 1.3362e-09 | 5.2736e-17 | 1.4112e-09 | 6.5035e-11 | -3.5157e-17 | -1.4112e-09 | -6.5035e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.88953 | 0.79769 | 0.95 | 0.88953 | 0.79769 | 6.1433e-13 | -128.7319 | 119.553 | 6.1531e-13 | -128.7319 | 119.553
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3946e-18 | -1.6131e-10 | -4.4541e-10 | 4.3946e-18 | 1.6131e-10 | 4.4541e-10 | 1.7579e-17 | 4.7039e-10 | 2.1678e-11 | -1.7579e-17 | -4.7039e-10 | -2.1678e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.88953 | 0.79769 | 0.95 | 0.88953 | 0.79769 | 6.1433e-13 | -128.7319 | 119.553 | 6.1426e-13 | -128.7319 | 119.553
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.7579e-17 | -3.2263e-10 | -8.9083e-10 | 1.8903e-31 | 3.2263e-10 | 8.9083e-10 | 3.5157e-17 | 9.4079e-10 | 4.3357e-11 | -1.7579e-17 | -9.4079e-10 | -4.3357e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.88953 | 0.79769 | 0.95 | 0.88953 | 0.79769 | 6.1531e-13 | -128.7319 | 119.553 | 6.1611e-13 | -128.7319 | 119.553
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.7893e-18 | -1.6131e-10 | -4.4541e-10 | 8.7893e-18 | 1.6131e-10 | 4.4541e-10 | 1.7579e-17 | 4.7039e-10 | 2.1678e-11 | -1.7579e-17 | -4.7039e-10 | -2.1679e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.88953 | 0.79769 | 0.95 | 0.88953 | 0.79769 | 6.1611e-13 | -128.7319 | 119.553 | 6.1635e-13 | -128.7319 | 119.553
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.7893e-18 | -1.6131e-10 | -4.4541e-10 | 8.7893e-18 | 1.6131e-10 | 4.4541e-10 | -1.7579e-17 | 4.7039e-10 | 2.1679e-11 | -1.7579e-17 | -4.7039e-10 | -2.1679e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.88953 | 0.79769 | 0.95 | 0.88953 | 0.79769 | 6.0671e-13 | -128.7319 | 119.553 | 6.0695e-13 | -128.7319 | 119.553
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.7893e-18 | -1.6131e-10 | -4.4541e-10 | 8.7893e-18 | 1.6131e-10 | 4.4541e-10 | -1.7579e-17 | 4.7039e-10 | 2.1679e-11 | -1.7579e-17 | -4.7039e-10 | -2.1679e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.88953 | 0.79769 | 0.95 | 0.88953 | 0.79769 | 6.0671e-13 | -128.7319 | 119.553 | 6.0695e-13 | -128.7319 | 119.553
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1973e-17 | -1.2905e-09 | -3.5633e-09 | -1.3184e-17 | 1.2905e-09 | 3.5633e-09 | 3.5157e-17 | 3.7632e-09 | 1.7343e-10 | -5.2736e-17 | -3.7632e-09 | -1.7343e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.88953 | 0.79769 | 0.95 | 0.88953 | 0.79769 | 6.0574e-13 | -128.7319 | 119.553 | 6.0771e-13 | -128.7319 | 119.553
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.7168e-31 | -3.2263e-10 | -8.9083e-10 | 8.7893e-18 | 3.2263e-10 | 8.9083e-10 | 3.5157e-17 | 9.4079e-10 | 4.3357e-11 | -5.2736e-17 | -9.4079e-10 | -4.3357e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.88953 | 0.79769 | 0.95 | 0.88953 | 0.79769 | 6.0574e-13 | -128.7319 | 119.553 | 6.0671e-13 | -128.7319 | 119.553
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.7168e-31 | -3.2263e-10 | -8.9083e-10 | 8.7893e-18 | 3.2263e-10 | 8.9083e-10 | 3.5157e-17 | 9.4079e-10 | 4.3357e-11 | -5.2736e-17 | -9.4079e-10 | -4.3357e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.88953 | 0.79769 | 0.95 | 0.88953 | 0.79769 | 6.0574e-13 | -128.7319 | 119.553 | 6.0671e-13 | -128.7319 | 119.553
Line4_2_6 | 0 | 1.455 | 1.455 | 0 | 1.455 | 1.455 | 0 | 0.33601 | 0.33601 | 0 | 0.33601 | 0.33601 | -3.7239e-31 | 0.24919 | -0.005316 | 0 | -0.20855 | 0.045962 | 3.5157e-17 | 0.030682 | 0.22336 | 0 | 0.011658 | -0.18102 | 0 | -142.8727 | 37.1273 | 0 | 37.1273 | -142.8727 | 0.95 | 0.74721 | 0.66491 | 0.95 | 0.62161 | 0.55581 | 6.0689e-13 | -135.8534 | 128.4907 | 6.0972e-13 | -146.0722 | 141.3743
Line5_6_7 | 0 | 1.455 | 1.455 | 0 | 1.455 | 1.455 | 0 | 0.33601 | 0.33601 | 0 | 0.33601 | 0.33601 | -7.0314e-17 | 0.20855 | -0.045962 | 7.0314e-17 | -0.1679 | 0.086608 | 2.1094e-16 | -0.011658 | 0.18102 | -2.1094e-16 | 0.053997 | -0.13868 | 0 | -142.8727 | 37.1273 | 0 | 37.1273 | -142.8727 | 0.95 | 0.62161 | 0.55581 | 0.95 | 0.52489 | 0.48658 | 6.0972e-13 | -146.0722 | 141.3743 | 6.0989e-13 | -160.7007 | 159.1134
Line6_7_8 | 0 | 1.455 | 1.455 | 0 | 1.455 | 1.455 | 0 | 0.33601 | 0.33601 | 0 | 0.33601 | 0.33601 | -7.4846e-31 | 0.1679 | -0.086608 | 7.4761e-31 | -0.12725 | 0.12725 | 7.0314e-17 | -0.053997 | 0.13868 | -7.0314e-17 | 0.096337 | -0.096337 | 0 | -142.8727 | 37.1273 | 0 | 37.1273 | -142.8727 | 0.95 | 0.52489 | 0.48658 | 0.95 | 0.475 | 0.475 | 6.0989e-13 | -160.7007 | 159.1134 | 6.0919e-13 | -180 | 180
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4063e-16 | 1.0547e-16 | -1.4063e-16 | -7.0314e-17 | -1.3735e-16 | 1.439e-16 | -7.0314e-17 | 1.4329e-09 | -1.4329e-09 | -7.4627e-31 | -1.4329e-09 | 1.4329e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.475 | 0.475 | 0.95 | 0.475 | 0.475 | 6.0919e-13 | -180 | 180 | 6.0811e-13 | -180 | 180
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4063e-16 | -1.4063e-16 | -1.0516e-22 | -7.4762e-31 | 1.0875e-16 | 3.2762e-18 | 1.4952e-30 | 1.4329e-09 | -1.4329e-09 | 7.0314e-17 | -1.4329e-09 | 1.4329e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.475 | 0.475 | 0.95 | 0.475 | 0.475 | 6.0919e-13 | -180 | 180 | 6.092e-13 | -180 | 180
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3184e-17 | -1.1292e-09 | -3.1179e-09 | -4.3946e-18 | 1.1292e-09 | 3.1179e-09 | 5.2736e-17 | 3.2928e-09 | 1.5175e-10 | -7.0314e-17 | -3.2928e-09 | -1.5175e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.88953 | 0.79769 | 0.95 | 0.88953 | 0.79769 | 6.0771e-13 | -128.7319 | 119.553 | 6.0997e-13 | -128.7319 | 119.553

## LL_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 1.3784 | 1.3784 | 0 | 1.3784 | 1.3784 | 0 | 0.31833 | 0.31833 | 0 | 0.31833 | 0.31833 | 3.3307e-17 | 0.26013 | 0.031709 | -3.3307e-17 | -0.22365 | 0.0047711 | 2.1812e-31 | 0.065537 | 0.23846 | -2.1836e-31 | -0.027537 | -0.20046 | 0 | -142.8727 | 37.1273 | 0 | 37.1273 | -142.8727 | 0.9 | 0.84271 | 0.7557 | 0.9 | 0.70788 | 0.62991 | 3.7522e-13 | -128.7319 | 119.553 | 3.7563e-13 | -135.8534 | 128.4907
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.249e-17 | -8.6869e-10 | -2.3986e-09 | 1.249e-17 | 8.6869e-10 | 2.3986e-09 | 4.996e-17 | 2.5331e-09 | 1.1674e-10 | -4.996e-17 | -2.5331e-09 | -1.1674e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.84271 | 0.7557 | 0.9 | 0.84271 | 0.7557 | 3.7946e-13 | -128.7319 | 119.553 | 3.8173e-13 | -128.7319 | 119.553
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.249e-17 | -7.2391e-10 | -1.9988e-09 | -4.1633e-18 | 7.2391e-10 | 1.9988e-09 | 4.996e-17 | 2.1109e-09 | 9.7283e-11 | -6.6613e-17 | -2.1109e-09 | -9.7283e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.84271 | 0.7557 | 0.9 | 0.84271 | 0.7557 | 3.8173e-13 | -128.7319 | 119.553 | 3.8381e-13 | -128.7319 | 119.553
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.249e-17 | -4.3434e-10 | -1.1993e-09 | 4.1633e-18 | 4.3434e-10 | 1.1993e-09 | 8.3668e-32 | 1.2665e-09 | 5.837e-11 | -1.6653e-17 | -1.2665e-09 | -5.837e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.84271 | 0.7557 | 0.9 | 0.84271 | 0.7557 | 3.8381e-13 | -128.7319 | 119.553 | 3.8479e-13 | -128.7319 | 119.553
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.249e-17 | -1.4478e-10 | -3.9976e-10 | -4.1633e-18 | 1.4478e-10 | 3.9976e-10 | 1.6653e-17 | 4.2218e-10 | 1.9457e-11 | -1.6653e-17 | -4.2218e-10 | -1.9457e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.84271 | 0.7557 | 0.9 | 0.84271 | 0.7557 | 3.8381e-13 | -128.7319 | 119.553 | 3.8375e-13 | -128.7319 | 119.553
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.498e-17 | -2.8956e-10 | -7.9952e-10 | 4.1633e-17 | 2.8956e-10 | 7.9952e-10 | 3.3307e-17 | 8.4436e-10 | 3.8913e-11 | -3.3307e-17 | -8.4436e-10 | -3.8913e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.84271 | 0.7557 | 0.9 | 0.84271 | 0.7557 | 3.8479e-13 | -128.7319 | 119.553 | 3.856e-13 | -128.7319 | 119.553
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1633e-18 | -1.4478e-10 | -3.9976e-10 | 4.1633e-18 | 1.4478e-10 | 3.9976e-10 | -1.6653e-17 | 4.2218e-10 | 1.9457e-11 | 1.6653e-17 | -4.2218e-10 | -1.9457e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.84271 | 0.7557 | 0.9 | 0.84271 | 0.7557 | 3.856e-13 | -128.7319 | 119.553 | 3.8584e-13 | -128.7319 | 119.553
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.1633e-18 | -1.4478e-10 | -3.9976e-10 | 4.1633e-18 | 1.4478e-10 | 3.9976e-10 | -1.6653e-17 | 4.2218e-10 | 1.9457e-11 | 2.7354e-32 | -4.2218e-10 | -1.9457e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.84271 | 0.7557 | 0.9 | 0.84271 | 0.7557 | 3.762e-13 | -128.7319 | 119.553 | 3.7644e-13 | -128.7319 | 119.553
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.1633e-18 | -1.4478e-10 | -3.9976e-10 | 4.1633e-18 | 1.4478e-10 | 3.9976e-10 | -1.6653e-17 | 4.2218e-10 | 1.9457e-11 | 2.7354e-32 | -4.2218e-10 | -1.9457e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.84271 | 0.7557 | 0.9 | 0.84271 | 0.7557 | 3.762e-13 | -128.7319 | 119.553 | 3.7644e-13 | -128.7319 | 119.553
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9143e-17 | -1.1582e-09 | -3.1981e-09 | -2.9143e-17 | 1.1582e-09 | 3.1981e-09 | 4.996e-17 | 3.3775e-09 | 1.5565e-10 | -4.996e-17 | -3.3775e-09 | -1.5565e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.84271 | 0.7557 | 0.9 | 0.84271 | 0.7557 | 3.7522e-13 | -128.7319 | 119.553 | 3.772e-13 | -128.7319 | 119.553
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.1633e-18 | -2.8956e-10 | -7.9952e-10 | 4.1633e-18 | 2.8956e-10 | 7.9952e-10 | 1.6653e-17 | 8.4436e-10 | 3.8913e-11 | -1.6653e-17 | -8.4436e-10 | -3.8913e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.84271 | 0.7557 | 0.9 | 0.84271 | 0.7557 | 3.7522e-13 | -128.7319 | 119.553 | 3.762e-13 | -128.7319 | 119.553
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.1633e-18 | -2.8956e-10 | -7.9952e-10 | 4.1633e-18 | 2.8956e-10 | 7.9952e-10 | 1.6653e-17 | 8.4436e-10 | 3.8913e-11 | -1.6653e-17 | -8.4436e-10 | -3.8913e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.84271 | 0.7557 | 0.9 | 0.84271 | 0.7557 | 3.7522e-13 | -128.7319 | 119.553 | 3.762e-13 | -128.7319 | 119.553
Line4_2_6 | 0 | 1.3784 | 1.3784 | 0 | 1.3784 | 1.3784 | 0 | 0.31833 | 0.31833 | 0 | 0.31833 | 0.31833 | 3.3307e-17 | 0.22365 | -0.0047711 | -3.3307e-17 | -0.18717 | 0.041251 | 3.3307e-17 | 0.027537 | 0.20046 | -3.3307e-17 | 0.010463 | -0.16246 | 0 | -142.8727 | 37.1273 | 0 | 37.1273 | -142.8727 | 0.9 | 0.70788 | 0.62991 | 0.9 | 0.5889 | 0.52656 | 3.7563e-13 | -135.8534 | 128.4907 | 3.7788e-13 | -146.0722 | 141.3743
Line5_6_7 | 0 | 1.3784 | 1.3784 | 0 | 1.3784 | 1.3784 | 0 | 0.31833 | 0.31833 | 0 | 0.31833 | 0.31833 | -6.59e-31 | 0.18717 | -0.041251 | 8.7992e-31 | -0.15069 | 0.077731 | 9.992e-17 | -0.010463 | 0.16246 | -1.3323e-16 | 0.048463 | -0.12446 | 0 | -142.8727 | 37.1273 | 0 | 37.1273 | -142.8727 | 0.9 | 0.5889 | 0.52656 | 0.9 | 0.49726 | 0.46097 | 3.7788e-13 | -146.0722 | 141.3743 | 3.7842e-13 | -160.7007 | 159.1134
Line6_7_8 | 0 | 1.3784 | 1.3784 | 0 | 1.3784 | 1.3784 | 0 | 0.31833 | 0.31833 | 0 | 0.31833 | 0.31833 | 6.6613e-17 | 0.15069 | -0.077731 | 4.3965e-31 | -0.11421 | 0.11421 | 6.6613e-17 | -0.048463 | 0.12446 | -6.6613e-17 | 0.086463 | -0.086463 | 0 | -142.8727 | 37.1273 | 0 | 37.1273 | -142.8727 | 0.9 | 0.49726 | 0.46097 | 0.9 | 0.45 | 0.45 | 3.7842e-13 | -160.7007 | 159.1134 | 3.7815e-13 | -180 | 180
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.6613e-17 | 6.6613e-17 | -8.4082e-23 | 8.7678e-31 | -6.3673e-17 | 2.9404e-18 | 1.3323e-16 | 1.286e-09 | -1.286e-09 | -1.3323e-16 | -1.286e-09 | 1.286e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.45 | 0.45 | 0.9 | 0.45 | 0.45 | 3.7815e-13 | -180 | 180 | 3.7707e-13 | -180 | 180
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.6613e-17 | -2.3315e-16 | -1.3323e-16 | -1.3323e-16 | 2.3609e-16 | 2.6939e-16 | 4.3965e-31 | 1.286e-09 | -1.286e-09 | -8.7998e-31 | -1.286e-09 | 1.286e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.45 | 0.45 | 0.9 | 0.45 | 0.45 | 3.7815e-13 | -180 | 180 | 3.7845e-13 | -180 | 180
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6653e-17 | -1.0135e-09 | -2.7983e-09 | -1.6653e-17 | 1.0135e-09 | 2.7983e-09 | 4.996e-17 | 2.9553e-09 | 1.362e-10 | -3.3307e-17 | -2.9553e-09 | -1.362e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.84271 | 0.7557 | 0.9 | 0.84271 | 0.7557 | 3.772e-13 | -128.7319 | 119.553 | 3.7946e-13 | -128.7319 | 119.553

## LL_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0.051843 | 0.051843 | 0 | 0.051843 | 0.051843 | 0 | 0.011973 | 0.011973 | 0 | 0.011973 | 0.011973 | 5.4933e-19 | 0.010966 | 0.0028847 | -1.0987e-18 | -0.010915 | -0.0028331 | 3.296e-18 | 0.0029326 | 0.010936 | -2.1973e-18 | -0.0028788 | -0.010882 | 0 | -135.2796 | 44.7204 | 0 | 44.7204 | -135.2796 | 0.95 | 0.94815 | 0.94465 | 0.95 | 0.94283 | 0.93921 | 3.7763e-14 | -120.3084 | 119.9432 | 3.7791e-14 | -120.5043 | 120.1275
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.06e-19 | -3.8309e-11 | -1.1119e-10 | -2.06e-19 | 3.8309e-11 | 1.1119e-10 | 2.7466e-18 | 1.0665e-10 | 1.9584e-11 | -1.648e-18 | -1.0665e-10 | -1.9584e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94815 | 0.94465 | 0.95 | 0.94815 | 0.94465 | 3.7902e-14 | -120.3084 | 119.9432 | 3.7976e-14 | -120.3084 | 119.9432
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.18e-19 | -3.1925e-11 | -9.2658e-11 | -6.18e-19 | 3.1925e-11 | 9.2658e-11 | 2.1973e-18 | 8.8872e-11 | 1.632e-11 | -2.7466e-18 | -8.8872e-11 | -1.632e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94815 | 0.94465 | 0.95 | 0.94815 | 0.94465 | 3.7976e-14 | -120.3084 | 119.9432 | 3.8046e-14 | -120.3084 | 119.9432
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.18e-19 | -1.9155e-11 | -5.5595e-11 | 6.18e-19 | 1.9155e-11 | 5.5595e-11 | 1.648e-18 | 5.3323e-11 | 9.7921e-12 | -1.0987e-18 | -5.3323e-11 | -9.7921e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94815 | 0.94465 | 0.95 | 0.94815 | 0.94465 | 3.8046e-14 | -120.3084 | 119.9432 | 3.8083e-14 | -120.3084 | 119.9432
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.06e-19 | -6.3849e-12 | -1.8532e-11 | 6.8666e-20 | 6.3849e-12 | 1.8532e-11 | 5.4933e-19 | 1.7774e-11 | 3.264e-12 | -5.4933e-19 | -1.7774e-11 | -3.264e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94815 | 0.94465 | 0.95 | 0.94815 | 0.94465 | 3.8046e-14 | -120.3084 | 119.9432 | 3.8045e-14 | -120.3084 | 119.9432
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.5533e-19 | -1.277e-11 | -3.7063e-11 | 4.8066e-19 | 1.277e-11 | 3.7063e-11 | -5.4933e-19 | 3.5549e-11 | 6.5281e-12 | -5.4933e-19 | -3.5549e-11 | -6.5281e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94815 | 0.94465 | 0.95 | 0.94815 | 0.94465 | 3.8083e-14 | -120.3084 | 119.9432 | 3.8115e-14 | -120.3084 | 119.9432
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.2399e-19 | -6.3849e-12 | -1.8532e-11 | 8.2399e-19 | 6.3849e-12 | 1.8532e-11 | 1.0987e-18 | 1.7774e-11 | 3.264e-12 | -1.648e-18 | -1.7774e-11 | -3.264e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94815 | 0.94465 | 0.95 | 0.94815 | 0.94465 | 3.8115e-14 | -120.3084 | 119.9432 | 3.8127e-14 | -120.3084 | 119.9432
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.06e-19 | -6.3849e-12 | -1.8532e-11 | 2.06e-19 | 6.3849e-12 | 1.8532e-11 | 5.4933e-19 | 1.7774e-11 | 3.264e-12 | 1.3595e-34 | -1.7774e-11 | -3.264e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94815 | 0.94465 | 0.95 | 0.94815 | 0.94465 | 3.7801e-14 | -120.3084 | 119.9432 | 3.7813e-14 | -120.3084 | 119.9432
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.06e-19 | -6.3849e-12 | -1.8532e-11 | 2.06e-19 | 6.3849e-12 | 1.8532e-11 | 5.4933e-19 | 1.7774e-11 | 3.264e-12 | 1.3595e-34 | -1.7774e-11 | -3.264e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94815 | 0.94465 | 0.95 | 0.94815 | 0.94465 | 3.7801e-14 | -120.3084 | 119.9432 | 3.7813e-14 | -120.3084 | 119.9432
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.03e-18 | -5.1079e-11 | -1.4825e-10 | -1.3047e-18 | 5.1079e-11 | 1.4825e-10 | 3.296e-18 | 1.422e-10 | 2.6112e-11 | -2.7466e-18 | -1.422e-10 | -2.6112e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94815 | 0.94465 | 0.95 | 0.94815 | 0.94465 | 3.7763e-14 | -120.3084 | 119.9432 | 3.7829e-14 | -120.3084 | 119.9432
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.18e-19 | -1.277e-11 | -3.7063e-11 | 6.18e-19 | 1.277e-11 | 3.7063e-11 | 2.7466e-18 | 3.5549e-11 | 6.5281e-12 | -2.1973e-18 | -3.5549e-11 | -6.5281e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94815 | 0.94465 | 0.95 | 0.94815 | 0.94465 | 3.7763e-14 | -120.3084 | 119.9432 | 3.7801e-14 | -120.3084 | 119.9432
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.18e-19 | -1.277e-11 | -3.7063e-11 | 6.18e-19 | 1.277e-11 | 3.7063e-11 | 2.7466e-18 | 3.5549e-11 | 6.5281e-12 | -2.1973e-18 | -3.5549e-11 | -6.5281e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94815 | 0.94465 | 0.95 | 0.94815 | 0.94465 | 3.7763e-14 | -120.3084 | 119.9432 | 3.7801e-14 | -120.3084 | 119.9432
Line4_2_6 | 0 | 0.051843 | 0.051843 | 0 | 0.051843 | 0.051843 | 0 | 0.011973 | 0.011973 | 0 | 0.011973 | 0.011973 | 1.0987e-18 | 0.010915 | 0.0028331 | -1.0987e-18 | -0.010863 | -0.0027815 | 2.1973e-18 | 0.0028788 | 0.010882 | -2.1973e-18 | -0.0028251 | -0.010828 | 0 | -135.2796 | 44.7204 | 0 | 44.7204 | -135.2796 | 0.95 | 0.94283 | 0.93921 | 0.95 | 0.93752 | 0.93379 | 3.7791e-14 | -120.5043 | 120.1275 | 3.7823e-14 | -120.7024 | 120.3141
Line5_6_7 | 0 | 0.051843 | 0.051843 | 0 | 0.051843 | 0.051843 | 0 | 0.011973 | 0.011973 | 0 | 0.011973 | 0.011973 | 3.296e-18 | 0.010863 | 0.0027815 | 2.8973e-33 | -0.010812 | -0.0027299 | 4.3946e-18 | 0.0028251 | 0.010828 | -4.3946e-18 | -0.0027713 | -0.010775 | 0 | -135.2796 | 44.7204 | 0 | 44.7204 | -135.2796 | 0.95 | 0.93752 | 0.93379 | 0.95 | 0.93223 | 0.92837 | 3.7823e-14 | -120.7024 | 120.3141 | 3.7774e-14 | -120.9028 | 120.5028
Line6_7_8 | 0 | 0.051843 | 0.051843 | 0 | 0.051843 | 0.051843 | 0 | 0.011973 | 0.011973 | 0 | 0.011973 | 0.011973 | -2.8973e-33 | 0.010812 | 0.0027299 | -2.1973e-18 | -0.01076 | -0.0026783 | 4.3946e-18 | 0.0027713 | 0.010775 | -4.3946e-18 | -0.0027175 | -0.010721 | 0 | -135.2796 | 44.7204 | 0 | 44.7204 | -135.2796 | 0.95 | 0.93223 | 0.92837 | 0.95 | 0.92694 | 0.92297 | 3.7774e-14 | -120.9028 | 120.5028 | 3.7745e-14 | -121.1055 | 120.6937
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1973e-18 | -7.7759e-11 | -9.1252e-11 | 0 | 7.7759e-11 | 9.1252e-11 | 2.1973e-18 | 6.2294e-11 | -3.8923e-11 | 0 | -6.2294e-11 | 3.8923e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.92694 | 0.92297 | 0.95 | 0.92694 | 0.92297 | 3.7745e-14 | -121.1055 | 120.6937 | 3.7711e-14 | -121.1055 | 120.6937
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3946e-18 | -7.7759e-11 | -9.1252e-11 | -2.1973e-18 | 7.7759e-11 | 9.1252e-11 | -4.3946e-18 | 6.2294e-11 | -3.8923e-11 | 6.5919e-18 | -6.2294e-11 | 3.8923e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.92694 | 0.92297 | 0.95 | 0.92694 | 0.92297 | 3.7745e-14 | -121.1055 | 120.6937 | 3.7744e-14 | -121.1055 | 120.6937
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.648e-18 | -4.4694e-11 | -1.2972e-10 | -1.3733e-18 | 4.4694e-11 | 1.2972e-10 | 2.7466e-18 | 1.2442e-10 | 2.2848e-11 | -2.1973e-18 | -1.2442e-10 | -2.2848e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94815 | 0.94465 | 0.95 | 0.94815 | 0.94465 | 3.7829e-14 | -120.3084 | 119.9432 | 3.7902e-14 | -120.3084 | 119.9432

## LL_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0.049114 | 0.049114 | 0 | 0.049114 | 0.049114 | 0 | 0.011342 | 0.011342 | 0 | 0.011342 | 0.011342 | 1.5613e-18 | 0.0098425 | 0.002589 | -2.0817e-18 | -0.0097961 | -0.0025427 | 7.5392e-34 | 0.002632 | 0.009815 | -1.0059e-33 | -0.0025837 | -0.0097667 | 0 | -135.2796 | 44.7204 | 0 | 44.7204 | -135.2796 | 0.9 | 0.89825 | 0.89493 | 0.9 | 0.89321 | 0.88978 | 2.7668e-14 | -120.3084 | 119.9432 | 2.7685e-14 | -120.5043 | 120.1275
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.301e-19 | -3.4383e-11 | -9.9793e-11 | 1.301e-19 | 3.4383e-11 | 9.9793e-11 | 2.6021e-18 | 9.5716e-11 | 1.7577e-11 | -2.6021e-18 | -9.5716e-11 | -1.7577e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89825 | 0.89493 | 0.9 | 0.89825 | 0.89493 | 2.7807e-14 | -120.3084 | 119.9432 | 2.7881e-14 | -120.3084 | 119.9432
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6021e-19 | -2.8652e-11 | -8.3161e-11 | -2.6021e-19 | 2.8652e-11 | 8.3161e-11 | 2.6021e-18 | 7.9764e-11 | 1.4648e-11 | -2.0817e-18 | -7.9764e-11 | -1.4648e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89825 | 0.89493 | 0.9 | 0.89825 | 0.89493 | 2.7881e-14 | -120.3084 | 119.9432 | 2.7951e-14 | -120.3084 | 119.9432
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9516e-19 | -1.7191e-11 | -4.9896e-11 | -1.9516e-19 | 1.7192e-11 | 4.9896e-11 | 5.2042e-19 | 4.7858e-11 | 8.7885e-12 | -1.0408e-18 | -4.7858e-11 | -8.7885e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89825 | 0.89493 | 0.9 | 0.89825 | 0.89493 | 2.7951e-14 | -120.3084 | 119.9432 | 2.7988e-14 | -120.3084 | 119.9432
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.5052e-20 | -5.7305e-12 | -1.6632e-11 | 6.5052e-20 | 5.7305e-12 | 1.6632e-11 | -3.1735e-35 | 1.5953e-11 | 2.9295e-12 | -1.0408e-18 | -1.5953e-11 | -2.9295e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89825 | 0.89493 | 0.9 | 0.89825 | 0.89493 | 2.7951e-14 | -120.3084 | 119.9432 | 2.795e-14 | -120.3084 | 119.9432
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.4311e-18 | -1.1461e-11 | -3.3264e-11 | 1.4311e-18 | 1.1461e-11 | 3.3264e-11 | -6.9908e-34 | 3.1905e-11 | 5.859e-12 | -5.2042e-19 | -3.1905e-11 | -5.859e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89825 | 0.89493 | 0.9 | 0.89825 | 0.89493 | 2.7988e-14 | -120.3084 | 119.9432 | 2.802e-14 | -120.3084 | 119.9432
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.0901e-34 | -5.7305e-12 | -1.6632e-11 | -2.6021e-19 | 5.7305e-12 | 1.6632e-11 | 1.0408e-18 | 1.5953e-11 | 2.9295e-12 | -1.0408e-18 | -1.5953e-11 | -2.9295e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89825 | 0.89493 | 0.9 | 0.89825 | 0.89493 | 2.802e-14 | -120.3084 | 119.9432 | 2.8032e-14 | -120.3084 | 119.9432
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.5052e-20 | -5.7305e-12 | -1.6632e-11 | 1.9516e-19 | 5.7305e-12 | 1.6632e-11 | 3.1457e-35 | 1.5953e-11 | 2.9295e-12 | 9.4412e-35 | -1.5953e-11 | -2.9295e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89825 | 0.89493 | 0.9 | 0.89825 | 0.89493 | 2.7706e-14 | -120.3084 | 119.9432 | 2.7718e-14 | -120.3084 | 119.9432
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.5052e-20 | -5.7305e-12 | -1.6632e-11 | 1.9516e-19 | 5.7305e-12 | 1.6632e-11 | 3.1457e-35 | 1.5953e-11 | 2.9295e-12 | 9.4412e-35 | -1.5953e-11 | -2.9295e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89825 | 0.89493 | 0.9 | 0.89825 | 0.89493 | 2.7706e-14 | -120.3084 | 119.9432 | 2.7718e-14 | -120.3084 | 119.9432
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6914e-18 | -4.5844e-11 | -1.3306e-10 | -1.4311e-18 | 4.5844e-11 | 1.3306e-10 | 2.6021e-18 | 1.2762e-10 | 2.3436e-11 | -3.1225e-18 | -1.2762e-10 | -2.3436e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89825 | 0.89493 | 0.9 | 0.89825 | 0.89493 | 2.7668e-14 | -120.3084 | 119.9432 | 2.7734e-14 | -120.3084 | 119.9432
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5131e-34 | -1.1461e-11 | -3.3264e-11 | 5.0331e-34 | 1.1461e-11 | 3.3264e-11 | 5.2042e-19 | 3.1905e-11 | 5.859e-12 | -1.0408e-18 | -3.1905e-11 | -5.859e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89825 | 0.89493 | 0.9 | 0.89825 | 0.89493 | 2.7668e-14 | -120.3084 | 119.9432 | 2.7706e-14 | -120.3084 | 119.9432
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5131e-34 | -1.1461e-11 | -3.3264e-11 | 5.0331e-34 | 1.1461e-11 | 3.3264e-11 | 5.2042e-19 | 3.1905e-11 | 5.859e-12 | -1.0408e-18 | -3.1905e-11 | -5.859e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89825 | 0.89493 | 0.9 | 0.89825 | 0.89493 | 2.7668e-14 | -120.3084 | 119.9432 | 2.7706e-14 | -120.3084 | 119.9432
Line4_2_6 | 0 | 0.049114 | 0.049114 | 0 | 0.049114 | 0.049114 | 0 | 0.011342 | 0.011342 | 0 | 0.011342 | 0.011342 | 1.0408e-18 | 0.0097961 | 0.0025427 | 5.0429e-34 | -0.0097498 | -0.0024964 | 2.0817e-18 | 0.0025837 | 0.0097667 | -1.0408e-18 | -0.0025355 | -0.0097185 | 0 | -135.2796 | 44.7204 | 0 | 44.7204 | -135.2796 | 0.9 | 0.89321 | 0.88978 | 0.9 | 0.88818 | 0.88464 | 2.7685e-14 | -120.5043 | 120.1275 | 2.776e-14 | -120.7024 | 120.3141
Line5_6_7 | 0 | 0.049114 | 0.049114 | 0 | 0.049114 | 0.049114 | 0 | 0.011342 | 0.011342 | 0 | 0.011342 | 0.011342 | 1.0408e-18 | 0.0097498 | 0.0024964 | 1.0408e-18 | -0.0097035 | -0.0024501 | 6.245e-18 | 0.0025355 | 0.0097185 | -6.245e-18 | -0.0024873 | -0.0096702 | 0 | -135.2796 | 44.7204 | 0 | 44.7204 | -135.2796 | 0.9 | 0.88818 | 0.88464 | 0.9 | 0.88316 | 0.87951 | 2.776e-14 | -120.7024 | 120.3141 | 2.7782e-14 | -120.9028 | 120.5028
Line6_7_8 | 0 | 0.049114 | 0.049114 | 0 | 0.049114 | 0.049114 | 0 | 0.011342 | 0.011342 | 0 | 0.011342 | 0.011342 | 0 | 0.0097035 | 0.0024501 | 0 | -0.0096572 | -0.0024038 | 0 | 0.0024873 | 0.0096702 | 0 | -0.002439 | -0.009622 | 0 | -135.2796 | 44.7204 | 0 | 44.7204 | -135.2796 | 0.9 | 0.88316 | 0.87951 | 0.9 | 0.87816 | 0.87439 | 2.7782e-14 | -120.9028 | 120.5028 | 2.7804e-14 | -121.1055 | 120.6937
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.0204e-33 | -6.9789e-11 | -8.1899e-11 | 2.0179e-33 | 6.9789e-11 | 8.1899e-11 | 4.1633e-18 | 5.5909e-11 | -3.4934e-11 | -4.1633e-18 | -5.5909e-11 | 3.4934e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.87816 | 0.87439 | 0.9 | 0.87816 | 0.87439 | 2.7804e-14 | -121.1055 | 120.6937 | 2.7771e-14 | -121.1055 | 120.6937
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1633e-18 | -6.9789e-11 | -8.1899e-11 | -2.0817e-18 | 6.9789e-11 | 8.1899e-11 | 2.0204e-33 | 5.5909e-11 | -3.4934e-11 | -2.0817e-18 | -5.5909e-11 | 3.4934e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.87816 | 0.87439 | 0.9 | 0.87816 | 0.87439 | 2.7804e-14 | -121.1055 | 120.6937 | 2.7825e-14 | -121.1055 | 120.6937
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4568e-19 | -4.0113e-11 | -1.1643e-10 | -5.8547e-19 | 4.0113e-11 | 1.1643e-10 | 2.6021e-18 | 1.1167e-10 | 2.0507e-11 | -2.0817e-18 | -1.1167e-10 | -2.0507e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89825 | 0.89493 | 0.9 | 0.89825 | 0.89493 | 2.7734e-14 | -120.3084 | 119.9432 | 2.7807e-14 | -120.3084 | 119.9432

## LG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.04766 | 2.2548e-06 | 2.2548e-06 | 0.04766 | 1.8803e-06 | 1.8803e-06 | 0.011007 | 5.2071e-07 | 5.2071e-07 | 0.011007 | 4.3425e-07 | 4.3425e-07 | 7.5715e-05 | 5.0734e-07 | -4.3899e-07 | -5.6785e-05 | -4.2903e-07 | 3.5986e-07 | 0.00015143 | -7.9194e-07 | -8.2752e-07 | -0.00011357 | 6.5637e-07 | 6.93e-07 | -89.5947 | -92.1536 | -92.1536 | 90.4053 | 87.3414 | 87.3414 | 0.015382 | 1.8062 | 1.799 | 0.011536 | 1.8058 | 1.7982 | -26.1597 | -149.5086 | 149.901 | -26.1597 | -149.4882 | 149.8993
Line10_11_12 | 2.2506e-06 | 2.2506e-06 | 2.2506e-06 | 1.8763e-06 | 1.8763e-06 | 1.8763e-06 | 5.1975e-07 | 5.1975e-07 | 5.1975e-07 | 4.3331e-07 | 4.3331e-07 | 4.3331e-07 | 3.2562e-09 | 5.0584e-07 | -4.3877e-07 | -2.6612e-09 | -4.2744e-07 | 3.5978e-07 | 7.3014e-09 | -7.9084e-07 | -8.2568e-07 | -6.1106e-09 | 6.556e-07 | 6.9152e-07 | -92.1242 | -92.1125 | -92.1125 | 87.3739 | 87.3879 | 87.3879 | 0.015382 | 1.8062 | 1.799 | 0.015382 | 1.8062 | 1.799 | -26.1597 | -149.5086 | 149.901 | -26.1596 | -149.5086 | 149.901
Line11_12_13 | 1.8755e-06 | 1.8755e-06 | 1.8755e-06 | 1.5012e-06 | 1.5012e-06 | 1.5012e-06 | 4.3312e-07 | 4.3313e-07 | 4.3313e-07 | 3.4669e-07 | 3.4669e-07 | 3.4669e-07 | 2.7135e-09 | 4.2153e-07 | -3.6564e-07 | -2.1185e-09 | -3.4313e-07 | 2.8665e-07 | 6.0845e-09 | -6.5903e-07 | -6.8807e-07 | -4.8936e-09 | 5.238e-07 | 5.5391e-07 | -92.1242 | -92.1125 | -92.1125 | 87.2485 | 87.263 | 87.263 | 0.015382 | 1.8062 | 1.799 | 0.015381 | 1.8062 | 1.799 | -26.1596 | -149.5086 | 149.901 | -26.1596 | -149.5086 | 149.901
Line12_13_15 | 1.1253e-06 | 1.1253e-06 | 1.1253e-06 | 0 | 0 | 0 | 2.5987e-07 | 2.5988e-07 | 2.5988e-07 | 0 | 0 | 0 | 1.6281e-09 | 2.5292e-07 | -2.1939e-07 | -1.0331e-09 | -1.7452e-07 | 1.4039e-07 | 3.6507e-09 | -3.9542e-07 | -4.1284e-07 | -2.4599e-09 | 2.6019e-07 | 2.7868e-07 | -92.1242 | -92.1125 | -92.1125 | 0 | 0 | 0 | 0.015381 | 1.8062 | 1.799 | 0.015381 | 1.8062 | 1.799 | -26.1596 | -149.5086 | 149.901 | -26.1596 | -149.5086 | 149.901
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4269e-10 | 8.4306e-08 | -7.3129e-08 | 5.2285e-11 | -5.91e-09 | -5.8624e-09 | 1.2169e-09 | -1.3181e-07 | -1.3761e-07 | -2.6108e-11 | -3.4251e-09 | 3.4527e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.015381 | 1.8062 | 1.799 | 0.015381 | 1.8062 | 1.799 | -26.1596 | -149.5086 | 149.901 | -26.1596 | -149.5086 | 149.901
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0854e-09 | 1.6861e-07 | -1.4626e-07 | -4.9041e-10 | -9.0216e-08 | 6.7266e-08 | 2.4338e-09 | -2.6361e-07 | -2.7523e-07 | -1.243e-09 | 1.2838e-07 | 1.4107e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0.015381 | 1.8062 | 1.799 | 0.015381 | 1.8062 | 1.799 | -26.1596 | -149.5086 | 149.901 | -26.1596 | -149.5086 | 149.901
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4269e-10 | 8.4306e-08 | -7.3129e-08 | 5.2285e-11 | -5.91e-09 | -5.8624e-09 | 1.2169e-09 | -1.3181e-07 | -1.3761e-07 | -2.6108e-11 | -3.4251e-09 | 3.4527e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.015381 | 1.8062 | 1.799 | 0.015381 | 1.8062 | 1.799 | -26.1596 | -149.5086 | 149.901 | -26.1596 | -149.5086 | 149.901
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4271e-10 | 8.4306e-08 | -7.3129e-08 | 5.2287e-11 | -5.91e-09 | -5.8624e-09 | 1.2169e-09 | -1.3181e-07 | -1.3761e-07 | -2.6109e-11 | -3.4251e-09 | 3.4527e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.015382 | 1.8062 | 1.799 | 0.015382 | 1.8062 | 1.799 | -26.1597 | -149.5086 | 149.901 | -26.1597 | -149.5086 | 149.901
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4271e-10 | 8.4306e-08 | -7.3129e-08 | 5.2287e-11 | -5.91e-09 | -5.8624e-09 | 1.2169e-09 | -1.3181e-07 | -1.3761e-07 | -2.6109e-11 | -3.4251e-09 | 3.4527e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.015382 | 1.8062 | 1.799 | 0.015382 | 1.8062 | 1.799 | -26.1597 | -149.5086 | 149.901 | -26.1597 | -149.5086 | 149.901
Line1_1_3 | 3.0008e-06 | 3.0008e-06 | 3.0008e-06 | 2.6264e-06 | 2.6265e-06 | 2.6265e-06 | 6.93e-07 | 6.93e-07 | 6.93e-07 | 6.0655e-07 | 6.0656e-07 | 6.0656e-07 | 4.3417e-09 | 6.7445e-07 | -5.8503e-07 | -3.7467e-09 | -5.9605e-07 | 5.0604e-07 | 9.7353e-09 | -1.0544e-06 | -1.1009e-06 | -8.5445e-09 | 9.1922e-07 | 9.6675e-07 | -92.1242 | -92.1125 | -92.1125 | 87.5173 | 87.5306 | 87.5306 | 0.015382 | 1.8062 | 1.799 | 0.015382 | 1.8062 | 1.799 | -26.1597 | -149.5086 | 149.901 | -26.1597 | -149.5086 | 149.901
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0854e-09 | 1.6861e-07 | -1.4626e-07 | -4.9042e-10 | -9.0216e-08 | 6.7266e-08 | 2.4338e-09 | -2.6361e-07 | -2.7523e-07 | -1.243e-09 | 1.2838e-07 | 1.4107e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0.015382 | 1.8062 | 1.799 | 0.015382 | 1.8062 | 1.799 | -26.1597 | -149.5086 | 149.901 | -26.1597 | -149.5086 | 149.901
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0854e-09 | 1.6861e-07 | -1.4626e-07 | -4.9042e-10 | -9.0216e-08 | 6.7266e-08 | 2.4338e-09 | -2.6361e-07 | -2.7523e-07 | -1.243e-09 | 1.2838e-07 | 1.4107e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0.015382 | 1.8062 | 1.799 | 0.015382 | 1.8062 | 1.799 | -26.1597 | -149.5086 | 149.901 | -26.1597 | -149.5086 | 149.901
Line4_2_6 | 0.04766 | 1.8795e-06 | 1.8795e-06 | 0.04766 | 1.5049e-06 | 1.5049e-06 | 0.011007 | 4.3406e-07 | 4.3406e-07 | 0.011007 | 3.4753e-07 | 3.4753e-07 | 5.6785e-05 | 4.2313e-07 | -3.6572e-07 | -3.7857e-05 | -3.4466e-07 | 2.8664e-07 | 0.00011357 | -6.5979e-07 | -6.8955e-07 | -7.5713e-05 | 5.2428e-07 | 5.5503e-07 | -89.5947 | -92.1605 | -92.1605 | 90.4053 | 87.2112 | 87.2112 | 0.011536 | 1.8058 | 1.7982 | 0.0076909 | 1.8053 | 1.7974 | -26.1597 | -149.4882 | 149.8993 | -26.1597 | -149.4679 | 149.8976
Line5_6_7 | 0.04766 | 1.504e-06 | 1.504e-06 | 0.047659 | 1.1292e-06 | 1.1292e-06 | 0.011007 | 3.4734e-07 | 3.4734e-07 | 0.011006 | 2.6077e-07 | 2.6077e-07 | 3.7857e-05 | 3.3876e-07 | -2.9248e-07 | -1.8928e-05 | -2.6014e-07 | 2.1345e-07 | 7.5713e-05 | -5.277e-07 | -5.5158e-07 | -3.7856e-05 | 3.9224e-07 | 4.1706e-07 | -89.5947 | -92.1668 | -92.1668 | 90.4053 | 86.9994 | 86.9994 | 0.0076909 | 1.8053 | 1.7974 | 0.0038454 | 1.8049 | 1.7967 | -26.1597 | -149.4679 | 149.8976 | -26.1597 | -149.4475 | 149.896
Line6_7_8 | 0.047659 | 1.1283e-06 | 1.1283e-06 | 0.047659 | 0 | 0 | 0.011006 | 2.6057e-07 | 2.6057e-07 | 0.011006 | 0 | 0 | 1.8928e-05 | 2.5425e-07 | -2.1929e-07 | -2.429e-14 | -1.7547e-07 | 1.4031e-07 | 3.7856e-05 | -3.9566e-07 | -4.1362e-07 | 1.5713e-14 | 2.6026e-07 | 2.7911e-07 | -89.5947 | -92.1721 | -92.1721 | 90.4053 | 0 | 0 | 0.0038454 | 1.8049 | 1.7967 | 0 | 1.8045 | 1.7959 | -26.1597 | -149.4475 | 149.896 | 0 | -149.427 | 149.8943
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9714e-19 | 8.4792e-08 | -7.3072e-08 | -2.9987e-17 | -5.8885e-09 | -5.8318e-09 | -1.1504e-19 | -1.3183e-07 | -1.3783e-07 | 1.8289e-17 | -3.4133e-09 | 3.4461e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8045 | 1.7959 | 0 | 1.8045 | 1.7959 | 0 | -149.427 | 149.8943 | 0 | -149.427 | 149.8943
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9714e-19 | 8.4792e-08 | -7.3072e-08 | -2.9987e-17 | -5.8885e-09 | -5.8318e-09 | -1.1504e-19 | -1.3183e-07 | -1.3783e-07 | 1.8289e-17 | -3.4133e-09 | 3.4461e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8045 | 1.7959 | 0 | 1.8045 | 1.7959 | 0 | -149.427 | 149.8943 | 0 | -149.427 | 149.8943
Line9_3_11 | 2.6257e-06 | 2.6257e-06 | 2.6257e-06 | 2.2514e-06 | 2.2514e-06 | 2.2514e-06 | 6.0637e-07 | 6.0638e-07 | 6.0638e-07 | 5.1993e-07 | 5.1993e-07 | 5.1993e-07 | 3.7989e-09 | 5.9014e-07 | -5.119e-07 | -3.2039e-09 | -5.1175e-07 | 4.3291e-07 | 8.5184e-09 | -9.2264e-07 | -9.6329e-07 | -7.3275e-09 | 7.8741e-07 | 8.2913e-07 | -92.1242 | -92.1125 | -92.1125 | 87.4575 | 87.4711 | 87.4711 | 0.015382 | 1.8062 | 1.799 | 0.015382 | 1.8062 | 1.799 | -26.1597 | -149.5086 | 149.901 | -26.1597 | -149.5086 | 149.901

## LG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.049921 | 2.3618e-06 | 2.3618e-06 | 0.049921 | 1.9696e-06 | 1.9696e-06 | 0.011529 | 5.4543e-07 | 5.4543e-07 | 0.011529 | 4.5486e-07 | 4.5486e-07 | 8.3068e-05 | 5.5672e-07 | -4.8173e-07 | -6.23e-05 | -4.7079e-07 | 3.949e-07 | 0.00016614 | -8.6891e-07 | -9.0795e-07 | -0.0001246 | 7.2016e-07 | 7.6035e-07 | -89.5934 | -92.1528 | -92.1528 | 90.4066 | 87.3422 | 87.3422 | 0.016111 | 1.892 | 1.8844 | 0.012084 | 1.8916 | 1.8836 | -26.1584 | -149.5046 | 149.8979 | -26.1584 | -149.4842 | 149.8962
Line10_11_12 | 2.3574e-06 | 2.3574e-06 | 2.3574e-06 | 1.9653e-06 | 1.9654e-06 | 1.9654e-06 | 5.4442e-07 | 5.4443e-07 | 5.4443e-07 | 4.5387e-07 | 4.5388e-07 | 4.5388e-07 | 3.5724e-09 | 5.5507e-07 | -4.8149e-07 | -2.9196e-09 | -4.6904e-07 | 3.9481e-07 | 8.0108e-09 | -8.677e-07 | -9.0592e-07 | -6.7043e-09 | 7.1933e-07 | 7.5873e-07 | -92.1239 | -92.1117 | -92.1117 | 87.3741 | 87.3887 | 87.3887 | 0.016111 | 1.892 | 1.8844 | 0.016111 | 1.892 | 1.8844 | -26.1584 | -149.5046 | 149.8979 | -26.1584 | -149.5046 | 149.8979
Line11_12_13 | 1.9645e-06 | 1.9645e-06 | 1.9645e-06 | 1.5725e-06 | 1.5725e-06 | 1.5725e-06 | 4.5368e-07 | 4.5369e-07 | 4.5369e-07 | 3.6314e-07 | 3.6315e-07 | 3.6315e-07 | 2.977e-09 | 4.6256e-07 | -4.0124e-07 | -2.3242e-09 | -3.7653e-07 | 3.1456e-07 | 6.6756e-09 | -7.2309e-07 | -7.5494e-07 | -5.3691e-09 | 5.7471e-07 | 6.0774e-07 | -92.1239 | -92.1117 | -92.1117 | 87.2486 | 87.2639 | 87.2639 | 0.016111 | 1.892 | 1.8844 | 0.016111 | 1.892 | 1.8844 | -26.1584 | -149.5046 | 149.8979 | -26.1583 | -149.5046 | 149.8979
Line12_13_15 | 1.1787e-06 | 1.1787e-06 | 1.1787e-06 | 0 | 0 | 0 | 2.7221e-07 | 2.7221e-07 | 2.7221e-07 | 0 | 0 | 0 | 1.7862e-09 | 2.7754e-07 | -2.4075e-07 | -1.1334e-09 | -1.9151e-07 | 1.5407e-07 | 4.0054e-09 | -4.3385e-07 | -4.5296e-07 | -2.6989e-09 | 2.8548e-07 | 3.0576e-07 | -92.1239 | -92.1117 | -92.1117 | 0 | 0 | 0 | 0.016111 | 1.892 | 1.8844 | 0.016111 | 1.892 | 1.8844 | -26.1583 | -149.5046 | 149.8979 | -26.1583 | -149.5046 | 149.8979
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.954e-10 | 9.2512e-08 | -8.0249e-08 | 5.7374e-11 | -6.484e-09 | -6.4316e-09 | 1.3351e-09 | -1.4462e-07 | -1.5099e-07 | -2.8647e-11 | -3.7583e-09 | 3.7885e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016111 | 1.892 | 1.8844 | 0.016111 | 1.892 | 1.8844 | -26.1583 | -149.5046 | 149.8979 | -26.1583 | -149.5046 | 149.8979
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1908e-09 | 1.8502e-07 | -1.605e-07 | -5.3802e-10 | -9.8996e-08 | 7.3817e-08 | 2.6702e-09 | -2.8923e-07 | -3.0197e-07 | -1.3638e-09 | 1.4086e-07 | 1.5478e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016111 | 1.892 | 1.8844 | 0.016111 | 1.892 | 1.8844 | -26.1583 | -149.5046 | 149.8979 | -26.1583 | -149.5046 | 149.8979
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.9539e-10 | 9.2512e-08 | -8.0249e-08 | 5.7374e-11 | -6.484e-09 | -6.4316e-09 | 1.3351e-09 | -1.4462e-07 | -1.5099e-07 | -2.8647e-11 | -3.7583e-09 | 3.7885e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016111 | 1.892 | 1.8844 | 0.016111 | 1.892 | 1.8844 | -26.1583 | -149.5046 | 149.8979 | -26.1583 | -149.5046 | 149.8979
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.9541e-10 | 9.2512e-08 | -8.0249e-08 | 5.7375e-11 | -6.484e-09 | -6.4316e-09 | 1.3352e-09 | -1.4462e-07 | -1.5099e-07 | -2.8648e-11 | -3.7583e-09 | 3.7885e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016111 | 1.892 | 1.8844 | 0.016111 | 1.892 | 1.8844 | -26.1584 | -149.5046 | 149.8979 | -26.1584 | -149.5046 | 149.8979
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.9541e-10 | 9.2512e-08 | -8.0249e-08 | 5.7375e-11 | -6.484e-09 | -6.4316e-09 | 1.3352e-09 | -1.4462e-07 | -1.5099e-07 | -2.8648e-11 | -3.7583e-09 | 3.7885e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016111 | 1.892 | 1.8844 | 0.016111 | 1.892 | 1.8844 | -26.1584 | -149.5046 | 149.8979 | -26.1584 | -149.5046 | 149.8979
Line1_1_3 | 3.1432e-06 | 3.1432e-06 | 3.1432e-06 | 2.7511e-06 | 2.7511e-06 | 2.7511e-06 | 7.2589e-07 | 7.259e-07 | 7.259e-07 | 6.3534e-07 | 6.3535e-07 | 6.3535e-07 | 4.7633e-09 | 7.4009e-07 | -6.4199e-07 | -4.1105e-09 | -6.5407e-07 | 5.5531e-07 | 1.0681e-08 | -1.1569e-06 | -1.2079e-06 | -9.3747e-09 | 1.0086e-06 | 1.0607e-06 | -92.1239 | -92.1117 | -92.1117 | 87.5175 | 87.5314 | 87.5314 | 0.016111 | 1.892 | 1.8844 | 0.016111 | 1.892 | 1.8844 | -26.1584 | -149.5046 | 149.8979 | -26.1584 | -149.5046 | 149.8979
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1908e-09 | 1.8502e-07 | -1.605e-07 | -5.3804e-10 | -9.8996e-08 | 7.3817e-08 | 2.6703e-09 | -2.8923e-07 | -3.0197e-07 | -1.3638e-09 | 1.4086e-07 | 1.5478e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016111 | 1.892 | 1.8844 | 0.016111 | 1.892 | 1.8844 | -26.1584 | -149.5046 | 149.8979 | -26.1584 | -149.5046 | 149.8979
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1908e-09 | 1.8502e-07 | -1.605e-07 | -5.3804e-10 | -9.8996e-08 | 7.3817e-08 | 2.6703e-09 | -2.8923e-07 | -3.0197e-07 | -1.3638e-09 | 1.4086e-07 | 1.5478e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016111 | 1.892 | 1.8844 | 0.016111 | 1.892 | 1.8844 | -26.1584 | -149.5046 | 149.8979 | -26.1584 | -149.5046 | 149.8979
Line4_2_6 | 0.049921 | 1.9687e-06 | 1.9687e-06 | 0.04992 | 1.5763e-06 | 1.5763e-06 | 0.011529 | 4.5466e-07 | 4.5466e-07 | 0.011529 | 3.6403e-07 | 3.6403e-07 | 6.23e-05 | 4.6431e-07 | -4.0133e-07 | -4.1533e-05 | -3.782e-07 | 3.1455e-07 | 0.0001246 | -7.2392e-07 | -7.5656e-07 | -8.3066e-05 | 5.7523e-07 | 6.0897e-07 | -89.5934 | -92.1597 | -92.1597 | 90.4066 | 87.212 | 87.212 | 0.012084 | 1.8916 | 1.8836 | 0.0080557 | 1.8911 | 1.8828 | -26.1584 | -149.4842 | 149.8962 | -26.1584 | -149.4638 | 149.8945
Line5_6_7 | 0.04992 | 1.5754e-06 | 1.5754e-06 | 0.04992 | 1.1828e-06 | 1.1828e-06 | 0.011529 | 3.6383e-07 | 3.6383e-07 | 0.011528 | 2.7315e-07 | 2.7315e-07 | 4.1533e-05 | 3.7173e-07 | -3.2096e-07 | -2.0766e-05 | -2.8546e-07 | 2.3424e-07 | 8.3066e-05 | -5.7899e-07 | -6.0518e-07 | -4.1533e-05 | 4.3036e-07 | 4.576e-07 | -89.5934 | -92.166 | -92.166 | 90.4066 | 87.0003 | 87.0003 | 0.0080557 | 1.8911 | 1.8828 | 0.0040278 | 1.8907 | 1.882 | -26.1584 | -149.4638 | 149.8945 | -26.1584 | -149.4434 | 149.8928
Line6_7_8 | 0.04992 | 1.1818e-06 | 1.1818e-06 | 0.049919 | 0 | 0 | 0.011528 | 2.7294e-07 | 2.7294e-07 | 0.011528 | 0 | 0 | 2.0766e-05 | 2.7899e-07 | -2.4065e-07 | -1.5898e-14 | -1.9255e-07 | 1.5398e-07 | 4.1533e-05 | -4.3411e-07 | -4.5381e-07 | 2.4191e-14 | 2.8555e-07 | 3.0623e-07 | -89.5934 | -92.1713 | -92.1713 | 90.4066 | 0 | 0 | 0.0040278 | 1.8907 | 1.882 | 0 | 1.8902 | 1.8812 | -26.1584 | -149.4434 | 149.8928 | 0 | -149.423 | 149.8911
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3408e-19 | 9.3045e-08 | -8.0187e-08 | -3.2908e-17 | -6.4604e-09 | -6.398e-09 | -1.849e-19 | -1.4465e-07 | -1.5123e-07 | 2.0074e-17 | -3.7453e-09 | 3.7813e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8902 | 1.8812 | 0 | 1.8902 | 1.8812 | 0 | -149.423 | 149.8911 | 0 | -149.423 | 149.8911
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3408e-19 | 9.3045e-08 | -8.0187e-08 | -3.2908e-17 | -6.4604e-09 | -6.398e-09 | -1.849e-19 | -1.4465e-07 | -1.5123e-07 | 2.0074e-17 | -3.7453e-09 | 3.7813e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8902 | 1.8812 | 0 | 1.8902 | 1.8812 | 0 | -149.423 | 149.8911 | 0 | -149.423 | 149.8911
Line9_3_11 | 2.7503e-06 | 2.7503e-06 | 2.7503e-06 | 2.3582e-06 | 2.3582e-06 | 2.3582e-06 | 6.3516e-07 | 6.3516e-07 | 6.3516e-07 | 5.4461e-07 | 5.4461e-07 | 5.4461e-07 | 4.1679e-09 | 6.4758e-07 | -5.6174e-07 | -3.515e-09 | -5.6155e-07 | 4.7506e-07 | 9.346e-09 | -1.0123e-06 | -1.0569e-06 | -8.0395e-09 | 8.6394e-07 | 9.0971e-07 | -92.1239 | -92.1117 | -92.1117 | 87.4577 | 87.4719 | 87.4719 | 0.016111 | 1.892 | 1.8844 | 0.016111 | 1.892 | 1.8844 | -26.1584 | -149.5046 | 149.8979 | -26.1584 | -149.5046 | 149.8979

## LG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.021507 | 1.0175e-06 | 1.0175e-06 | 0.021507 | 0 | 0 | 0.0049669 | 2.3498e-07 | 2.3498e-07 | 0.0049669 | 0 | 0 | 0.0023282 | 1.5e-07 | -2.405e-07 | -0.0023243 | -1.2738e-07 | 1.9953e-07 | 0.0023436 | -3.0879e-07 | -1.3518e-07 | -0.0023359 | 2.5634e-07 | 1.1443e-07 | -63.4713 | -66.0302 | -66.0302 | 116.5287 | 0 | 0 | 0.66509 | 1.461 | 1.1741 | 0.66344 | 1.4607 | 1.1738 | -18.2821 | -130.1221 | 143.31 | -18.329 | -130.1117 | 143.2999
Line10_11_12 | 1.0156e-06 | 1.0156e-06 | 1.0156e-06 | 0 | 0 | 0 | 2.3454e-07 | 2.3455e-07 | 2.3455e-07 | 0 | 0 | 0 | 1.0495e-07 | 1.495e-07 | -2.4015e-07 | -8.6647e-08 | -1.2687e-07 | 1.9922e-07 | 1.1541e-07 | -3.0833e-07 | -1.3476e-07 | -9.6979e-08 | 2.5595e-07 | 1.1409e-07 | -66.0007 | -65.9891 | -65.9891 | 0 | 0 | 0 | 0.66509 | 1.461 | 1.1741 | 0.66509 | 1.461 | 1.1741 | -18.2821 | -130.1221 | 143.31 | -18.2821 | -130.1221 | 143.31
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.7456e-08 | 1.2458e-07 | -2.0012e-07 | -6.9155e-08 | -1.0195e-07 | 1.592e-07 | 9.6176e-08 | -2.5694e-07 | -1.123e-07 | -7.7744e-08 | 2.0457e-07 | 9.1629e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0.66509 | 1.461 | 1.1741 | 0.66509 | 1.461 | 1.1741 | -18.2821 | -130.1221 | 143.31 | -18.2821 | -130.1221 | 143.31
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2474e-08 | 7.4749e-08 | -1.2007e-07 | -3.4173e-08 | -5.2122e-08 | 7.9147e-08 | 5.7706e-08 | -1.5417e-07 | -6.738e-08 | -3.9274e-08 | 1.0179e-07 | 4.6709e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0.66509 | 1.461 | 1.1741 | 0.66509 | 1.461 | 1.1741 | -18.2821 | -130.1221 | 143.31 | -18.2821 | -130.1221 | 143.31
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7491e-08 | 2.4916e-08 | -4.0025e-08 | 8.0942e-10 | -2.289e-09 | -9.0311e-10 | 1.9235e-08 | -5.1389e-08 | -2.246e-08 | -8.0324e-10 | -9.8852e-10 | 1.7887e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.66509 | 1.461 | 1.1741 | 0.66509 | 1.461 | 1.1741 | -18.2821 | -130.1221 | 143.31 | -18.2821 | -130.1221 | 143.31
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4982e-08 | 4.9833e-08 | -8.005e-08 | -1.6682e-08 | -2.7205e-08 | 3.9122e-08 | 3.847e-08 | -1.0278e-07 | -4.492e-08 | -2.0038e-08 | 5.04e-08 | 2.4249e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0.66509 | 1.461 | 1.1741 | 0.66509 | 1.461 | 1.1741 | -18.2821 | -130.1221 | 143.31 | -18.2821 | -130.1221 | 143.31
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7491e-08 | 2.4916e-08 | -4.0025e-08 | 8.0942e-10 | -2.289e-09 | -9.0311e-10 | 1.9235e-08 | -5.1389e-08 | -2.246e-08 | -8.0324e-10 | -9.8852e-10 | 1.7887e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.66509 | 1.461 | 1.1741 | 0.66509 | 1.461 | 1.1741 | -18.2821 | -130.1221 | 143.31 | -18.2821 | -130.1221 | 143.31
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7491e-08 | 2.4916e-08 | -4.0025e-08 | 8.0942e-10 | -2.289e-09 | -9.0311e-10 | 1.9235e-08 | -5.1389e-08 | -2.246e-08 | -8.0324e-10 | -9.8852e-10 | 1.7887e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.66509 | 1.461 | 1.1741 | 0.66509 | 1.461 | 1.1741 | -18.2821 | -130.1221 | 143.31 | -18.2821 | -130.1221 | 143.31
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7491e-08 | 2.4916e-08 | -4.0025e-08 | 8.0942e-10 | -2.289e-09 | -9.0311e-10 | 1.9235e-08 | -5.1389e-08 | -2.246e-08 | -8.0324e-10 | -9.8852e-10 | 1.7887e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.66509 | 1.461 | 1.1741 | 0.66509 | 1.461 | 1.1741 | -18.2821 | -130.1221 | 143.31 | -18.2821 | -130.1221 | 143.31
Line1_1_3 | 1.3541e-06 | 1.3542e-06 | 1.3542e-06 | 1.1852e-06 | 1.1852e-06 | 1.1852e-06 | 3.1273e-07 | 3.1273e-07 | 3.1273e-07 | 2.7372e-07 | 2.7372e-07 | 2.7372e-07 | 1.3993e-07 | 1.9933e-07 | -3.202e-07 | -1.2163e-07 | -1.767e-07 | 2.7927e-07 | 1.5388e-07 | -4.1111e-07 | -1.7968e-07 | -1.3545e-07 | 3.5873e-07 | 1.5901e-07 | -66.0007 | -65.9891 | -65.9891 | 113.6407 | 113.654 | 113.654 | 0.66509 | 1.461 | 1.1741 | 0.66509 | 1.461 | 1.1741 | -18.2821 | -130.1221 | 143.31 | -18.2821 | -130.1221 | 143.31
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4982e-08 | 4.9833e-08 | -8.005e-08 | -1.6682e-08 | -2.7205e-08 | 3.9122e-08 | 3.847e-08 | -1.0278e-07 | -4.492e-08 | -2.0038e-08 | 5.04e-08 | 2.4249e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0.66509 | 1.461 | 1.1741 | 0.66509 | 1.461 | 1.1741 | -18.2821 | -130.1221 | 143.31 | -18.2821 | -130.1221 | 143.31
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4982e-08 | 4.9833e-08 | -8.005e-08 | -1.6682e-08 | -2.7205e-08 | 3.9122e-08 | 3.847e-08 | -1.0278e-07 | -4.492e-08 | -2.0038e-08 | 5.04e-08 | 2.4249e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0.66509 | 1.461 | 1.1741 | 0.66509 | 1.461 | 1.1741 | -18.2821 | -130.1221 | 143.31 | -18.2821 | -130.1221 | 143.31
Line4_2_6 | 0.021507 | 0 | 0 | 0.021507 | 0 | 0 | 0.0049669 | 0 | 0 | 0.0049669 | 0 | 0 | 0.0023243 | 1.2509e-07 | -2.0043e-07 | -0.0023204 | -1.0243e-07 | 1.5946e-07 | 0.0023359 | -2.5733e-07 | -1.1265e-07 | -0.0023281 | 2.0487e-07 | 9.1897e-08 | -63.4713 | 0 | 0 | 116.5287 | 0 | 0 | 0.66344 | 1.4607 | 1.1738 | 0.66179 | 1.4605 | 1.1735 | -18.329 | -130.1117 | 143.2999 | -18.3761 | -130.1012 | 143.2897
Line5_6_7 | 0.021507 | 0 | 0 | 0.021507 | 0 | 0 | 0.0049669 | 0 | 0 | 0.0049668 | 0 | 0 | 0.0023204 | 1.0015e-07 | -1.6036e-07 | -0.0023165 | -7.7442e-08 | 1.1938e-07 | 0.0023281 | -2.0586e-07 | -9.0111e-08 | -0.0023204 | 1.534e-07 | 6.9358e-08 | -63.4712 | 0 | 0 | 116.5288 | 0 | 0 | 0.66179 | 1.4605 | 1.1735 | 0.66014 | 1.4603 | 1.1732 | -18.3761 | -130.1012 | 143.2897 | -18.4235 | -130.0908 | 143.2796
Line6_7_8 | 0.021507 | 0 | 0 | 0.021507 | 0 | 0 | 0.0049668 | 0 | 0 | 0.0049668 | 0 | 0 | 0.0023165 | 7.5158e-08 | -1.2027e-07 | -0.0023127 | -5.241e-08 | 7.9282e-08 | 0.0023204 | -1.5439e-07 | -6.7572e-08 | -0.0023127 | 1.0192e-07 | 4.6817e-08 | -63.4712 | 0 | 0 | 116.5288 | 0 | 0 | 0.66014 | 1.4603 | 1.1732 | 0.6585 | 1.4601 | 1.173 | -18.4235 | -130.0908 | 143.2796 | -18.4711 | -130.0804 | 143.2695
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7389e-08 | 2.5064e-08 | -4.0089e-08 | 8.1467e-10 | -2.2821e-09 | -8.962e-10 | 1.9065e-08 | -5.1454e-08 | -2.2516e-08 | -8.0323e-10 | -9.8389e-10 | 1.784e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6585 | 1.4601 | 1.173 | 0.6585 | 1.4601 | 1.173 | -18.4711 | -130.0804 | 143.2695 | -18.4711 | -130.0804 | 143.2695
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7389e-08 | 2.5064e-08 | -4.0089e-08 | 8.1467e-10 | -2.2821e-09 | -8.962e-10 | 1.9065e-08 | -5.1454e-08 | -2.2516e-08 | -8.0323e-10 | -9.8389e-10 | 1.784e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6585 | 1.4601 | 1.173 | 0.6585 | 1.4601 | 1.173 | -18.4711 | -130.0804 | 143.2695 | -18.4711 | -130.0804 | 143.2695
Line9_3_11 | 1.1849e-06 | 1.1849e-06 | 1.1849e-06 | 1.016e-06 | 1.016e-06 | 1.016e-06 | 2.7364e-07 | 2.7364e-07 | 2.7364e-07 | 2.3463e-07 | 2.3463e-07 | 2.3463e-07 | 1.2244e-07 | 1.7441e-07 | -2.8017e-07 | -1.0414e-07 | -1.5179e-07 | 2.3925e-07 | 1.3465e-07 | -3.5972e-07 | -1.5722e-07 | -1.1621e-07 | 3.0734e-07 | 1.3655e-07 | -66.0007 | -65.9891 | -65.9891 | 113.581 | 113.5946 | 113.5946 | 0.66509 | 1.461 | 1.1741 | 0.66509 | 1.461 | 1.1741 | -18.2821 | -130.1221 | 143.31 | -18.2821 | -130.1221 | 143.31

## LG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.02253 | 1.0659e-06 | 1.0659e-06 | 0.02253 | 0 | 0 | 0.0052031 | 2.4616e-07 | 2.4616e-07 | 0.005203 | 0 | 0 | 0.0025548 | 1.6462e-07 | -2.6393e-07 | -0.0025505 | -1.398e-07 | 2.1898e-07 | 0.0025717 | -3.3887e-07 | -1.4835e-07 | -0.0025632 | 2.8131e-07 | 1.2558e-07 | -63.4728 | -66.0322 | -66.0322 | 116.5272 | 0 | 0 | 0.6967 | 1.5305 | 1.23 | 0.69498 | 1.5302 | 1.2297 | -18.2836 | -130.1218 | 143.3073 | -18.3305 | -130.1114 | 143.2972
Line10_11_12 | 1.0639e-06 | 1.0639e-06 | 1.0639e-06 | 0 | 0 | 0 | 2.457e-07 | 2.4571e-07 | 2.4571e-07 | 0 | 0 | 0 | 1.1516e-07 | 1.6408e-07 | -2.6355e-07 | -9.5082e-08 | -1.3924e-07 | 2.1864e-07 | 1.2665e-07 | -3.3836e-07 | -1.4789e-07 | -1.0642e-07 | 2.8088e-07 | 1.252e-07 | -66.0033 | -65.9911 | -65.9911 | 0 | 0 | 0 | 0.6967 | 1.5305 | 1.23 | 0.6967 | 1.5305 | 1.23 | -18.2836 | -130.1218 | 143.3073 | -18.2836 | -130.1218 | 143.3073
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.597e-08 | 1.3673e-07 | -2.1963e-07 | -7.5888e-08 | -1.119e-07 | 1.7471e-07 | 1.0554e-07 | -2.8197e-07 | -1.2324e-07 | -8.5316e-08 | 2.2449e-07 | 1.0056e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6967 | 1.5305 | 1.23 | 0.6967 | 1.5305 | 1.23 | -18.2836 | -130.1218 | 143.3073 | -18.2836 | -130.1218 | 143.3073
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.7582e-08 | 8.2038e-08 | -1.3178e-07 | -3.75e-08 | -5.7204e-08 | 8.686e-08 | 6.3326e-08 | -1.6918e-07 | -7.3945e-08 | -4.3099e-08 | 1.117e-07 | 5.1259e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6967 | 1.5305 | 1.23 | 0.6967 | 1.5305 | 1.23 | -18.2836 | -130.1218 | 143.3073 | -18.2836 | -130.1218 | 143.3073
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9194e-08 | 2.7346e-08 | -4.3926e-08 | 8.8839e-10 | -2.5118e-09 | -9.9101e-10 | 2.1109e-08 | -5.6394e-08 | -2.4648e-08 | -8.8157e-10 | -1.0848e-09 | 1.9628e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6967 | 1.5305 | 1.23 | 0.6967 | 1.5305 | 1.23 | -18.2836 | -130.1218 | 143.3073 | -18.2836 | -130.1218 | 143.3073
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8388e-08 | 5.4692e-08 | -8.7851e-08 | -1.8306e-08 | -2.9858e-08 | 4.2935e-08 | 4.2217e-08 | -1.1279e-07 | -4.9296e-08 | -2.199e-08 | 5.5309e-08 | 2.6611e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6967 | 1.5305 | 1.23 | 0.6967 | 1.5305 | 1.23 | -18.2836 | -130.1218 | 143.3073 | -18.2836 | -130.1218 | 143.3073
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9194e-08 | 2.7346e-08 | -4.3926e-08 | 8.8839e-10 | -2.5118e-09 | -9.9101e-10 | 2.1109e-08 | -5.6394e-08 | -2.4648e-08 | -8.8157e-10 | -1.0848e-09 | 1.9628e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6967 | 1.5305 | 1.23 | 0.6967 | 1.5305 | 1.23 | -18.2836 | -130.1218 | 143.3073 | -18.2836 | -130.1218 | 143.3073
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9194e-08 | 2.7346e-08 | -4.3926e-08 | 8.8839e-10 | -2.5118e-09 | -9.9101e-10 | 2.1109e-08 | -5.6394e-08 | -2.4648e-08 | -8.8157e-10 | -1.0848e-09 | 1.9628e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6967 | 1.5305 | 1.23 | 0.6967 | 1.5305 | 1.23 | -18.2836 | -130.1218 | 143.3073 | -18.2836 | -130.1218 | 143.3073
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9194e-08 | 2.7346e-08 | -4.3926e-08 | 8.8839e-10 | -2.5118e-09 | -9.9101e-10 | 2.1109e-08 | -5.6394e-08 | -2.4648e-08 | -8.8157e-10 | -1.0848e-09 | 1.9628e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6967 | 1.5305 | 1.23 | 0.6967 | 1.5305 | 1.23 | -18.2836 | -130.1218 | 143.3073 | -18.2836 | -130.1218 | 143.3073
Line1_1_3 | 1.4186e-06 | 1.4186e-06 | 1.4186e-06 | 1.2416e-06 | 1.2416e-06 | 1.2416e-06 | 3.276e-07 | 3.2761e-07 | 3.2761e-07 | 2.8674e-07 | 2.8674e-07 | 2.8674e-07 | 1.5355e-07 | 2.1877e-07 | -3.514e-07 | -1.3347e-07 | -1.9393e-07 | 3.0649e-07 | 1.6887e-07 | -4.5115e-07 | -1.9719e-07 | -1.4864e-07 | 3.9367e-07 | 1.745e-07 | -66.0033 | -65.9911 | -65.9911 | 113.6381 | 113.6521 | 113.6521 | 0.6967 | 1.5305 | 1.23 | 0.6967 | 1.5305 | 1.23 | -18.2836 | -130.1218 | 143.3073 | -18.2836 | -130.1218 | 143.3073
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8388e-08 | 5.4692e-08 | -8.7851e-08 | -1.8306e-08 | -2.9858e-08 | 4.2935e-08 | 4.2217e-08 | -1.1279e-07 | -4.9296e-08 | -2.199e-08 | 5.5309e-08 | 2.6611e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6967 | 1.5305 | 1.23 | 0.6967 | 1.5305 | 1.23 | -18.2836 | -130.1218 | 143.3073 | -18.2836 | -130.1218 | 143.3073
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8388e-08 | 5.4692e-08 | -8.7851e-08 | -1.8306e-08 | -2.9858e-08 | 4.2935e-08 | 4.2217e-08 | -1.1279e-07 | -4.9296e-08 | -2.199e-08 | 5.5309e-08 | 2.6611e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6967 | 1.5305 | 1.23 | 0.6967 | 1.5305 | 1.23 | -18.2836 | -130.1218 | 143.3073 | -18.2836 | -130.1218 | 143.3073
Line4_2_6 | 0.02253 | 0 | 0 | 0.02253 | 0 | 0 | 0.005203 | 0 | 0 | 0.005203 | 0 | 0 | 0.0025505 | 1.3729e-07 | -2.1997e-07 | -0.0025463 | -1.1242e-07 | 1.75e-07 | 0.0025632 | -2.8239e-07 | -1.2362e-07 | -0.0025547 | 2.2483e-07 | 1.0085e-07 | -63.4728 | 0 | 0 | 116.5272 | 0 | 0 | 0.69498 | 1.5302 | 1.2297 | 0.69325 | 1.53 | 1.2294 | -18.3305 | -130.1114 | 143.2972 | -18.3776 | -130.101 | 143.2871
Line5_6_7 | 0.02253 | 0 | 0 | 0.022529 | 0 | 0 | 0.005203 | 0 | 0 | 0.0052029 | 0 | 0 | 0.0025463 | 1.0991e-07 | -1.7599e-07 | -0.002542 | -8.4993e-08 | 1.3101e-07 | 0.0025547 | -2.2591e-07 | -9.889e-08 | -0.0025463 | 1.6834e-07 | 7.6115e-08 | -63.4727 | 0 | 0 | 116.5273 | 0 | 0 | 0.69325 | 1.53 | 1.2294 | 0.69153 | 1.5298 | 1.2291 | -18.3776 | -130.101 | 143.2871 | -18.425 | -130.0905 | 143.2769
Line6_7_8 | 0.022529 | 0 | 0 | 0.022529 | 0 | 0 | 0.0052029 | 0 | 0 | 0.0052029 | 0 | 0 | 0.002542 | 8.2487e-08 | -1.32e-07 | -0.0025378 | -5.7519e-08 | 8.7009e-08 | 0.0025463 | -1.6942e-07 | -7.4156e-08 | -0.0025378 | 1.1185e-07 | 5.1378e-08 | -63.4727 | 0 | 0 | 116.5273 | 0 | 0 | 0.69153 | 1.5298 | 1.2291 | 0.6898 | 1.5295 | 1.2288 | -18.425 | -130.0905 | 143.2769 | -18.4726 | -130.0801 | 143.2668
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9082e-08 | 2.7508e-08 | -4.3996e-08 | 8.9415e-10 | -2.5042e-09 | -9.8343e-10 | 2.0922e-08 | -5.6465e-08 | -2.471e-08 | -8.8155e-10 | -1.0798e-09 | 1.9578e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6898 | 1.5295 | 1.2288 | 0.6898 | 1.5295 | 1.2288 | -18.4726 | -130.0801 | 143.2668 | -18.4726 | -130.0801 | 143.2668
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9082e-08 | 2.7508e-08 | -4.3996e-08 | 8.9415e-10 | -2.5042e-09 | -9.8343e-10 | 2.0922e-08 | -5.6465e-08 | -2.471e-08 | -8.8155e-10 | -1.0798e-09 | 1.9578e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6898 | 1.5295 | 1.2288 | 0.6898 | 1.5295 | 1.2288 | -18.4726 | -130.0801 | 143.2668 | -18.4726 | -130.0801 | 143.2668
Line9_3_11 | 1.2412e-06 | 1.2413e-06 | 1.2413e-06 | 1.0643e-06 | 1.0643e-06 | 1.0643e-06 | 2.8665e-07 | 2.8666e-07 | 2.8666e-07 | 2.4579e-07 | 2.4579e-07 | 2.4579e-07 | 1.3436e-07 | 1.9142e-07 | -3.0748e-07 | -1.1428e-07 | -1.6659e-07 | 2.6256e-07 | 1.4776e-07 | -3.9476e-07 | -1.7254e-07 | -1.2753e-07 | 3.3728e-07 | 1.4985e-07 | -66.0033 | -65.9911 | -65.9911 | 113.5784 | 113.5926 | 113.5926 | 0.6967 | 1.5305 | 1.23 | 0.6967 | 1.5305 | 1.23 | -18.2836 | -130.1218 | 143.3073 | -18.2836 | -130.1218 | 143.3073

## LG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.043112 | 2.0398e-06 | 2.0398e-06 | 0.043112 | 1.7011e-06 | 1.7011e-06 | 0.0099563 | 4.7107e-07 | 4.7107e-07 | 0.0099563 | 3.9286e-07 | 3.9286e-07 | 0.00011895 | 4.1452e-07 | -3.602e-07 | -8.9212e-05 | -3.5075e-07 | 2.9513e-07 | 0.00012391 | -6.5015e-07 | -6.7523e-07 | -9.293e-05 | 5.3883e-07 | 5.6552e-07 | -89.2484 | -91.8542 | -91.8542 | 90.7516 | 87.6333 | 87.6333 | 0.017252 | 1.6368 | 1.6246 | 0.012939 | 1.6366 | 1.6237 | -43.0792 | -149.3337 | 150.0679 | -43.0792 | -149.3047 | 150.0749
Line10_11_12 | 2.0359e-06 | 2.0359e-06 | 2.0359e-06 | 1.6973e-06 | 1.6973e-06 | 1.6973e-06 | 4.7016e-07 | 4.7017e-07 | 4.7017e-07 | 3.9197e-07 | 3.9197e-07 | 3.9197e-07 | 5.3533e-09 | 4.1273e-07 | -3.6054e-07 | -4.4182e-09 | -3.4879e-07 | 2.9567e-07 | 6.0934e-09 | -6.4953e-07 | -6.7338e-07 | -5.1189e-09 | 5.3848e-07 | 5.6399e-07 | -91.7787 | -91.7666 | -91.7666 | 87.7193 | 87.7338 | 87.7338 | 0.017251 | 1.6368 | 1.6246 | 0.017251 | 1.6368 | 1.6246 | -43.0791 | -149.3337 | 150.0679 | -43.0791 | -149.3337 | 150.0679
Line11_12_13 | 1.6966e-06 | 1.6966e-06 | 1.6966e-06 | 1.358e-06 | 1.358e-06 | 1.358e-06 | 3.918e-07 | 3.9181e-07 | 3.9181e-07 | 3.1361e-07 | 3.1361e-07 | 3.1361e-07 | 4.461e-09 | 3.4394e-07 | -3.0045e-07 | -3.526e-09 | -2.8e-07 | 2.3558e-07 | 5.0778e-09 | -5.4128e-07 | -5.6115e-07 | -4.1033e-09 | 4.3023e-07 | 4.5176e-07 | -91.7787 | -91.7666 | -91.7666 | 87.5939 | 87.609 | 87.609 | 0.017251 | 1.6368 | 1.6246 | 0.017251 | 1.6368 | 1.6246 | -43.0791 | -149.3337 | 150.0679 | -43.0791 | -149.3337 | 150.0679
Line12_13_15 | 1.0179e-06 | 1.0179e-06 | 1.0179e-06 | 0 | 0 | 0 | 2.3508e-07 | 2.3508e-07 | 2.3508e-07 | 0 | 0 | 0 | 2.6766e-09 | 2.0636e-07 | -1.8027e-07 | -1.7416e-09 | -1.4243e-07 | 1.154e-07 | 3.0467e-09 | -3.2477e-07 | -3.3669e-07 | -2.0722e-09 | 2.1372e-07 | 2.273e-07 | -91.7787 | -91.7666 | -91.7666 | 0 | 0 | 0 | 0.017251 | 1.6368 | 1.6246 | 0.017251 | 1.6368 | 1.6246 | -43.0791 | -149.3337 | 150.0679 | -43.0791 | -149.3337 | 150.0679
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.922e-10 | 6.8788e-08 | -6.009e-08 | 4.28e-11 | -4.8529e-09 | -4.7799e-09 | 1.0156e-09 | -1.0826e-07 | -1.1223e-07 | -4.1043e-11 | -2.7931e-09 | 2.8353e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.017251 | 1.6368 | 1.6246 | 0.017251 | 1.6368 | 1.6246 | -43.0791 | -149.3337 | 150.0679 | -43.0791 | -149.3337 | 150.0679
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7844e-09 | 1.3758e-07 | -1.2018e-07 | -8.494e-10 | -7.3641e-08 | 5.531e-08 | 2.0311e-09 | -2.1651e-07 | -2.2446e-07 | -1.0566e-09 | 1.0546e-07 | 1.1507e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0.017251 | 1.6368 | 1.6246 | 0.017251 | 1.6368 | 1.6246 | -43.0791 | -149.3337 | 150.0679 | -43.0791 | -149.3337 | 150.0679
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.922e-10 | 6.8788e-08 | -6.009e-08 | 4.28e-11 | -4.8529e-09 | -4.7799e-09 | 1.0156e-09 | -1.0826e-07 | -1.1223e-07 | -4.1043e-11 | -2.7931e-09 | 2.8353e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.017251 | 1.6368 | 1.6246 | 0.017251 | 1.6368 | 1.6246 | -43.0791 | -149.3337 | 150.0679 | -43.0791 | -149.3337 | 150.0679
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.9223e-10 | 6.8788e-08 | -6.009e-08 | 4.2801e-11 | -4.8529e-09 | -4.7799e-09 | 1.0156e-09 | -1.0826e-07 | -1.1223e-07 | -4.1044e-11 | -2.7931e-09 | 2.8353e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.017252 | 1.6368 | 1.6246 | 0.017252 | 1.6368 | 1.6246 | -43.0792 | -149.3337 | 150.0679 | -43.0792 | -149.3337 | 150.0679
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.9223e-10 | 6.8788e-08 | -6.009e-08 | 4.2801e-11 | -4.8529e-09 | -4.7799e-09 | 1.0156e-09 | -1.0826e-07 | -1.1223e-07 | -4.1044e-11 | -2.7931e-09 | 2.8353e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.017252 | 1.6368 | 1.6246 | 0.017252 | 1.6368 | 1.6246 | -43.0792 | -149.3337 | 150.0679 | -43.0792 | -149.3337 | 150.0679
Line1_1_3 | 2.7145e-06 | 2.7145e-06 | 2.7145e-06 | 2.3759e-06 | 2.3759e-06 | 2.3759e-06 | 6.2689e-07 | 6.2689e-07 | 6.2689e-07 | 5.4869e-07 | 5.4869e-07 | 5.4869e-07 | 7.1378e-09 | 5.503e-07 | -4.8072e-07 | -6.2027e-09 | -4.8637e-07 | 4.1585e-07 | 8.1247e-09 | -8.6604e-07 | -8.9784e-07 | -7.1501e-09 | 7.5499e-07 | 7.8845e-07 | -91.7787 | -91.7666 | -91.7666 | 87.8627 | 87.8765 | 87.8765 | 0.017252 | 1.6368 | 1.6246 | 0.017251 | 1.6368 | 1.6246 | -43.0792 | -149.3337 | 150.0679 | -43.0792 | -149.3337 | 150.0679
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7845e-09 | 1.3758e-07 | -1.2018e-07 | -8.4943e-10 | -7.3641e-08 | 5.531e-08 | 2.0312e-09 | -2.1651e-07 | -2.2446e-07 | -1.0566e-09 | 1.0546e-07 | 1.1507e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0.017252 | 1.6368 | 1.6246 | 0.017252 | 1.6368 | 1.6246 | -43.0792 | -149.3337 | 150.0679 | -43.0792 | -149.3337 | 150.0679
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7845e-09 | 1.3758e-07 | -1.2018e-07 | -8.4943e-10 | -7.3641e-08 | 5.531e-08 | 2.0312e-09 | -2.1651e-07 | -2.2446e-07 | -1.0566e-09 | 1.0546e-07 | 1.1507e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0.017252 | 1.6368 | 1.6246 | 0.017252 | 1.6368 | 1.6246 | -43.0792 | -149.3337 | 150.0679 | -43.0792 | -149.3337 | 150.0679
Line4_2_6 | 0.043112 | 1.7004e-06 | 1.7004e-06 | 0.043112 | 1.3615e-06 | 1.3615e-06 | 0.0099563 | 3.9268e-07 | 3.9268e-07 | 0.0099562 | 3.1442e-07 | 3.1442e-07 | 8.9212e-05 | 3.459e-07 | -2.999e-07 | -5.9474e-05 | -2.8192e-07 | 2.3494e-07 | 9.293e-05 | -5.4162e-07 | -5.6269e-07 | -6.1953e-05 | 4.3036e-07 | 4.5296e-07 | -89.2484 | -91.8686 | -91.8686 | 90.7516 | 87.4962 | 87.4962 | 0.012939 | 1.6366 | 1.6237 | 0.0086258 | 1.6363 | 1.6229 | -43.0792 | -149.3047 | 150.0749 | -43.0792 | -149.2757 | 150.0818
Line5_6_7 | 0.043112 | 1.3607e-06 | 1.3607e-06 | 0.043111 | 1.0216e-06 | 1.0216e-06 | 0.0099562 | 3.1424e-07 | 3.1424e-07 | 0.0099561 | 2.3592e-07 | 2.3592e-07 | 5.9474e-05 | 2.7708e-07 | -2.3971e-07 | -2.9737e-05 | -2.129e-07 | 1.7486e-07 | 6.1953e-05 | -4.3315e-07 | -4.5013e-07 | -3.0976e-05 | 3.2196e-07 | 3.4039e-07 | -89.2484 | -91.8819 | -91.8819 | 90.7516 | 87.2788 | 87.2788 | 0.0086258 | 1.6363 | 1.6229 | 0.0043129 | 1.6361 | 1.6221 | -43.0792 | -149.2757 | 150.0818 | -43.0792 | -149.2467 | 150.0887
Line6_7_8 | 0.043111 | 1.0208e-06 | 1.0208e-06 | 0.043111 | 0 | 0 | 0.0099561 | 2.3573e-07 | 2.3573e-07 | 0.009956 | 0 | 0 | 2.9737e-05 | 2.0805e-07 | -1.7962e-07 | 9.0739e-15 | -1.4367e-07 | 1.149e-07 | 3.0976e-05 | -3.2475e-07 | -3.3756e-07 | 4.0606e-15 | 2.1363e-07 | 2.2781e-07 | -89.2483 | -91.893 | -91.893 | 90.7517 | 0 | 0 | 0.0043129 | 1.6361 | 1.6221 | 0 | 1.6358 | 1.6212 | -43.0792 | -149.2467 | 150.0887 | 0 | -149.2177 | 150.0957
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.9987e-20 | 6.9415e-08 | -5.9825e-08 | -2.365e-17 | -4.8386e-09 | -4.7514e-09 | -3.5373e-20 | -1.082e-07 | -1.1249e-07 | 2.6631e-17 | -2.7814e-09 | 2.8318e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6358 | 1.6212 | 0 | 1.6358 | 1.6212 | 0 | -149.2177 | 150.0957 | 0 | -149.2177 | 150.0957
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.9987e-20 | 6.9415e-08 | -5.9825e-08 | -2.365e-17 | -4.8386e-09 | -4.7514e-09 | -3.5373e-20 | -1.082e-07 | -1.1249e-07 | 2.6631e-17 | -2.7814e-09 | 2.8318e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6358 | 1.6212 | 0 | 1.6358 | 1.6212 | 0 | -149.2177 | 150.0957 | 0 | -149.2177 | 150.0957
Line9_3_11 | 2.3752e-06 | 2.3752e-06 | 2.3752e-06 | 2.0366e-06 | 2.0366e-06 | 2.0366e-06 | 5.4852e-07 | 5.4853e-07 | 5.4853e-07 | 4.7033e-07 | 4.7033e-07 | 4.7033e-07 | 6.2456e-09 | 4.8152e-07 | -4.2063e-07 | -5.3105e-09 | -4.1758e-07 | 3.5576e-07 | 7.109e-09 | -7.5779e-07 | -7.8561e-07 | -6.1345e-09 | 6.4674e-07 | 6.7622e-07 | -91.7787 | -91.7666 | -91.7666 | 87.8029 | 87.817 | 87.817 | 0.017251 | 1.6368 | 1.6246 | 0.017251 | 1.6368 | 1.6246 | -43.0792 | -149.3337 | 150.0679 | -43.0791 | -149.3337 | 150.0679

## LG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.040843 | 1.9325e-06 | 1.9325e-06 | 0.040843 | 1.6116e-06 | 1.6116e-06 | 0.0094323 | 4.4628e-07 | 4.4628e-07 | 0.0094323 | 3.7218e-07 | 3.7218e-07 | 0.00010676 | 3.7203e-07 | -3.2329e-07 | -8.0069e-05 | -3.148e-07 | 2.6488e-07 | 0.00011121 | -5.8351e-07 | -6.0602e-07 | -8.3405e-05 | 4.836e-07 | 5.0756e-07 | -89.2484 | -91.8542 | -91.8542 | 90.7516 | 87.6333 | 87.6333 | 0.016344 | 1.5506 | 1.5391 | 0.012258 | 1.5504 | 1.5383 | -43.0792 | -149.3337 | 150.0679 | -43.0792 | -149.3047 | 150.0749
Line10_11_12 | 1.9287e-06 | 1.9287e-06 | 1.9287e-06 | 1.6079e-06 | 1.608e-06 | 1.608e-06 | 4.4542e-07 | 4.4542e-07 | 4.4542e-07 | 3.7134e-07 | 3.7134e-07 | 3.7134e-07 | 4.8046e-09 | 3.7043e-07 | -3.2359e-07 | -3.9654e-09 | -3.1304e-07 | 2.6537e-07 | 5.4689e-09 | -5.8296e-07 | -6.0436e-07 | -4.5942e-09 | 4.8329e-07 | 5.0618e-07 | -91.7787 | -91.7666 | -91.7666 | 87.7193 | 87.7338 | 87.7338 | 0.016343 | 1.5506 | 1.5391 | 0.016343 | 1.5506 | 1.5391 | -43.0791 | -149.3337 | 150.0679 | -43.0791 | -149.3337 | 150.0679
Line11_12_13 | 1.6073e-06 | 1.6073e-06 | 1.6073e-06 | 1.2865e-06 | 1.2865e-06 | 1.2865e-06 | 3.7118e-07 | 3.7119e-07 | 3.7119e-07 | 2.9711e-07 | 2.9711e-07 | 2.9711e-07 | 4.0038e-09 | 3.0869e-07 | -2.6966e-07 | -3.1646e-09 | -2.5131e-07 | 2.1144e-07 | 4.5574e-09 | -4.858e-07 | -5.0364e-07 | -3.6827e-09 | 3.8613e-07 | 4.0545e-07 | -91.7787 | -91.7666 | -91.7666 | 87.5939 | 87.609 | 87.609 | 0.016343 | 1.5506 | 1.5391 | 0.016343 | 1.5506 | 1.5391 | -43.0791 | -149.3337 | 150.0679 | -43.0791 | -149.3337 | 150.0679
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4023e-09 | 1.8521e-07 | -1.6179e-07 | -1.5631e-09 | -1.2783e-07 | 1.0357e-07 | 2.7344e-09 | -2.9148e-07 | -3.0218e-07 | -1.8598e-09 | 1.9181e-07 | 2.04e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016343 | 1.5506 | 1.5391 | 0.016343 | 1.5506 | 1.5391 | -43.0791 | -149.3337 | 150.0679 | -43.0791 | -149.3337 | 150.0679
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.0076e-10 | 6.1738e-08 | -5.3931e-08 | 3.8413e-11 | -4.3555e-09 | -4.29e-09 | 9.1147e-10 | -9.716e-08 | -1.0073e-07 | -3.6836e-11 | -2.5069e-09 | 2.5447e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016343 | 1.5506 | 1.5391 | 0.016343 | 1.5506 | 1.5391 | -43.0791 | -149.3337 | 150.0679 | -43.0791 | -149.3337 | 150.0679
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6015e-09 | 1.2348e-07 | -1.0786e-07 | -7.6234e-10 | -6.6093e-08 | 4.9641e-08 | 1.8229e-09 | -1.9432e-07 | -2.0145e-07 | -9.483e-10 | 9.4653e-08 | 1.0327e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016343 | 1.5506 | 1.5391 | 0.016343 | 1.5506 | 1.5391 | -43.0791 | -149.3337 | 150.0679 | -43.0791 | -149.3337 | 150.0679
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.0075e-10 | 6.1738e-08 | -5.3931e-08 | 3.8413e-11 | -4.3555e-09 | -4.29e-09 | 9.1147e-10 | -9.716e-08 | -1.0073e-07 | -3.6836e-11 | -2.5069e-09 | 2.5447e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016343 | 1.5506 | 1.5391 | 0.016343 | 1.5506 | 1.5391 | -43.0791 | -149.3337 | 150.0679 | -43.0791 | -149.3337 | 150.0679
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.0078e-10 | 6.1738e-08 | -5.3931e-08 | 3.8414e-11 | -4.3555e-09 | -4.29e-09 | 9.1149e-10 | -9.716e-08 | -1.0073e-07 | -3.6837e-11 | -2.5069e-09 | 2.5447e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016344 | 1.5506 | 1.5391 | 0.016344 | 1.5506 | 1.5391 | -43.0792 | -149.3337 | 150.0679 | -43.0792 | -149.3337 | 150.0679
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.0078e-10 | 6.1738e-08 | -5.3931e-08 | 3.8414e-11 | -4.3555e-09 | -4.29e-09 | 9.1149e-10 | -9.716e-08 | -1.0073e-07 | -3.6837e-11 | -2.5069e-09 | 2.5447e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016344 | 1.5506 | 1.5391 | 0.016344 | 1.5506 | 1.5391 | -43.0792 | -149.3337 | 150.0679 | -43.0792 | -149.3337 | 150.0679
Line1_1_3 | 2.5716e-06 | 2.5716e-06 | 2.5716e-06 | 2.2508e-06 | 2.2508e-06 | 2.2508e-06 | 5.9389e-07 | 5.939e-07 | 5.939e-07 | 5.1981e-07 | 5.1981e-07 | 5.1981e-07 | 6.4063e-09 | 4.939e-07 | -4.3145e-07 | -5.567e-09 | -4.3652e-07 | 3.7323e-07 | 7.292e-09 | -7.7728e-07 | -8.0582e-07 | -6.4173e-09 | 6.7761e-07 | 7.0764e-07 | -91.7787 | -91.7666 | -91.7666 | 87.8627 | 87.8765 | 87.8765 | 0.016344 | 1.5506 | 1.5391 | 0.016343 | 1.5506 | 1.5391 | -43.0792 | -149.3337 | 150.0679 | -43.0792 | -149.3337 | 150.0679
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6016e-09 | 1.2348e-07 | -1.0786e-07 | -7.6237e-10 | -6.6093e-08 | 4.9641e-08 | 1.823e-09 | -1.9432e-07 | -2.0145e-07 | -9.4833e-10 | 9.4653e-08 | 1.0327e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016344 | 1.5506 | 1.5391 | 0.016344 | 1.5506 | 1.5391 | -43.0792 | -149.3337 | 150.0679 | -43.0792 | -149.3337 | 150.0679
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6016e-09 | 1.2348e-07 | -1.0786e-07 | -7.6237e-10 | -6.6093e-08 | 4.9641e-08 | 1.823e-09 | -1.9432e-07 | -2.0145e-07 | -9.4833e-10 | 9.4653e-08 | 1.0327e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016344 | 1.5506 | 1.5391 | 0.016344 | 1.5506 | 1.5391 | -43.0792 | -149.3337 | 150.0679 | -43.0792 | -149.3337 | 150.0679
Line4_2_6 | 0.040843 | 1.6109e-06 | 1.6109e-06 | 0.040843 | 1.2898e-06 | 1.2898e-06 | 0.0094323 | 3.7202e-07 | 3.7202e-07 | 0.0094322 | 2.9787e-07 | 2.9787e-07 | 8.0069e-05 | 3.1045e-07 | -2.6916e-07 | -5.3379e-05 | -2.5303e-07 | 2.1086e-07 | 8.3405e-05 | -4.8611e-07 | -5.0502e-07 | -5.5603e-05 | 3.8625e-07 | 4.0654e-07 | -89.2484 | -91.8686 | -91.8686 | 90.7516 | 87.4962 | 87.4962 | 0.012258 | 1.5504 | 1.5383 | 0.0081718 | 1.5502 | 1.5375 | -43.0792 | -149.3047 | 150.0749 | -43.0792 | -149.2757 | 150.0818
Line5_6_7 | 0.040843 | 1.2891e-06 | 1.2891e-06 | 0.040842 | 0 | 0 | 0.0094322 | 2.977e-07 | 2.977e-07 | 0.0094321 | 0 | 0 | 5.3379e-05 | 2.4868e-07 | -2.1514e-07 | -2.6689e-05 | -1.9108e-07 | 1.5694e-07 | 5.5603e-05 | -3.8876e-07 | -4.04e-07 | -2.7801e-05 | 2.8896e-07 | 3.055e-07 | -89.2484 | -91.8819 | -91.8819 | 90.7516 | 0 | 0 | 0.0081718 | 1.5502 | 1.5375 | 0.0040859 | 1.55 | 1.5367 | -43.0792 | -149.2757 | 150.0818 | -43.0792 | -149.2467 | 150.0887
Line6_7_8 | 0.040842 | 0 | 0 | 0.040842 | 0 | 0 | 0.0094321 | 0 | 0 | 0.009432 | 0 | 0 | 2.6689e-05 | 1.8673e-07 | -1.6121e-07 | 8.1448e-15 | -1.2894e-07 | 1.0312e-07 | 2.7801e-05 | -2.9146e-07 | -3.0296e-07 | 3.6486e-15 | 1.9173e-07 | 2.0446e-07 | -89.2483 | 0 | 0 | 90.7517 | 0 | 0 | 0.0040859 | 1.55 | 1.5367 | 0 | 1.5497 | 1.5359 | -43.0792 | -149.2467 | 150.0887 | 0 | -149.2177 | 150.0957
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.2819e-20 | 6.23e-08 | -5.3693e-08 | -2.1226e-17 | -4.3427e-09 | -4.2644e-09 | -3.1781e-20 | -9.7113e-08 | -1.0096e-07 | 2.3901e-17 | -2.4964e-09 | 2.5416e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5497 | 1.5359 | 0 | 1.5497 | 1.5359 | 0 | -149.2177 | 150.0957 | 0 | -149.2177 | 150.0957
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.2819e-20 | 6.23e-08 | -5.3693e-08 | -2.1226e-17 | -4.3427e-09 | -4.2644e-09 | -3.1781e-20 | -9.7113e-08 | -1.0096e-07 | 2.3901e-17 | -2.4964e-09 | 2.5416e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5497 | 1.5359 | 0 | 1.5497 | 1.5359 | 0 | -149.2177 | 150.0957 | 0 | -149.2177 | 150.0957
Line9_3_11 | 2.2502e-06 | 2.2502e-06 | 2.2502e-06 | 1.9294e-06 | 1.9294e-06 | 1.9294e-06 | 5.1966e-07 | 5.1966e-07 | 5.1966e-07 | 4.4557e-07 | 4.4558e-07 | 4.4558e-07 | 5.6054e-09 | 4.3216e-07 | -3.7752e-07 | -4.7662e-09 | -3.7478e-07 | 3.193e-07 | 6.3804e-09 | -6.8012e-07 | -7.0509e-07 | -5.5057e-09 | 5.8045e-07 | 6.0691e-07 | -91.7787 | -91.7666 | -91.7666 | 87.8029 | 87.817 | 87.817 | 0.016343 | 1.5506 | 1.5391 | 0.016343 | 1.5506 | 1.5391 | -43.0792 | -149.3337 | 150.0679 | -43.0791 | -149.3337 | 150.0679

## LG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.019434 | 0 | 0 | 0.019434 | 0 | 0 | 0.0044881 | 0 | 0 | 0.0044881 | 0 | 0 | 0.0019125 | 1.2245e-07 | -1.966e-07 | -0.0019065 | -1.0404e-07 | 1.6309e-07 | 0.0019135 | -2.5255e-07 | -1.1009e-07 | -0.0019072 | 2.0964e-07 | 9.3221e-08 | -63.3333 | 0 | 0 | 116.6667 | 0 | 0 | 0.6028 | 1.3217 | 1.0611 | 0.60085 | 1.3216 | 1.0607 | -18.3181 | -130.0723 | 143.3079 | -18.3218 | -130.0568 | 143.3009
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.6237e-08 | 1.2183e-07 | -1.9639e-07 | -7.1203e-08 | -1.034e-07 | 1.6293e-07 | 9.4261e-08 | -2.5225e-07 | -1.0958e-07 | -7.9211e-08 | 2.094e-07 | 9.2778e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6028 | 1.3217 | 1.0611 | 0.6028 | 1.3217 | 1.0611 | -18.3181 | -130.0723 | 143.3079 | -18.3181 | -130.0723 | 143.3079
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.1864e-08 | 1.0152e-07 | -1.6366e-07 | -5.683e-08 | -8.3092e-08 | 1.302e-07 | 7.8551e-08 | -2.1021e-07 | -9.1315e-08 | -6.3501e-08 | 1.6736e-07 | 7.4515e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6028 | 1.3217 | 1.0611 | 0.6028 | 1.3217 | 1.0611 | -18.3181 | -130.0723 | 143.3079 | -18.3181 | -130.0723 | 143.3079
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3118e-08 | 6.0914e-08 | -9.8197e-08 | -2.8085e-08 | -4.2482e-08 | 6.4731e-08 | 4.7131e-08 | -1.2612e-07 | -5.4789e-08 | -3.208e-08 | 8.3278e-08 | 3.7989e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6028 | 1.3217 | 1.0611 | 0.6028 | 1.3217 | 1.0611 | -18.3181 | -130.0723 | 143.3079 | -18.3181 | -130.0723 | 143.3079
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4373e-08 | 2.0305e-08 | -3.2732e-08 | 6.6101e-10 | -1.8724e-09 | -7.3394e-10 | 1.571e-08 | -4.2042e-08 | -1.8263e-08 | -6.5993e-10 | -8.052e-10 | 1.4625e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6028 | 1.3217 | 1.0611 | 0.6028 | 1.3217 | 1.0611 | -18.3181 | -130.0723 | 143.3079 | -18.3181 | -130.0723 | 143.3079
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8746e-08 | 4.061e-08 | -6.5465e-08 | -1.3712e-08 | -2.2177e-08 | 3.1998e-08 | 3.142e-08 | -8.4083e-08 | -3.6526e-08 | -1.637e-08 | 4.1236e-08 | 1.9726e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6028 | 1.3217 | 1.0611 | 0.6028 | 1.3217 | 1.0611 | -18.3181 | -130.0723 | 143.3079 | -18.3181 | -130.0723 | 143.3079
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4373e-08 | 2.0305e-08 | -3.2732e-08 | 6.6101e-10 | -1.8724e-09 | -7.3394e-10 | 1.571e-08 | -4.2042e-08 | -1.8263e-08 | -6.5993e-10 | -8.052e-10 | 1.4625e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6028 | 1.3217 | 1.0611 | 0.6028 | 1.3217 | 1.0611 | -18.3181 | -130.0723 | 143.3079 | -18.3181 | -130.0723 | 143.3079
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4373e-08 | 2.0305e-08 | -3.2732e-08 | 6.6101e-10 | -1.8724e-09 | -7.3394e-10 | 1.571e-08 | -4.2042e-08 | -1.8263e-08 | -6.5993e-10 | -8.052e-10 | 1.4625e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6028 | 1.3217 | 1.0611 | 0.6028 | 1.3217 | 1.0611 | -18.3181 | -130.0723 | 143.3079 | -18.3181 | -130.0723 | 143.3079
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4373e-08 | 2.0305e-08 | -3.2732e-08 | 6.6101e-10 | -1.8724e-09 | -7.3394e-10 | 1.571e-08 | -4.2042e-08 | -1.8263e-08 | -6.5993e-10 | -8.052e-10 | 1.4625e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6028 | 1.3217 | 1.0611 | 0.6028 | 1.3217 | 1.0611 | -18.3181 | -130.0723 | 143.3079 | -18.3181 | -130.0723 | 143.3079
Line1_1_3 | 1.2236e-06 | 1.2237e-06 | 1.2237e-06 | 1.071e-06 | 1.071e-06 | 1.071e-06 | 2.8259e-07 | 2.8259e-07 | 2.8259e-07 | 2.4734e-07 | 2.4734e-07 | 2.4734e-07 | 1.1498e-07 | 1.6244e-07 | -2.6186e-07 | -9.9949e-08 | -1.4401e-07 | 2.2839e-07 | 1.2568e-07 | -3.3633e-07 | -1.461e-07 | -1.1063e-07 | 2.9349e-07 | 1.293e-07 | -65.8636 | -65.8515 | -65.8515 | 113.7778 | 113.7916 | 113.7916 | 0.6028 | 1.3217 | 1.0611 | 0.6028 | 1.3217 | 1.0611 | -18.3181 | -130.0723 | 143.3079 | -18.3181 | -130.0723 | 143.3079
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8746e-08 | 4.061e-08 | -6.5465e-08 | -1.3712e-08 | -2.2177e-08 | 3.1998e-08 | 3.142e-08 | -8.4083e-08 | -3.6526e-08 | -1.637e-08 | 4.1236e-08 | 1.9725e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6028 | 1.3217 | 1.0611 | 0.6028 | 1.3217 | 1.0611 | -18.3181 | -130.0723 | 143.3079 | -18.3181 | -130.0723 | 143.3079
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8746e-08 | 4.061e-08 | -6.5465e-08 | -1.3712e-08 | -2.2177e-08 | 3.1998e-08 | 3.142e-08 | -8.4083e-08 | -3.6526e-08 | -1.637e-08 | 4.1236e-08 | 1.9725e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6028 | 1.3217 | 1.0611 | 0.6028 | 1.3217 | 1.0611 | -18.3181 | -130.0723 | 143.3079 | -18.3181 | -130.0723 | 143.3079
Line4_2_6 | 0.019434 | 0 | 0 | 0.019434 | 0 | 0 | 0.0044881 | 0 | 0 | 0.0044881 | 0 | 0 | 0.0019065 | 1.0217e-07 | -1.6382e-07 | -0.0019004 | -8.3706e-08 | 1.3031e-07 | 0.0019072 | -2.1045e-07 | -9.176e-08 | -0.0019009 | 1.6754e-07 | 7.4878e-08 | -63.3333 | 0 | 0 | 116.6667 | 0 | 0 | 0.60085 | 1.3216 | 1.0607 | 0.59891 | 1.3214 | 1.0604 | -18.3218 | -130.0568 | 143.3009 | -18.3256 | -130.0413 | 143.2938
Line5_6_7 | 0.019434 | 0 | 0 | 0.019434 | 0 | 0 | 0.0044881 | 0 | 0 | 0.004488 | 0 | 0 | 0.0019004 | 8.1836e-08 | -1.3104e-07 | -0.0018944 | -6.3312e-08 | 9.7537e-08 | 0.0019009 | -1.6834e-07 | -7.3418e-08 | -0.0018946 | 1.2544e-07 | 5.6524e-08 | -63.3332 | 0 | 0 | 116.6668 | 0 | 0 | 0.59891 | 1.3214 | 1.0604 | 0.59697 | 1.3213 | 1.06 | -18.3256 | -130.0413 | 143.2938 | -18.3293 | -130.0257 | 143.2868
Line6_7_8 | 0.019434 | 0 | 0 | 0.019434 | 0 | 0 | 0.004488 | 0 | 0 | 0.004488 | 0 | 0 | 0.0018944 | 6.1443e-08 | -9.8265e-08 | -0.0018883 | -4.2861e-08 | 6.4769e-08 | 0.0018946 | -1.2625e-07 | -5.5064e-08 | -0.0018883 | 8.3348e-08 | 3.8158e-08 | -63.3332 | 0 | 0 | 116.6668 | 0 | 0 | 0.59697 | 1.3213 | 1.06 | 0.59502 | 1.3211 | 1.0596 | -18.3293 | -130.0257 | 143.2868 | -18.3331 | -130.0102 | 143.2798
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4176e-08 | 2.0497e-08 | -3.2748e-08 | 6.6927e-10 | -1.8677e-09 | -7.2652e-10 | 1.5582e-08 | -4.2074e-08 | -1.835e-08 | -6.5194e-10 | -7.9991e-10 | 1.4588e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.59502 | 1.3211 | 1.0596 | 0.59502 | 1.3211 | 1.0596 | -18.3331 | -130.0102 | 143.2798 | -18.3331 | -130.0102 | 143.2798
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4176e-08 | 2.0497e-08 | -3.2748e-08 | 6.6927e-10 | -1.8677e-09 | -7.2652e-10 | 1.5582e-08 | -4.2074e-08 | -1.835e-08 | -6.5194e-10 | -7.9991e-10 | 1.4588e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.59502 | 1.3211 | 1.0596 | 0.59502 | 1.3211 | 1.0596 | -18.3331 | -130.0102 | 143.2798 | -18.3331 | -130.0102 | 143.2798
Line9_3_11 | 1.0707e-06 | 1.0707e-06 | 1.0707e-06 | 0 | 0 | 0 | 2.4727e-07 | 2.4727e-07 | 2.4727e-07 | 0 | 0 | 0 | 1.0061e-07 | 1.4213e-07 | -2.2913e-07 | -8.5576e-08 | -1.237e-07 | 1.9566e-07 | 1.0997e-07 | -2.9429e-07 | -1.2784e-07 | -9.4921e-08 | 2.5144e-07 | 1.1104e-07 | -65.8636 | -65.8515 | -65.8515 | 0 | 0 | 0 | 0.6028 | 1.3217 | 1.0611 | 0.6028 | 1.3217 | 1.0611 | -18.3181 | -130.0723 | 143.3079 | -18.3181 | -130.0723 | 143.3079

## LG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.018411 | 0 | 0 | 0.018411 | 0 | 0 | 0.0042519 | 0 | 0 | 0.0042519 | 0 | 0 | 0.0017165 | 1.099e-07 | -1.7645e-07 | -0.0017111 | -9.3379e-08 | 1.4637e-07 | 0.0017174 | -2.2666e-07 | -9.8807e-08 | -0.0017118 | 1.8815e-07 | 8.3667e-08 | -63.3333 | 0 | 0 | 116.6667 | 0 | 0 | 0.57107 | 1.2522 | 1.0053 | 0.56923 | 1.252 | 1.0049 | -18.3181 | -130.0723 | 143.3079 | -18.3218 | -130.0568 | 143.3009
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7398e-08 | 1.0934e-07 | -1.7626e-07 | -6.3905e-08 | -9.2799e-08 | 1.4623e-07 | 8.46e-08 | -2.264e-07 | -9.8347e-08 | -7.1092e-08 | 1.8794e-07 | 8.3269e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0.57107 | 1.2522 | 1.0053 | 0.57107 | 1.2522 | 1.0053 | -18.3181 | -130.0723 | 143.3079 | -18.3181 | -130.0723 | 143.3079
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.4499e-08 | 9.1119e-08 | -1.4689e-07 | -5.1006e-08 | -7.4575e-08 | 1.1685e-07 | 7.05e-08 | -1.8866e-07 | -8.1956e-08 | -5.6992e-08 | 1.5021e-07 | 6.6877e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0.57107 | 1.2522 | 1.0053 | 0.57107 | 1.2522 | 1.0053 | -18.3181 | -130.0723 | 143.3079 | -18.3181 | -130.0723 | 143.3079
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8699e-08 | 5.4671e-08 | -8.8132e-08 | -2.5206e-08 | -3.8128e-08 | 5.8096e-08 | 4.23e-08 | -1.132e-07 | -4.9174e-08 | -2.8792e-08 | 7.4743e-08 | 3.4095e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0.57107 | 1.2522 | 1.0053 | 0.57107 | 1.2522 | 1.0053 | -18.3181 | -130.0723 | 143.3079 | -18.3181 | -130.0723 | 143.3079
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.29e-08 | 1.8224e-08 | -2.9377e-08 | 5.9326e-10 | -1.6805e-09 | -6.5872e-10 | 1.41e-08 | -3.7733e-08 | -1.6391e-08 | -5.9229e-10 | -7.2267e-10 | 1.3126e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.57107 | 1.2522 | 1.0053 | 0.57107 | 1.2522 | 1.0053 | -18.3181 | -130.0723 | 143.3079 | -18.3181 | -130.0723 | 143.3079
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5799e-08 | 3.6447e-08 | -5.8755e-08 | -1.2306e-08 | -1.9904e-08 | 2.8719e-08 | 2.82e-08 | -7.5465e-08 | -3.2782e-08 | -1.4692e-08 | 3.701e-08 | 1.7704e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0.57107 | 1.2522 | 1.0053 | 0.57107 | 1.2522 | 1.0053 | -18.3181 | -130.0723 | 143.3079 | -18.3181 | -130.0723 | 143.3079
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.29e-08 | 1.8224e-08 | -2.9377e-08 | 5.9326e-10 | -1.6805e-09 | -6.5872e-10 | 1.41e-08 | -3.7733e-08 | -1.6391e-08 | -5.9229e-10 | -7.2267e-10 | 1.3126e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.57107 | 1.2522 | 1.0053 | 0.57107 | 1.2522 | 1.0053 | -18.3181 | -130.0723 | 143.3079 | -18.3181 | -130.0723 | 143.3079
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.29e-08 | 1.8224e-08 | -2.9377e-08 | 5.9326e-10 | -1.6805e-09 | -6.5872e-10 | 1.41e-08 | -3.7733e-08 | -1.6391e-08 | -5.9229e-10 | -7.2267e-10 | 1.3126e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.57107 | 1.2522 | 1.0053 | 0.57107 | 1.2522 | 1.0053 | -18.3181 | -130.0723 | 143.3079 | -18.3181 | -130.0723 | 143.3079
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.29e-08 | 1.8224e-08 | -2.9377e-08 | 5.9326e-10 | -1.6805e-09 | -6.5872e-10 | 1.41e-08 | -3.7733e-08 | -1.6391e-08 | -5.9229e-10 | -7.2267e-10 | 1.3126e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.57107 | 1.2522 | 1.0053 | 0.57107 | 1.2522 | 1.0053 | -18.3181 | -130.0723 | 143.3079 | -18.3181 | -130.0723 | 143.3079
Line1_1_3 | 1.1592e-06 | 1.1593e-06 | 1.1593e-06 | 1.0146e-06 | 1.0146e-06 | 1.0146e-06 | 2.6772e-07 | 2.6772e-07 | 2.6772e-07 | 2.3432e-07 | 2.3432e-07 | 2.3432e-07 | 1.032e-07 | 1.4579e-07 | -2.3502e-07 | -8.9705e-08 | -1.2925e-07 | 2.0498e-07 | 1.128e-07 | -3.0186e-07 | -1.3113e-07 | -9.9292e-08 | 2.6341e-07 | 1.1605e-07 | -65.8636 | -65.8515 | -65.8515 | 113.7778 | 113.7916 | 113.7916 | 0.57107 | 1.2522 | 1.0053 | 0.57107 | 1.2522 | 1.0053 | -18.3181 | -130.0723 | 143.3079 | -18.3181 | -130.0723 | 143.3079
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5799e-08 | 3.6447e-08 | -5.8755e-08 | -1.2306e-08 | -1.9904e-08 | 2.8719e-08 | 2.82e-08 | -7.5465e-08 | -3.2782e-08 | -1.4692e-08 | 3.701e-08 | 1.7704e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0.57107 | 1.2522 | 1.0053 | 0.57107 | 1.2522 | 1.0053 | -18.3181 | -130.0723 | 143.3079 | -18.3181 | -130.0723 | 143.3079
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5799e-08 | 3.6447e-08 | -5.8755e-08 | -1.2306e-08 | -1.9904e-08 | 2.8719e-08 | 2.82e-08 | -7.5465e-08 | -3.2782e-08 | -1.4692e-08 | 3.701e-08 | 1.7704e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0.57107 | 1.2522 | 1.0053 | 0.57107 | 1.2522 | 1.0053 | -18.3181 | -130.0723 | 143.3079 | -18.3181 | -130.0723 | 143.3079
Line4_2_6 | 0.018411 | 0 | 0 | 0.018411 | 0 | 0 | 0.0042519 | 0 | 0 | 0.0042519 | 0 | 0 | 0.0017111 | 9.17e-08 | -1.4703e-07 | -0.0017056 | -7.5127e-08 | 1.1695e-07 | 0.0017118 | -1.8888e-07 | -8.2355e-08 | -0.0017061 | 1.5037e-07 | 6.7204e-08 | -63.3333 | 0 | 0 | 116.6667 | 0 | 0 | 0.56923 | 1.252 | 1.0049 | 0.56739 | 1.2519 | 1.0046 | -18.3218 | -130.0568 | 143.3009 | -18.3256 | -130.0413 | 143.2938
Line5_6_7 | 0.018411 | 0 | 0 | 0.018411 | 0 | 0 | 0.0042519 | 0 | 0 | 0.0042518 | 0 | 0 | 0.0017056 | 7.3448e-08 | -1.1761e-07 | -0.0017002 | -5.6823e-08 | 8.754e-08 | 0.0017061 | -1.5109e-07 | -6.5893e-08 | -0.0017004 | 1.1259e-07 | 5.0731e-08 | -63.3332 | 0 | 0 | 116.6668 | 0 | 0 | 0.56739 | 1.2519 | 1.0046 | 0.56555 | 1.2517 | 1.0042 | -18.3256 | -130.0413 | 143.2938 | -18.3293 | -130.0257 | 143.2868
Line6_7_8 | 0.018411 | 0 | 0 | 0.018411 | 0 | 0 | 0.0042518 | 0 | 0 | 0.0042518 | 0 | 0 | 0.0017002 | 5.5146e-08 | -8.8194e-08 | -0.0016948 | -3.8468e-08 | 5.8131e-08 | 0.0017004 | -1.1331e-07 | -4.9421e-08 | -0.0016948 | 7.4806e-08 | 3.4247e-08 | -63.3332 | 0 | 0 | 116.6668 | 0 | 0 | 0.56555 | 1.2517 | 1.0042 | 0.5637 | 1.2516 | 1.0039 | -18.3293 | -130.0257 | 143.2868 | -18.3331 | -130.0102 | 143.2798
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2723e-08 | 1.8396e-08 | -2.9391e-08 | 6.0068e-10 | -1.6763e-09 | -6.5205e-10 | 1.3985e-08 | -3.7762e-08 | -1.6469e-08 | -5.8512e-10 | -7.1793e-10 | 1.3093e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5637 | 1.2516 | 1.0039 | 0.5637 | 1.2516 | 1.0039 | -18.3331 | -130.0102 | 143.2798 | -18.3331 | -130.0102 | 143.2798
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2723e-08 | 1.8396e-08 | -2.9391e-08 | 6.0068e-10 | -1.6763e-09 | -6.5205e-10 | 1.3985e-08 | -3.7762e-08 | -1.6469e-08 | -5.8512e-10 | -7.1793e-10 | 1.3093e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5637 | 1.2516 | 1.0039 | 0.5637 | 1.2516 | 1.0039 | -18.3331 | -130.0102 | 143.2798 | -18.3331 | -130.0102 | 143.2798
Line9_3_11 | 1.0143e-06 | 1.0143e-06 | 1.0143e-06 | 0 | 0 | 0 | 2.3425e-07 | 2.3425e-07 | 2.3425e-07 | 0 | 0 | 0 | 9.0298e-08 | 1.2757e-07 | -2.0564e-07 | -7.6805e-08 | -1.1102e-07 | 1.7561e-07 | 9.87e-08 | -2.6413e-07 | -1.1474e-07 | -8.5192e-08 | 2.2567e-07 | 9.966e-08 | -65.8636 | -65.8515 | -65.8515 | 0 | 0 | 0 | 0.57107 | 1.2522 | 1.0053 | 0.57107 | 1.2522 | 1.0053 | -18.3181 | -130.0723 | 143.3079 | -18.3181 | -130.0723 | 143.3079

## LLG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 1.139e-06 | 1.8806 | 1.8896 | 0 | 1.8806 | 1.8896 | 2.6303e-07 | 0.4343 | 0.43638 | 0 | 0.4343 | 0.43638 | 1.7607e-08 | 0.14101 | 0.14327 | -1.7751e-08 | -0.10576 | -0.10745 | -4.1285e-07 | 0.28343 | 0.28513 | 3.4407e-07 | -0.21257 | -0.21385 | 87.6119 | -158.2231 | 22.4557 | 0 | 21.777 | -157.5443 | 1.571 | 0.72892 | 0.73124 | 1.5707 | 0.54669 | 0.54843 | 0.053953 | -94.6745 | 85.778 | 0.060264 | -94.6745 | 85.778
Line10_11_12 | 1.1369e-06 | 1.1539e-06 | 1.1198e-06 | 0 | 0 | 0 | 2.6254e-07 | 2.6648e-07 | 2.5861e-07 | 0 | 0 | 0 | 1.7278e-08 | -1.9404e-07 | 1.8904e-07 | -1.74e-08 | 1.6229e-07 | -1.5716e-07 | -4.121e-07 | 8.8948e-09 | -5.139e-09 | 3.4342e-07 | -6.2119e-09 | 2.6992e-09 | 87.6531 | 87.9501 | 87.3352 | 0 | 0 | 0 | 1.571 | 0.72892 | 0.73124 | 1.571 | 0.72892 | 0.73124 | 0.053951 | -94.6745 | 85.778 | 0.05395 | -94.6745 | 85.778
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4399e-08 | -1.617e-07 | 1.5753e-07 | -1.452e-08 | 1.2995e-07 | -1.2566e-07 | -3.4341e-07 | 7.4123e-09 | -4.2825e-09 | 2.7474e-07 | -4.7294e-09 | 1.8427e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.571 | 0.72892 | 0.73124 | 1.571 | 0.72892 | 0.73124 | 0.05395 | -94.6745 | 85.778 | 0.053949 | -94.6745 | 85.7779
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.6392e-09 | -9.7021e-08 | 9.4518e-08 | -8.7607e-09 | 6.5269e-08 | -6.2645e-08 | -2.0605e-07 | 4.4474e-09 | -2.5695e-09 | 1.3737e-07 | -1.7645e-09 | 1.297e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.571 | 0.72892 | 0.73124 | 1.571 | 0.72892 | 0.73124 | 0.053949 | -94.6745 | 85.7779 | 0.053949 | -94.6745 | 85.7779
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8797e-09 | -3.234e-08 | 3.1506e-08 | -3.0012e-09 | 5.8844e-10 | 3.6723e-10 | -6.8683e-08 | 1.4825e-09 | -8.5651e-10 | 5.695e-12 | 1.2004e-09 | -1.5833e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.571 | 0.72892 | 0.73124 | 1.571 | 0.72892 | 0.73124 | 0.053949 | -94.6745 | 85.7779 | 0.053949 | -94.6745 | 85.7779
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.7595e-09 | -6.4681e-08 | 6.3012e-08 | -5.8809e-09 | 3.2929e-08 | -3.1139e-08 | -1.3737e-07 | 2.9649e-09 | -1.713e-09 | 6.8689e-08 | -2.8202e-10 | -7.2681e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.571 | 0.72892 | 0.73124 | 1.571 | 0.72892 | 0.73124 | 0.053949 | -94.6745 | 85.7779 | 0.053948 | -94.6745 | 85.7779
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8797e-09 | -3.234e-08 | 3.1506e-08 | -3.0012e-09 | 5.8844e-10 | 3.6723e-10 | -6.8683e-08 | 1.4825e-09 | -8.5651e-10 | 5.6962e-12 | 1.2004e-09 | -1.5833e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.571 | 0.72892 | 0.73124 | 1.571 | 0.72892 | 0.73124 | 0.053948 | -94.6745 | 85.7779 | 0.053948 | -94.6745 | 85.7779
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8797e-09 | -3.234e-08 | 3.1506e-08 | -3.0012e-09 | 5.8844e-10 | 3.6723e-10 | -6.8683e-08 | 1.4825e-09 | -8.5651e-10 | 5.6965e-12 | 1.2004e-09 | -1.5833e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.571 | 0.72892 | 0.73124 | 1.571 | 0.72892 | 0.73124 | 0.053953 | -94.6745 | 85.778 | 0.053953 | -94.6745 | 85.778
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8797e-09 | -3.234e-08 | 3.1506e-08 | -3.0012e-09 | 5.8844e-10 | 3.6723e-10 | -6.8683e-08 | 1.4825e-09 | -8.5651e-10 | 5.6965e-12 | 1.2004e-09 | -1.5833e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.571 | 0.72892 | 0.73124 | 1.571 | 0.72892 | 0.73124 | 0.053953 | -94.6745 | 85.778 | 0.053953 | -94.6745 | 85.778
Line1_1_3 | 1.5158e-06 | 1.5385e-06 | 1.4931e-06 | 1.3267e-06 | 1.3494e-06 | 1.3041e-06 | 3.5006e-07 | 3.5531e-07 | 3.4481e-07 | 3.0639e-07 | 3.1163e-07 | 3.0116e-07 | 2.3038e-08 | -2.5872e-07 | 2.5205e-07 | -2.3159e-08 | 2.2697e-07 | -2.2018e-07 | -5.4946e-07 | 1.186e-08 | -6.852e-09 | 4.8079e-07 | -9.1768e-09 | 4.4122e-09 | 87.6531 | 87.9501 | 87.3352 | -92.7038 | -92.3592 | -93.074 | 1.571 | 0.72892 | 0.73124 | 1.571 | 0.72892 | 0.73124 | 0.053953 | -94.6745 | 85.778 | 0.053952 | -94.6745 | 85.778
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.7595e-09 | -6.4681e-08 | 6.3012e-08 | -5.8809e-09 | 3.2929e-08 | -3.1139e-08 | -1.3737e-07 | 2.9649e-09 | -1.713e-09 | 6.8689e-08 | -2.8203e-10 | -7.2681e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.571 | 0.72892 | 0.73124 | 1.571 | 0.72892 | 0.73124 | 0.053953 | -94.6745 | 85.778 | 0.053953 | -94.6745 | 85.778
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.7595e-09 | -6.4681e-08 | 6.3012e-08 | -5.8809e-09 | 3.2929e-08 | -3.1139e-08 | -1.3737e-07 | 2.9649e-09 | -1.713e-09 | 6.8689e-08 | -2.8203e-10 | -7.2681e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.571 | 0.72892 | 0.73124 | 1.571 | 0.72892 | 0.73124 | 0.053953 | -94.6745 | 85.778 | 0.053953 | -94.6745 | 85.778
Line4_2_6 | 0 | 1.8806 | 1.8896 | 0 | 1.8806 | 1.8896 | 0 | 0.4343 | 0.43638 | 0 | 0.4343 | 0.43638 | 1.4752e-08 | 0.10576 | 0.10745 | -1.4859e-08 | -0.070507 | -0.071633 | -3.4406e-07 | 0.21257 | 0.21385 | 2.7527e-07 | -0.14171 | -0.14256 | 0 | -158.223 | 22.4557 | 0 | 21.777 | -157.5443 | 1.5707 | 0.54669 | 0.54843 | 1.5703 | 0.36446 | 0.36562 | 0.060264 | -94.6745 | 85.778 | 0.066578 | -94.6745 | 85.778
Line5_6_7 | 0 | 1.8806 | 1.8896 | 0 | 1.8806 | 1.8896 | 0 | 0.4343 | 0.43638 | 0 | 0.4343 | 0.43638 | 1.1863e-08 | 0.070507 | 0.071633 | -1.1933e-08 | -0.035253 | -0.035817 | -2.7526e-07 | 0.14171 | 0.14256 | 2.0645e-07 | -0.070857 | -0.071282 | 0 | -158.223 | 22.4557 | 0 | 21.777 | -157.5443 | 1.5703 | 0.36446 | 0.36562 | 1.57 | 0.18223 | 0.18281 | 0.066578 | -94.6745 | 85.778 | 0.072895 | -94.6745 | 85.778
Line6_7_8 | 0 | 1.8806 | 1.8896 | 0 | 1.8806 | 1.8896 | 0 | 0.4343 | 0.43638 | 0 | 0.4343 | 0.43638 | 8.9394e-09 | 0.035253 | 0.035817 | -8.9716e-09 | 4.224e-13 | -3.5355e-13 | -2.0645e-07 | 0.070857 | 0.071282 | 1.3762e-07 | 2.8256e-13 | -2.8883e-13 | 0 | -158.223 | 22.4557 | 0 | 21.777 | -157.5443 | 1.57 | 0.18223 | 0.18281 | 1.5696 | 0 | 0 | 0.072895 | -94.6745 | 85.778 | 0.079214 | 0 | 0
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9905e-09 | 4.6749e-20 | 3.8229e-20 | -2.9905e-09 | 1.4513e-19 | -1.1111e-17 | -6.8808e-08 | -2.9416e-20 | -1.8367e-20 | 8.3547e-12 | 2.3119e-17 | -5.5022e-18 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5696 | 0 | 0 | 1.5696 | 0 | 0 | 0.079214 | 0 | 0 | 0.079214 | 0 | 0
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9905e-09 | 4.6749e-20 | 3.8229e-20 | -2.9905e-09 | 1.4513e-19 | -1.1111e-17 | -6.8808e-08 | -2.9416e-20 | -1.8367e-20 | 8.355e-12 | 2.3119e-17 | -5.5022e-18 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5696 | 0 | 0 | 1.5696 | 0 | 0 | 0.079214 | 0 | 0 | 0.079214 | 0 | 0
Line9_3_11 | 1.3263e-06 | 1.3462e-06 | 1.3064e-06 | 1.1372e-06 | 1.1571e-06 | 1.1174e-06 | 3.063e-07 | 3.109e-07 | 3.0171e-07 | 2.6264e-07 | 2.6722e-07 | 2.5806e-07 | 2.0158e-08 | -2.2638e-07 | 2.2054e-07 | -2.028e-08 | 1.9463e-07 | -1.8867e-07 | -4.8078e-07 | 1.0377e-08 | -5.9955e-09 | 4.121e-07 | -7.6943e-09 | 3.5557e-09 | 87.6531 | 87.9501 | 87.3352 | -92.7633 | -92.4106 | -93.1424 | 1.571 | 0.72892 | 0.73124 | 1.571 | 0.72892 | 0.73124 | 0.053952 | -94.6745 | 85.778 | 0.053951 | -94.6745 | 85.778

## LLG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 1.1931e-06 | 1.9517 | 1.9611 | 0 | 1.9517 | 1.9611 | 2.7555e-07 | 0.45073 | 0.45289 | 0 | 0.45073 | 0.45289 | 1.9321e-08 | 0.15188 | 0.15432 | -1.9479e-08 | -0.11391 | -0.11574 | -4.5307e-07 | 0.30528 | 0.30711 | 3.7759e-07 | -0.22896 | -0.23033 | 87.6123 | -158.3937 | 22.2922 | 0 | 21.6063 | -157.7078 | 1.6458 | 0.75649 | 0.75891 | 1.6454 | 0.56737 | 0.56918 | 0.054117 | -94.844 | 85.6133 | 0.060428 | -94.844 | 85.6133
Line10_11_12 | 1.1909e-06 | 1.2095e-06 | 1.1724e-06 | 0 | 1.0114e-06 | 0 | 2.7504e-07 | 2.7932e-07 | 2.7076e-07 | 0 | 2.3357e-07 | 0 | 1.896e-08 | -2.1105e-07 | 2.0539e-07 | -1.9094e-08 | 1.7654e-07 | -1.7074e-07 | -4.5225e-07 | 1.0332e-08 | -6.1415e-09 | 3.7688e-07 | -7.3132e-09 | 3.3892e-09 | 87.6534 | 87.9587 | 87.326 | 0 | -92.4719 | 0 | 1.6458 | 0.75649 | 0.75891 | 1.6458 | 0.75649 | 0.75891 | 0.054115 | -94.844 | 85.6132 | 0.054114 | -94.844 | 85.6132
Line11_12_13 | 0 | 1.0079e-06 | 0 | 0 | 0 | 0 | 0 | 2.3277e-07 | 0 | 0 | 0 | 0 | 1.58e-08 | -1.7588e-07 | 1.7116e-07 | -1.5934e-08 | 1.4137e-07 | -1.3651e-07 | -3.7687e-07 | 8.6102e-09 | -5.1179e-09 | 3.015e-07 | -5.5912e-09 | 2.3656e-09 | 0 | 87.9587 | 0 | 0 | 0 | 0 | 1.6458 | 0.75649 | 0.75891 | 1.6458 | 0.75649 | 0.75891 | 0.054114 | -94.844 | 85.6132 | 0.054113 | -94.844 | 85.6132
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.4802e-09 | -1.0553e-07 | 1.0269e-07 | -9.6135e-09 | 7.1014e-08 | -6.8048e-08 | -2.2612e-07 | 5.1661e-09 | -3.0707e-09 | 1.5076e-07 | -2.1471e-09 | 3.1842e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6458 | 0.75649 | 0.75891 | 1.6458 | 0.75649 | 0.75891 | 0.054113 | -94.844 | 85.6132 | 0.054113 | -94.844 | 85.6132
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1601e-09 | -3.5175e-08 | 3.4231e-08 | -3.2933e-09 | 6.6343e-10 | 4.1423e-10 | -7.5374e-08 | 1.722e-09 | -1.0236e-09 | 6.2702e-12 | 1.297e-09 | -1.7287e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6458 | 0.75649 | 0.75891 | 1.6458 | 0.75649 | 0.75891 | 0.054113 | -94.844 | 85.6132 | 0.054113 | -94.844 | 85.6132
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.3201e-09 | -7.0351e-08 | 6.8462e-08 | -6.4534e-09 | 3.5839e-08 | -3.3817e-08 | -1.5075e-07 | 3.4441e-09 | -2.0472e-09 | 7.5381e-08 | -4.2504e-10 | -7.0516e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6458 | 0.75649 | 0.75891 | 1.6458 | 0.75649 | 0.75891 | 0.054113 | -94.844 | 85.6132 | 0.054113 | -94.844 | 85.6132
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1601e-09 | -3.5175e-08 | 3.4231e-08 | -3.2933e-09 | 6.6343e-10 | 4.1423e-10 | -7.5374e-08 | 1.722e-09 | -1.0236e-09 | 6.2694e-12 | 1.297e-09 | -1.7287e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6458 | 0.75649 | 0.75891 | 1.6458 | 0.75649 | 0.75891 | 0.054113 | -94.844 | 85.6132 | 0.054112 | -94.844 | 85.6132
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1601e-09 | -3.5175e-08 | 3.4231e-08 | -3.2933e-09 | 6.6343e-10 | 4.1423e-10 | -7.5374e-08 | 1.7221e-09 | -1.0236e-09 | 6.2712e-12 | 1.297e-09 | -1.7287e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6458 | 0.75649 | 0.75891 | 1.6458 | 0.75649 | 0.75891 | 0.054117 | -94.844 | 85.6133 | 0.054117 | -94.844 | 85.6133
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1601e-09 | -3.5175e-08 | 3.4231e-08 | -3.2933e-09 | 6.6343e-10 | 4.1423e-10 | -7.5374e-08 | 1.7221e-09 | -1.0236e-09 | 6.2712e-12 | 1.297e-09 | -1.7287e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6458 | 0.75649 | 0.75891 | 1.6458 | 0.75649 | 0.75891 | 0.054117 | -94.844 | 85.6133 | 0.054117 | -94.844 | 85.6133
Line1_1_3 | 1.5879e-06 | 1.6127e-06 | 1.5632e-06 | 1.3898e-06 | 1.4145e-06 | 1.3652e-06 | 3.6672e-07 | 3.7243e-07 | 3.6101e-07 | 3.2097e-07 | 3.2667e-07 | 3.1528e-07 | 2.5281e-08 | -2.814e-07 | 2.7385e-07 | -2.5414e-08 | 2.4689e-07 | -2.392e-07 | -6.03e-07 | 1.3776e-08 | -8.1886e-09 | 5.2763e-07 | -1.0757e-08 | 5.4363e-09 | 87.6534 | 87.9587 | 87.326 | -92.7035 | -92.3491 | -93.0848 | 1.6458 | 0.75649 | 0.75891 | 1.6458 | 0.75649 | 0.75891 | 0.054117 | -94.844 | 85.6133 | 0.054116 | -94.844 | 85.6133
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.3201e-09 | -7.0351e-08 | 6.8462e-08 | -6.4534e-09 | 3.5839e-08 | -3.3817e-08 | -1.5075e-07 | 3.4441e-09 | -2.0472e-09 | 7.5381e-08 | -4.2506e-10 | -7.0516e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6458 | 0.75649 | 0.75891 | 1.6458 | 0.75649 | 0.75891 | 0.054117 | -94.844 | 85.6133 | 0.054117 | -94.844 | 85.6133
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.3201e-09 | -7.0351e-08 | 6.8462e-08 | -6.4534e-09 | 3.5839e-08 | -3.3817e-08 | -1.5075e-07 | 3.4441e-09 | -2.0472e-09 | 7.5381e-08 | -4.2506e-10 | -7.0516e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6458 | 0.75649 | 0.75891 | 1.6458 | 0.75649 | 0.75891 | 0.054117 | -94.844 | 85.6133 | 0.054117 | -94.844 | 85.6133
Line4_2_6 | 0 | 1.9517 | 1.9611 | 0 | 1.9517 | 1.9611 | 0 | 0.45073 | 0.45289 | 0 | 0.45073 | 0.45289 | 1.6188e-08 | 0.11391 | 0.11574 | -1.6305e-08 | -0.075938 | -0.077159 | -3.7758e-07 | 0.22896 | 0.23033 | 3.0209e-07 | -0.15264 | -0.15355 | 0 | -158.3937 | 22.2922 | 0 | 21.6063 | -157.7078 | 1.6454 | 0.56737 | 0.56918 | 1.645 | 0.37825 | 0.37945 | 0.060428 | -94.844 | 85.6133 | 0.066741 | -94.844 | 85.6133
Line5_6_7 | 0 | 1.9517 | 1.9611 | 0 | 1.9517 | 1.9611 | 0 | 0.45073 | 0.45289 | 0 | 0.45073 | 0.45289 | 1.3018e-08 | 0.075938 | 0.077159 | -1.3094e-08 | -0.037969 | -0.03858 | -3.0208e-07 | 0.15264 | 0.15355 | 2.2657e-07 | -0.07632 | -0.076777 | 0 | -158.3937 | 22.2922 | 0 | 21.6063 | -157.7078 | 1.645 | 0.37825 | 0.37945 | 1.6447 | 0.18912 | 0.18973 | 0.066741 | -94.844 | 85.6133 | 0.073058 | -94.844 | 85.6133
Line6_7_8 | 0 | 1.9517 | 1.9611 | 0 | 1.9517 | 1.9611 | 0 | 0.45073 | 0.45289 | 0 | 0.45073 | 0.45289 | 9.8096e-09 | 0.037969 | 0.03858 | -9.8449e-09 | 5.452e-13 | -4.5769e-13 | -2.2656e-07 | 0.07632 | 0.076777 | 1.5103e-07 | 7.3315e-14 | -9.6408e-14 | 0 | -158.3937 | 22.2922 | 0 | 21.6063 | -157.7078 | 1.6447 | 0.18912 | 0.18973 | 1.6443 | 0 | 0 | 0.073058 | -94.844 | 85.6133 | 0.079377 | 0 | 0
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2816e-09 | 3.1559e-20 | 2.6288e-20 | -3.2816e-09 | 1.6003e-19 | -1.2196e-17 | -7.5511e-08 | -5.1442e-20 | -3.5111e-20 | 9.1888e-12 | 2.5374e-17 | -6.0387e-18 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6443 | 0 | 0 | 1.6443 | 0 | 0 | 0.079377 | 0 | 0 | 0.079377 | 0 | 0
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2816e-09 | 3.1559e-20 | 2.6288e-20 | -3.2816e-09 | 1.6003e-19 | -1.2196e-17 | -7.5511e-08 | -5.1442e-20 | -3.5111e-20 | 9.1895e-12 | 2.5374e-17 | -6.0387e-18 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6443 | 0 | 0 | 1.6443 | 0 | 0 | 0.079377 | 0 | 0 | 0.079377 | 0 | 0
Line9_3_11 | 1.3894e-06 | 1.4111e-06 | 1.3678e-06 | 1.1914e-06 | 1.213e-06 | 1.1698e-06 | 3.2088e-07 | 3.2588e-07 | 3.1588e-07 | 2.7513e-07 | 2.8012e-07 | 2.7015e-07 | 2.212e-08 | -2.4623e-07 | 2.3962e-07 | -2.2254e-08 | 2.1172e-07 | -2.0497e-07 | -5.2762e-07 | 1.2054e-08 | -7.165e-09 | 4.5225e-07 | -9.0353e-09 | 4.4127e-09 | 87.6534 | 87.9587 | 87.326 | -92.7629 | -92.4003 | -93.1535 | 1.6458 | 0.75649 | 0.75891 | 1.6458 | 0.75649 | 0.75891 | 0.054116 | -94.844 | 85.6133 | 0.054115 | -94.844 | 85.6132

## LLG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0.026794 | 0.033352 | 0 | 0.026794 | 0.033352 | 0 | 0.0061877 | 0.0077024 | 0 | 0.0061877 | 0.0077024 | -4.55e-08 | 0.0036133 | 0.0056097 | 3.6288e-08 | -0.0036074 | -0.0055977 | -2.2339e-07 | 0.0036508 | 0.0056439 | 1.8659e-07 | -0.0036355 | -0.0056234 | 0 | -150.1519 | 56.5006 | 0 | 29.8483 | -123.4995 | 1.3673 | 0.83012 | 1.0331 | 1.3671 | 0.82769 | 1.0301 | 4.3835 | -104.8565 | 101.6748 | 4.3857 | -104.9293 | 101.6314
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.5576e-08 | -1.1872e-07 | 1.7141e-07 | 3.6374e-08 | 9.9489e-08 | -1.4298e-07 | -2.2295e-07 | 7.076e-08 | -1.273e-08 | 1.8619e-07 | -5.8132e-08 | 9.3576e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3673 | 0.83012 | 1.0331 | 1.3673 | 0.83012 | 1.0331 | 4.3835 | -104.8565 | 101.6748 | 4.3835 | -104.8564 | 101.6748
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.798e-08 | -9.8931e-08 | 1.4284e-07 | 2.8778e-08 | 7.9703e-08 | -1.1441e-07 | -1.8579e-07 | 5.8967e-08 | -1.0608e-08 | 1.4903e-07 | -4.6339e-08 | 7.236e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3673 | 0.83012 | 1.0331 | 1.3673 | 0.83012 | 1.0331 | 4.3835 | -104.8564 | 101.6748 | 4.3835 | -104.8564 | 101.6748
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.2788e-08 | -5.9359e-08 | 8.5704e-08 | 1.3586e-08 | 4.0131e-08 | -5.7274e-08 | -1.1147e-07 | 3.538e-08 | -6.3649e-09 | 7.4718e-08 | -2.2752e-08 | 2.9927e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3673 | 0.83012 | 1.0331 | 1.3673 | 0.83012 | 1.0331 | 4.3835 | -104.8564 | 101.6748 | 4.3835 | -104.8564 | 101.6748
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.596e-09 | -1.9786e-08 | 2.8568e-08 | -1.6062e-09 | 5.5827e-10 | -1.3777e-10 | -3.7158e-08 | 1.1793e-08 | -2.1216e-09 | 4.0234e-10 | 8.3491e-10 | -1.2506e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3673 | 0.83012 | 1.0331 | 1.3673 | 0.83012 | 1.0331 | 4.3835 | -104.8564 | 101.6748 | 4.3835 | -104.8564 | 101.6748
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.5192e-08 | -3.9572e-08 | 5.7136e-08 | 5.9899e-09 | 2.0344e-08 | -2.8706e-08 | -7.4316e-08 | 2.3587e-08 | -4.2433e-09 | 3.756e-08 | -1.0958e-08 | 8.7106e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3673 | 0.83012 | 1.0331 | 1.3673 | 0.83012 | 1.0331 | 4.3835 | -104.8564 | 101.6748 | 4.3835 | -104.8564 | 101.6748
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.596e-09 | -1.9786e-08 | 2.8568e-08 | -1.6062e-09 | 5.5827e-10 | -1.3777e-10 | -3.7158e-08 | 1.1793e-08 | -2.1216e-09 | 4.0234e-10 | 8.3491e-10 | -1.2506e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3673 | 0.83012 | 1.0331 | 1.3673 | 0.83012 | 1.0331 | 4.3835 | -104.8564 | 101.6748 | 4.3835 | -104.8564 | 101.6748
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.5961e-09 | -1.9786e-08 | 2.8568e-08 | -1.6062e-09 | 5.5827e-10 | -1.3777e-10 | -3.7158e-08 | 1.1793e-08 | -2.1216e-09 | 4.0234e-10 | 8.3491e-10 | -1.2506e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3673 | 0.83012 | 1.0331 | 1.3673 | 0.83012 | 1.0331 | 4.3835 | -104.8565 | 101.6748 | 4.3835 | -104.8565 | 101.6748
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.5961e-09 | -1.9786e-08 | 2.8568e-08 | -1.6062e-09 | 5.5827e-10 | -1.3777e-10 | -3.7158e-08 | 1.1793e-08 | -2.1216e-09 | 4.0234e-10 | 8.3491e-10 | -1.2506e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3673 | 0.83012 | 1.0331 | 1.3673 | 0.83012 | 1.0331 | 4.3835 | -104.8565 | 101.6748 | 4.3835 | -104.8565 | 101.6748
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.0768e-08 | -1.5829e-07 | 2.2854e-07 | 5.1566e-08 | 1.3906e-07 | -2.0011e-07 | -2.9726e-07 | 9.4347e-08 | -1.6973e-08 | 2.6051e-07 | -8.1719e-08 | 1.3601e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3673 | 0.83012 | 1.0331 | 1.3673 | 0.83012 | 1.0331 | 4.3835 | -104.8565 | 101.6748 | 4.3835 | -104.8565 | 101.6748
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.5192e-08 | -3.9572e-08 | 5.7136e-08 | 5.9899e-09 | 2.0344e-08 | -2.8706e-08 | -7.4316e-08 | 2.3587e-08 | -4.2433e-09 | 3.756e-08 | -1.0958e-08 | 8.7106e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3673 | 0.83012 | 1.0331 | 1.3673 | 0.83012 | 1.0331 | 4.3835 | -104.8565 | 101.6748 | 4.3835 | -104.8565 | 101.6748
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.5192e-08 | -3.9572e-08 | 5.7136e-08 | 5.9899e-09 | 2.0344e-08 | -2.8706e-08 | -7.4316e-08 | 2.3587e-08 | -4.2433e-09 | 3.756e-08 | -1.0958e-08 | 8.7106e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3673 | 0.83012 | 1.0331 | 1.3673 | 0.83012 | 1.0331 | 4.3835 | -104.8565 | 101.6748 | 4.3835 | -104.8565 | 101.6748
Line4_2_6 | 0 | 0.026794 | 0.033352 | 0 | 0.026794 | 0.033352 | 0 | 0.0061877 | 0.0077024 | 0 | 0.0061877 | 0.0077024 | -3.7892e-08 | 0.0036074 | 0.0055977 | 2.8691e-08 | -0.0036014 | -0.0055858 | -1.8619e-07 | 0.0036355 | 0.0056234 | 1.4937e-07 | -0.0036202 | -0.0056028 | 0 | -150.1517 | 56.5005 | 0 | 29.8486 | -123.4997 | 1.3671 | 0.82769 | 1.0301 | 1.3668 | 0.82525 | 1.0272 | 4.3857 | -104.9293 | 101.6314 | 4.3879 | -105.0026 | 101.5877
Line5_6_7 | 0 | 0.026794 | 0.033352 | 0 | 0.026794 | 0.033352 | 0 | 0.0061877 | 0.0077024 | 0 | 0.0061877 | 0.0077024 | -3.0295e-08 | 0.0036014 | 0.0055858 | 2.1106e-08 | -0.0035955 | -0.0055738 | -1.4897e-07 | 0.0036202 | 0.0056028 | 1.1214e-07 | -0.0036049 | -0.0055823 | 0 | -150.1514 | 56.5003 | 0 | 29.8488 | -123.4998 | 1.3668 | 0.82525 | 1.0272 | 1.3666 | 0.82282 | 1.0242 | 4.3879 | -105.0026 | 101.5877 | 4.3902 | -105.0763 | 101.5438
Line6_7_8 | 0 | 0.026794 | 0.033352 | 0 | 0.026794 | 0.033352 | 0 | 0.0061877 | 0.0077024 | 0 | 0.0061877 | 0.0077024 | -2.2707e-08 | 0.0035955 | 0.0055738 | 1.353e-08 | -0.0035895 | -0.0055618 | -1.1174e-07 | 0.0036049 | 0.0055823 | 7.4891e-08 | -0.0035896 | -0.0055618 | 0 | -150.1512 | 56.5002 | 0 | 29.8491 | -123.5 | 1.3666 | 0.82282 | 1.0242 | 1.3663 | 0.82039 | 1.0212 | 4.3902 | -105.0763 | 101.5438 | 4.3924 | -105.1504 | 101.4997
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.5653e-09 | -1.9591e-08 | 2.8266e-08 | -1.6003e-09 | 5.852e-10 | -9.5311e-11 | -3.7244e-08 | 1.1776e-08 | -2.1433e-09 | 4.0288e-10 | 8.0947e-10 | -1.2475e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3663 | 0.82039 | 1.0212 | 1.3663 | 0.82039 | 1.0212 | 4.3924 | -105.1504 | 101.4997 | 4.3924 | -105.1504 | 101.4997
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.5653e-09 | -1.9591e-08 | 2.8266e-08 | -1.6003e-09 | 5.852e-10 | -9.5311e-11 | -3.7244e-08 | 1.1776e-08 | -2.1433e-09 | 4.0288e-10 | 8.0947e-10 | -1.2475e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3663 | 0.82039 | 1.0212 | 1.3663 | 0.82039 | 1.0212 | 4.3924 | -105.1504 | 101.4997 | 4.3924 | -105.1504 | 101.4997
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.3172e-08 | -1.385e-07 | 1.9998e-07 | 4.397e-08 | 1.1928e-07 | -1.7155e-07 | -2.6011e-07 | 8.2554e-08 | -1.4851e-08 | 2.2335e-07 | -6.9926e-08 | 1.1479e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3673 | 0.83012 | 1.0331 | 1.3673 | 0.83012 | 1.0331 | 4.3835 | -104.8565 | 101.6748 | 4.3835 | -104.8565 | 101.6748

## LLG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0.028067 | 0.034936 | 0 | 0.028067 | 0.034936 | 0 | 0.0064818 | 0.0080682 | 0 | 0.0064818 | 0.0080682 | -4.9934e-08 | 0.0039649 | 0.0061551 | 3.9823e-08 | -0.0039584 | -0.006142 | -2.4517e-07 | 0.004006 | 0.0061927 | 2.0478e-07 | -0.0039892 | -0.0061702 | 0 | -150.159 | 56.4965 | 0 | 29.8412 | -123.5037 | 1.4324 | 0.86957 | 1.0822 | 1.4321 | 0.86702 | 1.0791 | 4.3831 | -104.8635 | 101.6706 | 4.3853 | -104.9364 | 101.6272
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.0017e-08 | -1.3027e-07 | 1.8809e-07 | 3.9918e-08 | 1.0917e-07 | -1.5689e-07 | -2.4468e-07 | 7.7668e-08 | -1.3978e-08 | 2.0434e-07 | -6.3807e-08 | 1.0275e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4324 | 0.86957 | 1.0822 | 1.4324 | 0.86957 | 1.0822 | 4.3831 | -104.8635 | 101.6706 | 4.3831 | -104.8635 | 101.6706
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.1681e-08 | -1.0856e-07 | 1.5674e-07 | 3.1582e-08 | 8.7461e-08 | -1.2555e-07 | -2.039e-07 | 6.4723e-08 | -1.1648e-08 | 1.6356e-07 | -5.0863e-08 | 7.9458e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4324 | 0.86957 | 1.0822 | 1.4324 | 0.86957 | 1.0822 | 4.3831 | -104.8635 | 101.6706 | 4.3831 | -104.8635 | 101.6706
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5009e-08 | -6.5136e-08 | 9.4046e-08 | 1.491e-08 | 4.4037e-08 | -6.2848e-08 | -1.2234e-07 | 3.8834e-08 | -6.9888e-09 | 8.2002e-08 | -2.4973e-08 | 3.2866e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4324 | 0.86957 | 1.0822 | 1.4324 | 0.86957 | 1.0822 | 4.3831 | -104.8635 | 101.6706 | 4.3831 | -104.8635 | 101.6706
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.3362e-09 | -2.1712e-08 | 3.1349e-08 | -1.7626e-09 | 6.1303e-10 | -1.5075e-10 | -4.078e-08 | 1.2945e-08 | -2.3296e-09 | 4.4152e-10 | 9.1581e-10 | -1.3726e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4324 | 0.86957 | 1.0822 | 1.4324 | 0.86957 | 1.0822 | 4.3831 | -104.8635 | 101.6706 | 4.3831 | -104.8635 | 101.6706
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.6672e-08 | -4.3424e-08 | 6.2697e-08 | 6.5736e-09 | 2.2325e-08 | -3.1499e-08 | -8.156e-08 | 2.5889e-08 | -4.6592e-09 | 4.1222e-08 | -1.2029e-08 | 9.5696e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4324 | 0.86957 | 1.0822 | 1.4324 | 0.86957 | 1.0822 | 4.3831 | -104.8635 | 101.6706 | 4.3831 | -104.8635 | 101.6706
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.3362e-09 | -2.1712e-08 | 3.1349e-08 | -1.7626e-09 | 6.1303e-10 | -1.5075e-10 | -4.078e-08 | 1.2945e-08 | -2.3296e-09 | 4.4152e-10 | 9.1581e-10 | -1.3726e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4324 | 0.86957 | 1.0822 | 1.4324 | 0.86957 | 1.0822 | 4.3831 | -104.8635 | 101.6706 | 4.3831 | -104.8635 | 101.6706
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.3362e-09 | -2.1712e-08 | 3.1349e-08 | -1.7626e-09 | 6.1303e-10 | -1.5075e-10 | -4.078e-08 | 1.2945e-08 | -2.3296e-09 | 4.4152e-10 | 9.1581e-10 | -1.3726e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4324 | 0.86957 | 1.0822 | 1.4324 | 0.86957 | 1.0822 | 4.3831 | -104.8635 | 101.6706 | 4.3831 | -104.8635 | 101.6706
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.3362e-09 | -2.1712e-08 | 3.1349e-08 | -1.7626e-09 | 6.1303e-10 | -1.5075e-10 | -4.078e-08 | 1.2945e-08 | -2.3296e-09 | 4.4152e-10 | 9.1581e-10 | -1.3726e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4324 | 0.86957 | 1.0822 | 1.4324 | 0.86957 | 1.0822 | 4.3831 | -104.8635 | 101.6706 | 4.3831 | -104.8635 | 101.6706
Line1_1_3 | 1.0066e-06 | 1.007e-06 | 1.0062e-06 | 0 | 0 | 0 | 2.3247e-07 | 2.3256e-07 | 2.3238e-07 | 0 | 0 | 0 | -6.669e-08 | -1.737e-07 | 2.5079e-07 | 5.6591e-08 | 1.526e-07 | -2.1959e-07 | -3.2624e-07 | 1.0356e-07 | -1.8637e-08 | 2.859e-07 | -8.9696e-08 | 1.4935e-08 | 105.9362 | 105.9396 | 105.9206 | 0 | 0 | 0 | 1.4324 | 0.86957 | 1.0822 | 1.4324 | 0.86957 | 1.0822 | 4.3831 | -104.8635 | 101.6706 | 4.3831 | -104.8635 | 101.6706
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.6672e-08 | -4.3424e-08 | 6.2697e-08 | 6.5736e-09 | 2.2325e-08 | -3.1499e-08 | -8.156e-08 | 2.5889e-08 | -4.6592e-09 | 4.1222e-08 | -1.2029e-08 | 9.5696e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4324 | 0.86957 | 1.0822 | 1.4324 | 0.86957 | 1.0822 | 4.3831 | -104.8635 | 101.6706 | 4.3831 | -104.8635 | 101.6706
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.6672e-08 | -4.3424e-08 | 6.2697e-08 | 6.5736e-09 | 2.2325e-08 | -3.1499e-08 | -8.156e-08 | 2.5889e-08 | -4.6592e-09 | 4.1222e-08 | -1.2029e-08 | 9.5696e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4324 | 0.86957 | 1.0822 | 1.4324 | 0.86957 | 1.0822 | 4.3831 | -104.8635 | 101.6706 | 4.3831 | -104.8635 | 101.6706
Line4_2_6 | 0 | 0.028067 | 0.034936 | 0 | 0.028067 | 0.034936 | 0 | 0.0064818 | 0.0080682 | 0 | 0.0064818 | 0.0080682 | -4.1584e-08 | 0.0039584 | 0.006142 | 3.1487e-08 | -0.0039518 | -0.0061289 | -2.0434e-07 | 0.0039892 | 0.0061701 | 1.6393e-07 | -0.0039724 | -0.0061476 | 0 | -150.1588 | 56.4963 | 0 | 29.8415 | -123.5038 | 1.4321 | 0.86702 | 1.0791 | 1.4319 | 0.86447 | 1.0759 | 4.3853 | -104.9364 | 101.6272 | 4.3875 | -105.0097 | 101.5836
Line5_6_7 | 0 | 0.028067 | 0.034936 | 0 | 0.028067 | 0.034936 | 0 | 0.0064818 | 0.0080682 | 0 | 0.0064818 | 0.0080681 | -3.3246e-08 | 0.0039518 | 0.0061289 | 2.3162e-08 | -0.0039453 | -0.0061158 | -1.6349e-07 | 0.0039724 | 0.0061476 | 1.2307e-07 | -0.0039556 | -0.0061251 | 0 | -150.1585 | 56.4962 | 0 | 29.8417 | -123.504 | 1.4319 | 0.86447 | 1.0759 | 1.4316 | 0.86192 | 1.0728 | 4.3875 | -105.0097 | 101.5836 | 4.3898 | -105.0834 | 101.5397
Line6_7_8 | 0 | 0.028067 | 0.034936 | 0 | 0.028067 | 0.034936 | 0 | 0.0064818 | 0.0080681 | 0 | 0.0064818 | 0.0080681 | -2.492e-08 | 0.0039453 | 0.0061158 | 1.4849e-08 | -0.0039387 | -0.0061026 | -1.2263e-07 | 0.0039556 | 0.0061251 | 8.2191e-08 | -0.0039388 | -0.0061026 | 0 | -150.1583 | 56.496 | 0 | 29.842 | -123.5041 | 1.4316 | 0.86192 | 1.0728 | 1.4314 | 0.85937 | 1.0697 | 4.3898 | -105.0834 | 101.5397 | 4.392 | -105.1575 | 101.4956
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.3025e-09 | -2.1497e-08 | 3.1018e-08 | -1.7561e-09 | 6.4257e-10 | -1.0417e-10 | -4.0875e-08 | 1.2926e-08 | -2.3534e-09 | 4.4211e-10 | 8.8789e-10 | -1.3693e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4314 | 0.85937 | 1.0697 | 1.4314 | 0.85937 | 1.0697 | 4.392 | -105.1575 | 101.4956 | 4.392 | -105.1575 | 101.4956
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.3025e-09 | -2.1497e-08 | 3.1018e-08 | -1.7561e-09 | 6.4257e-10 | -1.0417e-10 | -4.0875e-08 | 1.2926e-08 | -2.3534e-09 | 4.4211e-10 | 8.879e-10 | -1.3693e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4314 | 0.85937 | 1.0697 | 1.4314 | 0.85937 | 1.0697 | 4.392 | -105.1575 | 101.4956 | 4.392 | -105.1575 | 101.4956
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.8353e-08 | -1.5198e-07 | 2.1944e-07 | 4.8255e-08 | 1.3089e-07 | -1.8824e-07 | -2.8546e-07 | 9.0612e-08 | -1.6307e-08 | 2.4512e-07 | -7.6752e-08 | 1.2605e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4324 | 0.86957 | 1.0822 | 1.4324 | 0.86957 | 1.0822 | 4.3831 | -104.8635 | 101.6706 | 4.3831 | -104.8635 | 101.6706

## LLG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 1.0305e-06 | 1.4485 | 1.4615 | 0 | 1.4485 | 1.4615 | 2.3799e-07 | 0.33451 | 0.33753 | 0 | 0.33451 | 0.33753 | 1.4136e-08 | 0.16104 | 0.16414 | -1.4366e-08 | -0.12078 | -0.12311 | -3.3797e-07 | 0.16842 | 0.17031 | 2.8167e-07 | -0.12632 | -0.12773 | 87.7053 | -143.2176 | 37.4691 | 0 | 36.7824 | -142.5309 | 1.4213 | 0.6966 | 0.70078 | 1.421 | 0.52245 | 0.52558 | 0.10037 | -96.9331 | 83.5246 | 0.11249 | -96.9331 | 83.5246
Line10_11_12 | 1.0285e-06 | 1.0405e-06 | 1.0166e-06 | 0 | 0 | 0 | 2.3753e-07 | 2.403e-07 | 2.3477e-07 | 0 | 0 | 0 | 1.3593e-08 | -1.6671e-07 | 1.6416e-07 | -1.3784e-08 | 1.3938e-07 | -1.3664e-07 | -3.3734e-07 | 1.5094e-08 | -1.0898e-08 | 2.8112e-07 | -1.1628e-08 | 7.6304e-09 | 87.7929 | 88.2404 | 87.3225 | 0 | 0 | 0 | 1.4213 | 0.6966 | 0.70078 | 1.4213 | 0.6966 | 0.70078 | 0.10036 | -96.9331 | 83.5246 | 0.10036 | -96.9331 | 83.5246
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1328e-08 | -1.3893e-07 | 1.368e-07 | -1.1518e-08 | 1.1159e-07 | -1.0928e-07 | -2.8111e-07 | 1.2579e-08 | -9.0815e-09 | 2.249e-07 | -9.1122e-09 | 5.8141e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4213 | 0.6966 | 0.70078 | 1.4213 | 0.6966 | 0.70078 | 0.10036 | -96.9331 | 83.5246 | 0.10036 | -96.9331 | 83.5246
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7965e-09 | -8.3355e-08 | 8.2082e-08 | -6.9874e-09 | 5.6024e-08 | -5.4559e-08 | -1.6867e-07 | 7.5472e-09 | -5.4489e-09 | 1.1245e-07 | -4.0807e-09 | 2.1815e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4213 | 0.6966 | 0.70078 | 1.4213 | 0.6966 | 0.70078 | 0.10036 | -96.9331 | 83.5246 | 0.10036 | -96.9331 | 83.5246
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2655e-09 | -2.7785e-08 | 2.7361e-08 | -2.4564e-09 | 4.5323e-10 | 1.6221e-10 | -5.6223e-08 | 2.5157e-09 | -1.8163e-09 | 8.6723e-12 | 9.5071e-10 | -1.4511e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4213 | 0.6966 | 0.70078 | 1.4213 | 0.6966 | 0.70078 | 0.10036 | -96.9331 | 83.5246 | 0.10036 | -96.9331 | 83.5246
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.531e-09 | -5.557e-08 | 5.4721e-08 | -4.7219e-09 | 2.8238e-08 | -2.7198e-08 | -1.1245e-07 | 5.0314e-09 | -3.6326e-09 | 5.6232e-08 | -1.565e-09 | 3.6516e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4213 | 0.6966 | 0.70078 | 1.4213 | 0.6966 | 0.70078 | 0.10036 | -96.9331 | 83.5246 | 0.10036 | -96.9331 | 83.5246
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2655e-09 | -2.7785e-08 | 2.7361e-08 | -2.4564e-09 | 4.5323e-10 | 1.6221e-10 | -5.6223e-08 | 2.5157e-09 | -1.8163e-09 | 8.6724e-12 | 9.5071e-10 | -1.4511e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4213 | 0.6966 | 0.70078 | 1.4213 | 0.6966 | 0.70078 | 0.10036 | -96.9331 | 83.5246 | 0.10036 | -96.9331 | 83.5246
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2655e-09 | -2.7785e-08 | 2.7361e-08 | -2.4564e-09 | 4.5323e-10 | 1.6221e-10 | -5.6223e-08 | 2.5157e-09 | -1.8163e-09 | 8.6725e-12 | 9.5071e-10 | -1.4511e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4213 | 0.6966 | 0.70078 | 1.4213 | 0.6966 | 0.70078 | 0.10037 | -96.9331 | 83.5246 | 0.10037 | -96.9331 | 83.5246
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2655e-09 | -2.7785e-08 | 2.7361e-08 | -2.4564e-09 | 4.5323e-10 | 1.6221e-10 | -5.6223e-08 | 2.5157e-09 | -1.8163e-09 | 8.6725e-12 | 9.5071e-10 | -1.4511e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4213 | 0.6966 | 0.70078 | 1.4213 | 0.6966 | 0.70078 | 0.10037 | -96.9331 | 83.5246 | 0.10037 | -96.9331 | 83.5246
Line1_1_3 | 1.3714e-06 | 1.3874e-06 | 1.3555e-06 | 1.2003e-06 | 1.2162e-06 | 1.1845e-06 | 3.1671e-07 | 3.204e-07 | 3.1303e-07 | 2.772e-07 | 2.8088e-07 | 2.7354e-07 | 1.8124e-08 | -2.2228e-07 | 2.1888e-07 | -1.8315e-08 | 1.9495e-07 | -1.9136e-07 | -4.4978e-07 | 2.0126e-08 | -1.453e-08 | 3.9357e-07 | -1.6659e-08 | 1.1263e-08 | 87.7929 | 88.2404 | 87.3225 | -92.564 | -92.0488 | -93.107 | 1.4213 | 0.6966 | 0.70078 | 1.4213 | 0.6966 | 0.70078 | 0.10037 | -96.9331 | 83.5246 | 0.10036 | -96.9331 | 83.5246
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.531e-09 | -5.557e-08 | 5.4721e-08 | -4.7219e-09 | 2.8238e-08 | -2.7198e-08 | -1.1245e-07 | 5.0315e-09 | -3.6326e-09 | 5.6232e-08 | -1.565e-09 | 3.6516e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4213 | 0.6966 | 0.70078 | 1.4213 | 0.6966 | 0.70078 | 0.10037 | -96.9331 | 83.5246 | 0.10037 | -96.9331 | 83.5246
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.531e-09 | -5.557e-08 | 5.4721e-08 | -4.7219e-09 | 2.8238e-08 | -2.7198e-08 | -1.1245e-07 | 5.0315e-09 | -3.6326e-09 | 5.6232e-08 | -1.565e-09 | 3.6516e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4213 | 0.6966 | 0.70078 | 1.4213 | 0.6966 | 0.70078 | 0.10037 | -96.9331 | 83.5246 | 0.10037 | -96.9331 | 83.5246
Line4_2_6 | 0 | 1.4485 | 1.4615 | 0 | 1.4485 | 1.4615 | 0 | 0.33451 | 0.33753 | 0 | 0.33451 | 0.33753 | 1.1911e-08 | 0.12078 | 0.12311 | -1.2082e-08 | -0.080518 | -0.082072 | -2.8166e-07 | 0.12632 | 0.12773 | 2.2535e-07 | -0.084212 | -0.085153 | 0 | -143.2176 | 37.4691 | 0 | 36.7824 | -142.5309 | 1.421 | 0.52245 | 0.52558 | 1.4207 | 0.3483 | 0.35039 | 0.11249 | -96.9331 | 83.5246 | 0.12461 | -96.9331 | 83.5246
Line5_6_7 | 0 | 1.4485 | 1.4615 | 0 | 1.4485 | 1.4615 | 0 | 0.33451 | 0.33753 | 0 | 0.33451 | 0.33753 | 9.6296e-09 | 0.080518 | 0.082072 | -9.7408e-09 | -0.040259 | -0.041036 | -2.2534e-07 | 0.084212 | 0.085153 | 1.6901e-07 | -0.042106 | -0.042576 | 0 | -143.2176 | 37.4691 | 0 | 36.7824 | -142.5309 | 1.4207 | 0.3483 | 0.35039 | 1.4204 | 0.17415 | 0.17519 | 0.12461 | -96.9331 | 83.5246 | 0.13674 | -96.9331 | 83.5246
Line6_7_8 | 0 | 1.4485 | 1.4615 | 0 | 1.4485 | 1.4615 | 0 | 0.33451 | 0.33753 | 0 | 0.33451 | 0.33753 | 7.2909e-09 | 0.040259 | 0.041036 | -7.343e-09 | -1.8732e-14 | 2.4513e-14 | -1.69e-07 | 0.042106 | 0.042576 | 1.1267e-07 | -1.9503e-13 | 1.7748e-13 | 0 | -143.2176 | 37.4691 | 0 | 36.7824 | -142.5309 | 1.4204 | 0.17415 | 0.17519 | 1.4201 | 0 | 0 | 0.13674 | -96.9331 | 83.5246 | 0.14888 | 0 | 0
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4477e-09 | -2.0859e-20 | -1.648e-20 | -2.4477e-09 | 7.0884e-18 | -1.2421e-17 | -5.6327e-08 | -1.3804e-20 | -1.0364e-20 | 1.2853e-11 | 2.2366e-17 | -2.0019e-18 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4201 | 0 | 0 | 1.4201 | 0 | 0 | 0.14888 | 0 | 0 | 0.14888 | 0 | 0
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4477e-09 | -2.0859e-20 | -1.648e-20 | -2.4477e-09 | 7.0884e-18 | -1.2421e-17 | -5.6327e-08 | -1.3804e-20 | -1.0364e-20 | 1.2854e-11 | 2.2366e-17 | -2.0019e-18 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4201 | 0 | 0 | 1.4201 | 0 | 0 | 0.14888 | 0 | 0 | 0.14888 | 0 | 0
Line9_3_11 | 1.2e-06 | 1.214e-06 | 1.186e-06 | 1.0289e-06 | 1.0428e-06 | 1.015e-06 | 2.7712e-07 | 2.8035e-07 | 2.739e-07 | 2.3761e-07 | 2.4083e-07 | 2.3442e-07 | 1.5859e-08 | -1.945e-07 | 1.9152e-07 | -1.6049e-08 | 1.6716e-07 | -1.64e-07 | -3.9356e-07 | 1.761e-08 | -1.2714e-08 | 3.3735e-07 | -1.4144e-08 | 9.4467e-09 | 87.7929 | 88.2404 | 87.3225 | -92.6235 | -92.0969 | -93.1787 | 1.4213 | 0.6966 | 0.70078 | 1.4213 | 0.6966 | 0.70078 | 0.10036 | -96.9331 | 83.5246 | 0.10036 | -96.9331 | 83.5246

## LLG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 1.3722 | 1.3846 | 0 | 1.3722 | 1.3846 | 0 | 0.31691 | 0.31976 | 0 | 0.31691 | 0.31976 | 1.2687e-08 | 0.14453 | 0.14732 | -1.2893e-08 | -0.1084 | -0.11049 | -3.0333e-07 | 0.15116 | 0.15285 | 2.528e-07 | -0.11337 | -0.11464 | 0 | -143.2176 | 37.4691 | 0 | 36.7824 | -142.5309 | 1.3465 | 0.65994 | 0.66389 | 1.3462 | 0.49495 | 0.49792 | 0.10037 | -96.9331 | 83.5246 | 0.11249 | -96.9331 | 83.5246
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.22e-08 | -1.4962e-07 | 1.4734e-07 | -1.2371e-08 | 1.2509e-07 | -1.2264e-07 | -3.0276e-07 | 1.3547e-08 | -9.7809e-09 | 2.5231e-07 | -1.0436e-08 | 6.8483e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3465 | 0.65994 | 0.66389 | 1.3465 | 0.65994 | 0.66389 | 0.10036 | -96.9331 | 83.5246 | 0.10036 | -96.9331 | 83.5246
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0167e-08 | -1.2469e-07 | 1.2278e-07 | -1.0338e-08 | 1.0016e-07 | -9.808e-08 | -2.523e-07 | 1.1289e-08 | -8.1507e-09 | 2.0185e-07 | -8.1782e-09 | 5.2182e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3465 | 0.65994 | 0.66389 | 1.3465 | 0.65994 | 0.66389 | 0.10036 | -96.9331 | 83.5246 | 0.10036 | -96.9331 | 83.5246
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0999e-09 | -7.4812e-08 | 7.3669e-08 | -6.2713e-09 | 5.0281e-08 | -4.8967e-08 | -1.5138e-07 | 6.7736e-09 | -4.8904e-09 | 1.0093e-07 | -3.6625e-09 | 1.9579e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3465 | 0.65994 | 0.66389 | 1.3465 | 0.65994 | 0.66389 | 0.10036 | -96.9331 | 83.5246 | 0.10036 | -96.9331 | 83.5246
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0333e-09 | -2.4937e-08 | 2.4556e-08 | -2.2046e-09 | 4.0678e-10 | 1.4559e-10 | -5.046e-08 | 2.2579e-09 | -1.6301e-09 | 7.7834e-12 | 8.5327e-10 | -1.3024e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3465 | 0.65994 | 0.66389 | 1.3465 | 0.65994 | 0.66389 | 0.10036 | -96.9331 | 83.5246 | 0.10036 | -96.9331 | 83.5246
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0666e-09 | -4.9875e-08 | 4.9113e-08 | -4.238e-09 | 2.5344e-08 | -2.4411e-08 | -1.0092e-07 | 4.5157e-09 | -3.2603e-09 | 5.0468e-08 | -1.4046e-09 | 3.2773e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3465 | 0.65994 | 0.66389 | 1.3465 | 0.65994 | 0.66389 | 0.10036 | -96.9331 | 83.5246 | 0.10036 | -96.9331 | 83.5246
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0333e-09 | -2.4937e-08 | 2.4556e-08 | -2.2046e-09 | 4.0678e-10 | 1.4559e-10 | -5.046e-08 | 2.2579e-09 | -1.6301e-09 | 7.7836e-12 | 8.5327e-10 | -1.3024e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3465 | 0.65994 | 0.66389 | 1.3465 | 0.65994 | 0.66389 | 0.10036 | -96.9331 | 83.5246 | 0.10036 | -96.9331 | 83.5246
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0333e-09 | -2.4937e-08 | 2.4556e-08 | -2.2046e-09 | 4.0678e-10 | 1.4559e-10 | -5.046e-08 | 2.2579e-09 | -1.6301e-09 | 7.784e-12 | 8.5327e-10 | -1.3024e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3465 | 0.65994 | 0.66389 | 1.3465 | 0.65994 | 0.66389 | 0.10037 | -96.9331 | 83.5246 | 0.10037 | -96.9331 | 83.5246
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0333e-09 | -2.4937e-08 | 2.4556e-08 | -2.2046e-09 | 4.0678e-10 | 1.4559e-10 | -5.046e-08 | 2.2579e-09 | -1.6301e-09 | 7.784e-12 | 8.5327e-10 | -1.3024e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3465 | 0.65994 | 0.66389 | 1.3465 | 0.65994 | 0.66389 | 0.10037 | -96.9331 | 83.5246 | 0.10037 | -96.9331 | 83.5246
Line1_1_3 | 1.2992e-06 | 1.3144e-06 | 1.2841e-06 | 1.1371e-06 | 1.1522e-06 | 1.1221e-06 | 3.0004e-07 | 3.0354e-07 | 2.9656e-07 | 2.6261e-07 | 2.661e-07 | 2.5915e-07 | 1.6266e-08 | -1.995e-07 | 1.9645e-07 | -1.6438e-08 | 1.7497e-07 | -1.7175e-07 | -4.0368e-07 | 1.8063e-08 | -1.3041e-08 | 3.5323e-07 | -1.4952e-08 | 1.0109e-08 | 87.7929 | 88.2404 | 87.3225 | -92.564 | -92.0488 | -93.107 | 1.3465 | 0.65994 | 0.66389 | 1.3465 | 0.65994 | 0.66389 | 0.10037 | -96.9331 | 83.5246 | 0.10036 | -96.9331 | 83.5246
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0666e-09 | -4.9875e-08 | 4.9113e-08 | -4.2379e-09 | 2.5344e-08 | -2.4411e-08 | -1.0092e-07 | 4.5158e-09 | -3.2603e-09 | 5.0468e-08 | -1.4046e-09 | 3.2774e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3465 | 0.65994 | 0.66389 | 1.3465 | 0.65994 | 0.66389 | 0.10037 | -96.9331 | 83.5246 | 0.10037 | -96.9331 | 83.5246
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0666e-09 | -4.9875e-08 | 4.9113e-08 | -4.2379e-09 | 2.5344e-08 | -2.4411e-08 | -1.0092e-07 | 4.5158e-09 | -3.2603e-09 | 5.0468e-08 | -1.4046e-09 | 3.2774e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3465 | 0.65994 | 0.66389 | 1.3465 | 0.65994 | 0.66389 | 0.10037 | -96.9331 | 83.5246 | 0.10037 | -96.9331 | 83.5246
Line4_2_6 | 0 | 1.3722 | 1.3846 | 0 | 1.3722 | 1.3846 | 0 | 0.31691 | 0.31976 | 0 | 0.31691 | 0.31976 | 1.0691e-08 | 0.1084 | 0.11049 | -1.0843e-08 | -0.072266 | -0.07366 | -2.5279e-07 | 0.11337 | 0.11464 | 2.0225e-07 | -0.07558 | -0.076425 | 0 | -143.2176 | 37.4691 | 0 | 36.7824 | -142.5309 | 1.3462 | 0.49495 | 0.49792 | 1.3459 | 0.32997 | 0.33195 | 0.11249 | -96.9331 | 83.5246 | 0.12461 | -96.9331 | 83.5246
Line5_6_7 | 0 | 1.3722 | 1.3846 | 0 | 1.3722 | 1.3846 | 0 | 0.31691 | 0.31976 | 0 | 0.31691 | 0.31976 | 8.6426e-09 | 0.072266 | 0.07366 | -8.7424e-09 | -0.036133 | -0.03683 | -2.0224e-07 | 0.07558 | 0.076425 | 1.5169e-07 | -0.03779 | -0.038213 | 0 | -143.2176 | 37.4691 | 0 | 36.7824 | -142.5309 | 1.3459 | 0.32997 | 0.33195 | 1.3456 | 0.16498 | 0.16597 | 0.12461 | -96.9331 | 83.5246 | 0.13674 | -96.9331 | 83.5246
Line6_7_8 | 0 | 1.3722 | 1.3846 | 0 | 1.3722 | 1.3846 | 0 | 0.31691 | 0.31976 | 0 | 0.31691 | 0.31976 | 6.5437e-09 | 0.036133 | 0.03683 | -6.5904e-09 | -1.7344e-14 | 2.2567e-14 | -1.5168e-07 | 0.03779 | 0.038213 | 1.0112e-07 | -1.7127e-13 | 1.5558e-13 | 0 | -143.2176 | 37.4691 | 0 | 36.7824 | -142.5309 | 1.3456 | 0.16498 | 0.16597 | 1.3453 | 0 | 0 | 0.13674 | -96.9331 | 83.5246 | 0.14888 | 0 | 0
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1968e-09 | -1.8389e-20 | -1.4522e-20 | -2.1968e-09 | 6.3619e-18 | -1.1148e-17 | -5.0554e-08 | -1.2033e-20 | -8.9958e-21 | 1.1536e-11 | 2.0074e-17 | -1.7967e-18 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3453 | 0 | 0 | 1.3453 | 0 | 0 | 0.14888 | 0 | 0 | 0.14888 | 0 | 0
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1968e-09 | -1.8389e-20 | -1.4522e-20 | -2.1968e-09 | 6.3619e-18 | -1.1148e-17 | -5.0554e-08 | -1.2033e-20 | -8.9958e-21 | 1.1536e-11 | 2.0074e-17 | -1.7967e-18 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3453 | 0 | 0 | 1.3453 | 0 | 0 | 0.14888 | 0 | 0 | 0.14888 | 0 | 0
Line9_3_11 | 1.1368e-06 | 1.1501e-06 | 1.1236e-06 | 0 | 0 | 0 | 2.6253e-07 | 2.6559e-07 | 2.5949e-07 | 0 | 0 | 0 | 1.4233e-08 | -1.7456e-07 | 1.7189e-07 | -1.4404e-08 | 1.5003e-07 | -1.4719e-07 | -3.5322e-07 | 1.5805e-08 | -1.1411e-08 | 3.0277e-07 | -1.2694e-08 | 8.4785e-09 | 87.7929 | 88.2404 | 87.3225 | 0 | 0 | 0 | 1.3465 | 0.65994 | 0.66389 | 1.3465 | 0.65994 | 0.66389 | 0.10036 | -96.9331 | 83.5246 | 0.10036 | -96.9331 | 83.5246

## LLG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0.024134 | 0.030089 | 0 | 0.024134 | 0.030089 | 0 | 0.0055735 | 0.0069488 | 0 | 0.0055735 | 0.0069488 | -3.7283e-08 | 0.0029534 | 0.0045975 | 2.9706e-08 | -0.0029431 | -0.0045798 | -1.8274e-07 | 0.002964 | 0.0045915 | 1.5264e-07 | -0.002951 | -0.0045753 | 0 | -149.9924 | 56.7201 | 0 | 30.0079 | -123.2801 | 1.2368 | 0.75073 | 0.93506 | 1.2366 | 0.74779 | 0.93162 | 4.4011 | -104.8899 | 101.6832 | 4.4075 | -104.9148 | 101.6921
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.749e-08 | -9.6973e-08 | 1.4028e-07 | 2.9929e-08 | 8.1269e-08 | -1.1701e-07 | -1.8233e-07 | 5.8068e-08 | -1.0601e-08 | 1.5227e-07 | -4.7708e-08 | 7.8102e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2368 | 0.75073 | 0.93506 | 1.2368 | 0.75073 | 0.93506 | 4.4011 | -104.8899 | 101.6832 | 4.4011 | -104.8899 | 101.6832
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.1242e-08 | -8.0811e-08 | 1.169e-07 | 2.368e-08 | 6.5107e-08 | -9.3633e-08 | -1.5194e-07 | 4.839e-08 | -8.8338e-09 | 1.2188e-07 | -3.803e-08 | 6.0434e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2368 | 0.75073 | 0.93506 | 1.2368 | 0.75073 | 0.93506 | 4.4011 | -104.8899 | 101.6832 | 4.4011 | -104.8899 | 101.6832
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.8745e-08 | -4.8487e-08 | 7.0139e-08 | 1.1183e-08 | 3.2782e-08 | -4.6873e-08 | -9.1165e-08 | 2.9034e-08 | -5.3003e-09 | 6.1108e-08 | -1.8674e-08 | 2.5099e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2368 | 0.75073 | 0.93506 | 1.2368 | 0.75073 | 0.93506 | 4.4011 | -104.8899 | 101.6832 | 4.4011 | -104.8899 | 101.6832
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.2484e-09 | -1.6162e-08 | 2.338e-08 | -1.3134e-09 | 4.5811e-10 | -1.1382e-10 | -3.0388e-08 | 9.678e-09 | -1.7668e-09 | 3.3061e-10 | 6.8168e-10 | -1.0236e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2368 | 0.75073 | 0.93506 | 1.2368 | 0.75073 | 0.93506 | 4.4011 | -104.8899 | 101.6832 | 4.4011 | -104.8899 | 101.6832
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.2497e-08 | -3.2324e-08 | 4.6759e-08 | 4.935e-09 | 1.662e-08 | -2.3494e-08 | -6.0777e-08 | 1.9356e-08 | -3.5335e-09 | 3.0719e-08 | -8.9963e-09 | 7.4314e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2368 | 0.75073 | 0.93506 | 1.2368 | 0.75073 | 0.93506 | 4.4011 | -104.8899 | 101.6832 | 4.4011 | -104.8899 | 101.6832
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.2484e-09 | -1.6162e-08 | 2.338e-08 | -1.3134e-09 | 4.5811e-10 | -1.1382e-10 | -3.0388e-08 | 9.678e-09 | -1.7668e-09 | 3.3061e-10 | 6.8168e-10 | -1.0236e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2368 | 0.75073 | 0.93506 | 1.2368 | 0.75073 | 0.93506 | 4.4011 | -104.8899 | 101.6832 | 4.4011 | -104.8899 | 101.6832
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.2484e-09 | -1.6162e-08 | 2.338e-08 | -1.3134e-09 | 4.5811e-10 | -1.1382e-10 | -3.0388e-08 | 9.678e-09 | -1.7668e-09 | 3.3061e-10 | 6.8168e-10 | -1.0236e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2368 | 0.75073 | 0.93506 | 1.2368 | 0.75073 | 0.93506 | 4.4011 | -104.8899 | 101.6832 | 4.4011 | -104.8899 | 101.6832
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.2484e-09 | -1.6162e-08 | 2.338e-08 | -1.3134e-09 | 4.5811e-10 | -1.1382e-10 | -3.0388e-08 | 9.678e-09 | -1.7668e-09 | 3.3061e-10 | 6.8168e-10 | -1.0236e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2368 | 0.75073 | 0.93506 | 1.2368 | 0.75073 | 0.93506 | 4.4011 | -104.8899 | 101.6832 | 4.4011 | -104.8899 | 101.6832
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.9987e-08 | -1.293e-07 | 1.8704e-07 | 4.2425e-08 | 1.1359e-07 | -1.6377e-07 | -2.4311e-07 | 7.7424e-08 | -1.4134e-08 | 2.1305e-07 | -6.7064e-08 | 1.1344e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2368 | 0.75073 | 0.93506 | 1.2368 | 0.75073 | 0.93506 | 4.4011 | -104.8899 | 101.6832 | 4.4011 | -104.8899 | 101.6832
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.2497e-08 | -3.2324e-08 | 4.6759e-08 | 4.935e-09 | 1.662e-08 | -2.3494e-08 | -6.0777e-08 | 1.9356e-08 | -3.5335e-09 | 3.0719e-08 | -8.9963e-09 | 7.4315e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2368 | 0.75073 | 0.93506 | 1.2368 | 0.75073 | 0.93506 | 4.4011 | -104.8899 | 101.6832 | 4.4011 | -104.8899 | 101.6832
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.2497e-08 | -3.2324e-08 | 4.6759e-08 | 4.935e-09 | 1.662e-08 | -2.3494e-08 | -6.0777e-08 | 1.9356e-08 | -3.5335e-09 | 3.0719e-08 | -8.9963e-09 | 7.4315e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2368 | 0.75073 | 0.93506 | 1.2368 | 0.75073 | 0.93506 | 4.4011 | -104.8899 | 101.6832 | 4.4011 | -104.8899 | 101.6832
Line4_2_6 | 0 | 0.024134 | 0.030089 | 0 | 0.024134 | 0.030089 | 0 | 0.0055735 | 0.0069488 | 0 | 0.0055735 | 0.0069488 | -3.1018e-08 | 0.0029431 | 0.0045798 | 2.3464e-08 | -0.0029328 | -0.0045621 | -1.5231e-07 | 0.002951 | 0.0045753 | 1.222e-07 | -0.0029381 | -0.0045591 | 0 | -149.9921 | 56.7199 | 0 | 30.0081 | -123.2802 | 1.2366 | 0.74779 | 0.93162 | 1.2363 | 0.74484 | 0.92817 | 4.4075 | -104.9148 | 101.6921 | 4.4138 | -104.94 | 101.701
Line5_6_7 | 0 | 0.024134 | 0.030089 | 0 | 0.024134 | 0.030089 | 0 | 0.0055735 | 0.0069488 | 0 | 0.0055735 | 0.0069488 | -2.4775e-08 | 0.0029328 | 0.0045621 | 1.7245e-08 | -0.0029225 | -0.0045444 | -1.2187e-07 | 0.0029381 | 0.0045591 | 9.1744e-08 | -0.0029252 | -0.0045429 | 0 | -149.9919 | 56.7198 | 0 | 30.0084 | -123.2804 | 1.2363 | 0.74484 | 0.92817 | 1.2361 | 0.74189 | 0.92473 | 4.4138 | -104.94 | 101.701 | 4.4201 | -104.9653 | 101.7101
Line6_7_8 | 0 | 0.024134 | 0.030089 | 0 | 0.024134 | 0.030089 | 0 | 0.0055735 | 0.0069488 | 0 | 0.0055735 | 0.0069488 | -1.8554e-08 | 0.0029225 | 0.0045444 | 1.1047e-08 | -0.0029122 | -0.0045268 | -9.1412e-08 | 0.0029252 | 0.0045429 | 6.1271e-08 | -0.0029123 | -0.0045267 | 0 | -149.9916 | 56.7196 | 0 | 30.0086 | -123.2805 | 1.2361 | 0.74189 | 0.92473 | 1.2359 | 0.73895 | 0.92128 | 4.4201 | -104.9653 | 101.7101 | 4.4265 | -104.9909 | 101.7192
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.1778e-09 | -1.5991e-08 | 2.3058e-08 | -1.3082e-09 | 4.8403e-10 | -6.4955e-11 | -3.0469e-08 | 9.5455e-09 | -1.6769e-09 | 3.3225e-10 | 6.666e-10 | -1.0066e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2359 | 0.73895 | 0.92128 | 1.2359 | 0.73895 | 0.92128 | 4.4265 | -104.9909 | 101.7192 | 4.4265 | -104.9909 | 101.7192
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.1778e-09 | -1.5991e-08 | 2.3058e-08 | -1.3082e-09 | 4.8403e-10 | -6.4955e-11 | -3.0469e-08 | 9.5455e-09 | -1.6769e-09 | 3.3225e-10 | 6.666e-10 | -1.0066e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2359 | 0.73895 | 0.92128 | 1.2359 | 0.73895 | 0.92128 | 4.4265 | -104.9909 | 101.7192 | 4.4265 | -104.9909 | 101.7192
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.3739e-08 | -1.1314e-07 | 1.6366e-07 | 3.6177e-08 | 9.7431e-08 | -1.4039e-07 | -2.1272e-07 | 6.7746e-08 | -1.2367e-08 | 1.8266e-07 | -5.7386e-08 | 9.577e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2368 | 0.75073 | 0.93506 | 1.2368 | 0.75073 | 0.93506 | 4.4011 | -104.8899 | 101.6832 | 4.4011 | -104.8899 | 101.6832

## LLG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0.022864 | 0.028506 | 0 | 0.022864 | 0.028506 | 0 | 0.0052801 | 0.0065831 | 0 | 0.0052801 | 0.0065831 | -3.3462e-08 | 0.0026507 | 0.0041263 | 2.6661e-08 | -0.0026414 | -0.0041104 | -1.6401e-07 | 0.0026602 | 0.0041209 | 1.37e-07 | -0.0026486 | -0.0041064 | 0 | -149.9924 | 56.7201 | 0 | 30.0079 | -123.2801 | 1.1717 | 0.71122 | 0.88585 | 1.1715 | 0.70843 | 0.88259 | 4.4011 | -104.8899 | 101.6832 | 4.4075 | -104.9148 | 101.6921
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.3648e-08 | -8.7034e-08 | 1.259e-07 | 2.6861e-08 | 7.2939e-08 | -1.0502e-07 | -1.6364e-07 | 5.2117e-08 | -9.5141e-09 | 1.3667e-07 | -4.2819e-08 | 7.0097e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1717 | 0.71122 | 0.88585 | 1.1717 | 0.71122 | 0.88585 | 4.4011 | -104.8899 | 101.6832 | 4.4011 | -104.8899 | 101.6832
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.804e-08 | -7.2528e-08 | 1.0492e-07 | 2.1253e-08 | 5.8434e-08 | -8.4036e-08 | -1.3637e-07 | 4.343e-08 | -7.9284e-09 | 1.0939e-07 | -3.4133e-08 | 5.424e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1717 | 0.71122 | 0.88585 | 1.1717 | 0.71122 | 0.88585 | 4.4011 | -104.8899 | 101.6832 | 4.4011 | -104.8899 | 101.6832
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.6824e-08 | -4.3517e-08 | 6.295e-08 | 1.0037e-08 | 2.9422e-08 | -4.2069e-08 | -8.1822e-08 | 2.6058e-08 | -4.7571e-09 | 5.4844e-08 | -1.676e-08 | 2.2527e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1717 | 0.71122 | 0.88585 | 1.1717 | 0.71122 | 0.88585 | 4.4011 | -104.8899 | 101.6832 | 4.4011 | -104.8899 | 101.6832
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.608e-09 | -1.4506e-08 | 2.0983e-08 | -1.1788e-09 | 4.1115e-10 | -1.0215e-10 | -2.7274e-08 | 8.6861e-09 | -1.5857e-09 | 2.9672e-10 | 6.1181e-10 | -9.1871e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1717 | 0.71122 | 0.88585 | 1.1717 | 0.71122 | 0.88585 | 4.4011 | -104.8899 | 101.6832 | 4.4011 | -104.8899 | 101.6832
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.1216e-08 | -2.9011e-08 | 4.1967e-08 | 4.4292e-09 | 1.4917e-08 | -2.1086e-08 | -5.4548e-08 | 1.7372e-08 | -3.1714e-09 | 2.7571e-08 | -8.0743e-09 | 6.6697e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1717 | 0.71122 | 0.88585 | 1.1717 | 0.71122 | 0.88585 | 4.4011 | -104.8899 | 101.6832 | 4.4011 | -104.8899 | 101.6832
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.608e-09 | -1.4506e-08 | 2.0983e-08 | -1.1788e-09 | 4.1115e-10 | -1.0215e-10 | -2.7274e-08 | 8.6861e-09 | -1.5857e-09 | 2.9672e-10 | 6.1181e-10 | -9.1871e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1717 | 0.71122 | 0.88585 | 1.1717 | 0.71122 | 0.88585 | 4.4011 | -104.8899 | 101.6832 | 4.4011 | -104.8899 | 101.6832
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.608e-09 | -1.4506e-08 | 2.0983e-08 | -1.1788e-09 | 4.1115e-10 | -1.0215e-10 | -2.7274e-08 | 8.6861e-09 | -1.5857e-09 | 2.9672e-10 | 6.1181e-10 | -9.1871e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1717 | 0.71122 | 0.88585 | 1.1717 | 0.71122 | 0.88585 | 4.4011 | -104.8899 | 101.6832 | 4.4011 | -104.8899 | 101.6832
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.608e-09 | -1.4506e-08 | 2.0983e-08 | -1.1788e-09 | 4.1115e-10 | -1.0215e-10 | -2.7274e-08 | 8.6861e-09 | -1.5857e-09 | 2.9672e-10 | 6.1181e-10 | -9.1871e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1717 | 0.71122 | 0.88585 | 1.1717 | 0.71122 | 0.88585 | 4.4011 | -104.8899 | 101.6832 | 4.4011 | -104.8899 | 101.6832
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.4864e-08 | -1.1605e-07 | 1.6787e-07 | 3.8077e-08 | 1.0195e-07 | -1.4699e-07 | -2.1819e-07 | 6.9489e-08 | -1.2685e-08 | 1.9121e-07 | -6.0191e-08 | 1.0181e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1717 | 0.71122 | 0.88585 | 1.1717 | 0.71122 | 0.88585 | 4.4011 | -104.8899 | 101.6832 | 4.4011 | -104.8899 | 101.6832
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.1216e-08 | -2.9011e-08 | 4.1967e-08 | 4.4292e-09 | 1.4917e-08 | -2.1086e-08 | -5.4548e-08 | 1.7372e-08 | -3.1714e-09 | 2.7571e-08 | -8.0743e-09 | 6.6698e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1717 | 0.71122 | 0.88585 | 1.1717 | 0.71122 | 0.88585 | 4.4011 | -104.8899 | 101.6832 | 4.4011 | -104.8899 | 101.6832
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.1216e-08 | -2.9011e-08 | 4.1967e-08 | 4.4292e-09 | 1.4917e-08 | -2.1086e-08 | -5.4548e-08 | 1.7372e-08 | -3.1714e-09 | 2.7571e-08 | -8.0743e-09 | 6.6698e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1717 | 0.71122 | 0.88585 | 1.1717 | 0.71122 | 0.88585 | 4.4011 | -104.8899 | 101.6832 | 4.4011 | -104.8899 | 101.6832
Line4_2_6 | 0 | 0.022864 | 0.028506 | 0 | 0.022864 | 0.028506 | 0 | 0.0052801 | 0.0065831 | 0 | 0.0052801 | 0.0065831 | -2.7839e-08 | 0.0026414 | 0.0041104 | 2.1059e-08 | -0.0026322 | -0.0040945 | -1.367e-07 | 0.0026486 | 0.0041064 | 1.0968e-07 | -0.002637 | -0.0040919 | 0 | -149.9921 | 56.7199 | 0 | 30.0081 | -123.2802 | 1.1715 | 0.70843 | 0.88259 | 1.1713 | 0.70564 | 0.87932 | 4.4075 | -104.9148 | 101.6921 | 4.4138 | -104.94 | 101.701
Line5_6_7 | 0 | 0.022864 | 0.028506 | 0 | 0.022864 | 0.028506 | 0 | 0.0052801 | 0.0065831 | 0 | 0.0052801 | 0.0065831 | -2.2236e-08 | 0.0026322 | 0.0040945 | 1.5477e-08 | -0.002623 | -0.0040787 | -1.0938e-07 | 0.002637 | 0.0040919 | 8.234e-08 | -0.0026254 | -0.0040773 | 0 | -149.9919 | 56.7198 | 0 | 30.0084 | -123.2804 | 1.1713 | 0.70564 | 0.87932 | 1.171 | 0.70285 | 0.87606 | 4.4138 | -104.94 | 101.701 | 4.4201 | -104.9653 | 101.7101
Line6_7_8 | 0 | 0.022864 | 0.028506 | 0 | 0.022864 | 0.028505 | 0 | 0.0052801 | 0.0065831 | 0 | 0.0052801 | 0.0065831 | -1.6652e-08 | 0.002623 | 0.0040787 | 9.9151e-09 | -0.0026137 | -0.0040628 | -8.2043e-08 | 0.0026254 | 0.0040773 | 5.4991e-08 | -0.0026138 | -0.0040628 | 0 | -149.9916 | 56.7196 | 0 | 30.0086 | -123.2805 | 1.171 | 0.70285 | 0.87606 | 1.1708 | 0.70006 | 0.87279 | 4.4201 | -104.9653 | 101.7101 | 4.4265 | -104.9909 | 101.7192
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.5446e-09 | -1.4352e-08 | 2.0694e-08 | -1.1741e-09 | 4.3442e-10 | -5.8298e-11 | -2.7347e-08 | 8.5671e-09 | -1.5051e-09 | 2.982e-10 | 5.9828e-10 | -9.0345e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1708 | 0.70006 | 0.87279 | 1.1708 | 0.70006 | 0.87279 | 4.4265 | -104.9909 | 101.7192 | 4.4265 | -104.9909 | 101.7192
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.5446e-09 | -1.4352e-08 | 2.0694e-08 | -1.1741e-09 | 4.3442e-10 | -5.8298e-11 | -2.7347e-08 | 8.5671e-09 | -1.5051e-09 | 2.982e-10 | 5.9828e-10 | -9.0345e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1708 | 0.70006 | 0.87279 | 1.1708 | 0.70006 | 0.87279 | 4.4265 | -104.9909 | 101.7192 | 4.4265 | -104.9909 | 101.7192
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.9256e-08 | -1.0154e-07 | 1.4688e-07 | 3.2469e-08 | 8.7445e-08 | -1.26e-07 | -1.9092e-07 | 6.0803e-08 | -1.11e-08 | 1.6394e-07 | -5.1505e-08 | 8.5954e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1717 | 0.71122 | 0.88585 | 1.1717 | 0.71122 | 0.88585 | 4.4011 | -104.8899 | 101.6832 | 4.4011 | -104.8899 | 101.6832