## LLL_max_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 3.4587 | 3.4587 | 0 | 0 | 119.8128 | 119.8128 | 37.3233 | -18.6616 | 42.3476 | -21.1738 | -71.7883 | 108.2117 | 0.47113 | 0.23557 | -23.1798 | -23.1798
Line_1 | 3.4587 | 3.4587 | 6.7756 | 0 | 119.8128 | 119.8128 | -1e-07 | 18.6616 | -1e-07 | 21.1738 | 108.2117 | -71.7883 | 0 | 0.23557 | 0 | -23.1798
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23557 | 0.23557 | -23.1798 | -23.1798

## LLL_max_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 3.4587 | 3.4587 | 0 | 0 | 119.8128 | 119.8128 | 37.3233 | -18.6616 | 42.3476 | -21.1738 | -71.7883 | 108.2117 | 0.47113 | 0.23557 | -23.1798 | -23.1798
Line_1 | 3.4587 | 3.4587 | 6.7756 | 0 | 119.8128 | 119.8128 | -1e-07 | 18.6616 | -1e-07 | 21.1738 | 108.2117 | -71.7883 | 0 | 0.23557 | 0 | -23.1798
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23557 | 0.23557 | -23.1798 | -23.1798

## LLL_max_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 1.2119 | 1.2119 | 0 | 0 | 41.9813 | 41.9813 | 26.6127 | -24.3216 | 27.2296 | -24.63 | -54.0862 | 125.9138 | 0.90694 | 0.82453 | -8.4298 | -8.7252
Line_1 | 1.2119 | 1.2119 | 2.3741 | 0 | 41.9813 | 41.9813 | -22.0304 | 24.3216 | -22.0304 | 24.63 | 125.9138 | -54.0862 | 0.74213 | 0.82453 | -9.0862 | -8.7252
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.82453 | 0.82453 | -8.7252 | -8.7252

## LLL_max_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 1.2119 | 1.2119 | 0 | 0 | 41.9813 | 41.9813 | 26.6127 | -24.3216 | 27.2296 | -24.63 | -54.0862 | 125.9138 | 0.90694 | 0.82453 | -8.4298 | -8.7252
Line_1 | 1.2119 | 1.2119 | 2.3741 | 0 | 41.9813 | 41.9813 | -22.0304 | 24.3216 | -22.0304 | 24.63 | 125.9138 | -54.0862 | 0.74213 | 0.82453 | -9.0862 | -8.7252
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.82453 | 0.82453 | -8.7252 | -8.7252

## LLL_min_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 2.7686 | 2.7686 | 0 | 0 | 95.9057 | 95.9057 | 45.916 | -22.958 | 27.1338 | -13.5669 | -59.5744 | 120.4256 | 0.55611 | 0.27805 | -28.9937 | -28.9937
Line_1 | 2.7686 | 2.7686 | 4.6525 | 0 | 95.9057 | 95.9057 | -1e-07 | 22.958 | -1e-07 | 13.5669 | 120.4256 | -59.5744 | 0 | 0.27805 | 0 | -28.9937
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27805 | 0.27805 | -28.9937 | -28.9937

## LLL_min_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 2.7686 | 2.7686 | 0 | 0 | 95.9057 | 95.9057 | 45.916 | -22.958 | 27.1338 | -13.5669 | -59.5744 | 120.4256 | 0.55611 | 0.27805 | -28.9937 | -28.9937
Line_1 | 2.7686 | 2.7686 | 4.6525 | 0 | 95.9057 | 95.9057 | -1e-07 | 22.958 | -1e-07 | 13.5669 | 120.4256 | -59.5744 | 0 | 0.27805 | 0 | -28.9937
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27805 | 0.27805 | -28.9937 | -28.9937

## LLL_min_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 1.0349 | 1.0349 | 0 | 0 | 35.8516 | 35.8516 | 22.4832 | -19.2749 | 19.8585 | -17.9626 | -50.3977 | 129.6023 | 0.83671 | 0.7349 | -8.9447 | -7.416
Line_1 | 1.0349 | 1.0349 | 1.7392 | 0 | 35.8516 | 35.8516 | -16.0667 | 19.2749 | -16.0667 | 17.9626 | 129.6023 | -50.3977 | 0.63377 | 0.7349 | -5.3977 | -7.416
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7349 | 0.7349 | -7.416 | -7.416

## LLL_min_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 1.0349 | 1.0349 | 0 | 0 | 35.8516 | 35.8516 | 22.4832 | -19.2749 | 19.8585 | -17.9626 | -50.3977 | 129.6023 | 0.83671 | 0.7349 | -8.9447 | -7.416
Line_1 | 1.0349 | 1.0349 | 1.7392 | 0 | 35.8516 | 35.8516 | -16.0667 | 19.2749 | -16.0667 | 17.9626 | 129.6023 | -50.3977 | 0.63377 | 0.7349 | -5.3977 | -7.416
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7349 | 0.7349 | -7.416 | -7.416

## LL_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 2.9953 | 2.9953 | 0 | 2.9953 | 2.9953 | 0 | 34.587 | 34.587 | 0 | 34.587 | 34.587 | -1.0421e-14 | 27.4008 | -8.7391 | 1.5455e-28 | -22.7354 | 13.4045 | 2.0843e-14 | 4.6417 | 16.5321 | -1.0421e-14 | 0.65175 | -11.2386 | 0 | -161.7883 | 18.2117 | 0 | 18.2117 | -161.7883 | 1.1 | 0.80351 | 0.54066 | 1.1 | 0.65761 | 0.50575 | 8.3565e-13 | -152.1736 | 136.0734 | 8.497e-13 | -163.4303 | 158.2346
Line_1 | 0 | 2.9953 | 2.9953 | 0 | 2.9953 | 2.9953 | 0 | 34.587 | 34.587 | 0 | 34.587 | 34.587 | 2.6053e-14 | -18.0699 | 18.0699 | -3.6475e-14 | 22.7354 | -13.4045 | -1.2506e-13 | 5.9452 | -5.9452 | 1.3027e-13 | -0.65175 | 11.2386 | 0 | 18.2117 | -161.7883 | 0 | -161.7883 | 18.2117 | 1.1 | 0.55 | 0.55 | 1.1 | 0.65761 | 0.50575 | 9.9707e-13 | 180 | -180 | 8.497e-13 | -163.4303 | 158.2346
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -9.3792e-14 | 3.4057e-10 | 6.644e-10 | 7.816e-14 | -3.4054e-10 | -6.6441e-10 | 9.3792e-14 | -1.8235e-09 | 1.2624e-09 | -8.8581e-14 | 1.8234e-09 | -1.2624e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.65761 | 0.50575 | 1.1 | 0.65761 | 0.50575 | 7.0815e-13 | -163.4303 | 158.2346 | 8.497e-13 | -163.4303 | 158.2346

## LL_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 2.9953 | 2.9953 | 0 | 2.9953 | 2.9953 | 0 | 34.587 | 34.587 | 0 | 34.587 | 34.587 | -1.0421e-14 | 27.4008 | -8.7391 | 1.5455e-28 | -22.7354 | 13.4045 | 2.0843e-14 | 4.6417 | 16.5321 | -1.0421e-14 | 0.65175 | -11.2386 | 0 | -161.7883 | 18.2117 | 0 | 18.2117 | -161.7883 | 1.1 | 0.80351 | 0.54066 | 1.1 | 0.65761 | 0.50575 | 8.3565e-13 | -152.1736 | 136.0734 | 8.497e-13 | -163.4303 | 158.2346
Line_1 | 0 | 2.9953 | 2.9953 | 0 | 2.9953 | 2.9953 | 0 | 34.587 | 34.587 | 0 | 34.587 | 34.587 | 2.6053e-14 | -18.0699 | 18.0699 | -3.6475e-14 | 22.7354 | -13.4045 | -1.2506e-13 | 5.9452 | -5.9452 | 1.3027e-13 | -0.65175 | 11.2386 | 0 | 18.2117 | -161.7883 | 0 | -161.7883 | 18.2117 | 1.1 | 0.55 | 0.55 | 1.1 | 0.65761 | 0.50575 | 9.9707e-13 | 180 | -180 | 8.497e-13 | -163.4303 | 158.2346
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -9.3792e-14 | 3.4057e-10 | 6.644e-10 | 7.816e-14 | -3.4054e-10 | -6.6441e-10 | 9.3792e-14 | -1.8235e-09 | 1.2624e-09 | -8.8581e-14 | 1.8234e-09 | -1.2624e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.65761 | 0.50575 | 1.1 | 0.65761 | 0.50575 | 7.0815e-13 | -163.4303 | 158.2346 | 8.497e-13 | -163.4303 | 158.2346

## LL_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 1.5688 | 1.5688 | 0 | 1.5688 | 1.5688 | 0 | 18.1144 | 18.1144 | 0 | 18.1144 | 18.1144 | -2.6053e-15 | 17.2205 | 0.20321 | 1.959e-29 | -15.9408 | 1.0765 | 7.816e-15 | 3.8735 | 14.2393 | -2.6053e-15 | -2.4216 | -12.7873 | 0 | -148.6532 | 31.3468 | 0 | 31.3468 | -148.6532 | 1.1 | 0.97441 | 0.78616 | 1.1 | 0.89011 | 0.70842 | 4.2383e-13 | -135.9762 | 120.5292 | 4.3082e-13 | -140.0155 | 126.1589
Line_1 | 0 | 1.5688 | 1.5688 | 0 | 1.5688 | 1.5688 | 0 | 18.1144 | 18.1144 | 0 | 18.1144 | 18.1144 | 1.5632e-14 | -14.6611 | 2.3562 | -1.8237e-14 | 15.9408 | -1.0765 | -6.5133e-14 | -0.96958 | -11.3353 | 7.0344e-14 | 2.4216 | 12.7873 | 0 | 31.3468 | -148.6532 | 0 | -148.6532 | 31.3468 | 1.1 | 0.81113 | 0.63914 | 1.1 | 0.89011 | 0.70842 | 5.1553e-13 | -144.8696 | 133.0893 | 4.3082e-13 | -140.0155 | 126.1589
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.0843e-14 | 4.6824e-10 | 1.0006e-09 | 2.0843e-14 | -4.6824e-10 | -1.0006e-09 | 3.3869e-14 | -1.2288e-09 | 3.0652e-10 | -2.8659e-14 | 1.2288e-09 | -3.0651e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.89011 | 0.70842 | 1.1 | 0.89011 | 0.70842 | 3.6257e-13 | -140.0155 | 126.1589 | 4.3082e-13 | -140.0155 | 126.1589

## LL_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 1.5688 | 1.5688 | 0 | 1.5688 | 1.5688 | 0 | 18.1144 | 18.1144 | 0 | 18.1144 | 18.1144 | -2.6053e-15 | 17.2205 | 0.20321 | 1.959e-29 | -15.9408 | 1.0765 | 7.816e-15 | 3.8735 | 14.2393 | -2.6053e-15 | -2.4216 | -12.7873 | 0 | -148.6532 | 31.3468 | 0 | 31.3468 | -148.6532 | 1.1 | 0.97441 | 0.78616 | 1.1 | 0.89011 | 0.70842 | 4.2383e-13 | -135.9762 | 120.5292 | 4.3082e-13 | -140.0155 | 126.1589
Line_1 | 0 | 1.5688 | 1.5688 | 0 | 1.5688 | 1.5688 | 0 | 18.1144 | 18.1144 | 0 | 18.1144 | 18.1144 | 1.5632e-14 | -14.6611 | 2.3562 | -1.8237e-14 | 15.9408 | -1.0765 | -6.5133e-14 | -0.96958 | -11.3353 | 7.0344e-14 | 2.4216 | 12.7873 | 0 | 31.3468 | -148.6532 | 0 | -148.6532 | 31.3468 | 1.1 | 0.81113 | 0.63914 | 1.1 | 0.89011 | 0.70842 | 5.1553e-13 | -144.8696 | 133.0893 | 4.3082e-13 | -140.0155 | 126.1589
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.0843e-14 | 4.6824e-10 | 1.0006e-09 | 2.0843e-14 | -4.6824e-10 | -1.0006e-09 | 3.3869e-14 | -1.2288e-09 | 3.0652e-10 | -2.8659e-14 | 1.2288e-09 | -3.0651e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.89011 | 0.70842 | 1.1 | 0.89011 | 0.70842 | 3.6257e-13 | -140.0155 | 126.1589 | 4.3082e-13 | -140.0155 | 126.1589

## LL_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 2.3976 | 2.3976 | 0 | 2.3976 | 2.3976 | 0 | 27.6856 | 27.6856 | 0 | 27.6856 | 27.6856 | -1.1842e-14 | 23.4155 | -0.45749 | 8.2897e-15 | -17.676 | 6.197 | 7.1054e-15 | -0.22679 | 13.7937 | -4.737e-15 | 3.6185 | -10.402 | 0 | -149.5744 | 30.4256 | 0 | 30.4256 | -149.5744 | 1 | 0.8458 | 0.4985 | 1 | 0.65169 | 0.43734 | 9.046e-13 | -150.1294 | 122.3252 | 9.1609e-13 | -161.1438 | 151.2099
Line_1 | 0 | 2.3976 | 2.3976 | 0 | 2.3976 | 2.3976 | 0 | 27.6856 | 27.6856 | 0 | 27.6856 | 27.6856 | 1.8948e-14 | -11.9365 | 11.9365 | -2.1316e-14 | 17.676 | -6.197 | -6.3949e-14 | 7.0103 | -7.0103 | 7.1054e-14 | -3.6185 | 10.402 | 0 | 30.4256 | -149.5744 | 0 | -149.5744 | 30.4256 | 1 | 0.5 | 0.5 | 1 | 0.65169 | 0.43734 | 1.0873e-12 | -180 | 180 | 9.1609e-13 | -161.1438 | 151.2099
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -9.4739e-15 | 2.4224e-10 | 6.7018e-10 | 5.9212e-15 | -2.4224e-10 | -6.7018e-10 | 5.2106e-14 | -1.5722e-09 | 8.309e-10 | -4.9738e-14 | 1.5722e-09 | -8.309e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.65169 | 0.43734 | 1 | 0.65169 | 0.43734 | 7.4102e-13 | -161.1438 | 151.2099 | 9.1609e-13 | -161.1438 | 151.2099

## LL_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 2.3976 | 2.3976 | 0 | 2.3976 | 2.3976 | 0 | 27.6856 | 27.6856 | 0 | 27.6856 | 27.6856 | -1.1842e-14 | 23.4155 | -0.45749 | 8.2897e-15 | -17.676 | 6.197 | 7.1054e-15 | -0.22679 | 13.7937 | -4.737e-15 | 3.6185 | -10.402 | 0 | -149.5744 | 30.4256 | 0 | 30.4256 | -149.5744 | 1 | 0.8458 | 0.4985 | 1 | 0.65169 | 0.43734 | 9.046e-13 | -150.1294 | 122.3252 | 9.1609e-13 | -161.1438 | 151.2099
Line_1 | 0 | 2.3976 | 2.3976 | 0 | 2.3976 | 2.3976 | 0 | 27.6856 | 27.6856 | 0 | 27.6856 | 27.6856 | 1.8948e-14 | -11.9365 | 11.9365 | -2.1316e-14 | 17.676 | -6.197 | -6.3949e-14 | 7.0103 | -7.0103 | 7.1054e-14 | -3.6185 | 10.402 | 0 | 30.4256 | -149.5744 | 0 | -149.5744 | 30.4256 | 1 | 0.5 | 0.5 | 1 | 0.65169 | 0.43734 | 1.0873e-12 | -180 | 180 | 9.1609e-13 | -161.1438 | 151.2099
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -9.4739e-15 | 2.4224e-10 | 6.7018e-10 | 5.9212e-15 | -2.4224e-10 | -6.7018e-10 | 5.2106e-14 | -1.5722e-09 | 8.309e-10 | -4.9738e-14 | 1.5722e-09 | -8.309e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.65169 | 0.43734 | 1 | 0.65169 | 0.43734 | 7.4102e-13 | -161.1438 | 151.2099 | 9.1609e-13 | -161.1438 | 151.2099

## LL_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 1.3081 | 1.3081 | 0 | 1.3081 | 1.3081 | 0 | 15.105 | 15.105 | 0 | 15.105 | 15.105 | -4.737e-15 | 13.7181 | 1.6719 | 2.9606e-15 | -12.0096 | 0.036546 | 4.737e-15 | 1.7406 | 10.8539 | -4.737e-15 | -0.73098 | -9.8443 | 0 | -142.8911 | 37.1089 | 0 | 37.1089 | -142.8911 | 1 | 0.91546 | 0.72704 | 1 | 0.79654 | 0.65173 | 4.9989e-13 | -135.6599 | 118.3519 | 5.0359e-13 | -139.408 | 127.3216
Line_1 | 0 | 1.3081 | 1.3081 | 0 | 1.3081 | 1.3081 | 0 | 15.105 | 15.105 | 0 | 15.105 | 15.105 | 8.2897e-15 | -10.3011 | 1.745 | -1.0658e-14 | 12.0096 | -0.036546 | -3.7896e-14 | 0.27863 | -8.8347 | 3.5527e-14 | 0.73098 | 9.8443 | 0 | 37.1089 | -142.8911 | 0 | -142.8911 | 37.1089 | 1 | 0.68221 | 0.59619 | 1 | 0.79654 | 0.65173 | 5.9905e-13 | -144.4405 | 138.2821 | 5.0359e-13 | -139.408 | 127.3216
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.5168e-29 | 4.2829e-10 | 8.1275e-10 | -2.3685e-15 | -4.2829e-10 | -8.1275e-10 | 1.1842e-14 | -9.7053e-10 | 3.0451e-10 | -1.1842e-14 | 9.7053e-10 | -3.0451e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.79654 | 0.65173 | 1 | 0.79654 | 0.65173 | 4.1206e-13 | -139.408 | 127.3216 | 5.0359e-13 | -139.408 | 127.3216

## LL_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 1.3081 | 1.3081 | 0 | 1.3081 | 1.3081 | 0 | 15.105 | 15.105 | 0 | 15.105 | 15.105 | -4.737e-15 | 13.7181 | 1.6719 | 2.9606e-15 | -12.0096 | 0.036546 | 4.737e-15 | 1.7406 | 10.8539 | -4.737e-15 | -0.73098 | -9.8443 | 0 | -142.8911 | 37.1089 | 0 | 37.1089 | -142.8911 | 1 | 0.91546 | 0.72704 | 1 | 0.79654 | 0.65173 | 4.9989e-13 | -135.6599 | 118.3519 | 5.0359e-13 | -139.408 | 127.3216
Line_1 | 0 | 1.3081 | 1.3081 | 0 | 1.3081 | 1.3081 | 0 | 15.105 | 15.105 | 0 | 15.105 | 15.105 | 8.2897e-15 | -10.3011 | 1.745 | -1.0658e-14 | 12.0096 | -0.036546 | -3.7896e-14 | 0.27863 | -8.8347 | 3.5527e-14 | 0.73098 | 9.8443 | 0 | 37.1089 | -142.8911 | 0 | -142.8911 | 37.1089 | 1 | 0.68221 | 0.59619 | 1 | 0.79654 | 0.65173 | 5.9905e-13 | -144.4405 | 138.2821 | 5.0359e-13 | -139.408 | 127.3216
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.5168e-29 | 4.2829e-10 | 8.1275e-10 | -2.3685e-15 | -4.2829e-10 | -8.1275e-10 | 1.1842e-14 | -9.7053e-10 | 3.0451e-10 | -1.1842e-14 | 9.7053e-10 | -3.0451e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.79654 | 0.65173 | 1 | 0.79654 | 0.65173 | 4.1206e-13 | -139.408 | 127.3216 | 5.0359e-13 | -139.408 | 127.3216

## LG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 3.4587 | 1.7293 | 1.7293 | 3.4587 | 1.7293 | 1.7293 | 39.9376 | 19.9688 | 19.9688 | 39.9376 | 19.9688 | 19.9688 | 12.4411 | -14.9597 | 21.1802 | -6.2205 | 16.5148 | -19.6251 | 14.1159 | 9.4742 | -2.4162 | -7.0579 | -7.7097 | 4.1807 | -71.7883 | 108.2117 | 108.2117 | 108.2117 | -71.7883 | -71.7883 |  | 0.47113 | 0.88675 | 1.0675 | 0.23557 | 0.91271 | 1.0048 | -23.1798 | -104.1349 | 101.7036 | -23.1798 | -96.813 | 96.1858
Line_1 | 3.4587 | 1.7293 | 1.7293 | 3.4587 | 1.7293 | 1.7293 | 39.9376 | 19.9688 | 19.9688 | 39.9376 | 19.9688 | 19.9688 | 4.6138e-10 | 18.0699 | -18.0699 | 6.2205 | -16.5148 | 19.6251 | -3.2846e-10 | -5.9452 | 5.9452 | 7.0579 | 7.7097 | -4.1807 | 108.2117 | -71.7883 | -71.7883 | -71.7883 | 108.2117 | 108.2117 |  | 0 | 0.95263 | 0.95263 | 0.23557 | 0.91271 | 1.0048 | 0 | -90 | 90 | -23.1798 | -96.813 | 96.1858
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.9295e-10 | 2.7757e-10 | -1.6557e-10 | -8.9281e-10 | -2.7687e-10 | 1.6474e-10 | -4.5341e-10 | 5.3372e-10 | -6.4128e-10 | 4.5357e-10 | -5.3405e-10 | 6.4146e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.23557 | 0.91271 | 1.0048 | 0.23557 | 0.91271 | 1.0048 | -23.1798 | -96.813 | 96.1858 | -23.1798 | -96.813 | 96.1858

## LG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 3.4587 | 1.7293 | 1.7293 | 3.4587 | 1.7293 | 1.7293 | 39.9376 | 19.9688 | 19.9688 | 39.9376 | 19.9688 | 19.9688 | 12.4411 | -14.9597 | 21.1802 | -6.2205 | 16.5148 | -19.6251 | 14.1159 | 9.4742 | -2.4162 | -7.0579 | -7.7097 | 4.1807 | -71.7883 | 108.2117 | 108.2117 | 108.2117 | -71.7883 | -71.7883 |  | 0.47113 | 0.88675 | 1.0675 | 0.23557 | 0.91271 | 1.0048 | -23.1798 | -104.1349 | 101.7036 | -23.1798 | -96.813 | 96.1858
Line_1 | 3.4587 | 1.7293 | 1.7293 | 3.4587 | 1.7293 | 1.7293 | 39.9376 | 19.9688 | 19.9688 | 39.9376 | 19.9688 | 19.9688 | 4.6138e-10 | 18.0699 | -18.0699 | 6.2205 | -16.5148 | 19.6251 | -3.2846e-10 | -5.9452 | 5.9452 | 7.0579 | 7.7097 | -4.1807 | 108.2117 | -71.7883 | -71.7883 | -71.7883 | 108.2117 | 108.2117 |  | 0 | 0.95263 | 0.95263 | 0.23557 | 0.91271 | 1.0048 | 0 | -90 | 90 | -23.1798 | -96.813 | 96.1858
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.9295e-10 | 2.7757e-10 | -1.6557e-10 | -8.9281e-10 | -2.7687e-10 | 1.6474e-10 | -4.5341e-10 | 5.3372e-10 | -6.4128e-10 | 4.5357e-10 | -5.3405e-10 | 6.4146e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.23557 | 0.91271 | 1.0048 | 0.23557 | 0.91271 | 1.0048 | -23.1798 | -96.813 | 96.1858 | -23.1798 | -96.813 | 96.1858

## LG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.90836 | 0.45418 | 0.45418 | 0.90836 | 0.45418 | 0.45418 | 10.4888 | 5.2444 | 5.2444 | 10.4888 | 5.2444 | 5.2444 | 7.0465 | -2.1644 | 5.6876 | -6.6174 | 2.2716 | -5.5803 | 7.162 | 4.8802 | -1.2992 | -6.6752 | -4.7585 | 1.4209 | -51.7978 | 128.2022 | 128.2022 | 128.2022 | -51.7978 | -51.7978 |  | 0.9579 | 1.018 | 1.1124 | 0.89613 | 1.0054 | 1.098 | -6.332 | -117.8804 | 115.3351 | -6.5488 | -116.2786 | 113.9167
Line_1 | 0.90836 | 0.45418 | 0.45418 | 0.90836 | 0.45418 | 0.45418 | 10.4888 | 5.2444 | 5.2444 | 10.4888 | 5.2444 | 5.2444 | -6.1883 | 2.3789 | -5.4731 | 6.6174 | -2.2716 | 5.5803 | -6.1883 | -4.6368 | 1.5426 | 6.6752 | 4.7585 | -1.4209 | 128.2022 | -51.7978 | -51.7978 | -51.7978 | 128.2022 | 128.2022 |  | 0.83438 | 0.99371 | 1.0843 | 0.89613 | 1.0054 | 1.098 | -6.7978 | -114.6376 | 112.4615 | -6.5488 | -116.2786 | 113.9167
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.6405e-10 | 1.6013e-10 | -5.4736e-11 | -8.6391e-10 | -1.6003e-10 | 5.45e-11 | -5.045e-10 | 6.8191e-11 | -1.8202e-10 | 5.0464e-10 | -6.8389e-11 | 1.8207e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.89613 | 1.0054 | 1.098 | 0.89613 | 1.0054 | 1.098 | -6.5488 | -116.2786 | 113.9167 | -6.5488 | -116.2786 | 113.9167

## LG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.90836 | 0.45418 | 0.45418 | 0.90836 | 0.45418 | 0.45418 | 10.4888 | 5.2444 | 5.2444 | 10.4888 | 5.2444 | 5.2444 | 7.0465 | -2.1644 | 5.6876 | -6.6174 | 2.2716 | -5.5803 | 7.162 | 4.8802 | -1.2992 | -6.6752 | -4.7585 | 1.4209 | -51.7978 | 128.2022 | 128.2022 | 128.2022 | -51.7978 | -51.7978 |  | 0.9579 | 1.018 | 1.1124 | 0.89613 | 1.0054 | 1.098 | -6.332 | -117.8804 | 115.3351 | -6.5488 | -116.2786 | 113.9167
Line_1 | 0.90836 | 0.45418 | 0.45418 | 0.90836 | 0.45418 | 0.45418 | 10.4888 | 5.2444 | 5.2444 | 10.4888 | 5.2444 | 5.2444 | -6.1883 | 2.3789 | -5.4731 | 6.6174 | -2.2716 | 5.5803 | -6.1883 | -4.6368 | 1.5426 | 6.6752 | 4.7585 | -1.4209 | 128.2022 | -51.7978 | -51.7978 | -51.7978 | 128.2022 | 128.2022 |  | 0.83438 | 0.99371 | 1.0843 | 0.89613 | 1.0054 | 1.098 | -6.7978 | -114.6376 | 112.4615 | -6.5488 | -116.2786 | 113.9167
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.6405e-10 | 1.6013e-10 | -5.4736e-11 | -8.6391e-10 | -1.6003e-10 | 5.45e-11 | -5.045e-10 | 6.8191e-11 | -1.8202e-10 | 5.0464e-10 | -6.8389e-11 | 1.8207e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.89613 | 1.0054 | 1.098 | 0.89613 | 1.0054 | 1.098 | -6.5488 | -116.2786 | 113.9167 | -6.5488 | -116.2786 | 113.9167

## LG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 2.7686 | 1.3843 | 1.3843 | 2.7686 | 1.3843 | 1.3843 | 31.9686 | 15.9843 | 15.9843 | 31.9686 | 15.9843 | 15.9843 | 15.3053 | -8.1101 | 15.7628 | -7.6527 | 10.0233 | -13.8496 | 9.0446 | 9.2714 | -4.7491 | -4.5223 | -8.1408 | 5.8797 | -59.5744 | 120.4256 | 120.4256 | 120.4256 | -59.5744 | -59.5744 |  | 0.55611 | 0.77063 | 1.0299 | 0.27805 | 0.80784 | 0.9413 | -28.9937 | -108.3967 | 103.6588 | -28.9937 | -98.6576 | 97.4226
Line_1 | 2.7686 | 1.3843 | 1.3843 | 2.7686 | 1.3843 | 1.3843 | 31.9686 | 15.9843 | 15.9843 | 31.9686 | 15.9843 | 15.9843 | -1.839e-10 | 11.9365 | -11.9365 | 7.6527 | -10.0233 | 13.8496 | -3.9448e-11 | -7.0103 | 7.0103 | 4.5223 | 8.1408 | -5.8797 | 120.4256 | -59.5744 | -59.5744 | -59.5744 | 120.4256 | 120.4256 |  | 0 | 0.86603 | 0.86603 | 0.27805 | 0.80784 | 0.9413 | 0 | -90 | 90 | -28.9937 | -98.6576 | 97.4226
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.9114e-10 | 2.0299e-10 | 1.8266e-11 | -6.9098e-10 | -2.0256e-10 | -1.8862e-11 | -5.8475e-10 | 7.608e-10 | -9.1731e-10 | 5.8485e-10 | -7.6115e-10 | 9.1757e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.27805 | 0.80784 | 0.9413 | 0.27805 | 0.80784 | 0.9413 | -28.9937 | -98.6576 | 97.4226 | -28.9937 | -98.6576 | 97.4226

## LG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 2.7686 | 1.3843 | 1.3843 | 2.7686 | 1.3843 | 1.3843 | 31.9686 | 15.9843 | 15.9843 | 31.9686 | 15.9843 | 15.9843 | 15.3053 | -8.1101 | 15.7628 | -7.6527 | 10.0233 | -13.8496 | 9.0446 | 9.2714 | -4.7491 | -4.5223 | -8.1408 | 5.8797 | -59.5744 | 120.4256 | 120.4256 | 120.4256 | -59.5744 | -59.5744 |  | 0.55611 | 0.77063 | 1.0299 | 0.27805 | 0.80784 | 0.9413 | -28.9937 | -108.3967 | 103.6588 | -28.9937 | -98.6576 | 97.4226
Line_1 | 2.7686 | 1.3843 | 1.3843 | 2.7686 | 1.3843 | 1.3843 | 31.9686 | 15.9843 | 15.9843 | 31.9686 | 15.9843 | 15.9843 | -1.839e-10 | 11.9365 | -11.9365 | 7.6527 | -10.0233 | 13.8496 | -3.9448e-11 | -7.0103 | 7.0103 | 4.5223 | 8.1408 | -5.8797 | 120.4256 | -59.5744 | -59.5744 | -59.5744 | 120.4256 | 120.4256 |  | 0 | 0.86603 | 0.86603 | 0.27805 | 0.80784 | 0.9413 | 0 | -90 | 90 | -28.9937 | -98.6576 | 97.4226
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.9114e-10 | 2.0299e-10 | 1.8266e-11 | -6.9098e-10 | -2.0256e-10 | -1.8862e-11 | -5.8475e-10 | 7.608e-10 | -9.1731e-10 | 5.8485e-10 | -7.6115e-10 | 9.1757e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.27805 | 0.80784 | 0.9413 | 0.27805 | 0.80784 | 0.9413 | -28.9937 | -98.6576 | 97.4226 | -28.9937 | -98.6576 | 97.4226

## LG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.78654 | 0.39327 | 0.39327 | 0.78654 | 0.39327 | 0.39327 | 9.0822 | 4.5411 | 4.5411 | 9.0822 | 4.5411 | 4.5411 | 5.8752 | -1.5037 | 4.4413 | -5.2575 | 1.6582 | -4.2869 | 5.3699 | 3.9174 | -1.2325 | -5.0049 | -3.8261 | 1.3237 | -49.0996 | 130.9004 | 130.9004 | 130.9004 | -49.0996 | -49.0996 |  | 0.87638 | 0.92403 | 1.015 | 0.79923 | 0.91828 | 0.988 | -6.6725 | -118.0997 | 115.3912 | -5.5099 | -115.6689 | 113.7408
Line_1 | 0.78654 | 0.39327 | 0.39327 | 0.78654 | 0.39327 | 0.39327 | 9.0822 | 4.5411 | 4.5411 | 9.0822 | 4.5411 | 4.5411 | -4.6399 | 1.8126 | -4.1325 | 5.2575 | -1.6582 | 4.2869 | -4.6399 | -3.7349 | 1.415 | 5.0049 | 3.8261 | -1.3237 | 130.9004 | -49.0996 | -49.0996 | -49.0996 | 130.9004 | 130.9004 |  | 0.72249 | 0.9142 | 0.96189 | 0.79923 | 0.91828 | 0.988 | -4.0996 | -113.212 | 111.9993 | -5.5099 | -115.6689 | 113.7408
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.574e-10 | 1.7155e-10 | 3.3268e-11 | -6.5729e-10 | -1.7148e-10 | -3.3451e-11 | -3.3821e-10 | 1.877e-10 | -2.7156e-10 | 3.3831e-10 | -1.8787e-10 | 2.7162e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.79923 | 0.91828 | 0.988 | 0.79923 | 0.91828 | 0.988 | -5.5099 | -115.6689 | 113.7408 | -5.5099 | -115.6689 | 113.7408

## LG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.78654 | 0.39327 | 0.39327 | 0.78654 | 0.39327 | 0.39327 | 9.0822 | 4.5411 | 4.5411 | 9.0822 | 4.5411 | 4.5411 | 5.8752 | -1.5037 | 4.4413 | -5.2575 | 1.6582 | -4.2869 | 5.3699 | 3.9174 | -1.2325 | -5.0049 | -3.8261 | 1.3237 | -49.0996 | 130.9004 | 130.9004 | 130.9004 | -49.0996 | -49.0996 |  | 0.87638 | 0.92403 | 1.015 | 0.79923 | 0.91828 | 0.988 | -6.6725 | -118.0997 | 115.3912 | -5.5099 | -115.6689 | 113.7408
Line_1 | 0.78654 | 0.39327 | 0.39327 | 0.78654 | 0.39327 | 0.39327 | 9.0822 | 4.5411 | 4.5411 | 9.0822 | 4.5411 | 4.5411 | -4.6399 | 1.8126 | -4.1325 | 5.2575 | -1.6582 | 4.2869 | -4.6399 | -3.7349 | 1.415 | 5.0049 | 3.8261 | -1.3237 | 130.9004 | -49.0996 | -49.0996 | -49.0996 | 130.9004 | 130.9004 |  | 0.72249 | 0.9142 | 0.96189 | 0.79923 | 0.91828 | 0.988 | -4.0996 | -113.212 | 111.9993 | -5.5099 | -115.6689 | 113.7408
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.574e-10 | 1.7155e-10 | 3.3268e-11 | -6.5729e-10 | -1.7148e-10 | -3.3451e-11 | -3.3821e-10 | 1.877e-10 | -2.7156e-10 | 3.3831e-10 | -1.8787e-10 | 2.7162e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.79923 | 0.91828 | 0.988 | 0.79923 | 0.91828 | 0.988 | -5.5099 | -115.6689 | 113.7408 | -5.5099 | -115.6689 | 113.7408

## LLG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 3.4587 | 3.4587 | 3.4587 | 3.4587 | 3.4587 | 3.4587 | 39.9376 | 39.9376 | 39.9376 | 39.9376 | 39.9376 | 39.9376 | 12.4411 | 12.4411 | 12.4411 | -6.2205 | -6.2205 | -6.2205 | 14.1159 | 14.1159 | 14.1159 | -7.0579 | -7.0579 | -7.0579 | -71.7883 | 168.2117 | 48.2117 | 108.2117 | -11.7883 | -131.7883 |  | 0.47113 | 0.47113 | 0.47113 | 0.23557 | 0.23557 | 0.23557 | -23.1798 | -143.1798 | 96.8202 | -23.1798 | -143.1798 | 96.8202
Line_1 | 3.4587 | 3.4587 | 3.4587 | 3.4587 | 3.4587 | 3.4587 | 39.9376 | 39.9376 | 39.9376 | 39.9376 | 39.9376 | 39.9376 | 5.4091e-10 | 5.3886e-10 | 5.365e-10 | 6.2205 | 6.2205 | 6.2205 | -1.469e-08 | -3.3669e-10 | -3.3675e-10 | 7.0579 | 7.0579 | 7.0579 | 108.2117 | -11.7883 | -131.7883 | -71.7883 | 168.2117 | 48.2117 |  | 0 | 0 | 0 | 0.23557 | 0.23557 | 0.23557 | 0 | 0 | 0 | -23.1798 | -143.1798 | 96.8202
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2395e-10 | 1.0306e-09 | 7.5536e-10 | -2.2421e-10 | -1.0307e-09 | -7.5495e-10 | -2.151e-10 | -6.7159e-11 | -8.3969e-10 | 2.148e-10 | 6.7552e-11 | 8.3961e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.23557 | 0.23557 | 0.23557 | 0.23557 | 0.23557 | 0.23557 | -23.1798 | -143.1798 | 96.8202 | -23.1798 | -143.1798 | 96.8202

## LLG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 3.4587 | 3.4587 | 3.4587 | 3.4587 | 3.4587 | 3.4587 | 39.9376 | 39.9376 | 39.9376 | 39.9376 | 39.9376 | 39.9376 | 12.4411 | 12.4411 | 12.4411 | -6.2205 | -6.2205 | -6.2205 | 14.1159 | 14.1159 | 14.1159 | -7.0579 | -7.0579 | -7.0579 | -71.7883 | 168.2117 | 48.2117 | 108.2117 | -11.7883 | -131.7883 |  | 0.47113 | 0.47113 | 0.47113 | 0.23557 | 0.23557 | 0.23557 | -23.1798 | -143.1798 | 96.8202 | -23.1798 | -143.1798 | 96.8202
Line_1 | 3.4587 | 3.4587 | 3.4587 | 3.4587 | 3.4587 | 3.4587 | 39.9376 | 39.9376 | 39.9376 | 39.9376 | 39.9376 | 39.9376 | 5.4091e-10 | 5.3886e-10 | 5.365e-10 | 6.2205 | 6.2205 | 6.2205 | -1.469e-08 | -3.3669e-10 | -3.3675e-10 | 7.0579 | 7.0579 | 7.0579 | 108.2117 | -11.7883 | -131.7883 | -71.7883 | 168.2117 | 48.2117 |  | 0 | 0 | 0 | 0.23557 | 0.23557 | 0.23557 | 0 | 0 | 0 | -23.1798 | -143.1798 | 96.8202
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2395e-10 | 1.0306e-09 | 7.5536e-10 | -2.2421e-10 | -1.0307e-09 | -7.5495e-10 | -2.151e-10 | -6.7159e-11 | -8.3969e-10 | 2.148e-10 | 6.7552e-11 | 8.3961e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.23557 | 0.23557 | 0.23557 | 0.23557 | 0.23557 | 0.23557 | -23.1798 | -143.1798 | 96.8202 | -23.1798 | -143.1798 | 96.8202

## LLG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.51744 | 1.1036 | 1.0579 | 0.51744 | 1.1036 | 1.0579 | 5.9749 | 12.7429 | 12.215 | 5.9749 | 12.7429 | 12.215 | 4.2946 | 10.9764 | 4.4773 | -4.1553 | -10.3431 | -3.8954 | 4.3321 | 5.7387 | 10.0421 | -4.1741 | -5.0202 | -9.3819 | -48.8662 | -157.5874 | 50.0104 | 131.1338 | 22.4126 | -129.9896 |  | 1.0209 | 0.97199 | 0.90012 | 0.98577 | 0.90223 | 0.83163 | -3.6172 | -129.9857 | 115.9806 | -3.7372 | -131.697 | 117.462
Line_1 | 0.51744 | 1.1036 | 1.0579 | 0.51744 | 1.1036 | 1.0579 | 5.9749 | 12.7429 | 12.215 | 5.9749 | 12.7429 | 12.215 | -4.0161 | -9.7098 | -3.3135 | 4.1553 | 10.3431 | 3.8954 | -4.0161 | -4.3016 | -8.7216 | 4.1741 | 5.0202 | 9.3819 | 131.1338 | 22.4126 | -129.9896 | -48.8662 | -157.5874 | 50.0104 |  | 0.95059 | 0.8334 | 0.7638 | 0.98577 | 0.90223 | 0.83163 | -3.8662 | -133.693 | 119.2079 | -3.7372 | -131.697 | 117.462
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3175e-10 | 8.161e-10 | 8.5032e-10 | -1.3193e-10 | -8.1613e-10 | -8.5011e-10 | -1.4291e-10 | -6.0642e-10 | -3.9612e-10 | 1.4274e-10 | 6.0665e-10 | 3.9607e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.98577 | 0.90223 | 0.83163 | 0.98577 | 0.90223 | 0.83163 | -3.7372 | -131.697 | 117.462 | -3.7372 | -131.697 | 117.462

## LLG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.51744 | 1.1036 | 1.0579 | 0.51744 | 1.1036 | 1.0579 | 5.9749 | 12.7429 | 12.215 | 5.9749 | 12.7429 | 12.215 | 4.2946 | 10.9764 | 4.4773 | -4.1553 | -10.3431 | -3.8954 | 4.3321 | 5.7387 | 10.0421 | -4.1741 | -5.0202 | -9.3819 | -48.8662 | -157.5874 | 50.0104 | 131.1338 | 22.4126 | -129.9896 |  | 1.0209 | 0.97199 | 0.90012 | 0.98577 | 0.90223 | 0.83163 | -3.6172 | -129.9857 | 115.9806 | -3.7372 | -131.697 | 117.462
Line_1 | 0.51744 | 1.1036 | 1.0579 | 0.51744 | 1.1036 | 1.0579 | 5.9749 | 12.7429 | 12.215 | 5.9749 | 12.7429 | 12.215 | -4.0161 | -9.7098 | -3.3135 | 4.1553 | 10.3431 | 3.8954 | -4.0161 | -4.3016 | -8.7216 | 4.1741 | 5.0202 | 9.3819 | 131.1338 | 22.4126 | -129.9896 | -48.8662 | -157.5874 | 50.0104 |  | 0.95059 | 0.8334 | 0.7638 | 0.98577 | 0.90223 | 0.83163 | -3.8662 | -133.693 | 119.2079 | -3.7372 | -131.697 | 117.462
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3175e-10 | 8.161e-10 | 8.5032e-10 | -1.3193e-10 | -8.1613e-10 | -8.5011e-10 | -1.4291e-10 | -6.0642e-10 | -3.9612e-10 | 1.4274e-10 | 6.0665e-10 | 3.9607e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.98577 | 0.90223 | 0.83163 | 0.98577 | 0.90223 | 0.83163 | -3.7372 | -131.697 | 117.462 | -3.7372 | -131.697 | 117.462

## LLG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 2.7686 | 2.7686 | 2.7686 | 2.7686 | 2.7686 | 2.7686 | 31.9686 | 31.9686 | 31.9686 | 31.9686 | 31.9686 | 31.9686 | 15.3053 | 15.3053 | 15.3053 | -7.6527 | -7.6527 | -7.6527 | 9.0446 | 9.0446 | 9.0446 | -4.5223 | -4.5223 | -4.5223 | -59.5744 | -179.5744 | 60.4256 | 120.4256 | 0.42557 | -119.5744 |  | 0.55611 | 0.55611 | 0.55611 | 0.27805 | 0.27805 | 0.27805 | -28.9937 | -148.9937 | 91.0063 | -28.9937 | -148.9937 | 91.0063
Line_1 | 2.7686 | 2.7686 | 2.7686 | 2.7686 | 2.7686 | 2.7686 | 31.9686 | 31.9686 | 31.9686 | 31.9686 | 31.9686 | 31.9686 | -2.6575e-10 | -2.6717e-10 | -2.6936e-10 | 7.6527 | 7.6527 | 7.6527 | -9.4054e-09 | -2.0895e-10 | -2.0874e-10 | 4.5223 | 4.5223 | 4.5223 | 120.4256 | 0.42557 | -119.5744 | -59.5744 | -179.5744 | 60.4256 |  | 0 | 0 | 0 | 0.27805 | 0.27805 | 0.27805 | 0 | 0 | 0 | -28.9937 | -148.9937 | 91.0063
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4251e-10 | 8.4803e-10 | 5.3427e-10 | -4.4284e-10 | -8.4803e-10 | -5.3394e-10 | -3.1303e-10 | -4.412e-10 | -7.283e-10 | 3.1284e-10 | 4.4158e-10 | 7.2812e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.27805 | 0.27805 | 0.27805 | 0.27805 | 0.27805 | 0.27805 | -28.9937 | -148.9937 | 91.0063 | -28.9937 | -148.9937 | 91.0063

## LLG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 2.7686 | 2.7686 | 2.7686 | 2.7686 | 2.7686 | 2.7686 | 31.9686 | 31.9686 | 31.9686 | 31.9686 | 31.9686 | 31.9686 | 15.3053 | 15.3053 | 15.3053 | -7.6527 | -7.6527 | -7.6527 | 9.0446 | 9.0446 | 9.0446 | -4.5223 | -4.5223 | -4.5223 | -59.5744 | -179.5744 | 60.4256 | 120.4256 | 0.42557 | -119.5744 |  | 0.55611 | 0.55611 | 0.55611 | 0.27805 | 0.27805 | 0.27805 | -28.9937 | -148.9937 | 91.0063 | -28.9937 | -148.9937 | 91.0063
Line_1 | 2.7686 | 2.7686 | 2.7686 | 2.7686 | 2.7686 | 2.7686 | 31.9686 | 31.9686 | 31.9686 | 31.9686 | 31.9686 | 31.9686 | -2.6575e-10 | -2.6717e-10 | -2.6936e-10 | 7.6527 | 7.6527 | 7.6527 | -9.4054e-09 | -2.0895e-10 | -2.0874e-10 | 4.5223 | 4.5223 | 4.5223 | 120.4256 | 0.42557 | -119.5744 | -59.5744 | -179.5744 | 60.4256 |  | 0 | 0 | 0 | 0.27805 | 0.27805 | 0.27805 | 0 | 0 | 0 | -28.9937 | -148.9937 | 91.0063
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4251e-10 | 8.4803e-10 | 5.3427e-10 | -4.4284e-10 | -8.4803e-10 | -5.3394e-10 | -3.1303e-10 | -4.412e-10 | -7.283e-10 | 3.1284e-10 | 4.4158e-10 | 7.2812e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.27805 | 0.27805 | 0.27805 | 0.27805 | 0.27805 | 0.27805 | -28.9937 | -148.9937 | 91.0063 | -28.9937 | -148.9937 | 91.0063

## LLG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.45692 | 0.93653 | 0.91322 | 0.45692 | 0.93653 | 0.91322 | 5.276 | 10.8141 | 10.545 | 5.276 | 10.8141 | 10.545 | 3.5485 | 8.8113 | 4.2045 | -3.34 | -7.9357 | -3.3718 | 3.3779 | 4.0053 | 7.6129 | -3.2548 | -3.4878 | -7.1209 | -47.3802 | -154.497 | 54.0693 | 132.6198 | 25.503 | -125.9307 |  | 0.92858 | 0.89503 | 0.82473 | 0.88393 | 0.80157 | 0.74716 | -3.7905 | -130.0522 | 115.1582 | -3.1209 | -130.7708 | 118.731
Line_1 | 0.45692 | 0.93653 | 0.91322 | 0.45692 | 0.93653 | 0.91322 | 5.276 | 10.8141 | 10.545 | 5.276 | 10.8141 | 10.545 | -3.1316 | -7.06 | -2.5392 | 3.34 | 7.9357 | 3.3718 | -3.1316 | -2.9704 | -6.6288 | 3.2548 | 3.4878 | 7.1209 | 132.6198 | 25.503 | -125.9307 | -47.3802 | -154.497 | 54.0693 |  | 0.83941 | 0.70828 | 0.67316 | 0.88393 | 0.80157 | 0.74716 | -2.3802 | -131.679 | 123.1098 | -3.1209 | -130.7708 | 118.731
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6441e-10 | 6.4222e-10 | 6.8817e-10 | -2.6456e-10 | -6.4224e-10 | -6.88e-10 | -1.0466e-10 | -5.1222e-10 | -1.695e-10 | 1.0452e-10 | 5.124e-10 | 1.6946e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.88393 | 0.80157 | 0.74716 | 0.88393 | 0.80157 | 0.74716 | -3.1209 | -130.7708 | 118.731 | -3.1209 | -130.7708 | 118.731

## LLG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.45692 | 0.93653 | 0.91322 | 0.45692 | 0.93653 | 0.91322 | 5.276 | 10.8141 | 10.545 | 5.276 | 10.8141 | 10.545 | 3.5485 | 8.8113 | 4.2045 | -3.34 | -7.9357 | -3.3718 | 3.3779 | 4.0053 | 7.6129 | -3.2548 | -3.4878 | -7.1209 | -47.3802 | -154.497 | 54.0693 | 132.6198 | 25.503 | -125.9307 |  | 0.92858 | 0.89503 | 0.82473 | 0.88393 | 0.80157 | 0.74716 | -3.7905 | -130.0522 | 115.1582 | -3.1209 | -130.7708 | 118.731
Line_1 | 0.45692 | 0.93653 | 0.91322 | 0.45692 | 0.93653 | 0.91322 | 5.276 | 10.8141 | 10.545 | 5.276 | 10.8141 | 10.545 | -3.1316 | -7.06 | -2.5392 | 3.34 | 7.9357 | 3.3718 | -3.1316 | -2.9704 | -6.6288 | 3.2548 | 3.4878 | 7.1209 | 132.6198 | 25.503 | -125.9307 | -47.3802 | -154.497 | 54.0693 |  | 0.83941 | 0.70828 | 0.67316 | 0.88393 | 0.80157 | 0.74716 | -2.3802 | -131.679 | 123.1098 | -3.1209 | -130.7708 | 118.731
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6441e-10 | 6.4222e-10 | 6.8817e-10 | -2.6456e-10 | -6.4224e-10 | -6.88e-10 | -1.0466e-10 | -5.1222e-10 | -1.695e-10 | 1.0452e-10 | 5.124e-10 | 1.6946e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.88393 | 0.80157 | 0.74716 | 0.88393 | 0.80157 | 0.74716 | -3.1209 | -130.7708 | 118.731 | -3.1209 | -130.7708 | 118.731