## LLL_max_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 3.6999 | 3.6999 | 0 | 0 | 128.1693 | 128.1693 | 35.5926 | -14.237 | 40.3839 | -16.1536 | -73.5107 | 106.4893 | 0.41999 | 0.168 | -24.9022 | -24.9022
Line_1 | 2.4666 | 2.4666 | 4.9647 | 0 | 85.4462 | 85.4462 | -1e-07 | 9.4914 | -1e-07 | 10.769 | 106.4893 | -73.5107 | 0 | 0.168 | 0 | -24.9022
Line_2 | 1.2333 | 1.2333 | 0 | 0 | 42.7231 | 42.7231 | -2.3728 | 4.7457 | -2.6923 | 5.3845 | 106.4893 | -73.5107 | 0.083999 | 0.168 | -24.9022 | -24.9022
Line_3 | 1.2333 | 1.2333 | 2.4824 | 0 | 42.7231 | 42.7231 | -1e-07 | 2.3728 | -1e-07 | 2.6923 | 106.4893 | -73.5107 | 0 | 0.083999 | 0 | -24.9022

## LLL_max_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 3.6999 | 3.6999 | 0 | 0 | 128.1693 | 128.1693 | 35.5926 | -14.237 | 40.3839 | -16.1536 | -73.5107 | 106.4893 | 0.41999 | 0.168 | -24.9022 | -24.9022
Line_1 | 2.4666 | 2.4666 | 4.9647 | 0 | 85.4462 | 85.4462 | -1e-07 | 9.4914 | -1e-07 | 10.769 | 106.4893 | -73.5107 | 0 | 0.168 | 0 | -24.9022
Line_2 | 1.2333 | 1.2333 | 0 | 0 | 42.7231 | 42.7231 | -2.3728 | 4.7457 | -2.6923 | 5.3845 | 106.4893 | -73.5107 | 0.083999 | 0.168 | -24.9022 | -24.9022
Line_3 | 1.2333 | 1.2333 | 2.4824 | 0 | 42.7231 | 42.7231 | -1e-07 | 2.3728 | -1e-07 | 2.6923 | 106.4893 | -73.5107 | 0 | 0.083999 | 0 | -24.9022

## LLL_max_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 1.2428 | 1.2428 | 0 | 0 | 43.0531 | 43.0531 | 27.1857 | -24.7761 | 27.7264 | -24.9923 | -54.2264 | 125.7736 | 0.90192 | 0.81741 | -8.6624 | -8.9775
Line_1 | 0.82856 | 0.82856 | 1.6677 | 0 | 28.7021 | 28.7021 | -15.4464 | 16.5174 | -15.4464 | 16.6616 | 125.7736 | -54.2264 | 0.76108 | 0.81741 | -9.2264 | -8.9775
Line_2 | 0.41428 | 0.41428 | 0 | 0 | 14.351 | 14.351 | -7.991 | 8.2587 | -8.027 | 8.3308 | 125.7736 | -54.2264 | 0.78924 | 0.81741 | -9.0975 | -8.9775
Line_3 | 0.41428 | 0.41428 | 0.83384 | 0 | 14.351 | 14.351 | -7.7232 | 7.991 | -7.7232 | 8.027 | 125.7736 | -54.2264 | 0.76108 | 0.78924 | -9.2264 | -9.0975

## LLL_max_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 1.2428 | 1.2428 | 0 | 0 | 43.0531 | 43.0531 | 27.1857 | -24.7761 | 27.7264 | -24.9923 | -54.2264 | 125.7736 | 0.90192 | 0.81741 | -8.6624 | -8.9775
Line_1 | 0.82856 | 0.82856 | 1.6677 | 0 | 28.7021 | 28.7021 | -15.4464 | 16.5174 | -15.4464 | 16.6616 | 125.7736 | -54.2264 | 0.76108 | 0.81741 | -9.2264 | -8.9775
Line_2 | 0.41428 | 0.41428 | 0 | 0 | 14.351 | 14.351 | -7.991 | 8.2587 | -8.027 | 8.3308 | 125.7736 | -54.2264 | 0.78924 | 0.81741 | -9.0975 | -8.9775
Line_3 | 0.41428 | 0.41428 | 0.83384 | 0 | 14.351 | 14.351 | -7.7232 | 7.991 | -7.7232 | 8.027 | 125.7736 | -54.2264 | 0.76108 | 0.78924 | -9.2264 | -9.0975

## LLL_min_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 3.0092 | 3.0092 | 0 | 0 | 104.2421 | 104.2421 | 45.2043 | -18.0817 | 26.7133 | -10.6853 | -62.3733 | 117.6267 | 0.50371 | 0.20148 | -31.7926 | -31.7926
Line_1 | 2.0061 | 2.0061 | 3.4722 | 0 | 69.4947 | 69.4947 | -1e-07 | 12.0545 | -1e-07 | 7.1235 | 117.6267 | -62.3733 | 0 | 0.20148 | 0 | -31.7926
Line_2 | 1.0031 | 1.0031 | 0 | 0 | 34.7474 | 34.7474 | -3.0136 | 6.0272 | -1.7809 | 3.5618 | 117.6267 | -62.3733 | 0.10074 | 0.20148 | -31.7926 | -31.7926
Line_3 | 1.0031 | 1.0031 | 1.7361 | 0 | 34.7474 | 34.7474 | -1e-07 | 3.0136 | -1e-07 | 1.7809 | 117.6267 | -62.3733 | 0 | 0.10074 | 0 | -31.7926

## LLL_min_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 3.0092 | 3.0092 | 0 | 0 | 104.2421 | 104.2421 | 45.2043 | -18.0817 | 26.7133 | -10.6853 | -62.3733 | 117.6267 | 0.50371 | 0.20148 | -31.7926 | -31.7926
Line_1 | 2.0061 | 2.0061 | 3.4722 | 0 | 69.4947 | 69.4947 | -1e-07 | 12.0545 | -1e-07 | 7.1235 | 117.6267 | -62.3733 | 0 | 0.20148 | 0 | -31.7926
Line_2 | 1.0031 | 1.0031 | 0 | 0 | 34.7474 | 34.7474 | -3.0136 | 6.0272 | -1.7809 | 3.5618 | 117.6267 | -62.3733 | 0.10074 | 0.20148 | -31.7926 | -31.7926
Line_3 | 1.0031 | 1.0031 | 1.7361 | 0 | 34.7474 | 34.7474 | -1e-07 | 3.0136 | -1e-07 | 1.7809 | 117.6267 | -62.3733 | 0 | 0.10074 | 0 | -31.7926

## LLL_min_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 1.0697 | 1.0697 | 0 | 0 | 37.0569 | 37.0569 | 22.8777 | -19.4502 | 20.541 | -18.5155 | -51.0933 | 128.9067 | 0.8297 | 0.72467 | -9.1739 | -7.5036
Line_1 | 0.71316 | 0.71316 | 1.2343 | 0 | 24.7046 | 24.7046 | -11.4434 | 12.9668 | -11.4434 | 12.3437 | 128.9067 | -51.0933 | 0.65508 | 0.72467 | -6.0933 | -7.5036
Line_2 | 0.35658 | 0.35658 | 0 | 0 | 12.3523 | 12.3523 | -6.1026 | 6.4834 | -5.9468 | 6.1718 | 128.9067 | -51.0933 | 0.68982 | 0.72467 | -6.834 | -7.5036
Line_3 | 0.35658 | 0.35658 | 0.61717 | 0 | 12.3523 | 12.3523 | -5.7217 | 6.1026 | -5.7217 | 5.9468 | 128.9067 | -51.0933 | 0.65508 | 0.68982 | -6.0933 | -6.834

## LLL_min_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 1.0697 | 1.0697 | 0 | 0 | 37.0569 | 37.0569 | 22.8777 | -19.4502 | 20.541 | -18.5155 | -51.0933 | 128.9067 | 0.8297 | 0.72467 | -9.1739 | -7.5036
Line_1 | 0.71316 | 0.71316 | 1.2343 | 0 | 24.7046 | 24.7046 | -11.4434 | 12.9668 | -11.4434 | 12.3437 | 128.9067 | -51.0933 | 0.65508 | 0.72467 | -6.0933 | -7.5036
Line_2 | 0.35658 | 0.35658 | 0 | 0 | 12.3523 | 12.3523 | -6.1026 | 6.4834 | -5.9468 | 6.1718 | 128.9067 | -51.0933 | 0.68982 | 0.72467 | -6.834 | -7.5036
Line_3 | 0.35658 | 0.35658 | 0.61717 | 0 | 12.3523 | 12.3523 | -5.7217 | 6.1026 | -5.7217 | 5.9468 | 128.9067 | -51.0933 | 0.65508 | 0.68982 | -6.0933 | -6.834

## LL_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 3.2042 | 3.2042 | 0 | 3.2042 | 3.2042 | 0 | 36.9993 | 36.9993 | 0 | 36.9993 | 36.9993 | -5.2106e-15 | 28.4108 | -10.6145 | -1.6977e-28 | -23.0719 | 15.9534 | -5.2106e-15 | 4.32 | 15.8719 | 1.0421e-14 | 1.7376 | -9.8143 | 0 | -163.5107 | 16.4893 | 0 | 16.4893 | -163.5107 | 1.1 | 0.7767 | 0.51607 | 1.1 | 0.62534 | 0.50624 | 9.2244e-13 | -154.8648 | 140.2623 | 9.3339e-13 | -167.8176 | 164.89
Line_1 | 0 | 2.1362 | 2.1362 | 0 | 2.1362 | 2.1362 | 0 | 24.6662 | 24.6662 | 0 | 24.6662 | 24.6662 | 3.5194e-28 | -13.0085 | 13.0085 | -1.0421e-14 | 15.3813 | -10.6356 | -2.0843e-14 | 3.8506 | -3.8506 | 3.1264e-14 | -1.1584 | 6.5429 | 0 | 16.4893 | -163.5107 | 0 | -163.5107 | 16.4893 | 1.1 | 0.55 | 0.55 | 1.1 | 0.62534 | 0.50624 | 9.6746e-13 | 180 | -180 | 9.3339e-13 | -167.8176 | 164.89
Line_2 | 0 | 1.0681 | 1.0681 | 0 | 1.0681 | 1.0681 | 0 | 12.3331 | 12.3331 | 0 | 12.3331 | 12.3331 | -3.1264e-14 | -7.0974 | 5.911 | 2.0843e-14 | 7.6906 | -5.3178 | 3.1264e-14 | 1.2523 | -2.5984 | -2.6053e-14 | -0.57919 | 3.2714 | 0 | 16.4893 | -163.5107 | 0 | -163.5107 | 16.4893 | 1.1 | 0.58437 | 0.52354 | 1.1 | 0.62534 | 0.50624 | 8.7328e-13 | -173.5168 | 172.7598 | 9.3339e-13 | -167.8176 | 164.89
Line_3 | 0 | 1.0681 | 1.0681 | 0 | 1.0681 | 1.0681 | 0 | 12.3331 | 12.3331 | 0 | 12.3331 | 12.3331 | 3.1264e-14 | -6.5042 | 6.5042 | -4.1685e-14 | 7.0974 | -5.911 | -5.2106e-14 | 1.9253 | -1.9253 | 5.7317e-14 | -1.2523 | 2.5984 | 0 | 16.4893 | -163.5107 | 0 | -163.5107 | 16.4893 | 1.1 | 0.55 | 0.55 | 1.1 | 0.58437 | 0.52354 | 9.6746e-13 | 180 | -180 | 8.7328e-13 | -173.5168 | 172.7598

## LL_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 3.2042 | 3.2042 | 0 | 3.2042 | 3.2042 | 0 | 36.9993 | 36.9993 | 0 | 36.9993 | 36.9993 | -5.2106e-15 | 28.4108 | -10.6145 | -1.6977e-28 | -23.0719 | 15.9534 | -5.2106e-15 | 4.32 | 15.8719 | 1.0421e-14 | 1.7376 | -9.8143 | 0 | -163.5107 | 16.4893 | 0 | 16.4893 | -163.5107 | 1.1 | 0.7767 | 0.51607 | 1.1 | 0.62534 | 0.50624 | 9.2244e-13 | -154.8648 | 140.2623 | 9.3339e-13 | -167.8176 | 164.89
Line_1 | 0 | 2.1362 | 2.1362 | 0 | 2.1362 | 2.1362 | 0 | 24.6662 | 24.6662 | 0 | 24.6662 | 24.6662 | 3.5194e-28 | -13.0085 | 13.0085 | -1.0421e-14 | 15.3813 | -10.6356 | -2.0843e-14 | 3.8506 | -3.8506 | 3.1264e-14 | -1.1584 | 6.5429 | 0 | 16.4893 | -163.5107 | 0 | -163.5107 | 16.4893 | 1.1 | 0.55 | 0.55 | 1.1 | 0.62534 | 0.50624 | 9.6746e-13 | 180 | -180 | 9.3339e-13 | -167.8176 | 164.89
Line_2 | 0 | 1.0681 | 1.0681 | 0 | 1.0681 | 1.0681 | 0 | 12.3331 | 12.3331 | 0 | 12.3331 | 12.3331 | -3.1264e-14 | -7.0974 | 5.911 | 2.0843e-14 | 7.6906 | -5.3178 | 3.1264e-14 | 1.2523 | -2.5984 | -2.6053e-14 | -0.57919 | 3.2714 | 0 | 16.4893 | -163.5107 | 0 | -163.5107 | 16.4893 | 1.1 | 0.58437 | 0.52354 | 1.1 | 0.62534 | 0.50624 | 8.7328e-13 | -173.5168 | 172.7598 | 9.3339e-13 | -167.8176 | 164.89
Line_3 | 0 | 1.0681 | 1.0681 | 0 | 1.0681 | 1.0681 | 0 | 12.3331 | 12.3331 | 0 | 12.3331 | 12.3331 | 3.1264e-14 | -6.5042 | 6.5042 | -4.1685e-14 | 7.0974 | -5.911 | -5.2106e-14 | 1.9253 | -1.9253 | 5.7317e-14 | -1.2523 | 2.5984 | 0 | 16.4893 | -163.5107 | 0 | -163.5107 | 16.4893 | 1.1 | 0.55 | 0.55 | 1.1 | 0.58437 | 0.52354 | 9.6746e-13 | 180 | -180 | 8.7328e-13 | -173.5168 | 172.7598

## LL_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 1.6287 | 1.6287 | 0 | 1.6287 | 1.6287 | 0 | 18.8063 | 18.8063 | 0 | 18.8063 | 18.8063 | -2.6053e-15 | 17.8002 | 0.06044 | -2.6053e-15 | -16.4209 | 1.3189 | -1.3027e-14 | 3.9189 | 14.5607 | 1.3027e-14 | -2.3539 | -12.9957 | 0 | -149.0411 | 30.9589 | 0 | 30.9589 | -149.0411 | 1.1 | 0.96917 | 0.77425 | 1.1 | 0.88208 | 0.69458 | 4.5637e-13 | -136.625 | 120.7211 | 4.6068e-13 | -140.8835 | 126.7539
Line_1 | 0 | 1.0858 | 1.0858 | 0 | 1.0858 | 1.0858 | 0 | 12.5375 | 12.5375 | 0 | 12.5375 | 12.5375 | -2.6053e-15 | -10.3342 | 1.4923 | -2.6053e-15 | 10.9473 | -0.87927 | -1.3027e-14 | -0.87368 | -7.9682 | 1.5632e-14 | 1.5692 | 8.6638 | 0 | 30.9589 | -149.0411 | 0 | -149.0411 | 30.9589 | 1.1 | 0.8272 | 0.6466 | 1.1 | 0.88208 | 0.69458 | 4.8256e-13 | -144.2087 | 131.5665 | 4.6068e-13 | -140.8835 | 126.7539
Line_2 | 0 | 0.54289 | 0.54289 | 0 | 0.54289 | 0.54289 | 0 | 6.2688 | 6.2688 | 0 | 6.2688 | 6.2688 | -2.3448e-14 | -5.3204 | 0.59289 | 2.0843e-14 | 5.4736 | -0.43963 | 1.3027e-14 | -0.61073 | -4.158 | -1.0421e-14 | 0.78462 | 4.3319 | 0 | 30.9589 | -149.0411 | 0 | -149.0411 | 30.9589 | 1.1 | 0.85428 | 0.67 | 1.1 | 0.88208 | 0.69458 | 4.2863e-13 | -142.4927 | 129.0741 | 4.6068e-13 | -140.8835 | 126.7539
Line_3 | 0 | 0.54289 | 0.54289 | 0 | 0.54289 | 0.54289 | 0 | 6.2688 | 6.2688 | 0 | 6.2688 | 6.2688 | 2.3448e-14 | -5.1671 | 0.74615 | -2.6053e-14 | 5.3204 | -0.59289 | -2.3448e-14 | -0.43684 | -3.9841 | 2.8659e-14 | 0.61073 | 4.158 | 0 | 30.9589 | -149.0411 | 0 | -149.0411 | 30.9589 | 1.1 | 0.8272 | 0.6466 | 1.1 | 0.85428 | 0.67 | 4.8256e-13 | -144.2087 | 131.5665 | 4.2863e-13 | -142.4927 | 129.0741

## LL_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 1.6287 | 1.6287 | 0 | 1.6287 | 1.6287 | 0 | 18.8063 | 18.8063 | 0 | 18.8063 | 18.8063 | -2.6053e-15 | 17.8002 | 0.06044 | -2.6053e-15 | -16.4209 | 1.3189 | -1.3027e-14 | 3.9189 | 14.5607 | 1.3027e-14 | -2.3539 | -12.9957 | 0 | -149.0411 | 30.9589 | 0 | 30.9589 | -149.0411 | 1.1 | 0.96917 | 0.77425 | 1.1 | 0.88208 | 0.69458 | 4.5637e-13 | -136.625 | 120.7211 | 4.6068e-13 | -140.8835 | 126.7539
Line_1 | 0 | 1.0858 | 1.0858 | 0 | 1.0858 | 1.0858 | 0 | 12.5375 | 12.5375 | 0 | 12.5375 | 12.5375 | -2.6053e-15 | -10.3342 | 1.4923 | -2.6053e-15 | 10.9473 | -0.87927 | -1.3027e-14 | -0.87368 | -7.9682 | 1.5632e-14 | 1.5692 | 8.6638 | 0 | 30.9589 | -149.0411 | 0 | -149.0411 | 30.9589 | 1.1 | 0.8272 | 0.6466 | 1.1 | 0.88208 | 0.69458 | 4.8256e-13 | -144.2087 | 131.5665 | 4.6068e-13 | -140.8835 | 126.7539
Line_2 | 0 | 0.54289 | 0.54289 | 0 | 0.54289 | 0.54289 | 0 | 6.2688 | 6.2688 | 0 | 6.2688 | 6.2688 | -2.3448e-14 | -5.3204 | 0.59289 | 2.0843e-14 | 5.4736 | -0.43963 | 1.3027e-14 | -0.61073 | -4.158 | -1.0421e-14 | 0.78462 | 4.3319 | 0 | 30.9589 | -149.0411 | 0 | -149.0411 | 30.9589 | 1.1 | 0.85428 | 0.67 | 1.1 | 0.88208 | 0.69458 | 4.2863e-13 | -142.4927 | 129.0741 | 4.6068e-13 | -140.8835 | 126.7539
Line_3 | 0 | 0.54289 | 0.54289 | 0 | 0.54289 | 0.54289 | 0 | 6.2688 | 6.2688 | 0 | 6.2688 | 6.2688 | 2.3448e-14 | -5.1671 | 0.74615 | -2.6053e-14 | 5.3204 | -0.59289 | -2.3448e-14 | -0.43684 | -3.9841 | 2.8659e-14 | 0.61073 | 4.158 | 0 | 30.9589 | -149.0411 | 0 | -149.0411 | 30.9589 | 1.1 | 0.8272 | 0.6466 | 1.1 | 0.85428 | 0.67 | 4.8256e-13 | -144.2087 | 131.5665 | 4.2863e-13 | -142.4927 | 129.0741

## LL_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 2.6061 | 2.6061 | 0 | 2.6061 | 2.6061 | 0 | 30.0921 | 30.0921 | 0 | 30.0921 | 30.0921 | 4.0264e-14 | 24.6317 | -2.0295 | -4.0264e-14 | -17.851 | 8.8102 | -2.1316e-14 | -0.29866 | 13.6553 | 2.1316e-14 | 4.3057 | -9.6483 | 0 | -152.3733 | 27.6267 | 0 | 27.6267 | -152.3733 | 1 | 0.8186 | 0.45877 | 1 | 0.61023 | 0.43419 | 9.1775e-13 | -153.068 | 126.0805 | 8.9964e-13 | -165.934 | 160.0269
Line_1 | 0 | 1.7374 | 1.7374 | 0 | 1.7374 | 1.7374 | 0 | 20.0614 | 20.0614 | 0 | 20.0614 | 20.0614 | -3.079e-14 | -8.8871 | 8.8871 | 3.079e-14 | 11.9007 | -5.8735 | -2.3685e-15 | 4.6513 | -4.6513 | 4.737e-15 | -2.8704 | 6.4322 | 0 | 27.6267 | -152.3733 | 0 | -152.3733 | 27.6267 | 1 | 0.5 | 0.5 | 1 | 0.61023 | 0.43419 | 9.437e-13 | -180 | 180 | 8.9964e-13 | -165.934 | 160.0269
Line_2 | 0 | 0.86868 | 0.86868 | 0 | 0.86868 | 0.86868 | 0 | 10.0307 | 10.0307 | 0 | 10.0307 | 10.0307 | -4.5001e-14 | -5.1969 | 3.6901 | 4.2633e-14 | 5.9503 | -2.9367 | 5.4475e-14 | 1.8804 | -2.7709 | -5.2106e-14 | -1.4352 | 3.2161 | 0 | 27.6267 | -152.3733 | 0 | -152.3733 | 27.6267 | 1 | 0.55098 | 0.46005 | 1 | 0.61023 | 0.43419 | 8.129e-13 | -172.2653 | 170.7242 | 8.9964e-13 | -165.934 | 160.0269
Line_3 | 0 | 0.86868 | 0.86868 | 0 | 0.86868 | 0.86868 | 0 | 10.0307 | 10.0307 | 0 | 10.0307 | 10.0307 | 1.4211e-14 | -4.4435 | 4.4435 | -1.1842e-14 | 5.1969 | -3.6901 | -5.2106e-14 | 2.3257 | -2.3257 | 6.158e-14 | -1.8804 | 2.7709 | 0 | 27.6267 | -152.3733 | 0 | -152.3733 | 27.6267 | 1 | 0.5 | 0.5 | 1 | 0.55098 | 0.46005 | 9.437e-13 | -180 | 180 | 8.129e-13 | -172.2653 | 170.7242

## LL_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 2.6061 | 2.6061 | 0 | 2.6061 | 2.6061 | 0 | 30.0921 | 30.0921 | 0 | 30.0921 | 30.0921 | 4.0264e-14 | 24.6317 | -2.0295 | -4.0264e-14 | -17.851 | 8.8102 | -2.1316e-14 | -0.29866 | 13.6553 | 2.1316e-14 | 4.3057 | -9.6483 | 0 | -152.3733 | 27.6267 | 0 | 27.6267 | -152.3733 | 1 | 0.8186 | 0.45877 | 1 | 0.61023 | 0.43419 | 9.1775e-13 | -153.068 | 126.0805 | 8.9964e-13 | -165.934 | 160.0269
Line_1 | 0 | 1.7374 | 1.7374 | 0 | 1.7374 | 1.7374 | 0 | 20.0614 | 20.0614 | 0 | 20.0614 | 20.0614 | -3.079e-14 | -8.8871 | 8.8871 | 3.079e-14 | 11.9007 | -5.8735 | -2.3685e-15 | 4.6513 | -4.6513 | 4.737e-15 | -2.8704 | 6.4322 | 0 | 27.6267 | -152.3733 | 0 | -152.3733 | 27.6267 | 1 | 0.5 | 0.5 | 1 | 0.61023 | 0.43419 | 9.437e-13 | -180 | 180 | 8.9964e-13 | -165.934 | 160.0269
Line_2 | 0 | 0.86868 | 0.86868 | 0 | 0.86868 | 0.86868 | 0 | 10.0307 | 10.0307 | 0 | 10.0307 | 10.0307 | -4.5001e-14 | -5.1969 | 3.6901 | 4.2633e-14 | 5.9503 | -2.9367 | 5.4475e-14 | 1.8804 | -2.7709 | -5.2106e-14 | -1.4352 | 3.2161 | 0 | 27.6267 | -152.3733 | 0 | -152.3733 | 27.6267 | 1 | 0.55098 | 0.46005 | 1 | 0.61023 | 0.43419 | 8.129e-13 | -172.2653 | 170.7242 | 8.9964e-13 | -165.934 | 160.0269
Line_3 | 0 | 0.86868 | 0.86868 | 0 | 0.86868 | 0.86868 | 0 | 10.0307 | 10.0307 | 0 | 10.0307 | 10.0307 | 1.4211e-14 | -4.4435 | 4.4435 | -1.1842e-14 | 5.1969 | -3.6901 | -5.2106e-14 | 2.3257 | -2.3257 | 6.158e-14 | -1.8804 | 2.7709 | 0 | 27.6267 | -152.3733 | 0 | -152.3733 | 27.6267 | 1 | 0.5 | 0.5 | 1 | 0.55098 | 0.46005 | 9.437e-13 | -180 | 180 | 8.129e-13 | -172.2653 | 170.7242

## LL_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 1.3721 | 1.3721 | 0 | 1.3721 | 1.3721 | 0 | 15.8432 | 15.8432 | 0 | 15.8432 | 15.8432 | 2.3093e-14 | 14.2512 | 1.4266 | -2.3093e-14 | -12.3717 | 0.45296 | -1.6579e-14 | 1.9064 | 11.2087 | 1.4211e-14 | -0.79565 | -10.098 | 0 | -144.0449 | 35.9551 | 0 | 35.9551 | -144.0449 | 1 | 0.90753 | 0.71319 | 1 | 0.7825 | 0.63801 | 4.9441e-13 | -136.4258 | 118.7019 | 4.8149e-13 | -140.3651 | 128.5235
Line_1 | 0 | 0.9147 | 0.9147 | 0 | 0.9147 | 0.9147 | 0 | 10.5621 | 10.5621 | 0 | 10.5621 | 10.5621 | -1.6579e-14 | -7.4125 | 1.1373 | 1.6579e-14 | 8.2478 | -0.30197 | -2.3685e-15 | -0.036791 | -6.2383 | -2.3685e-15 | 0.53044 | 6.732 | 0 | 35.9551 | -144.0449 | 0 | -144.0449 | 35.9551 | 1 | 0.70181 | 0.60037 | 1 | 0.7825 | 0.63801 | 5.0443e-13 | -143.7605 | 136.2873 | 4.8149e-13 | -140.3651 | 128.5235
Line_2 | 0 | 0.45735 | 0.45735 | 0 | 0.45735 | 0.45735 | 0 | 5.2811 | 5.2811 | 0 | 5.2811 | 5.2811 | -1.4803e-14 | -3.9151 | 0.35982 | 1.5987e-14 | 4.1239 | -0.15099 | 2.1316e-14 | -0.14181 | -3.2426 | -2.3685e-14 | 0.26522 | 3.366 | 0 | 35.9551 | -144.0449 | 0 | -144.0449 | 35.9551 | 1 | 0.74183 | 0.61777 | 1 | 0.7825 | 0.63801 | 4.3583e-13 | -141.9705 | 132.2872 | 4.8149e-13 | -140.3651 | 128.5235
Line_3 | 0 | 0.45735 | 0.45735 | 0 | 0.45735 | 0.45735 | 0 | 5.2811 | 5.2811 | 0 | 5.2811 | 5.2811 | -1.1842e-15 | -3.7062 | 0.56866 | -1.8016e-28 | 3.9151 | -0.35982 | -2.3685e-14 | -0.018396 | -3.1192 | 2.3685e-14 | 0.14181 | 3.2426 | 0 | 35.9551 | -144.0449 | 0 | -144.0449 | 35.9551 | 1 | 0.70181 | 0.60037 | 1 | 0.74183 | 0.61777 | 5.0443e-13 | -143.7605 | 136.2873 | 4.3583e-13 | -141.9705 | 132.2872

## LL_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 1.3721 | 1.3721 | 0 | 1.3721 | 1.3721 | 0 | 15.8432 | 15.8432 | 0 | 15.8432 | 15.8432 | 2.3093e-14 | 14.2512 | 1.4266 | -2.3093e-14 | -12.3717 | 0.45296 | -1.6579e-14 | 1.9064 | 11.2087 | 1.4211e-14 | -0.79565 | -10.098 | 0 | -144.0449 | 35.9551 | 0 | 35.9551 | -144.0449 | 1 | 0.90753 | 0.71319 | 1 | 0.7825 | 0.63801 | 4.9441e-13 | -136.4258 | 118.7019 | 4.8149e-13 | -140.3651 | 128.5235
Line_1 | 0 | 0.9147 | 0.9147 | 0 | 0.9147 | 0.9147 | 0 | 10.5621 | 10.5621 | 0 | 10.5621 | 10.5621 | -1.6579e-14 | -7.4125 | 1.1373 | 1.6579e-14 | 8.2478 | -0.30197 | -2.3685e-15 | -0.036791 | -6.2383 | -2.3685e-15 | 0.53044 | 6.732 | 0 | 35.9551 | -144.0449 | 0 | -144.0449 | 35.9551 | 1 | 0.70181 | 0.60037 | 1 | 0.7825 | 0.63801 | 5.0443e-13 | -143.7605 | 136.2873 | 4.8149e-13 | -140.3651 | 128.5235
Line_2 | 0 | 0.45735 | 0.45735 | 0 | 0.45735 | 0.45735 | 0 | 5.2811 | 5.2811 | 0 | 5.2811 | 5.2811 | -1.4803e-14 | -3.9151 | 0.35982 | 1.5987e-14 | 4.1239 | -0.15099 | 2.1316e-14 | -0.14181 | -3.2426 | -2.3685e-14 | 0.26522 | 3.366 | 0 | 35.9551 | -144.0449 | 0 | -144.0449 | 35.9551 | 1 | 0.74183 | 0.61777 | 1 | 0.7825 | 0.63801 | 4.3583e-13 | -141.9705 | 132.2872 | 4.8149e-13 | -140.3651 | 128.5235
Line_3 | 0 | 0.45735 | 0.45735 | 0 | 0.45735 | 0.45735 | 0 | 5.2811 | 5.2811 | 0 | 5.2811 | 5.2811 | -1.1842e-15 | -3.7062 | 0.56866 | -1.8016e-28 | 3.9151 | -0.35982 | -2.3685e-14 | -0.018396 | -3.1192 | 2.3685e-14 | 0.14181 | 3.2426 | 0 | 35.9551 | -144.0449 | 0 | -144.0449 | 35.9551 | 1 | 0.70181 | 0.60037 | 1 | 0.74183 | 0.61777 | 5.0443e-13 | -143.7605 | 136.2873 | 4.3583e-13 | -141.9705 | 132.2872

## LG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 3.6999 | 1.85 | 1.85 | 3.6999 | 1.85 | 1.85 | 42.7231 | 21.3615 | 21.3615 | 42.7231 | 21.3615 | 21.3615 | 11.8642 | -16.5466 | 22.4787 | -4.7457 | 18.3263 | -20.6991 | 13.4613 | 9.1413 | -2.4106 | -5.3845 | -7.1221 | 4.4298 | -73.5107 | 106.4893 | 106.4893 | 106.4893 | -73.5107 | -73.5107 |  | 0.41999 | 0.88495 | 1.0583 | 0.168 | 0.92042 | 0.99093 | -24.9022 | -102.4294 | 100.3683 | -24.9022 | -94.7482 | 94.4096
Line_1 | 2.4666 | 1.2333 | 1.2333 | 2.4666 | 1.2333 | 1.2333 | 28.4821 | 14.241 | 14.241 | 28.4821 | 14.241 | 14.241 | 3.6273e-10 | 13.0085 | -13.0085 | 3.1638 | -12.2175 | 13.7994 | -2.4228e-10 | -3.8506 | 3.8506 | 3.5897 | 4.7481 | -2.9532 | 106.4893 | -73.5107 | -73.5107 | -73.5107 | 106.4893 | 106.4893 |  | 0 | 0.95263 | 0.95263 | 0.168 | 0.92042 | 0.99093 | 0 | -90 | 90 | -24.9022 | -94.7482 | 94.4096
Line_2 | 1.2333 | 0.61665 | 0.61665 | 1.2333 | 0.61665 | 0.61665 | 14.241 | 7.1205 | 7.1205 | 14.241 | 7.1205 | 7.1205 | -0.79095 | 6.3065 | -6.702 | 1.5819 | -6.1088 | 6.8997 | -0.89742 | -2.1497 | 1.701 | 1.7948 | 2.374 | -1.4766 | 106.4893 | -73.5107 | -73.5107 | -73.5107 | 106.4893 | 106.4893 |  | 0.083999 | 0.93572 | 0.97106 | 0.168 | 0.92042 | 0.99093 | -24.9022 | -92.3332 | 92.2483 | -24.9022 | -94.7482 | 94.4096
Line_3 | 1.2333 | 0.61665 | 0.61665 | 1.2333 | 0.61665 | 0.61665 | 14.241 | 7.1205 | 7.1205 | 14.241 | 7.1205 | 7.1205 | 1.8137e-10 | 6.5042 | -6.5042 | 0.79095 | -6.3065 | 6.702 | -1.2114e-10 | -1.9253 | 1.9253 | 0.89742 | 2.1497 | -1.701 | 106.4893 | -73.5107 | -73.5107 | -73.5107 | 106.4893 | 106.4893 |  | 0 | 0.95263 | 0.95263 | 0.083999 | 0.93572 | 0.97106 | 0 | -90 | 90 | -24.9022 | -92.3332 | 92.2483

## LG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 3.6999 | 1.85 | 1.85 | 3.6999 | 1.85 | 1.85 | 42.7231 | 21.3615 | 21.3615 | 42.7231 | 21.3615 | 21.3615 | 11.8642 | -16.5466 | 22.4787 | -4.7457 | 18.3263 | -20.6991 | 13.4613 | 9.1413 | -2.4106 | -5.3845 | -7.1221 | 4.4298 | -73.5107 | 106.4893 | 106.4893 | 106.4893 | -73.5107 | -73.5107 |  | 0.41999 | 0.88495 | 1.0583 | 0.168 | 0.92042 | 0.99093 | -24.9022 | -102.4294 | 100.3683 | -24.9022 | -94.7482 | 94.4096
Line_1 | 2.4666 | 1.2333 | 1.2333 | 2.4666 | 1.2333 | 1.2333 | 28.4821 | 14.241 | 14.241 | 28.4821 | 14.241 | 14.241 | 3.6273e-10 | 13.0085 | -13.0085 | 3.1638 | -12.2175 | 13.7994 | -2.4228e-10 | -3.8506 | 3.8506 | 3.5897 | 4.7481 | -2.9532 | 106.4893 | -73.5107 | -73.5107 | -73.5107 | 106.4893 | 106.4893 |  | 0 | 0.95263 | 0.95263 | 0.168 | 0.92042 | 0.99093 | 0 | -90 | 90 | -24.9022 | -94.7482 | 94.4096
Line_2 | 1.2333 | 0.61665 | 0.61665 | 1.2333 | 0.61665 | 0.61665 | 14.241 | 7.1205 | 7.1205 | 14.241 | 7.1205 | 7.1205 | -0.79095 | 6.3065 | -6.702 | 1.5819 | -6.1088 | 6.8997 | -0.89742 | -2.1497 | 1.701 | 1.7948 | 2.374 | -1.4766 | 106.4893 | -73.5107 | -73.5107 | -73.5107 | 106.4893 | 106.4893 |  | 0.083999 | 0.93572 | 0.97106 | 0.168 | 0.92042 | 0.99093 | -24.9022 | -92.3332 | 92.2483 | -24.9022 | -94.7482 | 94.4096
Line_3 | 1.2333 | 0.61665 | 0.61665 | 1.2333 | 0.61665 | 0.61665 | 14.241 | 7.1205 | 7.1205 | 14.241 | 7.1205 | 7.1205 | 1.8137e-10 | 6.5042 | -6.5042 | 0.79095 | -6.3065 | 6.702 | -1.2114e-10 | -1.9253 | 1.9253 | 0.89742 | 2.1497 | -1.701 | 106.4893 | -73.5107 | -73.5107 | -73.5107 | 106.4893 | 106.4893 |  | 0 | 0.95263 | 0.95263 | 0.083999 | 0.93572 | 0.97106 | 0 | -90 | 90 | -24.9022 | -92.3332 | 92.2483

## LG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.92568 | 0.46284 | 0.46284 | 0.92568 | 0.46284 | 0.46284 | 10.6889 | 5.3444 | 5.3444 | 10.6889 | 5.3444 | 5.3444 | 7.1693 | -2.2119 | 5.7966 | -6.7237 | 2.3233 | -5.6852 | 7.2693 | 4.9617 | -1.3271 | -6.7637 | -4.8353 | 1.4534 | -51.8587 | 128.1413 | 128.1413 | 128.1413 | -51.8587 | -51.8587 |  | 0.95519 | 1.0165 | 1.1127 | 0.89225 | 1.0038 | 1.098 | -6.462 | -117.8317 | 115.2463 | -6.6888 | -116.1951 | 113.8004
Line_1 | 0.61712 | 0.30856 | 0.30856 | 0.61712 | 0.30856 | 0.30856 | 7.1259 | 3.563 | 3.563 | 7.1259 | 3.563 | 3.563 | -4.2844 | 1.5984 | -3.7406 | 4.4825 | -1.5489 | 3.7901 | -4.2844 | -3.1674 | 1.0251 | 4.5091 | 3.2235 | -0.96896 | 128.1413 | -51.8587 | -51.8587 | -51.8587 | 128.1413 | 128.1413 |  | 0.85029 | 0.99575 | 1.0886 | 0.89225 | 1.0038 | 1.098 | -6.8587 | -115.0815 | 112.8153 | -6.6888 | -116.1951 | 113.8004
Line_2 | 0.30856 | 0.15428 | 0.15428 | 0.30856 | 0.15428 | 0.15428 | 3.563 | 1.7815 | 1.7815 | 3.563 | 1.7815 | 1.7815 | -2.1917 | 0.78681 | -1.8827 | 2.2412 | -0.77443 | 1.8951 | -2.1984 | -1.5977 | 0.49853 | 2.2546 | 1.6118 | -0.48448 | 128.1413 | -51.8587 | -51.8587 | -51.8587 | 128.1413 | 128.1413 |  | 0.87127 | 0.9997 | 1.0932 | 0.89225 | 1.0038 | 1.098 | -6.7717 | -115.6405 | 113.31 | -6.6888 | -116.1951 | 113.8004
Line_3 | 0.30856 | 0.15428 | 0.15428 | 0.30856 | 0.15428 | 0.15428 | 3.563 | 1.7815 | 1.7815 | 3.563 | 1.7815 | 1.7815 | -2.1422 | 0.79919 | -1.8703 | 2.1917 | -0.78681 | 1.8827 | -2.1422 | -1.5837 | 0.51257 | 2.1984 | 1.5977 | -0.49853 | 128.1413 | -51.8587 | -51.8587 | -51.8587 | 128.1413 | 128.1413 |  | 0.85029 | 0.99575 | 1.0886 | 0.87127 | 0.9997 | 1.0932 | -6.8587 | -115.0815 | 112.8153 | -6.7717 | -115.6405 | 113.31

## LG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.92568 | 0.46284 | 0.46284 | 0.92568 | 0.46284 | 0.46284 | 10.6889 | 5.3444 | 5.3444 | 10.6889 | 5.3444 | 5.3444 | 7.1693 | -2.2119 | 5.7966 | -6.7237 | 2.3233 | -5.6852 | 7.2693 | 4.9617 | -1.3271 | -6.7637 | -4.8353 | 1.4534 | -51.8587 | 128.1413 | 128.1413 | 128.1413 | -51.8587 | -51.8587 |  | 0.95519 | 1.0165 | 1.1127 | 0.89225 | 1.0038 | 1.098 | -6.462 | -117.8317 | 115.2463 | -6.6888 | -116.1951 | 113.8004
Line_1 | 0.61712 | 0.30856 | 0.30856 | 0.61712 | 0.30856 | 0.30856 | 7.1259 | 3.563 | 3.563 | 7.1259 | 3.563 | 3.563 | -4.2844 | 1.5984 | -3.7406 | 4.4825 | -1.5489 | 3.7901 | -4.2844 | -3.1674 | 1.0251 | 4.5091 | 3.2235 | -0.96896 | 128.1413 | -51.8587 | -51.8587 | -51.8587 | 128.1413 | 128.1413 |  | 0.85029 | 0.99575 | 1.0886 | 0.89225 | 1.0038 | 1.098 | -6.8587 | -115.0815 | 112.8153 | -6.6888 | -116.1951 | 113.8004
Line_2 | 0.30856 | 0.15428 | 0.15428 | 0.30856 | 0.15428 | 0.15428 | 3.563 | 1.7815 | 1.7815 | 3.563 | 1.7815 | 1.7815 | -2.1917 | 0.78681 | -1.8827 | 2.2412 | -0.77443 | 1.8951 | -2.1984 | -1.5977 | 0.49853 | 2.2546 | 1.6118 | -0.48448 | 128.1413 | -51.8587 | -51.8587 | -51.8587 | 128.1413 | 128.1413 |  | 0.87127 | 0.9997 | 1.0932 | 0.89225 | 1.0038 | 1.098 | -6.7717 | -115.6405 | 113.31 | -6.6888 | -116.1951 | 113.8004
Line_3 | 0.30856 | 0.15428 | 0.15428 | 0.30856 | 0.15428 | 0.15428 | 3.563 | 1.7815 | 1.7815 | 3.563 | 1.7815 | 1.7815 | -2.1422 | 0.79919 | -1.8703 | 2.1917 | -0.78681 | 1.8827 | -2.1422 | -1.5837 | 0.51257 | 2.1984 | 1.5977 | -0.49853 | 128.1413 | -51.8587 | -51.8587 | -51.8587 | 128.1413 | 128.1413 |  | 0.85029 | 0.99575 | 1.0886 | 0.87127 | 0.9997 | 1.0932 | -6.8587 | -115.0815 | 112.8153 | -6.7717 | -115.6405 | 113.31

## LG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 3.0092 | 1.5046 | 1.5046 | 3.0092 | 1.5046 | 1.5046 | 34.7474 | 17.3737 | 17.3737 | 34.7474 | 17.3737 | 17.3737 | 15.0681 | -9.5636 | 17.0976 | -6.0272 | 11.8238 | -14.8374 | 8.9044 | 9.2031 | -4.7509 | -3.5618 | -7.8674 | 6.0865 | -62.3733 | 117.6267 | 117.6267 | 117.6267 | -62.3733 | -62.3733 |  | 0.50371 | 0.76394 | 1.0214 | 0.20148 | 0.81745 | 0.92308 | -31.7926 | -106.2728 | 102.0978 | -31.7926 | -96.0127 | 95.3225
Line_1 | 2.0061 | 1.0031 | 1.0031 | 2.0061 | 1.0031 | 1.0031 | 23.1649 | 11.5825 | 11.5825 | 23.1649 | 11.5825 | 11.5825 | -1.4694e-10 | 8.8871 | -8.8871 | 4.0182 | -7.8825 | 9.8916 | -3.9283e-11 | -4.6513 | 4.6513 | 2.3745 | 5.245 | -4.0577 | 117.6267 | -62.3733 | -62.3733 | -62.3733 | 117.6267 | 117.6267 |  | 0 | 0.86603 | 0.86603 | 0.20148 | 0.81745 | 0.92308 | 0 | -90 | 90 | -31.7926 | -96.0127 | 95.3225
Line_2 | 1.0031 | 0.50154 | 0.50154 | 1.0031 | 0.50154 | 0.50154 | 11.5825 | 5.7912 | 5.7912 | 11.5825 | 5.7912 | 5.7912 | -1.0045 | 4.1924 | -4.6947 | 2.0091 | -3.9413 | 4.9458 | -0.59363 | -2.4741 | 2.1773 | 1.1873 | 2.6225 | -2.0288 | 117.6267 | -62.3733 | -62.3733 | -62.3733 | 117.6267 | 117.6267 |  | 0.10074 | 0.84058 | 0.89359 | 0.20148 | 0.81745 | 0.92308 | -31.7926 | -92.9195 | 92.7462 | -31.7926 | -96.0127 | 95.3225
Line_3 | 1.0031 | 0.50154 | 0.50154 | 1.0031 | 0.50154 | 0.50154 | 11.5825 | 5.7912 | 5.7912 | 11.5825 | 5.7912 | 5.7912 | -7.3471e-11 | 4.4435 | -4.4435 | 1.0045 | -4.1924 | 4.6947 | -1.9641e-11 | -2.3257 | 2.3257 | 0.59363 | 2.4741 | -2.1773 | 117.6267 | -62.3733 | -62.3733 | -62.3733 | 117.6267 | 117.6267 |  | 0 | 0.86603 | 0.86603 | 0.10074 | 0.84058 | 0.89359 | 0 | -90 | 90 | -31.7926 | -92.9195 | 92.7462

## LG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 3.0092 | 1.5046 | 1.5046 | 3.0092 | 1.5046 | 1.5046 | 34.7474 | 17.3737 | 17.3737 | 34.7474 | 17.3737 | 17.3737 | 15.0681 | -9.5636 | 17.0976 | -6.0272 | 11.8238 | -14.8374 | 8.9044 | 9.2031 | -4.7509 | -3.5618 | -7.8674 | 6.0865 | -62.3733 | 117.6267 | 117.6267 | 117.6267 | -62.3733 | -62.3733 |  | 0.50371 | 0.76394 | 1.0214 | 0.20148 | 0.81745 | 0.92308 | -31.7926 | -106.2728 | 102.0978 | -31.7926 | -96.0127 | 95.3225
Line_1 | 2.0061 | 1.0031 | 1.0031 | 2.0061 | 1.0031 | 1.0031 | 23.1649 | 11.5825 | 11.5825 | 23.1649 | 11.5825 | 11.5825 | -1.4694e-10 | 8.8871 | -8.8871 | 4.0182 | -7.8825 | 9.8916 | -3.9283e-11 | -4.6513 | 4.6513 | 2.3745 | 5.245 | -4.0577 | 117.6267 | -62.3733 | -62.3733 | -62.3733 | 117.6267 | 117.6267 |  | 0 | 0.86603 | 0.86603 | 0.20148 | 0.81745 | 0.92308 | 0 | -90 | 90 | -31.7926 | -96.0127 | 95.3225
Line_2 | 1.0031 | 0.50154 | 0.50154 | 1.0031 | 0.50154 | 0.50154 | 11.5825 | 5.7912 | 5.7912 | 11.5825 | 5.7912 | 5.7912 | -1.0045 | 4.1924 | -4.6947 | 2.0091 | -3.9413 | 4.9458 | -0.59363 | -2.4741 | 2.1773 | 1.1873 | 2.6225 | -2.0288 | 117.6267 | -62.3733 | -62.3733 | -62.3733 | 117.6267 | 117.6267 |  | 0.10074 | 0.84058 | 0.89359 | 0.20148 | 0.81745 | 0.92308 | -31.7926 | -92.9195 | 92.7462 | -31.7926 | -96.0127 | 95.3225
Line_3 | 1.0031 | 0.50154 | 0.50154 | 1.0031 | 0.50154 | 0.50154 | 11.5825 | 5.7912 | 5.7912 | 11.5825 | 5.7912 | 5.7912 | -7.3471e-11 | 4.4435 | -4.4435 | 1.0045 | -4.1924 | 4.6947 | -1.9641e-11 | -2.3257 | 2.3257 | 0.59363 | 2.4741 | -2.1773 | 117.6267 | -62.3733 | -62.3733 | -62.3733 | 117.6267 | 117.6267 |  | 0 | 0.86603 | 0.86603 | 0.10074 | 0.84058 | 0.89359 | 0 | -90 | 90 | -31.7926 | -92.9195 | 92.7462

## LG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.80665 | 0.40333 | 0.40333 | 0.80665 | 0.40333 | 0.40333 | 9.3144 | 4.6572 | 4.6572 | 9.3144 | 4.6572 | 4.6572 | 5.9629 | -1.5803 | 4.5618 | -5.3133 | 1.7428 | -4.3994 | 5.52 | 3.9945 | -1.2345 | -5.1361 | -3.8986 | 1.3305 | -49.591 | 130.409 | 130.409 | 130.409 | -49.591 | -49.591 |  | 0.87238 | 0.92239 | 1.0147 | 0.79338 | 0.91693 | 0.98689 | -6.7998 | -118.0059 | 115.2663 | -5.5623 | -115.5051 | 113.5823
Line_1 | 0.53777 | 0.26888 | 0.26888 | 0.53777 | 0.26888 | 0.26888 | 6.2096 | 3.1048 | 3.1048 | 6.2096 | 3.1048 | 3.1048 | -3.2535 | 1.234 | -2.8607 | 3.5422 | -1.1618 | 2.9329 | -3.2535 | -2.5564 | 0.92965 | 3.4241 | 2.599 | -0.887 | 130.409 | -49.591 | -49.591 | -49.591 | 130.409 | 130.409 |  | 0.74096 | 0.91427 | 0.96882 | 0.79338 | 0.91693 | 0.98689 | -4.591 | -113.8233 | 112.4065 | -5.5623 | -115.5051 | 113.5823
Line_2 | 0.26888 | 0.13444 | 0.13444 | 0.26888 | 0.13444 | 0.13444 | 3.1048 | 1.5524 | 1.5524 | 3.1048 | 1.5524 | 1.5524 | -1.6989 | 0.59897 | -1.4484 | 1.7711 | -0.58092 | 1.4665 | -1.6694 | -1.2889 | 0.45416 | 1.712 | 1.2995 | -0.4435 | 130.409 | -49.591 | -49.591 | -49.591 | 130.409 | 130.409 |  | 0.76714 | 0.9155 | 0.97781 | 0.79338 | 0.91693 | 0.98689 | -5.0932 | -114.6654 | 112.9998 | -5.5623 | -115.5051 | 113.5823
Line_3 | 0.26888 | 0.13444 | 0.13444 | 0.26888 | 0.13444 | 0.13444 | 3.1048 | 1.5524 | 1.5524 | 3.1048 | 1.5524 | 1.5524 | -1.6267 | 0.61701 | -1.4304 | 1.6989 | -0.59897 | 1.4484 | -1.6267 | -1.2782 | 0.46483 | 1.6694 | 1.2889 | -0.45416 | 130.409 | -49.591 | -49.591 | -49.591 | 130.409 | 130.409 |  | 0.74096 | 0.91427 | 0.96882 | 0.76714 | 0.9155 | 0.97781 | -4.591 | -113.8233 | 112.4065 | -5.0932 | -114.6654 | 112.9998

## LG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.80665 | 0.40333 | 0.40333 | 0.80665 | 0.40333 | 0.40333 | 9.3144 | 4.6572 | 4.6572 | 9.3144 | 4.6572 | 4.6572 | 5.9629 | -1.5803 | 4.5618 | -5.3133 | 1.7428 | -4.3994 | 5.52 | 3.9945 | -1.2345 | -5.1361 | -3.8986 | 1.3305 | -49.591 | 130.409 | 130.409 | 130.409 | -49.591 | -49.591 |  | 0.87238 | 0.92239 | 1.0147 | 0.79338 | 0.91693 | 0.98689 | -6.7998 | -118.0059 | 115.2663 | -5.5623 | -115.5051 | 113.5823
Line_1 | 0.53777 | 0.26888 | 0.26888 | 0.53777 | 0.26888 | 0.26888 | 6.2096 | 3.1048 | 3.1048 | 6.2096 | 3.1048 | 3.1048 | -3.2535 | 1.234 | -2.8607 | 3.5422 | -1.1618 | 2.9329 | -3.2535 | -2.5564 | 0.92965 | 3.4241 | 2.599 | -0.887 | 130.409 | -49.591 | -49.591 | -49.591 | 130.409 | 130.409 |  | 0.74096 | 0.91427 | 0.96882 | 0.79338 | 0.91693 | 0.98689 | -4.591 | -113.8233 | 112.4065 | -5.5623 | -115.5051 | 113.5823
Line_2 | 0.26888 | 0.13444 | 0.13444 | 0.26888 | 0.13444 | 0.13444 | 3.1048 | 1.5524 | 1.5524 | 3.1048 | 1.5524 | 1.5524 | -1.6989 | 0.59897 | -1.4484 | 1.7711 | -0.58092 | 1.4665 | -1.6694 | -1.2889 | 0.45416 | 1.712 | 1.2995 | -0.4435 | 130.409 | -49.591 | -49.591 | -49.591 | 130.409 | 130.409 |  | 0.76714 | 0.9155 | 0.97781 | 0.79338 | 0.91693 | 0.98689 | -5.0932 | -114.6654 | 112.9998 | -5.5623 | -115.5051 | 113.5823
Line_3 | 0.26888 | 0.13444 | 0.13444 | 0.26888 | 0.13444 | 0.13444 | 3.1048 | 1.5524 | 1.5524 | 3.1048 | 1.5524 | 1.5524 | -1.6267 | 0.61701 | -1.4304 | 1.6989 | -0.59897 | 1.4484 | -1.6267 | -1.2782 | 0.46483 | 1.6694 | 1.2889 | -0.45416 | 130.409 | -49.591 | -49.591 | -49.591 | 130.409 | 130.409 |  | 0.74096 | 0.91427 | 0.96882 | 0.76714 | 0.9155 | 0.97781 | -4.591 | -113.8233 | 112.4065 | -5.0932 | -114.6654 | 112.9998

## LLG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 3.6999 | 3.6999 | 3.6999 | 3.6999 | 3.6999 | 3.6999 | 42.7231 | 42.7231 | 42.7231 | 42.7231 | 42.7231 | 42.7231 | 11.8642 | 11.8642 | 11.8642 | -4.7457 | -4.7457 | -4.7457 | 13.4613 | 13.4613 | 13.4613 | -5.3845 | -5.3845 | -5.3845 | -73.5107 | 166.4893 | 46.4893 | 106.4893 | -13.5107 | -133.5107 |  | 0.41999 | 0.41999 | 0.41999 | 0.168 | 0.168 | 0.168 | -24.9022 | -144.9022 | 95.0978 | -24.9022 | -144.9022 | 95.0978
Line_1 | 2.4666 | 2.4666 | 2.4666 | 2.4666 | 2.4666 | 2.4666 | 28.4821 | 28.4821 | 28.4821 | 28.4821 | 28.4821 | 28.4821 | 4.1798e-10 | 4.1668e-10 | 4.15e-10 | 3.1638 | 3.1638 | 3.1638 | -1.1197e-08 | -2.4645e-10 | -2.4669e-10 | 3.5897 | 3.5897 | 3.5897 | 106.4893 | -13.5107 | -133.5107 | -73.5107 | 166.4893 | 46.4893 |  | 0 | 0 | 0 | 0.168 | 0.168 | 0.168 | 0 | 0 | 0 | -24.9022 | -144.9022 | 95.0978
Line_2 | 1.2333 | 1.2333 | 1.2333 | 1.2333 | 1.2333 | 1.2333 | 14.241 | 14.241 | 14.241 | 14.241 | 14.241 | 14.241 | -0.79095 | -0.79095 | -0.79095 | 1.5819 | 1.5819 | 1.5819 | -0.89742 | -0.89742 | -0.89742 | 1.7948 | 1.7948 | 1.7948 | 106.4893 | -13.5107 | -133.5107 | -73.5107 | 166.4893 | 46.4893 |  | 0.083999 | 0.083999 | 0.083999 | 0.168 | 0.168 | 0.168 | -24.9022 | -144.9022 | 95.0978 | -24.9022 | -144.9022 | 95.0978
Line_3 | 1.2333 | 1.2333 | 1.2333 | 1.2333 | 1.2333 | 1.2333 | 14.241 | 14.241 | 14.241 | 14.241 | 14.241 | 14.241 | 2.0899e-10 | 2.0834e-10 | 2.075e-10 | 0.79095 | 0.79095 | 0.79095 | -5.5983e-09 | -1.2322e-10 | -1.2334e-10 | 0.89742 | 0.89742 | 0.89742 | 106.4893 | -13.5107 | -133.5107 | -73.5107 | 166.4893 | 46.4893 |  | 0 | 0 | 0 | 0.083999 | 0.083999 | 0.083999 | 0 | 0 | 0 | -24.9022 | -144.9022 | 95.0978

## LLG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 3.6999 | 3.6999 | 3.6999 | 3.6999 | 3.6999 | 3.6999 | 42.7231 | 42.7231 | 42.7231 | 42.7231 | 42.7231 | 42.7231 | 11.8642 | 11.8642 | 11.8642 | -4.7457 | -4.7457 | -4.7457 | 13.4613 | 13.4613 | 13.4613 | -5.3845 | -5.3845 | -5.3845 | -73.5107 | 166.4893 | 46.4893 | 106.4893 | -13.5107 | -133.5107 |  | 0.41999 | 0.41999 | 0.41999 | 0.168 | 0.168 | 0.168 | -24.9022 | -144.9022 | 95.0978 | -24.9022 | -144.9022 | 95.0978
Line_1 | 2.4666 | 2.4666 | 2.4666 | 2.4666 | 2.4666 | 2.4666 | 28.4821 | 28.4821 | 28.4821 | 28.4821 | 28.4821 | 28.4821 | 4.1798e-10 | 4.1668e-10 | 4.15e-10 | 3.1638 | 3.1638 | 3.1638 | -1.1197e-08 | -2.4645e-10 | -2.4669e-10 | 3.5897 | 3.5897 | 3.5897 | 106.4893 | -13.5107 | -133.5107 | -73.5107 | 166.4893 | 46.4893 |  | 0 | 0 | 0 | 0.168 | 0.168 | 0.168 | 0 | 0 | 0 | -24.9022 | -144.9022 | 95.0978
Line_2 | 1.2333 | 1.2333 | 1.2333 | 1.2333 | 1.2333 | 1.2333 | 14.241 | 14.241 | 14.241 | 14.241 | 14.241 | 14.241 | -0.79095 | -0.79095 | -0.79095 | 1.5819 | 1.5819 | 1.5819 | -0.89742 | -0.89742 | -0.89742 | 1.7948 | 1.7948 | 1.7948 | 106.4893 | -13.5107 | -133.5107 | -73.5107 | 166.4893 | 46.4893 |  | 0.083999 | 0.083999 | 0.083999 | 0.168 | 0.168 | 0.168 | -24.9022 | -144.9022 | 95.0978 | -24.9022 | -144.9022 | 95.0978
Line_3 | 1.2333 | 1.2333 | 1.2333 | 1.2333 | 1.2333 | 1.2333 | 14.241 | 14.241 | 14.241 | 14.241 | 14.241 | 14.241 | 2.0899e-10 | 2.0834e-10 | 2.075e-10 | 0.79095 | 0.79095 | 0.79095 | -5.5983e-09 | -1.2322e-10 | -1.2334e-10 | 0.89742 | 0.89742 | 0.89742 | 106.4893 | -13.5107 | -133.5107 | -73.5107 | 166.4893 | 46.4893 |  | 0 | 0 | 0 | 0.083999 | 0.083999 | 0.083999 | 0 | 0 | 0 | -24.9022 | -144.9022 | 95.0978

## LLG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.52302 | 1.1311 | 1.0837 | 0.52302 | 1.1311 | 1.0837 | 6.0393 | 13.0611 | 12.513 | 6.0393 | 13.0611 | 12.513 | 4.3404 | 11.2551 | 4.5079 | -4.1981 | -10.5898 | -3.8973 | 4.3723 | 5.7995 | 10.2498 | -4.2109 | -5.0447 | -9.5569 | -48.8689 | -157.5345 | 49.676 | 131.1311 | 22.4655 | -130.324 |  | 1.0201 | 0.96941 | 0.89485 | 0.98456 | 0.89809 | 0.82483 | -3.6591 | -130.2734 | 115.9357 | -3.782 | -132.0628 | 117.4905
Line_1 | 0.34868 | 0.75408 | 0.72244 | 0.34868 | 0.75408 | 0.72244 | 4.0262 | 8.7074 | 8.342 | 4.0262 | 8.7074 | 8.342 | -2.7355 | -6.7642 | -2.3268 | 2.7987 | 7.0599 | 2.5982 | -2.7355 | -3.0276 | -6.0634 | 2.8073 | 3.3631 | 6.3713 | 131.1311 | 22.4655 | -130.324 | -48.8689 | -157.5345 | 49.676 |  | 0.96085 | 0.8511 | 0.77853 | 0.98456 | 0.89809 | 0.82483 | -3.8689 | -133.4214 | 118.6818 | -3.782 | -132.0628 | 117.4905
Line_2 | 0.17434 | 0.37704 | 0.36122 | 0.17434 | 0.37704 | 0.36122 | 2.0131 | 4.3537 | 4.171 | 2.0131 | 4.3537 | 4.171 | -1.3836 | -3.456 | -1.2312 | 1.3994 | 3.5299 | 1.2991 | -1.3857 | -1.5977 | -3.1087 | 1.4036 | 1.6816 | 3.1856 | 131.1311 | 22.4655 | -130.324 | -48.8689 | -157.5345 | 49.676 |  | 0.97271 | 0.87453 | 0.80164 | 0.98456 | 0.89809 | 0.82483 | -3.8249 | -132.7238 | 118.069 | -3.782 | -132.0628 | 117.4905
Line_3 | 0.17434 | 0.37704 | 0.36122 | 0.17434 | 0.37704 | 0.36122 | 2.0131 | 4.3537 | 4.171 | 2.0131 | 4.3537 | 4.171 | -1.3678 | -3.3821 | -1.1634 | 1.3836 | 3.456 | 1.2312 | -1.3678 | -1.5138 | -3.0317 | 1.3857 | 1.5977 | 3.1087 | 131.1311 | 22.4655 | -130.324 | -48.8689 | -157.5345 | 49.676 |  | 0.96085 | 0.8511 | 0.77853 | 0.97271 | 0.87453 | 0.80164 | -3.8689 | -133.4214 | 118.6818 | -3.8249 | -132.7238 | 118.069

## LLG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.52302 | 1.1311 | 1.0837 | 0.52302 | 1.1311 | 1.0837 | 6.0393 | 13.0611 | 12.513 | 6.0393 | 13.0611 | 12.513 | 4.3404 | 11.2551 | 4.5079 | -4.1981 | -10.5898 | -3.8973 | 4.3723 | 5.7995 | 10.2498 | -4.2109 | -5.0447 | -9.5569 | -48.8689 | -157.5345 | 49.676 | 131.1311 | 22.4655 | -130.324 |  | 1.0201 | 0.96941 | 0.89485 | 0.98456 | 0.89809 | 0.82483 | -3.6591 | -130.2734 | 115.9357 | -3.782 | -132.0628 | 117.4905
Line_1 | 0.34868 | 0.75408 | 0.72244 | 0.34868 | 0.75408 | 0.72244 | 4.0262 | 8.7074 | 8.342 | 4.0262 | 8.7074 | 8.342 | -2.7355 | -6.7642 | -2.3268 | 2.7987 | 7.0599 | 2.5982 | -2.7355 | -3.0276 | -6.0634 | 2.8073 | 3.3631 | 6.3713 | 131.1311 | 22.4655 | -130.324 | -48.8689 | -157.5345 | 49.676 |  | 0.96085 | 0.8511 | 0.77853 | 0.98456 | 0.89809 | 0.82483 | -3.8689 | -133.4214 | 118.6818 | -3.782 | -132.0628 | 117.4905
Line_2 | 0.17434 | 0.37704 | 0.36122 | 0.17434 | 0.37704 | 0.36122 | 2.0131 | 4.3537 | 4.171 | 2.0131 | 4.3537 | 4.171 | -1.3836 | -3.456 | -1.2312 | 1.3994 | 3.5299 | 1.2991 | -1.3857 | -1.5977 | -3.1087 | 1.4036 | 1.6816 | 3.1856 | 131.1311 | 22.4655 | -130.324 | -48.8689 | -157.5345 | 49.676 |  | 0.97271 | 0.87453 | 0.80164 | 0.98456 | 0.89809 | 0.82483 | -3.8249 | -132.7238 | 118.069 | -3.782 | -132.0628 | 117.4905
Line_3 | 0.17434 | 0.37704 | 0.36122 | 0.17434 | 0.37704 | 0.36122 | 2.0131 | 4.3537 | 4.171 | 2.0131 | 4.3537 | 4.171 | -1.3678 | -3.3821 | -1.1634 | 1.3836 | 3.456 | 1.2312 | -1.3678 | -1.5138 | -3.0317 | 1.3857 | 1.5977 | 3.1087 | 131.1311 | 22.4655 | -130.324 | -48.8689 | -157.5345 | 49.676 |  | 0.96085 | 0.8511 | 0.77853 | 0.97271 | 0.87453 | 0.80164 | -3.8689 | -133.4214 | 118.6818 | -3.8249 | -132.7238 | 118.069

## LLG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 3.0092 | 3.0092 | 3.0092 | 3.0092 | 3.0092 | 3.0092 | 34.7474 | 34.7474 | 34.7474 | 34.7474 | 34.7474 | 34.7474 | 15.0681 | 15.0681 | 15.0681 | -6.0272 | -6.0272 | -6.0272 | 8.9044 | 8.9044 | 8.9044 | -3.5618 | -3.5618 | -3.5618 | -62.3733 | 177.6267 | 57.6267 | 117.6267 | -2.3733 | -122.3733 |  | 0.50371 | 0.50371 | 0.50371 | 0.20148 | 0.20148 | 0.20148 | -31.7926 | -151.7926 | 88.2074 | -31.7926 | -151.7926 | 88.2074
Line_1 | 2.0061 | 2.0061 | 2.0061 | 2.0061 | 2.0061 | 2.0061 | 23.1649 | 23.1649 | 23.1649 | 23.1649 | 23.1649 | 23.1649 | -1.9999e-10 | -2.0104e-10 | -2.0259e-10 | 4.0182 | 4.0182 | 4.0182 | -7.4077e-09 | -1.6445e-10 | -1.643e-10 | 2.3745 | 2.3745 | 2.3745 | 117.6267 | -2.3733 | -122.3733 | -62.3733 | 177.6267 | 57.6267 |  | 0 | 0 | 0 | 0.20148 | 0.20148 | 0.20148 | 0 | 0 | 0 | -31.7926 | -151.7926 | 88.2074
Line_2 | 1.0031 | 1.0031 | 1.0031 | 1.0031 | 1.0031 | 1.0031 | 11.5825 | 11.5825 | 11.5825 | 11.5825 | 11.5825 | 11.5825 | -1.0045 | -1.0045 | -1.0045 | 2.0091 | 2.0091 | 2.0091 | -0.59363 | -0.59363 | -0.59363 | 1.1873 | 1.1873 | 1.1873 | 117.6267 | -2.3733 | -122.3733 | -62.3733 | 177.6267 | 57.6267 |  | 0.10074 | 0.10074 | 0.10074 | 0.20148 | 0.20148 | 0.20148 | -31.7926 | -151.7926 | 88.2074 | -31.7926 | -151.7926 | 88.2074
Line_3 | 1.0031 | 1.0031 | 1.0031 | 1.0031 | 1.0031 | 1.0031 | 11.5825 | 11.5825 | 11.5825 | 11.5825 | 11.5825 | 11.5825 | -9.9995e-11 | -1.0052e-10 | -1.013e-10 | 1.0045 | 1.0045 | 1.0045 | -3.7038e-09 | -8.2224e-11 | -8.215e-11 | 0.59363 | 0.59363 | 0.59363 | 117.6267 | -2.3733 | -122.3733 | -62.3733 | 177.6267 | 57.6267 |  | 0 | 0 | 0 | 0.10074 | 0.10074 | 0.10074 | 0 | 0 | 0 | -31.7926 | -151.7926 | 88.2074

## LLG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 3.0092 | 3.0092 | 3.0092 | 3.0092 | 3.0092 | 3.0092 | 34.7474 | 34.7474 | 34.7474 | 34.7474 | 34.7474 | 34.7474 | 15.0681 | 15.0681 | 15.0681 | -6.0272 | -6.0272 | -6.0272 | 8.9044 | 8.9044 | 8.9044 | -3.5618 | -3.5618 | -3.5618 | -62.3733 | 177.6267 | 57.6267 | 117.6267 | -2.3733 | -122.3733 |  | 0.50371 | 0.50371 | 0.50371 | 0.20148 | 0.20148 | 0.20148 | -31.7926 | -151.7926 | 88.2074 | -31.7926 | -151.7926 | 88.2074
Line_1 | 2.0061 | 2.0061 | 2.0061 | 2.0061 | 2.0061 | 2.0061 | 23.1649 | 23.1649 | 23.1649 | 23.1649 | 23.1649 | 23.1649 | -1.9999e-10 | -2.0104e-10 | -2.0259e-10 | 4.0182 | 4.0182 | 4.0182 | -7.4077e-09 | -1.6445e-10 | -1.643e-10 | 2.3745 | 2.3745 | 2.3745 | 117.6267 | -2.3733 | -122.3733 | -62.3733 | 177.6267 | 57.6267 |  | 0 | 0 | 0 | 0.20148 | 0.20148 | 0.20148 | 0 | 0 | 0 | -31.7926 | -151.7926 | 88.2074
Line_2 | 1.0031 | 1.0031 | 1.0031 | 1.0031 | 1.0031 | 1.0031 | 11.5825 | 11.5825 | 11.5825 | 11.5825 | 11.5825 | 11.5825 | -1.0045 | -1.0045 | -1.0045 | 2.0091 | 2.0091 | 2.0091 | -0.59363 | -0.59363 | -0.59363 | 1.1873 | 1.1873 | 1.1873 | 117.6267 | -2.3733 | -122.3733 | -62.3733 | 177.6267 | 57.6267 |  | 0.10074 | 0.10074 | 0.10074 | 0.20148 | 0.20148 | 0.20148 | -31.7926 | -151.7926 | 88.2074 | -31.7926 | -151.7926 | 88.2074
Line_3 | 1.0031 | 1.0031 | 1.0031 | 1.0031 | 1.0031 | 1.0031 | 11.5825 | 11.5825 | 11.5825 | 11.5825 | 11.5825 | 11.5825 | -9.9995e-11 | -1.0052e-10 | -1.013e-10 | 1.0045 | 1.0045 | 1.0045 | -3.7038e-09 | -8.2224e-11 | -8.215e-11 | 0.59363 | 0.59363 | 0.59363 | 117.6267 | -2.3733 | -122.3733 | -62.3733 | 177.6267 | 57.6267 |  | 0 | 0 | 0 | 0.10074 | 0.10074 | 0.10074 | 0 | 0 | 0 | -31.7926 | -151.7926 | 88.2074

## LLG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.4637 | 0.96846 | 0.94134 | 0.4637 | 0.96846 | 0.94134 | 5.3544 | 11.1828 | 10.8696 | 5.3544 | 11.1828 | 10.8696 | 3.5831 | 9.0613 | 4.1691 | -3.3684 | -8.1249 | -3.2844 | 3.4367 | 4.1348 | 7.854 | -3.3099 | -3.5815 | -7.3312 | -47.6372 | -154.9189 | 53.1389 | 132.3628 | 25.0811 | -126.8611 |  | 0.92725 | 0.89066 | 0.81806 | 0.88198 | 0.79401 | 0.73906 | -3.8316 | -130.3907 | 115.1783 | -3.1395 | -131.1308 | 119.0062
Line_1 | 0.30914 | 0.64564 | 0.62756 | 0.30914 | 0.64564 | 0.62756 | 3.5696 | 7.4552 | 7.2464 | 3.5696 | 7.4552 | 7.2464 | -2.1502 | -5.0004 | -1.7964 | 2.2456 | 5.4166 | 2.1896 | -2.1502 | -2.1417 | -4.6551 | 2.2066 | 2.3877 | 4.8875 | 132.3628 | 25.0811 | -126.8611 | -47.6372 | -154.9189 | 53.1389 |  | 0.85188 | 0.72966 | 0.68858 | 0.88198 | 0.79401 | 0.73906 | -2.6372 | -131.7331 | 122.0371 | -3.1395 | -131.1308 | 119.0062
Line_2 | 0.15457 | 0.32282 | 0.31378 | 0.15457 | 0.32282 | 0.31378 | 1.7848 | 3.7276 | 3.6232 | 1.7848 | 3.7276 | 3.6232 | -1.099 | -2.6042 | -0.99651 | 1.1228 | 2.7083 | 1.0948 | -1.0892 | -1.1323 | -2.3856 | 1.1033 | 1.1938 | 2.4437 | 132.3628 | 25.0811 | -126.8611 | -47.6372 | -154.9189 | 53.1389 |  | 0.86692 | 0.76182 | 0.71357 | 0.88198 | 0.79401 | 0.73906 | -2.8927 | -131.4192 | 120.4681 | -3.1395 | -131.1308 | 119.0062
Line_3 | 0.15457 | 0.32282 | 0.31378 | 0.15457 | 0.32282 | 0.31378 | 1.7848 | 3.7276 | 3.6232 | 1.7848 | 3.7276 | 3.6232 | -1.0751 | -2.5002 | -0.89821 | 1.099 | 2.6042 | 0.99651 | -1.0751 | -1.0709 | -2.3276 | 1.0892 | 1.1323 | 2.3856 | 132.3628 | 25.0811 | -126.8611 | -47.6372 | -154.9189 | 53.1389 |  | 0.85188 | 0.72966 | 0.68858 | 0.86692 | 0.76182 | 0.71357 | -2.6372 | -131.7331 | 122.0371 | -2.8927 | -131.4192 | 120.4681

## LLG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.4637 | 0.96846 | 0.94134 | 0.4637 | 0.96846 | 0.94134 | 5.3544 | 11.1828 | 10.8696 | 5.3544 | 11.1828 | 10.8696 | 3.5831 | 9.0613 | 4.1691 | -3.3684 | -8.1249 | -3.2844 | 3.4367 | 4.1348 | 7.854 | -3.3099 | -3.5815 | -7.3312 | -47.6372 | -154.9189 | 53.1389 | 132.3628 | 25.0811 | -126.8611 |  | 0.92725 | 0.89066 | 0.81806 | 0.88198 | 0.79401 | 0.73906 | -3.8316 | -130.3907 | 115.1783 | -3.1395 | -131.1308 | 119.0062
Line_1 | 0.30914 | 0.64564 | 0.62756 | 0.30914 | 0.64564 | 0.62756 | 3.5696 | 7.4552 | 7.2464 | 3.5696 | 7.4552 | 7.2464 | -2.1502 | -5.0004 | -1.7964 | 2.2456 | 5.4166 | 2.1896 | -2.1502 | -2.1417 | -4.6551 | 2.2066 | 2.3877 | 4.8875 | 132.3628 | 25.0811 | -126.8611 | -47.6372 | -154.9189 | 53.1389 |  | 0.85188 | 0.72966 | 0.68858 | 0.88198 | 0.79401 | 0.73906 | -2.6372 | -131.7331 | 122.0371 | -3.1395 | -131.1308 | 119.0062
Line_2 | 0.15457 | 0.32282 | 0.31378 | 0.15457 | 0.32282 | 0.31378 | 1.7848 | 3.7276 | 3.6232 | 1.7848 | 3.7276 | 3.6232 | -1.099 | -2.6042 | -0.99651 | 1.1228 | 2.7083 | 1.0948 | -1.0892 | -1.1323 | -2.3856 | 1.1033 | 1.1938 | 2.4437 | 132.3628 | 25.0811 | -126.8611 | -47.6372 | -154.9189 | 53.1389 |  | 0.86692 | 0.76182 | 0.71357 | 0.88198 | 0.79401 | 0.73906 | -2.8927 | -131.4192 | 120.4681 | -3.1395 | -131.1308 | 119.0062
Line_3 | 0.15457 | 0.32282 | 0.31378 | 0.15457 | 0.32282 | 0.31378 | 1.7848 | 3.7276 | 3.6232 | 1.7848 | 3.7276 | 3.6232 | -1.0751 | -2.5002 | -0.89821 | 1.099 | 2.6042 | 0.99651 | -1.0751 | -1.0709 | -2.3276 | 1.0892 | 1.1323 | 2.3856 | 132.3628 | 25.0811 | -126.8611 | -47.6372 | -154.9189 | 53.1389 |  | 0.85188 | 0.72966 | 0.68858 | 0.86692 | 0.76182 | 0.71357 | -2.6372 | -131.7331 | 122.0371 | -2.8927 | -131.4192 | 120.4681