## LLL_max_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.70184 | 0.70184 | -7.4193 | -7.4193
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.70184 | 0.70184 | -7.4193 | -7.4193
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.70184 | 0.70184 | -7.4193 | -7.4193
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.70184 | 0.70184 | -7.4193 | -7.4193
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.70184 | 0.70184 | -7.4193 | -7.4193
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.70184 | 0.70184 | -7.4193 | -7.4193
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.70184 | 0.70184 | -7.4193 | -7.4193
Line16_4_18 | 3.6243 | 3.6243 | 0 | 7.0007 | 2.511 | 2.511 | 0.39406 | -1e-07 | 0.78812 | -1e-07 | -70.8543 | 109.1457 | 0.35092 | 0 | -7.4193 | 0
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.70184 | 0.70184 | -7.4193 | -7.4193
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.70184 | 0.70184 | -7.4193 | -7.4193
Line2_1_4 | 3.6243 | 3.6243 | 0 | 0 | 2.511 | 2.511 | 0.78812 | -0.39406 | 1.5762 | -0.78812 | -70.8543 | 109.1457 | 0.70184 | 0.35092 | -7.4193 | -7.4193
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.70184 | 0.70184 | -7.4193 | -7.4193
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.70184 | 0.70184 | -7.4193 | -7.4193
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.70184 | 0.70184 | -7.4193 | -7.4193
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.70184 | 0.70184 | -7.4193 | -7.4193
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.70184 | 0.70184 | -7.4193 | -7.4193
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.70184 | 0.70184 | -7.4193 | -7.4193
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.70184 | 0.70184 | -7.4193 | -7.4193

## LLL_max_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72372 | 0.72372 | -7.6495 | -7.6495
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72372 | 0.72372 | -7.6495 | -7.6495
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72372 | 0.72372 | -7.6495 | -7.6495
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72372 | 0.72372 | -7.6495 | -7.6495
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72372 | 0.72372 | -7.6495 | -7.6495
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72372 | 0.72372 | -7.6495 | -7.6495
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72372 | 0.72372 | -7.6495 | -7.6495
Line16_4_18 | 3.7373 | 3.7373 | 0 | 7.2438 | 2.5893 | 2.5893 | 0.41902 | -1e-07 | 0.83803 | -1e-07 | -71.0844 | 108.9156 | 0.36186 | 0 | -7.6495 | 0
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72372 | 0.72372 | -7.6495 | -7.6495
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72372 | 0.72372 | -7.6495 | -7.6495
Line2_1_4 | 3.7373 | 3.7373 | 0 | 0 | 2.5893 | 2.5893 | 0.83803 | -0.41902 | 1.6761 | -0.83803 | -71.0844 | 108.9156 | 0.72372 | 0.36186 | -7.6495 | -7.6495
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72372 | 0.72372 | -7.6495 | -7.6495
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72372 | 0.72372 | -7.6495 | -7.6495
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72372 | 0.72372 | -7.6495 | -7.6495
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72372 | 0.72372 | -7.6495 | -7.6495
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72372 | 0.72372 | -7.6495 | -7.6495
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72372 | 0.72372 | -7.6495 | -7.6495
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72372 | 0.72372 | -7.6495 | -7.6495

## LLL_max_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.12051 | -0.12051
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.12051 | -0.12051
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.12051 | -0.12051
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.12051 | -0.12051
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.12051 | -0.12051
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.12051 | -0.12051
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.12051 | -0.12051
Line16_4_18 | 0.034003 | 0.034003 | 0 | 0.065681 | 0.023558 | 0.023558 | 0.017378 | -0.017343 | 0.017412 | -0.017343 | -45.2344 | 134.7656 | 1.0442 | 1.0411 | -0.17729 | -0.23442
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.12051 | -0.12051
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.12051 | -0.12051
Line2_1_4 | 0.034003 | 0.034003 | 0 | 0 | 0.023558 | 0.023558 | 0.017412 | -0.017378 | 0.017482 | -0.017412 | -45.2344 | 134.7656 | 1.0474 | 1.0442 | -0.12051 | -0.17729
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.12051 | -0.12051
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.12051 | -0.12051
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.12051 | -0.12051
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.12051 | -0.12051
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.12051 | -0.12051
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.12051 | -0.12051
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.12051 | -0.12051

## LLL_max_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12619 | -0.12619
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12619 | -0.12619
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12619 | -0.12619
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12619 | -0.12619
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12619 | -0.12619
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12619 | -0.12619
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12619 | -0.12619
Line16_4_18 | 0.035618 | 0.035618 | 0 | 0.069037 | 0.024677 | 0.024677 | 0.019068 | -0.01903 | 0.019106 | -0.01903 | -45.2401 | 134.7599 | 1.0938 | 1.0906 | -0.18297 | -0.2401
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12619 | -0.12619
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12619 | -0.12619
Line2_1_4 | 0.035618 | 0.035618 | 0 | 0 | 0.024677 | 0.024677 | 0.019106 | -0.019068 | 0.019182 | -0.019106 | -45.2401 | 134.7599 | 1.0971 | 1.0938 | -0.12619 | -0.18297
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12619 | -0.12619
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12619 | -0.12619
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12619 | -0.12619
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12619 | -0.12619
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12619 | -0.12619
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12619 | -0.12619
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12619 | -0.12619

## LLL_min_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.695 | 0.695 | -11.6026 | -11.6026
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.695 | 0.695 | -11.6026 | -11.6026
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.695 | 0.695 | -11.6026 | -11.6026
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.695 | 0.695 | -11.6026 | -11.6026
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.695 | 0.695 | -11.6026 | -11.6026
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.695 | 0.695 | -11.6026 | -11.6026
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.695 | 0.695 | -11.6026 | -11.6026
Line16_4_18 | 2.8946 | 2.8946 | 0 | 4.7808 | 2.0055 | 2.0055 | 0.48263 | -1e-07 | 0.50274 | -1e-07 | -57.7717 | 122.2283 | 0.3475 | 0 | -11.6026 | 0
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.695 | 0.695 | -11.6026 | -11.6026
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.695 | 0.695 | -11.6026 | -11.6026
Line2_1_4 | 2.8946 | 2.8946 | 0 | 0 | 2.0055 | 2.0055 | 0.96525 | -0.48263 | 1.0055 | -0.50274 | -57.7717 | 122.2283 | 0.695 | 0.3475 | -11.6026 | -11.6026
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.695 | 0.695 | -11.6026 | -11.6026
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.695 | 0.695 | -11.6026 | -11.6026
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.695 | 0.695 | -11.6026 | -11.6026
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.695 | 0.695 | -11.6026 | -11.6026
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.695 | 0.695 | -11.6026 | -11.6026
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.695 | 0.695 | -11.6026 | -11.6026
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.695 | 0.695 | -11.6026 | -11.6026

## LLL_min_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65842 | 0.65842 | -11.6026 | -11.6026
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65842 | 0.65842 | -11.6026 | -11.6026
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65842 | 0.65842 | -11.6026 | -11.6026
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65842 | 0.65842 | -11.6026 | -11.6026
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65842 | 0.65842 | -11.6026 | -11.6026
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65842 | 0.65842 | -11.6026 | -11.6026
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65842 | 0.65842 | -11.6026 | -11.6026
Line16_4_18 | 2.7423 | 2.7423 | 0 | 4.5292 | 1.8999 | 1.8999 | 0.43316 | -1e-07 | 0.45121 | -1e-07 | -57.7717 | 122.2283 | 0.32921 | 0 | -11.6026 | 0
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65842 | 0.65842 | -11.6026 | -11.6026
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65842 | 0.65842 | -11.6026 | -11.6026
Line2_1_4 | 2.7423 | 2.7423 | 0 | 0 | 1.8999 | 1.8999 | 0.86632 | -0.43316 | 0.90242 | -0.45121 | -57.7717 | 122.2283 | 0.65842 | 0.32921 | -11.6026 | -11.6026
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65842 | 0.65842 | -11.6026 | -11.6026
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65842 | 0.65842 | -11.6026 | -11.6026
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65842 | 0.65842 | -11.6026 | -11.6026
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65842 | 0.65842 | -11.6026 | -11.6026
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65842 | 0.65842 | -11.6026 | -11.6026
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65842 | 0.65842 | -11.6026 | -11.6026
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65842 | 0.65842 | -11.6026 | -11.6026

## LLL_min_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94754 | 0.94754 | -0.12527 | -0.12527
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94754 | 0.94754 | -0.12527 | -0.12527
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94754 | 0.94754 | -0.12527 | -0.12527
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94754 | 0.94754 | -0.12527 | -0.12527
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94754 | 0.94754 | -0.12527 | -0.12527
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94754 | 0.94754 | -0.12527 | -0.12527
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94754 | 0.94754 | -0.12527 | -0.12527
Line16_4_18 | 0.030706 | 0.030706 | 0 | 0.050714 | 0.021274 | 0.021274 | 0.014197 | -0.014143 | 0.014199 | -0.014143 | -45.1344 | 134.8656 | 0.94385 | 0.94017 | -0.1298 | -0.13436
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94754 | 0.94754 | -0.12527 | -0.12527
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94754 | 0.94754 | -0.12527 | -0.12527
Line2_1_4 | 0.030706 | 0.030706 | 0 | 0 | 0.021274 | 0.021274 | 0.014251 | -0.014197 | 0.014256 | -0.014199 | -45.1344 | 134.8656 | 0.94754 | 0.94385 | -0.12527 | -0.1298
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94754 | 0.94754 | -0.12527 | -0.12527
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94754 | 0.94754 | -0.12527 | -0.12527
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94754 | 0.94754 | -0.12527 | -0.12527
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94754 | 0.94754 | -0.12527 | -0.12527
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94754 | 0.94754 | -0.12527 | -0.12527
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94754 | 0.94754 | -0.12527 | -0.12527
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94754 | 0.94754 | -0.12527 | -0.12527

## LLL_min_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89767 | 0.89767 | -0.12527 | -0.12527
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89767 | 0.89767 | -0.12527 | -0.12527
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89767 | 0.89767 | -0.12527 | -0.12527
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89767 | 0.89767 | -0.12527 | -0.12527
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89767 | 0.89767 | -0.12527 | -0.12527
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89767 | 0.89767 | -0.12527 | -0.12527
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89767 | 0.89767 | -0.12527 | -0.12527
Line16_4_18 | 0.02909 | 0.02909 | 0 | 0.048045 | 0.020154 | 0.020154 | 0.012742 | -0.012693 | 0.012744 | -0.012693 | -45.1344 | 134.8656 | 0.89418 | 0.89069 | -0.1298 | -0.13436
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89767 | 0.89767 | -0.12527 | -0.12527
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89767 | 0.89767 | -0.12527 | -0.12527
Line2_1_4 | 0.02909 | 0.02909 | 0 | 0 | 0.020154 | 0.020154 | 0.012791 | -0.012742 | 0.012795 | -0.012744 | -45.1344 | 134.8656 | 0.89767 | 0.89418 | -0.12527 | -0.1298
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89767 | 0.89767 | -0.12527 | -0.12527
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89767 | 0.89767 | -0.12527 | -0.12527
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89767 | 0.89767 | -0.12527 | -0.12527
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89767 | 0.89767 | -0.12527 | -0.12527
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89767 | 0.89767 | -0.12527 | -0.12527
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89767 | 0.89767 | -0.12527 | -0.12527
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89767 | 0.89767 | -0.12527 | -0.12527

## LL_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.4893e-15 | -3.0235e-09 | -4.8365e-09 | -6.5281e-15 | 3.0235e-09 | 4.8365e-09 | -2.6812e-15 | 5.1114e-09 | -1.9712e-09 | 2.6618e-15 | -5.1114e-09 | 1.9712e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.85292 | 0.7501 | 1.05 | 0.85292 | 0.7501 | 4.0311e-13 | -135.0364 | 126.5322 | 3.2459e-13 | -135.0364 | 126.5322
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3132e-15 | -3.0235e-09 | -4.8365e-09 | -4.3909e-15 | 3.0235e-09 | 4.8365e-09 | -1.6709e-15 | 5.1114e-09 | -1.9712e-09 | 1.6709e-15 | -5.1114e-09 | 1.9712e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.85292 | 0.7501 | 1.05 | 0.85292 | 0.7501 | 2.832e-13 | -135.0364 | 126.5322 | 2.2644e-13 | -135.0364 | 126.5322
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2744e-15 | -2.5196e-09 | -4.0305e-09 | -4.2744e-15 | 2.5196e-09 | 4.0305e-09 | -1.6709e-15 | 4.2595e-09 | -1.6426e-09 | 1.632e-15 | -4.2595e-09 | 1.6426e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.85292 | 0.7501 | 1.05 | 0.85292 | 0.7501 | 2.2644e-13 | -135.0364 | 126.5322 | 1.7253e-13 | -135.0364 | 126.5322
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3315e-16 | -1.5118e-09 | -2.4183e-09 | -2.3315e-16 | 1.5118e-09 | 2.4183e-09 | 9.7145e-17 | 2.5557e-09 | -9.8558e-10 | -5.8287e-17 | -2.5557e-09 | 9.8558e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.85292 | 0.7501 | 1.05 | 0.85292 | 0.7501 | 1.7253e-13 | -135.0364 | 126.5322 | 1.69e-13 | -135.0364 | 126.5322
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1966e-15 | -5.0392e-10 | -8.0609e-10 | -4.1189e-15 | 5.0392e-10 | 8.0609e-10 | -1.7097e-15 | 8.5191e-10 | -3.2852e-10 | 1.7486e-15 | -8.5191e-10 | 3.2852e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.85292 | 0.7501 | 1.05 | 0.85292 | 0.7501 | 1.7253e-13 | -135.0364 | 126.5322 | 1.2029e-13 | -135.0364 | 126.5322
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7716e-17 | -1.0078e-09 | -1.6122e-09 | -7.7716e-17 | 1.0078e-09 | 1.6122e-09 | 2.2923e-31 | 1.7038e-09 | -6.5706e-10 | 1.9429e-17 | -1.7038e-09 | 6.5706e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.85292 | 0.7501 | 1.05 | 0.85292 | 0.7501 | 1.69e-13 | -135.0364 | 126.5322 | 1.6722e-13 | -135.0364 | 126.5322
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8858e-17 | -5.0392e-10 | -8.0609e-10 | -7.7716e-17 | 5.0392e-10 | 8.0609e-10 | -1.9429e-17 | 8.5191e-10 | -3.2853e-10 | 3.8858e-17 | -8.5191e-10 | 3.2853e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.85292 | 0.7501 | 1.05 | 0.85292 | 0.7501 | 1.6722e-13 | -135.0364 | 126.5322 | 1.667e-13 | -135.0364 | 126.5322
Line16_4_18 | 0 | 3.1387 | 3.1387 | 0 | 3.1387 | 3.1387 | 0 | 0.72485 | 0.72485 | 0 | 0.72485 | 0.72485 | -1.5543e-16 | 0.45801 | -0.26098 | 7.7716e-17 | -0.3595 | 0.3595 | -1.7272e-30 | 0.072221 | 0.32184 | 8.6005e-31 | 0.12481 | -0.12481 | 0 | -160.8543 | 19.1457 | 0 | 19.1457 | -160.8543 | 1.05 | 0.63968 | 0.57164 | 1.05 | 0.525 | 0.525 | 6.3668e-13 | -151.8935 | 148.1848 | 6.3407e-13 | 180 | -180
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.3647e-15 | -5.0393e-10 | -8.0609e-10 | -9.3647e-15 | 5.0393e-10 | 8.0609e-10 | -4.8184e-15 | 8.519e-10 | -3.2852e-10 | 4.8184e-15 | -8.519e-10 | 3.2852e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.85292 | 0.7501 | 1.05 | 0.85292 | 0.7501 | 2.7983e-13 | -135.0364 | 126.5322 | 1.6176e-13 | -135.0364 | 126.5322
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5852e-15 | -4.0314e-09 | -6.4487e-09 | -4.6241e-15 | 4.0314e-09 | 6.4487e-09 | -1.5737e-15 | 6.8153e-09 | -2.6282e-09 | 1.5737e-15 | -6.8153e-09 | 2.6282e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.85292 | 0.7501 | 1.05 | 0.85292 | 0.7501 | 4.0311e-13 | -135.0364 | 126.5322 | 3.4214e-13 | -135.0364 | 126.5322
Line2_1_4 | 0 | 3.1387 | 3.1387 | 0 | 3.1387 | 3.1387 | 0 | 0.72485 | 0.72485 | 0 | 0.72485 | 0.72485 | -1.8963e-14 | 0.55653 | -0.16247 | 1.8885e-14 | -0.45801 | 0.26098 | 1.053e-14 | 0.26925 | 0.51887 | -1.0569e-14 | -0.072221 | -0.32184 | 0 | -160.8543 | 19.1457 | 0 | 19.1457 | -160.8543 | 1.05 | 0.85292 | 0.7501 | 1.05 | 0.63968 | 0.57164 | 4.0311e-13 | -135.0364 | 126.5322 | 6.3668e-13 | -151.8935 | 148.1848
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.6756e-15 | -1.0078e-09 | -1.6122e-09 | -9.7145e-15 | 1.0078e-09 | 1.6122e-09 | -4.7989e-15 | 1.7038e-09 | -6.5705e-10 | 4.7795e-15 | -1.7038e-09 | 6.5705e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.85292 | 0.7501 | 1.05 | 0.85292 | 0.7501 | 4.0311e-13 | -135.0364 | 126.5322 | 2.7983e-13 | -135.0364 | 126.5322
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.4893e-15 | -2.5196e-09 | -4.0305e-09 | -6.4504e-15 | 2.5196e-09 | 4.0305e-09 | -2.8172e-15 | 4.2595e-09 | -1.6426e-09 | 2.7978e-15 | -4.2595e-09 | 1.6426e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.85292 | 0.7501 | 1.05 | 0.85292 | 0.7501 | 3.2459e-13 | -135.0364 | 126.5322 | 2.4776e-13 | -135.0364 | 126.5322
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.1007e-15 | -2.0157e-09 | -3.2244e-09 | -6.1395e-15 | 2.0157e-09 | 3.2244e-09 | -2.7783e-15 | 3.4076e-09 | -1.3141e-09 | 2.7395e-15 | -3.4076e-09 | 1.3141e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.85292 | 0.7501 | 1.05 | 0.85292 | 0.7501 | 2.4776e-13 | -135.0364 | 126.5322 | 1.7294e-13 | -135.0364 | 126.5322
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9429e-16 | -1.5118e-09 | -2.4183e-09 | -1.5543e-16 | 1.5118e-09 | 2.4183e-09 | -1.1657e-16 | 2.5557e-09 | -9.8558e-10 | 9.7145e-17 | -2.5557e-09 | 9.8558e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.85292 | 0.7501 | 1.05 | 0.85292 | 0.7501 | 1.7294e-13 | -135.0364 | 126.5322 | 1.7016e-13 | -135.0364 | 126.5322
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8858e-17 | -5.0392e-10 | -8.0609e-10 | -3.8858e-17 | 5.0392e-10 | 8.0609e-10 | -5.8287e-17 | 8.5191e-10 | -3.2853e-10 | 3.8858e-17 | -8.5191e-10 | 3.2853e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.85292 | 0.7501 | 1.05 | 0.85292 | 0.7501 | 1.7016e-13 | -135.0364 | 126.5322 | 1.6912e-13 | -135.0364 | 126.5322
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7311e-31 | -5.0392e-10 | -8.0609e-10 | -1.147e-31 | 5.0392e-10 | 8.0609e-10 | -5.8287e-17 | 8.5191e-10 | -3.2853e-10 | 3.8858e-17 | -8.5191e-10 | 3.2853e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.85292 | 0.7501 | 1.05 | 0.85292 | 0.7501 | 1.7016e-13 | -135.0364 | 126.5322 | 1.6912e-13 | -135.0364 | 126.5322
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4686e-15 | -3.5274e-09 | -5.6426e-09 | -4.4686e-15 | 3.5274e-09 | 5.6426e-09 | -1.6515e-15 | 5.9633e-09 | -2.2997e-09 | 1.6709e-15 | -5.9633e-09 | 2.2997e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.85292 | 0.7501 | 1.05 | 0.85292 | 0.7501 | 3.4214e-13 | -135.0364 | 126.5322 | 2.832e-13 | -135.0364 | 126.5322

## LL_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.9204e-15 | -3.3669e-09 | -5.3859e-09 | -6.9204e-15 | 3.3669e-09 | 5.3859e-09 | -2.8089e-15 | 5.759e-09 | -2.262e-09 | 2.8089e-15 | -5.759e-09 | 2.262e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.88719 | 0.77689 | 1.1 | 0.88719 | 0.77689 | 4.2531e-13 | -135.5593 | 126.9102 | 3.511e-13 | -135.5593 | 126.9102
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7221e-15 | -3.3669e-09 | -5.3859e-09 | -4.7221e-15 | 3.3669e-09 | 5.3859e-09 | -1.8319e-15 | 5.759e-09 | -2.262e-09 | 1.7505e-15 | -5.759e-09 | 2.262e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.88719 | 0.77689 | 1.1 | 0.88719 | 0.77689 | 3.0935e-13 | -135.5593 | 126.9102 | 2.5433e-13 | -135.5593 | 126.9102
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4372e-15 | -2.8058e-09 | -4.4883e-09 | -4.5186e-15 | 2.8058e-09 | 4.4883e-09 | -1.7505e-15 | 4.7992e-09 | -1.885e-09 | 1.7505e-15 | -4.7992e-09 | 1.885e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.88719 | 0.77689 | 1.1 | 0.88719 | 0.77689 | 2.5433e-13 | -135.5593 | 126.9102 | 2.028e-13 | -135.5593 | 126.9102
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0354e-16 | -1.6835e-09 | -2.693e-09 | -2.4425e-16 | 1.6835e-09 | 2.693e-09 | 8.1416e-17 | 2.8795e-09 | -1.131e-09 | -1.2212e-16 | -2.8795e-09 | 1.131e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.88719 | 0.77689 | 1.1 | 0.88719 | 0.77689 | 2.028e-13 | -135.5593 | 126.9102 | 1.9916e-13 | -135.5593 | 126.9102
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0301e-15 | -5.6115e-10 | -8.9765e-10 | -4.0708e-15 | 5.6115e-10 | 8.9765e-10 | -1.7097e-15 | 9.5983e-10 | -3.7699e-10 | 1.669e-15 | -9.5983e-10 | 3.7699e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.88719 | 0.77689 | 1.1 | 0.88719 | 0.77689 | 2.028e-13 | -135.5593 | 126.9102 | 1.5837e-13 | -135.5593 | 126.9102
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.8301e-31 | -1.1223e-09 | -1.7953e-09 | 2.804e-31 | 1.1223e-09 | 1.7953e-09 | 8.1416e-17 | 1.9197e-09 | -7.54e-10 | -8.1416e-17 | -1.9197e-09 | 7.54e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.88719 | 0.77689 | 1.1 | 0.88719 | 0.77689 | 1.9916e-13 | -135.5593 | 126.9102 | 1.9733e-13 | -135.5593 | 126.9102
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.0708e-17 | -5.6115e-10 | -8.9765e-10 | 4.0708e-17 | 5.6115e-10 | 8.9765e-10 | -4.0708e-17 | 9.5983e-10 | -3.77e-10 | 8.1416e-17 | -9.5983e-10 | 3.77e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.88719 | 0.77689 | 1.1 | 0.88719 | 0.77689 | 1.9733e-13 | -135.5593 | 126.9102 | 1.968e-13 | -135.5593 | 126.9102
Line16_4_18 | 0 | 3.2366 | 3.2366 | 0 | 3.2366 | 3.2366 | 0 | 0.74746 | 0.74746 | 0 | 0.74746 | 0.74746 | -1.6283e-16 | 0.49365 | -0.28415 | 1.6283e-16 | -0.3889 | 0.3889 | 8.1416e-17 | 0.07624 | 0.34278 | -8.1416e-17 | 0.13327 | -0.13327 | 0 | -161.0844 | 18.9156 | 0 | 18.9156 | -161.0844 | 1.1 | 0.66828 | 0.59567 | 1.1 | 0.55 | 0.55 | 6.4987e-13 | -152.305 | 148.5727 | 6.4768e-13 | 180 | 180
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.8514e-15 | -5.6116e-10 | -8.9765e-10 | -9.8514e-15 | 5.6116e-10 | 8.9765e-10 | -5.1292e-15 | 9.5983e-10 | -3.7699e-10 | 5.1699e-15 | -9.5983e-10 | 3.7699e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.88719 | 0.77689 | 1.1 | 0.88719 | 0.77689 | 3.0403e-13 | -135.5593 | 126.9102 | 1.9004e-13 | -135.5593 | 126.9102
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.0071e-15 | -4.4892e-09 | -7.1812e-09 | -5.0071e-15 | 4.4892e-09 | 7.1812e-09 | -1.7097e-15 | 7.6787e-09 | -3.016e-09 | 1.7097e-15 | -7.6787e-09 | 3.016e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.88719 | 0.77689 | 1.1 | 0.88719 | 0.77689 | 4.2531e-13 | -135.5593 | 126.9102 | 3.6668e-13 | -135.5593 | 126.9102
Line2_1_4 | 0 | 3.2366 | 3.2366 | 0 | 3.2366 | 3.2366 | 0 | 0.74746 | 0.74746 | 0 | 0.74746 | 0.74746 | -2.0273e-14 | 0.59841 | -0.17939 | 2.0273e-14 | -0.49365 | 0.28415 | 1.1358e-14 | 0.28575 | 0.55229 | -1.1317e-14 | -0.07624 | -0.34278 | 0 | -161.0844 | 18.9156 | 0 | 18.9156 | -161.0844 | 1.1 | 0.88719 | 0.77689 | 1.1 | 0.66828 | 0.59567 | 4.2531e-13 | -135.5593 | 126.9102 | 6.4987e-13 | -152.305 | 148.5727
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0503e-14 | -1.1223e-09 | -1.7953e-09 | -1.0503e-14 | 1.1223e-09 | 1.7953e-09 | -5.1699e-15 | 1.9197e-09 | -7.5399e-10 | 5.2106e-15 | -1.9197e-09 | 7.5399e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.88719 | 0.77689 | 1.1 | 0.88719 | 0.77689 | 4.2531e-13 | -135.5593 | 126.9102 | 3.0403e-13 | -135.5593 | 126.9102
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.8797e-15 | -2.8058e-09 | -4.4883e-09 | -6.9204e-15 | 2.8058e-09 | 4.4883e-09 | -2.8903e-15 | 4.7992e-09 | -1.885e-09 | 2.8903e-15 | -4.7992e-09 | 1.885e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.88719 | 0.77689 | 1.1 | 0.88719 | 0.77689 | 3.511e-13 | -135.5593 | 126.9102 | 2.7614e-13 | -135.5593 | 126.9102
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.4319e-15 | -2.2446e-09 | -3.5906e-09 | -6.4726e-15 | 2.2446e-09 | 3.5906e-09 | -2.8496e-15 | 3.8393e-09 | -1.508e-09 | 2.8903e-15 | -3.8393e-09 | 1.508e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.88719 | 0.77689 | 1.1 | 0.88719 | 0.77689 | 2.7614e-13 | -135.5593 | 126.9102 | 2.0647e-13 | -135.5593 | 126.9102
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0708e-17 | -1.6835e-09 | -2.693e-09 | -1.2212e-16 | 1.6835e-09 | 2.693e-09 | -8.1416e-17 | 2.8795e-09 | -1.131e-09 | 8.1416e-17 | -2.8795e-09 | 1.131e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.88719 | 0.77689 | 1.1 | 0.88719 | 0.77689 | 2.0647e-13 | -135.5593 | 126.9102 | 2.0361e-13 | -135.5593 | 126.9102
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.6115e-10 | -8.9765e-10 | 0 | 5.6115e-10 | 8.9765e-10 | 0 | 9.5983e-10 | -3.77e-10 | 0 | -9.5983e-10 | 3.77e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.88719 | 0.77689 | 1.1 | 0.88719 | 0.77689 | 2.0361e-13 | -135.5593 | 126.9102 | 2.0253e-13 | -135.5593 | 126.9102
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.1416e-17 | -5.6115e-10 | -8.9765e-10 | -1.2212e-16 | 5.6115e-10 | 8.9765e-10 | -4.0708e-17 | 9.5983e-10 | -3.77e-10 | -4.3169e-31 | -9.5983e-10 | 3.77e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.88719 | 0.77689 | 1.1 | 0.88719 | 0.77689 | 2.0361e-13 | -135.5593 | 126.9102 | 2.0253e-13 | -135.5593 | 126.9102
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8036e-15 | -3.9281e-09 | -6.2836e-09 | -4.7629e-15 | 3.9281e-09 | 6.2836e-09 | -1.6283e-15 | 6.7188e-09 | -2.639e-09 | 1.669e-15 | -6.7188e-09 | 2.639e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.88719 | 0.77689 | 1.1 | 0.88719 | 0.77689 | 3.6668e-13 | -135.5593 | 126.9102 | 3.0935e-13 | -135.5593 | 126.9102

## LL_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2052e-16 | -4.6325e-11 | -1.333e-10 | -1.1991e-16 | 4.6325e-11 | 1.333e-10 | -3.6429e-17 | 1.2762e-10 | 2.3032e-11 | 3.6429e-17 | -1.2762e-10 | -2.3032e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0442 | 1.05 | 1.048 | 1.0442 | 6.4632e-15 | -120.3021 | 119.9453 | 5.0805e-15 | -120.3021 | 119.9453
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7412e-17 | -4.6325e-11 | -1.333e-10 | -7.8019e-17 | 4.6325e-11 | 1.333e-10 | -2.6715e-17 | 1.2762e-10 | 2.3032e-11 | 2.6715e-17 | -1.2762e-10 | -2.3032e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0442 | 1.05 | 1.048 | 1.0442 | 4.3262e-15 | -120.3021 | 119.9453 | 3.307e-15 | -120.3021 | 119.9453
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.9537e-17 | -3.8604e-11 | -1.1109e-10 | -7.9537e-17 | 3.8604e-11 | 1.1109e-10 | -3.0358e-17 | 1.0635e-10 | 1.9193e-11 | 3.0358e-17 | -1.0635e-10 | -1.9193e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0442 | 1.05 | 1.048 | 1.0442 | 3.307e-15 | -120.3021 | 119.9453 | 2.3115e-15 | -120.3021 | 119.9453
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7322e-18 | -2.3162e-11 | -6.6652e-11 | -2.7322e-18 | 2.3162e-11 | 6.6652e-11 | 1.8215e-18 | 6.3811e-11 | 1.1516e-11 | -2.4286e-18 | -6.3811e-11 | -1.1516e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0442 | 1.05 | 1.048 | 1.0442 | 2.3115e-15 | -120.3021 | 119.9453 | 2.2513e-15 | -120.3021 | 119.9453
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.468e-17 | -7.7208e-12 | -2.2217e-11 | -7.468e-17 | 7.7209e-12 | 2.2217e-11 | -3.2179e-17 | 2.127e-11 | 3.8387e-12 | 3.2786e-17 | -2.127e-11 | -3.8387e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0442 | 1.05 | 1.048 | 1.0442 | 2.3115e-15 | -120.3021 | 119.9453 | 1.3934e-15 | -120.3021 | 119.9453
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6429e-18 | -1.5442e-11 | -4.4435e-11 | -3.0358e-18 | 1.5442e-11 | 4.4435e-11 | -6.0715e-19 | 4.2541e-11 | 7.6773e-12 | -1.1773e-34 | -4.2541e-11 | -7.6773e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0442 | 1.05 | 1.048 | 1.0442 | 2.2513e-15 | -120.3021 | 119.9453 | 2.222e-15 | -120.3021 | 119.9453
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.0715e-19 | -7.7208e-12 | -2.2217e-11 | 6.0715e-19 | 7.7208e-12 | 2.2217e-11 | 1.2143e-18 | 2.127e-11 | 3.8387e-12 | -1.8215e-18 | -2.127e-11 | -3.8387e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0442 | 1.05 | 1.048 | 1.0442 | 2.222e-15 | -120.3021 | 119.9453 | 2.2032e-15 | -120.3021 | 119.9453
Line16_4_18 | 0 | 0.0584 | 0.0584 | 0 | 0.0584 | 0.0584 | 0 | 0.013487 | 0.013487 | 0 | 0.013487 | 0.013487 | 2.4286e-18 | 0.013608 | 0.0035134 | -1.2143e-18 | -0.013574 | -0.0034793 | -2.4286e-18 | 0.0036287 | 0.013561 | -2.2276e-34 | -0.0035605 | -0.013493 | 0 | -135.4649 | 44.5351 | 0 | 44.5351 | -135.4649 | 1.05 | 1.0442 | 1.0387 | 1.05 | 1.0405 | 1.0331 | 1.056e-14 | -120.5336 | 120.01 | 1.0511e-14 | -120.7668 | 120.0754
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7182e-16 | -7.7209e-12 | -2.2217e-11 | -1.7182e-16 | 7.7209e-12 | 2.2217e-11 | -8.0144e-17 | 2.127e-11 | 3.8388e-12 | 7.893e-17 | -2.127e-11 | -3.8388e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0442 | 1.05 | 1.048 | 1.0442 | 4.2804e-15 | -120.3021 | 119.9453 | 2.1387e-15 | -120.3021 | 119.9453
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.2573e-17 | -6.1766e-11 | -1.7774e-10 | -8.1966e-17 | 6.1766e-11 | 1.7774e-10 | -2.4893e-17 | 1.7016e-10 | 3.0709e-11 | 2.4893e-17 | -1.7016e-10 | -3.0709e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0442 | 1.05 | 1.048 | 1.0442 | 6.4632e-15 | -120.3021 | 119.9453 | 5.385e-15 | -120.3021 | 119.9453
Line2_1_4 | 0 | 0.0584 | 0.0584 | 0 | 0.0584 | 0.0584 | 0 | 0.013487 | 0.013487 | 0 | 0.013487 | 0.013487 | -3.4668e-16 | 0.013642 | 0.0035475 | 3.4608e-16 | -0.013608 | -0.0035134 | 1.5422e-16 | 0.003697 | 0.013629 | -1.5422e-16 | -0.0036287 | -0.013561 | 0 | -135.4649 | 44.5351 | 0 | 44.5351 | -135.4649 | 1.05 | 1.048 | 1.0442 | 1.05 | 1.0442 | 1.0387 | 6.4632e-15 | -120.3021 | 119.9453 | 1.056e-14 | -120.5336 | 120.01
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7699e-16 | -1.5442e-11 | -4.4435e-11 | -1.7638e-16 | 1.5442e-11 | 4.4435e-11 | -7.6501e-17 | 4.2541e-11 | 7.6775e-12 | 7.6501e-17 | -4.2541e-11 | -7.6775e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0442 | 1.05 | 1.048 | 1.0442 | 6.4632e-15 | -120.3021 | 119.9453 | 4.2804e-15 | -120.3021 | 119.9453
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2173e-16 | -3.8604e-11 | -1.1109e-10 | -1.2234e-16 | 3.8604e-11 | 1.1109e-10 | -3.8251e-17 | 1.0635e-10 | 1.9193e-11 | 3.8858e-17 | -1.0635e-10 | -1.9193e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0442 | 1.05 | 1.048 | 1.0442 | 5.0805e-15 | -120.3021 | 119.9453 | 3.6953e-15 | -120.3021 | 119.9453
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1718e-16 | -3.0883e-11 | -8.887e-11 | -1.1718e-16 | 3.0883e-11 | 8.887e-11 | -4.1894e-17 | 8.5081e-11 | 1.5355e-11 | 4.3715e-17 | -8.5081e-11 | -1.5355e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0442 | 1.05 | 1.048 | 1.0442 | 3.6953e-15 | -120.3021 | 119.9453 | 2.3182e-15 | -120.3021 | 119.9453
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0358e-18 | -2.3162e-11 | -6.6652e-11 | -3.6429e-18 | 2.3162e-11 | 6.6652e-11 | -6.0715e-19 | 6.3811e-11 | 1.1516e-11 | -1.2143e-18 | -6.3811e-11 | -1.1516e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0442 | 1.05 | 1.048 | 1.0442 | 2.3182e-15 | -120.3021 | 119.9453 | 2.2605e-15 | -120.3021 | 119.9453
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0358e-19 | -7.7208e-12 | -2.2217e-11 | -9.1073e-19 | 7.7208e-12 | 2.2217e-11 | 1.1977e-35 | 2.127e-11 | 3.8387e-12 | -3.5702e-35 | -2.127e-11 | -3.8387e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0442 | 1.05 | 1.048 | 1.0442 | 2.2605e-15 | -120.3021 | 119.9453 | 2.2461e-15 | -120.3021 | 119.9453
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.7208e-12 | -2.2217e-11 | -6.0715e-19 | 7.7208e-12 | 2.2217e-11 | 0 | 2.127e-11 | 3.8387e-12 | 1.2143e-18 | -2.127e-11 | -3.8387e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0442 | 1.05 | 1.048 | 1.0442 | 2.2605e-15 | -120.3021 | 119.9453 | 2.2461e-15 | -120.3021 | 119.9453
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.1055e-17 | -5.4046e-11 | -1.5552e-10 | -8.1662e-17 | 5.4046e-11 | 1.5552e-10 | -2.55e-17 | 1.4889e-10 | 2.6871e-11 | 2.6715e-17 | -1.4889e-10 | -2.6871e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0442 | 1.05 | 1.048 | 1.0442 | 5.385e-15 | -120.3021 | 119.9453 | 4.3262e-15 | -120.3021 | 119.9453

## LL_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3103e-16 | -5.3219e-11 | -1.5314e-10 | -1.3039e-16 | 5.3219e-11 | 1.5314e-10 | -3.7528e-17 | 1.4664e-10 | 2.6437e-11 | 3.8164e-17 | -1.4664e-10 | -2.6437e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0936 | 1.1 | 1.0978 | 1.0936 | 7.0758e-15 | -120.3163 | 119.9428 | 5.7319e-15 | -120.3163 | 119.9428
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.7459e-17 | -5.3219e-11 | -1.5314e-10 | -8.7459e-17 | 5.3219e-11 | 1.5314e-10 | -3.0531e-17 | 1.4664e-10 | 2.6437e-11 | 3.0531e-17 | -1.4664e-10 | -2.6437e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0936 | 1.1 | 1.0978 | 1.0936 | 4.9515e-15 | -120.3163 | 119.9428 | 3.9202e-15 | -120.3163 | 119.9428
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.5551e-17 | -4.4349e-11 | -1.2762e-10 | -8.6823e-17 | 4.4349e-11 | 1.2762e-10 | -3.1167e-17 | 1.222e-10 | 2.2031e-11 | 3.1167e-17 | -1.222e-10 | -2.2031e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0936 | 1.1 | 1.0978 | 1.0936 | 3.9202e-15 | -120.3163 | 119.9428 | 2.9275e-15 | -120.3163 | 119.9428
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1344e-18 | -2.6609e-11 | -7.6572e-11 | -3.4984e-18 | 2.6609e-11 | 7.6572e-11 | 3.1803e-18 | 7.332e-11 | 1.3218e-11 | -3.1803e-18 | -7.332e-11 | -1.3218e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0936 | 1.1 | 1.0978 | 1.0936 | 2.9275e-15 | -120.3163 | 119.9428 | 2.8644e-15 | -120.3163 | 119.9428
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.8413e-17 | -8.8698e-12 | -2.5524e-11 | -8.7777e-17 | 8.8698e-12 | 2.5524e-11 | -3.3711e-17 | 2.444e-11 | 4.4062e-12 | 3.3711e-17 | -2.444e-11 | -4.4062e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0936 | 1.1 | 1.0978 | 1.0936 | 2.9275e-15 | -120.3163 | 119.9428 | 1.9178e-15 | -120.3163 | 119.9428
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2262e-18 | -1.7739e-11 | -5.1048e-11 | -1.5902e-18 | 1.7739e-11 | 5.1048e-11 | 2.5443e-18 | 4.888e-11 | 8.8123e-12 | -2.5443e-18 | -4.888e-11 | -8.8123e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0936 | 1.1 | 1.0978 | 1.0936 | 2.8644e-15 | -120.3163 | 119.9428 | 2.8338e-15 | -120.3163 | 119.9428
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1803e-19 | -8.8698e-12 | -2.5524e-11 | 3.1803e-19 | 8.8698e-12 | 2.5524e-11 | 1.5729e-35 | 2.444e-11 | 4.4061e-12 | -6.3607e-19 | -2.444e-11 | -4.4061e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0936 | 1.1 | 1.0978 | 1.0936 | 2.8338e-15 | -120.3163 | 119.9428 | 2.814e-15 | -120.3163 | 119.9428
Line16_4_18 | 0 | 0.061167 | 0.061167 | 0 | 0.061167 | 0.061167 | 0 | 0.014126 | 0.014126 | 0 | 0.014126 | 0.014126 | -2.5443e-18 | 0.01493 | 0.0038518 | 2.5443e-18 | -0.014893 | -0.0038144 | -2.5443e-18 | 0.0039805 | 0.014876 | 4.9206e-34 | -0.0039057 | -0.014801 | 0 | -135.4761 | 44.5239 | 0 | 44.5239 | -135.4761 | 1.1 | 1.0938 | 1.0878 | 1.1 | 1.0899 | 1.0821 | 1.1134e-14 | -120.5478 | 120.0075 | 1.1081e-14 | -120.781 | 120.073
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8891e-16 | -8.8699e-12 | -2.5524e-11 | -1.8828e-16 | 8.8699e-12 | 2.5524e-11 | -8.7777e-17 | 2.444e-11 | 4.4063e-12 | 8.8413e-17 | -2.444e-11 | -4.4063e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0936 | 1.1 | 1.0978 | 1.0936 | 4.8685e-15 | -120.3163 | 119.9428 | 2.7529e-15 | -120.3163 | 119.9428
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.9685e-17 | -7.0958e-11 | -2.0419e-10 | -8.9049e-17 | 7.0958e-11 | 2.0419e-10 | -2.3534e-17 | 1.9552e-10 | 3.5249e-11 | 2.6079e-17 | -1.9552e-10 | -3.5249e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0936 | 1.1 | 1.0978 | 1.0936 | 7.0758e-15 | -120.3163 | 119.9428 | 6.019e-15 | -120.3163 | 119.9428
Line2_1_4 | 0 | 0.061167 | 0.061167 | 0 | 0.061167 | 0.061167 | 0 | 0.014126 | 0.014126 | 0 | 0.014126 | 0.014126 | -3.7782e-16 | 0.014968 | 0.0038892 | 3.7909e-16 | -0.01493 | -0.0038518 | 1.7428e-16 | 0.0040553 | 0.014951 | -1.7301e-16 | -0.0039805 | -0.014876 | 0 | -135.4761 | 44.5239 | 0 | 44.5239 | -135.4761 | 1.1 | 1.0978 | 1.0936 | 1.1 | 1.0938 | 1.0878 | 7.0758e-15 | -120.3163 | 119.9428 | 1.1134e-14 | -120.5478 | 120.0075
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9464e-16 | -1.774e-11 | -5.1048e-11 | -1.9527e-16 | 1.774e-11 | 5.1048e-11 | -8.1416e-17 | 4.888e-11 | 8.8125e-12 | 8.2688e-17 | -4.888e-11 | -8.8124e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0936 | 1.1 | 1.0978 | 1.0936 | 7.0758e-15 | -120.3163 | 119.9428 | 4.8685e-15 | -120.3163 | 119.9428
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3326e-16 | -4.4349e-11 | -1.2762e-10 | -1.3326e-16 | 4.4349e-11 | 1.2762e-10 | -3.8164e-17 | 1.222e-10 | 2.2031e-11 | 3.88e-17 | -1.222e-10 | -2.2031e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0936 | 1.1 | 1.0978 | 1.0936 | 5.7319e-15 | -120.3163 | 119.9428 | 4.3555e-15 | -120.3163 | 119.9428
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2849e-16 | -3.5479e-11 | -1.021e-10 | -1.2849e-16 | 3.5479e-11 | 1.021e-10 | -4.5161e-17 | 9.776e-11 | 1.7625e-11 | 4.5161e-17 | -9.776e-11 | -1.7625e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0936 | 1.1 | 1.0978 | 1.0936 | 4.3555e-15 | -120.3163 | 119.9428 | 2.9825e-15 | -120.3163 | 119.9428
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4525e-18 | -2.6609e-11 | -7.6572e-11 | -4.4525e-18 | 2.6609e-11 | 7.6572e-11 | -6.3607e-19 | 7.332e-11 | 1.3218e-11 | 6.3607e-19 | -7.332e-11 | -1.3218e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0936 | 1.1 | 1.0978 | 1.0936 | 2.9825e-15 | -120.3163 | 119.9428 | 2.922e-15 | -120.3163 | 119.9428
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.3607e-19 | -8.8697e-12 | -2.5524e-11 | 6.3607e-19 | 8.8698e-12 | 2.5524e-11 | 6.3607e-19 | 2.444e-11 | 4.4061e-12 | -6.3607e-19 | -2.444e-11 | -4.4061e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0936 | 1.1 | 1.0978 | 1.0936 | 2.922e-15 | -120.3163 | 119.9428 | 2.907e-15 | -120.3163 | 119.9428
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.8697e-12 | -2.5524e-11 | -6.3607e-19 | 8.8698e-12 | 2.5524e-11 | 0 | 2.444e-11 | 4.4061e-12 | -3.2272e-35 | -2.444e-11 | -4.4061e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0936 | 1.1 | 1.0978 | 1.0936 | 2.922e-15 | -120.3163 | 119.9428 | 2.907e-15 | -120.3163 | 119.9428
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.9049e-17 | -6.2088e-11 | -1.7867e-10 | -8.9685e-17 | 6.2088e-11 | 1.7867e-10 | -2.6079e-17 | 1.7108e-10 | 3.0843e-11 | 2.6715e-17 | -1.7108e-10 | -3.0843e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0936 | 1.1 | 1.0978 | 1.0936 | 6.019e-15 | -120.3163 | 119.9428 | 4.9515e-15 | -120.3163 | 119.9428

## LL_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6651e-15 | -1.4366e-09 | -3.9666e-09 | -3.6651e-15 | 1.4366e-09 | 3.9666e-09 | -3.252e-15 | 4.6273e-09 | -2.4518e-10 | 3.2872e-15 | -4.6273e-09 | 2.4518e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.83839 | 0.68767 | 0.95 | 0.83839 | 0.68767 | 4.2403e-13 | -135.3123 | 120.9775 | 3.4325e-13 | -135.3123 | 120.9775
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7754e-15 | -1.4366e-09 | -3.9666e-09 | -1.7754e-15 | 1.4366e-09 | 3.9666e-09 | -1.7227e-15 | 4.6273e-09 | -2.4518e-10 | 1.7051e-15 | -4.6273e-09 | 2.4518e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.83839 | 0.68767 | 0.95 | 0.83839 | 0.68767 | 3.5975e-13 | -135.3123 | 120.9775 | 3.2606e-13 | -135.3123 | 120.9775
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7842e-15 | -1.1972e-09 | -3.3055e-09 | -1.7842e-15 | 1.1972e-09 | 3.3055e-09 | -1.6875e-15 | 3.8561e-09 | -2.0432e-10 | 1.7051e-15 | -3.8561e-09 | 2.0432e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.83839 | 0.68767 | 0.95 | 0.83839 | 0.68767 | 3.2606e-13 | -135.3123 | 120.9775 | 2.9182e-13 | -135.3123 | 120.9775
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6368e-17 | -7.1829e-10 | -1.9833e-09 | -8.7893e-18 | 7.1829e-10 | 1.9833e-09 | 3.5157e-17 | 2.3137e-09 | -1.2259e-10 | -1.7579e-17 | -2.3136e-09 | 1.2259e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.83839 | 0.68767 | 0.95 | 0.83839 | 0.68767 | 2.9182e-13 | -135.3123 | 120.9775 | 2.9287e-13 | -135.3123 | 120.9775
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0655e-15 | -2.3943e-10 | -6.611e-10 | -2.0479e-15 | 2.3943e-10 | 6.611e-10 | -1.8633e-15 | 7.7122e-10 | -4.0862e-11 | 1.8985e-15 | -7.7122e-10 | 4.0862e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.83839 | 0.68767 | 0.95 | 0.83839 | 0.68767 | 2.9182e-13 | -135.3123 | 120.9775 | 2.4726e-13 | -135.3123 | 120.9775
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.7893e-18 | -4.7886e-10 | -1.3222e-09 | -8.7893e-18 | 4.7886e-10 | 1.3222e-09 | 1.7579e-17 | 1.5424e-09 | -8.1728e-11 | -1.7579e-17 | -1.5424e-09 | 8.1728e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.83839 | 0.68767 | 0.95 | 0.83839 | 0.68767 | 2.9287e-13 | -135.3123 | 120.9775 | 2.9355e-13 | -135.3123 | 120.9775
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7579e-17 | -2.3943e-10 | -6.611e-10 | 1.7579e-17 | 2.3943e-10 | 6.611e-10 | 1.7579e-17 | 7.7122e-10 | -4.0864e-11 | -1.7579e-17 | -7.7122e-10 | 4.0864e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.83839 | 0.68767 | 0.95 | 0.83839 | 0.68767 | 2.9355e-13 | -135.3123 | 120.9775 | 2.9317e-13 | -135.3123 | 120.9775
Line16_4_18 | 0 | 2.5068 | 2.5068 | 0 | 2.5068 | 2.5068 | 0 | 0.57893 | 0.57893 | 0 | 0.57893 | 0.57893 | 0 | 0.35328 | -0.11197 | 0 | -0.23262 | 0.23262 | 0 | -0.020967 | 0.27233 | 0 | 0.14665 | -0.14665 | 0 | -147.7717 | 32.2283 | 0 | 32.2283 | -147.7717 | 0.95 | 0.6113 | 0.50862 | 0.95 | 0.475 | 0.475 | 6.6916e-13 | -151.1682 | 144.5775 | 6.6796e-13 | -180 | 180
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3351e-15 | -2.3944e-10 | -6.611e-10 | -5.3527e-15 | 2.3944e-10 | 6.611e-10 | -5.045e-15 | 7.7122e-10 | -4.0859e-11 | 5.045e-15 | -7.7122e-10 | 4.0859e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.83839 | 0.68767 | 0.95 | 0.83839 | 0.68767 | 2.996e-13 | -135.3123 | 120.9775 | 1.7905e-13 | -135.3123 | 120.9775
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7842e-15 | -1.9154e-09 | -5.2888e-09 | -1.7842e-15 | 1.9154e-09 | 5.2888e-09 | -1.6875e-15 | 6.1697e-09 | -3.2691e-10 | 1.7051e-15 | -6.1697e-09 | 3.2691e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.83839 | 0.68767 | 0.95 | 0.83839 | 0.68767 | 4.2403e-13 | -135.3123 | 120.9775 | 3.9136e-13 | -135.3123 | 120.9775
Line2_1_4 | 0 | 2.5068 | 2.5068 | 0 | 2.5068 | 2.5068 | 0 | 0.57893 | 0.57893 | 0 | 0.57893 | 0.57893 | -1.0266e-14 | 0.47394 | 0.0086903 | 1.0266e-14 | -0.35328 | 0.11197 | 1.1039e-14 | 0.10472 | 0.39802 | -1.1039e-14 | 0.020967 | -0.27233 | 0 | -147.7717 | 32.2283 | 0 | 32.2283 | -147.7717 | 0.95 | 0.83839 | 0.68767 | 0.95 | 0.6113 | 0.50862 | 4.2403e-13 | -135.3123 | 120.9775 | 6.6916e-13 | -151.1682 | 144.5775
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3263e-15 | -4.7887e-10 | -1.3222e-09 | -5.3263e-15 | 4.7887e-10 | 1.3222e-09 | -5.1681e-15 | 1.5424e-09 | -8.1723e-11 | 5.2032e-15 | -1.5424e-09 | 8.1723e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.83839 | 0.68767 | 0.95 | 0.83839 | 0.68767 | 4.2403e-13 | -135.3123 | 120.9775 | 2.996e-13 | -135.3123 | 120.9775
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6388e-15 | -1.1972e-09 | -3.3055e-09 | -3.6212e-15 | 1.1972e-09 | 3.3055e-09 | -3.2696e-15 | 3.8561e-09 | -2.0432e-10 | 3.252e-15 | -3.8561e-09 | 2.0432e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.83839 | 0.68767 | 0.95 | 0.83839 | 0.68767 | 3.4325e-13 | -135.3123 | 120.9775 | 2.6343e-13 | -135.3123 | 120.9775
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5245e-15 | -9.5772e-10 | -2.6444e-09 | -3.5069e-15 | 9.5772e-10 | 2.6444e-09 | -3.1993e-15 | 3.0849e-09 | -1.6345e-10 | 3.1993e-15 | -3.0849e-09 | 1.6345e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.83839 | 0.68767 | 0.95 | 0.83839 | 0.68767 | 2.6343e-13 | -135.3123 | 120.9775 | 1.8593e-13 | -135.3123 | 120.9775
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3946e-17 | -7.1829e-10 | -1.9833e-09 | -2.6368e-17 | 7.1829e-10 | 1.9833e-09 | 1.0547e-16 | 2.3136e-09 | -1.2259e-10 | -1.0547e-16 | -2.3136e-09 | 1.2259e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.83839 | 0.68767 | 0.95 | 0.83839 | 0.68767 | 1.8593e-13 | -135.3123 | 120.9775 | 1.8684e-13 | -135.3123 | 120.9775
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7579e-17 | -2.3943e-10 | -6.611e-10 | -1.7579e-17 | 2.3943e-10 | 6.611e-10 | 5.7324e-32 | 7.7122e-10 | -4.0864e-11 | -1.7579e-17 | -7.7122e-10 | 4.0864e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.83839 | 0.68767 | 0.95 | 0.83839 | 0.68767 | 1.8684e-13 | -135.3123 | 120.9775 | 1.8669e-13 | -135.3123 | 120.9775
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.7579e-17 | -2.3943e-10 | -6.611e-10 | 1.7579e-17 | 2.3943e-10 | 6.611e-10 | 3.5157e-17 | 7.7122e-10 | -4.0864e-11 | -5.2736e-17 | -7.7122e-10 | 4.0864e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.83839 | 0.68767 | 0.95 | 0.83839 | 0.68767 | 1.8684e-13 | -135.3123 | 120.9775 | 1.8669e-13 | -135.3123 | 120.9775
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.793e-15 | -1.676e-09 | -4.6277e-09 | -1.793e-15 | 1.676e-09 | 4.6277e-09 | -1.7227e-15 | 5.3985e-09 | -2.8605e-10 | 1.7051e-15 | -5.3985e-09 | 2.8605e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.83839 | 0.68767 | 0.95 | 0.83839 | 0.68767 | 3.9136e-13 | -135.3123 | 120.9775 | 3.5975e-13 | -135.3123 | 120.9775

## LL_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2724e-15 | -1.2893e-09 | -3.56e-09 | -3.2724e-15 | 1.2893e-09 | 3.56e-09 | -2.931e-15 | 4.153e-09 | -2.2005e-10 | 2.931e-15 | -4.153e-09 | 2.2005e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.79426 | 0.65148 | 0.9 | 0.79426 | 0.65148 | 4.2521e-13 | -135.3123 | 120.9775 | 3.4456e-13 | -135.3123 | 120.9775
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821e-15 | -1.2893e-09 | -3.56e-09 | -1.5821e-15 | 1.2893e-09 | 3.56e-09 | -1.5821e-15 | 4.153e-09 | -2.2005e-10 | 1.5821e-15 | -4.153e-09 | 2.2005e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.79426 | 0.65148 | 0.9 | 0.79426 | 0.65148 | 3.6071e-13 | -135.3123 | 120.9775 | 3.2699e-13 | -135.3123 | 120.9775
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6237e-15 | -1.0745e-09 | -2.9667e-09 | -1.607e-15 | 1.0745e-09 | 2.9667e-09 | -1.5654e-15 | 3.4609e-09 | -1.8338e-10 | 1.5321e-15 | -3.4609e-09 | 1.8338e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.79426 | 0.65148 | 0.9 | 0.79426 | 0.65148 | 3.2699e-13 | -135.3123 | 120.9775 | 2.9371e-13 | -135.3123 | 120.9775
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.3267e-18 | -6.4467e-10 | -1.78e-09 | 8.3267e-18 | 6.4467e-10 | 1.78e-09 | 4.996e-17 | 2.0765e-09 | -1.1003e-10 | -6.6613e-17 | -2.0765e-09 | 1.1003e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.79426 | 0.65148 | 0.9 | 0.79426 | 0.65148 | 2.9371e-13 | -135.3123 | 120.9775 | 2.9477e-13 | -135.3123 | 120.9775
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6903e-15 | -2.1489e-10 | -5.9334e-10 | -1.6903e-15 | 2.1489e-10 | 5.9334e-10 | -1.7653e-15 | 6.9217e-10 | -3.6674e-11 | 1.7653e-15 | -6.9217e-10 | 3.6674e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.79426 | 0.65148 | 0.9 | 0.79426 | 0.65148 | 2.9371e-13 | -135.3123 | 120.9775 | 2.4899e-13 | -135.3123 | 120.9775
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.7135e-31 | -4.2978e-10 | -1.1867e-09 | -1.6653e-17 | 4.2978e-10 | 1.1867e-09 | 3.3307e-17 | 1.3843e-09 | -7.3352e-11 | -4.996e-17 | -1.3843e-09 | 7.3352e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.79426 | 0.65148 | 0.9 | 0.79426 | 0.65148 | 2.9477e-13 | -135.3123 | 120.9775 | 2.9544e-13 | -135.3123 | 120.9775
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6653e-17 | -2.1489e-10 | -5.9334e-10 | -3.3307e-17 | 2.1489e-10 | 5.9334e-10 | 4.996e-17 | 6.9217e-10 | -3.6676e-11 | -4.996e-17 | -6.9217e-10 | 3.6676e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.79426 | 0.65148 | 0.9 | 0.79426 | 0.65148 | 2.9544e-13 | -135.3123 | 120.9775 | 2.9507e-13 | -135.3123 | 120.9775
Line16_4_18 | 0 | 2.3749 | 2.3749 | 0 | 2.3749 | 2.3749 | 0 | 0.54846 | 0.54846 | 0 | 0.54846 | 0.54846 | 0 | 0.31707 | -0.10049 | -6.6613e-17 | -0.20878 | 0.20878 | 0 | -0.018818 | 0.24442 | 6.6613e-17 | 0.13162 | -0.13162 | 0 | -147.7717 | 32.2283 | 0 | 32.2283 | -147.7717 | 0.9 | 0.57913 | 0.48185 | 0.9 | 0.45 | 0.45 | 6.7411e-13 | -151.1682 | 144.5775 | 6.729e-13 | -180 | 180
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7462e-15 | -2.149e-10 | -5.9334e-10 | -4.7295e-15 | 2.149e-10 | 5.9334e-10 | -4.563e-15 | 6.9217e-10 | -3.6671e-11 | 4.5297e-15 | -6.9217e-10 | 3.6671e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.79426 | 0.65148 | 0.9 | 0.79426 | 0.65148 | 3.0078e-13 | -135.3123 | 120.9775 | 1.7999e-13 | -135.3123 | 120.9775
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6237e-15 | -1.7191e-09 | -4.7467e-09 | -1.607e-15 | 1.7191e-09 | 4.7467e-09 | -1.5321e-15 | 5.5374e-09 | -2.934e-10 | 1.5155e-15 | -5.5374e-09 | 2.934e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.79426 | 0.65148 | 0.9 | 0.79426 | 0.65148 | 4.2521e-13 | -135.3123 | 120.9775 | 3.9249e-13 | -135.3123 | 120.9775
Line2_1_4 | 0 | 2.3749 | 2.3749 | 0 | 2.3749 | 2.3749 | 0 | 0.54846 | 0.54846 | 0 | 0.54846 | 0.54846 | -9.3592e-15 | 0.42536 | 0.0077996 | 9.3592e-15 | -0.31707 | 0.10049 | 9.9587e-15 | 0.093984 | 0.35722 | -9.9254e-15 | 0.018818 | -0.24442 | 0 | -147.7717 | 32.2283 | 0 | 32.2283 | -147.7717 | 0.9 | 0.79426 | 0.65148 | 0.9 | 0.57913 | 0.48185 | 4.2521e-13 | -135.3123 | 120.9775 | 6.7411e-13 | -151.1682 | 144.5775
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7795e-15 | -4.2979e-10 | -1.1867e-09 | -4.7795e-15 | 4.2979e-10 | 1.1867e-09 | -4.6629e-15 | 1.3843e-09 | -7.3347e-11 | 4.6796e-15 | -1.3843e-09 | 7.3347e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.79426 | 0.65148 | 0.9 | 0.79426 | 0.65148 | 4.2521e-13 | -135.3123 | 120.9775 | 3.0078e-13 | -135.3123 | 120.9775
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2557e-15 | -1.0745e-09 | -2.9667e-09 | -3.2391e-15 | 1.0745e-09 | 2.9667e-09 | -2.8977e-15 | 3.4609e-09 | -1.8338e-10 | 2.9143e-15 | -3.4609e-09 | 1.8338e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.79426 | 0.65148 | 0.9 | 0.79426 | 0.65148 | 3.4456e-13 | -135.3123 | 120.9775 | 2.638e-13 | -135.3123 | 120.9775
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2224e-15 | -8.5956e-10 | -2.3734e-09 | -3.2058e-15 | 8.5956e-10 | 2.3734e-09 | -2.8977e-15 | 2.7687e-09 | -1.467e-10 | 2.9143e-15 | -2.7687e-09 | 1.467e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.79426 | 0.65148 | 0.9 | 0.79426 | 0.65148 | 2.638e-13 | -135.3123 | 120.9775 | 1.8399e-13 | -135.3123 | 120.9775
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3307e-17 | -6.4467e-10 | -1.78e-09 | -3.3307e-17 | 6.4467e-10 | 1.78e-09 | 1.1657e-16 | 2.0765e-09 | -1.1003e-10 | -9.992e-17 | -2.0765e-09 | 1.1003e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.79426 | 0.65148 | 0.9 | 0.79426 | 0.65148 | 1.8399e-13 | -135.3123 | 120.9775 | 1.849e-13 | -135.3123 | 120.9775
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6653e-17 | -2.1489e-10 | -5.9334e-10 | -1.6653e-17 | 2.1489e-10 | 5.9334e-10 | -1.6653e-17 | 6.9217e-10 | -3.6676e-11 | 1.6653e-17 | -6.9217e-10 | 3.6676e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.79426 | 0.65148 | 0.9 | 0.79426 | 0.65148 | 1.849e-13 | -135.3123 | 120.9775 | 1.8475e-13 | -135.3123 | 120.9775
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3267e-18 | -2.1489e-10 | -5.9334e-10 | 8.3267e-18 | 2.1489e-10 | 5.9334e-10 | 2.6872e-32 | 6.9217e-10 | -3.6676e-11 | 2.6849e-32 | -6.9217e-10 | 3.6676e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.79426 | 0.65148 | 0.9 | 0.79426 | 0.65148 | 1.849e-13 | -135.3123 | 120.9775 | 1.8475e-13 | -135.3123 | 120.9775
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6237e-15 | -1.5042e-09 | -4.1534e-09 | -1.5904e-15 | 1.5042e-09 | 4.1534e-09 | -1.4988e-15 | 4.8452e-09 | -2.5673e-10 | 1.4988e-15 | -4.8452e-09 | 2.5673e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.79426 | 0.65148 | 0.9 | 0.79426 | 0.65148 | 3.9249e-13 | -135.3123 | 120.9775 | 3.6071e-13 | -135.3123 | 120.9775

## LL_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.0751e-17 | -3.8862e-11 | -1.1288e-10 | -8.0751e-17 | 3.8862e-11 | 1.1288e-10 | -6.6469e-17 | 1.0829e-10 | 1.9912e-11 | 6.6469e-17 | -1.0829e-10 | -1.9912e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94812 | 0.94457 | 0.95 | 0.94812 | 0.94457 | 8.4272e-15 | -120.3131 | 119.9422 | 6.7019e-15 | -120.3131 | 119.9422
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0925e-17 | -3.8862e-11 | -1.1288e-10 | -4.0925e-17 | 3.8862e-11 | 1.1288e-10 | -3.5157e-17 | 1.0829e-10 | 1.9912e-11 | 3.5157e-17 | -1.0829e-10 | -1.9912e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94812 | 0.94457 | 0.95 | 0.94812 | 0.94457 | 6.9942e-15 | -120.3131 | 119.9422 | 6.2524e-15 | -120.3131 | 119.9422
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0238e-17 | -3.2385e-11 | -9.4068e-11 | -4.0238e-17 | 3.2385e-11 | 9.4068e-11 | -3.4058e-17 | 9.0245e-11 | 1.6594e-11 | 3.4608e-17 | -9.0245e-11 | -1.6594e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94812 | 0.94457 | 0.95 | 0.94812 | 0.94457 | 6.2524e-15 | -120.3131 | 119.9422 | 5.5244e-15 | -120.3131 | 119.9422
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.0593e-34 | -1.9431e-11 | -5.6441e-11 | 1.5948e-34 | 1.9431e-11 | 5.6441e-11 | 1.0987e-18 | 5.4147e-11 | 9.9561e-12 | -1.648e-18 | -5.4147e-11 | -9.9561e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94812 | 0.94457 | 0.95 | 0.94812 | 0.94457 | 5.5244e-15 | -120.3131 | 119.9422 | 5.5447e-15 | -120.3131 | 119.9422
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5938e-17 | -6.477e-12 | -1.8814e-11 | -4.5938e-17 | 6.477e-12 | 1.8814e-11 | -3.7904e-17 | 1.8049e-11 | 3.3188e-12 | 3.7904e-17 | -1.8049e-11 | -3.3188e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94812 | 0.94457 | 0.95 | 0.94812 | 0.94457 | 5.5244e-15 | -120.3131 | 119.9422 | 4.5739e-15 | -120.3131 | 119.9422
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.03e-18 | -1.2954e-11 | -3.7627e-11 | -1.03e-18 | 1.2954e-11 | 3.7627e-11 | 1.0987e-18 | 3.6098e-11 | 6.6374e-12 | -1.0987e-18 | -3.6098e-11 | -6.6374e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94812 | 0.94457 | 0.95 | 0.94812 | 0.94457 | 5.5447e-15 | -120.3131 | 119.9422 | 5.5604e-15 | -120.3131 | 119.9422
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.9266e-19 | -6.477e-12 | -1.8814e-11 | -6.18e-19 | 6.477e-12 | 1.8814e-11 | 5.4933e-19 | 1.8049e-11 | 3.3187e-12 | -5.9898e-35 | -1.8049e-11 | -3.3187e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94812 | 0.94457 | 0.95 | 0.94812 | 0.94457 | 5.5604e-15 | -120.3131 | 119.9422 | 5.5532e-15 | -120.3131 | 119.9422
Line16_4_18 | 0 | 0.052639 | 0.052639 | 0 | 0.052639 | 0.052639 | 0 | 0.012156 | 0.012156 | 0 | 0.012156 | 0.012156 | -2.6322e-34 | 0.011082 | 0.0028784 | -1.0987e-18 | -0.011029 | -0.0028252 | 1.0987e-18 | 0.0029185 | 0.011047 | -1.0987e-18 | -0.0028631 | -0.010991 | 0 | -135.266 | 44.734 | 0 | 44.734 | -135.266 | 0.95 | 0.94272 | 0.93905 | 0.95 | 0.93734 | 0.93354 | 1.3727e-14 | -120.5122 | 120.1294 | 1.3692e-14 | -120.7135 | 120.3187
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1625e-16 | -6.4771e-12 | -1.8814e-11 | -1.1653e-16 | 6.4771e-12 | 1.8814e-11 | -1.0327e-16 | 1.8049e-11 | 3.3188e-12 | 1.0272e-16 | -1.8049e-11 | -3.3188e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94812 | 0.94457 | 0.95 | 0.94812 | 0.94457 | 5.7745e-15 | -120.3131 | 119.9422 | 3.1973e-15 | -120.3131 | 119.9422
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0513e-17 | -5.1816e-11 | -1.5051e-10 | -4.0513e-17 | 5.1816e-11 | 1.5051e-10 | -3.3509e-17 | 1.4439e-10 | 2.655e-11 | 3.4058e-17 | -1.4439e-10 | -2.655e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94812 | 0.94457 | 0.95 | 0.94812 | 0.94457 | 8.4272e-15 | -120.3131 | 119.9422 | 7.6986e-15 | -120.3131 | 119.9422
Line2_1_4 | 0 | 0.052639 | 0.052639 | 0 | 0.052639 | 0.052639 | 0 | 0.012156 | 0.012156 | 0 | 0.012156 | 0.012156 | -2.3127e-16 | 0.011136 | 0.0029316 | 2.3072e-16 | -0.011082 | -0.0028784 | 2.2962e-16 | 0.0029739 | 0.011102 | -2.3072e-16 | -0.0029185 | -0.011047 | 0 | -135.266 | 44.734 | 0 | 44.734 | -135.266 | 0.95 | 0.94812 | 0.94457 | 0.95 | 0.94272 | 0.93905 | 8.4272e-15 | -120.3131 | 119.9422 | 1.3727e-14 | -120.5122 | 120.1294
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1859e-16 | -1.2954e-11 | -3.7627e-11 | -1.1859e-16 | 1.2954e-11 | 3.7627e-11 | -1.0657e-16 | 3.6098e-11 | 6.6375e-12 | 1.0657e-16 | -3.6098e-11 | -6.6375e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94812 | 0.94457 | 0.95 | 0.94812 | 0.94457 | 8.4272e-15 | -120.3131 | 119.9422 | 5.7745e-15 | -120.3131 | 119.9422
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.0339e-17 | -3.2385e-11 | -9.4068e-11 | -8.0614e-17 | 3.2385e-11 | 9.4068e-11 | -6.6469e-17 | 9.0245e-11 | 1.6594e-11 | 6.6469e-17 | -9.0245e-11 | -1.6594e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94812 | 0.94457 | 0.95 | 0.94812 | 0.94457 | 6.7019e-15 | -120.3131 | 119.9422 | 4.9883e-15 | -120.3131 | 119.9422
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.0477e-17 | -2.5908e-11 | -7.5255e-11 | -8.0477e-17 | 2.5908e-11 | 7.5255e-11 | -6.4821e-17 | 7.2196e-11 | 1.3275e-11 | 6.537e-17 | -7.2196e-11 | -1.3275e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94812 | 0.94457 | 0.95 | 0.94812 | 0.94457 | 4.9883e-15 | -120.3131 | 119.9422 | 3.2927e-15 | -120.3131 | 119.9422
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.8666e-19 | -1.9431e-11 | -5.6441e-11 | -6.8666e-19 | 1.9431e-11 | 5.6441e-11 | 2.1973e-18 | 5.4147e-11 | 9.9561e-12 | -2.7466e-18 | -5.4147e-11 | -9.9561e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94812 | 0.94457 | 0.95 | 0.94812 | 0.94457 | 3.2927e-15 | -120.3131 | 119.9422 | 3.3134e-15 | -120.3131 | 119.9422
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.06e-19 | -6.477e-12 | -1.8814e-11 | -4.8066e-19 | 6.477e-12 | 1.8814e-11 | -5.4933e-19 | 1.8049e-11 | 3.3187e-12 | -2.7788e-35 | -1.8049e-11 | -3.3187e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94812 | 0.94457 | 0.95 | 0.94812 | 0.94457 | 3.3134e-15 | -120.3131 | 119.9422 | 3.3123e-15 | -120.3131 | 119.9422
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.5533e-19 | -6.477e-12 | -1.8814e-11 | -7.5533e-19 | 6.477e-12 | 1.8814e-11 | -5.4933e-19 | 1.8049e-11 | 3.3187e-12 | -4.3667e-35 | -1.8049e-11 | -3.3187e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94812 | 0.94457 | 0.95 | 0.94812 | 0.94457 | 3.3134e-15 | -120.3131 | 119.9422 | 3.3123e-15 | -120.3131 | 119.9422
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0994e-17 | -4.5339e-11 | -1.317e-10 | -4.0994e-17 | 4.5339e-11 | 1.317e-10 | -3.4608e-17 | 1.2634e-10 | 2.3231e-11 | 3.4058e-17 | -1.2634e-10 | -2.3231e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94812 | 0.94457 | 0.95 | 0.94812 | 0.94457 | 7.6986e-15 | -120.3131 | 119.9422 | 6.9942e-15 | -120.3131 | 119.9422

## LL_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.2858e-17 | -3.4879e-11 | -1.0131e-10 | -7.2858e-17 | 3.4879e-11 | 1.0131e-10 | -5.9848e-17 | 9.7195e-11 | 1.7871e-11 | 5.9848e-17 | -9.7195e-11 | -1.7871e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89822 | 0.89485 | 0.9 | 0.89822 | 0.89485 | 8.417e-15 | -120.3131 | 119.9422 | 6.6863e-15 | -120.3131 | 119.9422
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6364e-17 | -3.4879e-11 | -1.0131e-10 | -3.6364e-17 | 3.4879e-11 | 1.0131e-10 | -3.1745e-17 | 9.7195e-11 | 1.7871e-11 | 3.1745e-17 | -9.7195e-11 | -1.7871e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89822 | 0.89485 | 0.9 | 0.89822 | 0.89485 | 6.9815e-15 | -120.3131 | 119.9422 | 6.2389e-15 | -120.3131 | 119.9422
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5779e-17 | -2.9066e-11 | -8.4427e-11 | -3.5518e-17 | 2.9066e-11 | 8.4427e-11 | -2.9664e-17 | 8.0996e-11 | 1.4893e-11 | 3.0184e-17 | -8.0996e-11 | -1.4893e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89822 | 0.89485 | 0.9 | 0.89822 | 0.89485 | 6.2389e-15 | -120.3131 | 119.9422 | 5.5238e-15 | -120.3131 | 119.9422
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.0035e-34 | -1.7439e-11 | -5.0656e-11 | 2.6021e-19 | 1.7439e-11 | 5.0656e-11 | 1.0408e-18 | 4.8598e-11 | 8.9356e-12 | -5.2042e-19 | -4.8598e-11 | -8.9356e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89822 | 0.89485 | 0.9 | 0.89822 | 0.89485 | 5.5238e-15 | -120.3131 | 119.9422 | 5.5442e-15 | -120.3131 | 119.9422
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0137e-17 | -5.8132e-12 | -1.6885e-11 | -4.0137e-17 | 5.8132e-12 | 1.6885e-11 | -3.2266e-17 | 1.6199e-11 | 2.9786e-12 | 3.2786e-17 | -1.6199e-11 | -2.9786e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89822 | 0.89485 | 0.9 | 0.89822 | 0.89485 | 5.5238e-15 | -120.3131 | 119.9422 | 4.6405e-15 | -120.3131 | 119.9422
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.301e-19 | -1.1626e-11 | -3.3771e-11 | -1.301e-19 | 1.1626e-11 | 3.3771e-11 | 1.5613e-18 | 3.2398e-11 | 5.9571e-12 | -1.0408e-18 | -3.2398e-11 | -5.9571e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89822 | 0.89485 | 0.9 | 0.89822 | 0.89485 | 5.5442e-15 | -120.3131 | 119.9422 | 5.5598e-15 | -120.3131 | 119.9422
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.01e-34 | -5.8131e-12 | -1.6885e-11 | 1.513e-34 | 5.8131e-12 | 1.6885e-11 | 1.0408e-18 | 1.6199e-11 | 2.9785e-12 | -1.5613e-18 | -1.6199e-11 | -2.9785e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89822 | 0.89485 | 0.9 | 0.89822 | 0.89485 | 5.5598e-15 | -120.3131 | 119.9422 | 5.5527e-15 | -120.3131 | 119.9422
Line16_4_18 | 0 | 0.049869 | 0.049869 | 0 | 0.049869 | 0.049869 | 0 | 0.011517 | 0.011517 | 0 | 0.011517 | 0.011517 | 0 | 0.0099465 | 0.0025834 | 0 | -0.0098987 | -0.0025356 | 0 | 0.0026194 | 0.0099144 | 0 | -0.0025697 | -0.0098647 | 0 | -135.266 | 44.734 | 0 | 44.734 | -135.266 | 0.9 | 0.89311 | 0.88962 | 0.9 | 0.888 | 0.8844 | 1.374e-14 | -120.5122 | 120.1294 | 1.3704e-14 | -120.7135 | 120.3187
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0356e-16 | -5.8133e-12 | -1.6885e-11 | -1.0356e-16 | 5.8133e-12 | 1.6885e-11 | -9.3675e-17 | 1.6199e-11 | 2.9787e-12 | 9.3675e-17 | -1.6199e-11 | -2.9787e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89822 | 0.89485 | 0.9 | 0.89822 | 0.89485 | 5.763e-15 | -120.3131 | 119.9422 | 3.1874e-15 | -120.3131 | 119.9422
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7795e-17 | -4.6505e-11 | -1.3508e-10 | -3.7795e-17 | 4.6505e-11 | 1.3508e-10 | -3.0705e-17 | 1.2959e-10 | 2.3828e-11 | 3.1745e-17 | -1.2959e-10 | -2.3828e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89822 | 0.89485 | 0.9 | 0.89822 | 0.89485 | 8.417e-15 | -120.3131 | 119.9422 | 7.6839e-15 | -120.3131 | 119.9422
Line2_1_4 | 0 | 0.049869 | 0.049869 | 0 | 0.049869 | 0.049869 | 0 | 0.011517 | 0.011517 | 0 | 0.011517 | 0.011517 | -2.0869e-16 | 0.0099942 | 0.0026311 | 2.0817e-16 | -0.0099465 | -0.0025834 | 2.0609e-16 | 0.0026691 | 0.0099642 | -2.0609e-16 | -0.0026194 | -0.0099144 | 0 | -135.266 | 44.734 | 0 | 44.734 | -135.266 | 0.9 | 0.89822 | 0.89485 | 0.9 | 0.89311 | 0.88962 | 8.417e-15 | -120.3131 | 119.9422 | 1.374e-14 | -120.5122 | 120.1294
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0603e-16 | -1.1626e-11 | -3.3771e-11 | -1.0603e-16 | 1.1626e-11 | 3.3771e-11 | -9.6277e-17 | 3.2398e-11 | 5.9572e-12 | 9.6277e-17 | -3.2398e-11 | -5.9572e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89822 | 0.89485 | 0.9 | 0.89822 | 0.89485 | 8.417e-15 | -120.3131 | 119.9422 | 5.763e-15 | -120.3131 | 119.9422
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.2468e-17 | -2.9066e-11 | -8.4427e-11 | -7.2208e-17 | 2.9066e-11 | 8.4427e-11 | -6.0368e-17 | 8.0996e-11 | 1.4893e-11 | 6.0368e-17 | -8.0996e-11 | -1.4893e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89822 | 0.89485 | 0.9 | 0.89822 | 0.89485 | 6.6863e-15 | -120.3131 | 119.9422 | 4.967e-15 | -120.3131 | 119.9422
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.0517e-17 | -2.3253e-11 | -6.7542e-11 | -7.0777e-17 | 2.3253e-11 | 6.7542e-11 | -6.0368e-17 | 6.4797e-11 | 1.1914e-11 | 6.0889e-17 | -6.4797e-11 | -1.1914e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89822 | 0.89485 | 0.9 | 0.89822 | 0.89485 | 4.967e-15 | -120.3131 | 119.9422 | 3.2637e-15 | -120.3131 | 119.9422
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1709e-18 | -1.7439e-11 | -5.0656e-11 | -1.1709e-18 | 1.7439e-11 | 5.0656e-11 | 1.5613e-18 | 4.8598e-11 | 8.9357e-12 | -5.2042e-19 | -4.8598e-11 | -8.9357e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89822 | 0.89485 | 0.9 | 0.89822 | 0.89485 | 3.2637e-15 | -120.3131 | 119.9422 | 3.2845e-15 | -120.3131 | 119.9422
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.9031e-19 | -5.8131e-12 | -1.6885e-11 | 6.5052e-19 | 5.8131e-12 | 1.6885e-11 | 1.5613e-18 | 1.6199e-11 | 2.9785e-12 | -1.5613e-18 | -1.6199e-11 | -2.9785e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89822 | 0.89485 | 0.9 | 0.89822 | 0.89485 | 3.2845e-15 | -120.3131 | 119.9422 | 3.2834e-15 | -120.3131 | 119.9422
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9031e-19 | -5.8131e-12 | -1.6885e-11 | 1.301e-19 | 5.8131e-12 | 1.6885e-11 | 1.0408e-18 | 1.6199e-11 | 2.9786e-12 | -1.5613e-18 | -1.6199e-11 | -2.9786e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89822 | 0.89485 | 0.9 | 0.89822 | 0.89485 | 3.2845e-15 | -120.3131 | 119.9422 | 3.2834e-15 | -120.3131 | 119.9422
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5909e-17 | -4.0692e-11 | -1.182e-10 | -3.5649e-17 | 4.0692e-11 | 1.182e-10 | -3.0705e-17 | 1.1339e-10 | 2.085e-11 | 3.1225e-17 | -1.1339e-10 | -2.085e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89822 | 0.89485 | 0.9 | 0.89822 | 0.89485 | 7.6839e-15 | -120.3131 | 119.9422 | 6.9815e-15 | -120.3131 | 119.9422

## LG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.0275e-09 | -2.1267e-09 | -3.8625e-10 | 5.0275e-09 | 2.1267e-09 | 3.8625e-10 | 2.008e-09 | -2.7588e-09 | 3.7634e-09 | -2.008e-09 | 2.7588e-09 | -3.7634e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.72912 | 0.93847 | 1.0192 | 0.72912 | 0.93847 | 1.0192 | -6.8485 | -112.6867 | 110.8013 | -6.8485 | -112.6867 | 110.8013
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.0273e-09 | -2.1266e-09 | -3.8659e-10 | 5.0273e-09 | 2.1266e-09 | 3.8659e-10 | 2.0081e-09 | -2.7591e-09 | 3.7635e-09 | -2.0081e-09 | 2.7591e-09 | -3.7635e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.72912 | 0.93847 | 1.0192 | 0.72912 | 0.93847 | 1.0192 | -6.8485 | -112.6867 | 110.8013 | -6.8485 | -112.6867 | 110.8013
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.1894e-09 | -1.7722e-09 | -3.2207e-10 | 4.1894e-09 | 1.7722e-09 | 3.2207e-10 | 1.6734e-09 | -2.2992e-09 | 3.1362e-09 | -1.6734e-09 | 2.2992e-09 | -3.1362e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.72912 | 0.93847 | 1.0192 | 0.72912 | 0.93847 | 1.0192 | -6.8485 | -112.6867 | 110.8013 | -6.8485 | -112.6867 | 110.8013
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5135e-09 | -1.0632e-09 | -1.9354e-10 | 2.5135e-09 | 1.0632e-09 | 1.9354e-10 | 1.0042e-09 | -1.3798e-09 | 1.8819e-09 | -1.0042e-09 | 1.3798e-09 | -1.8819e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.72912 | 0.93847 | 1.0192 | 0.72912 | 0.93847 | 1.0192 | -6.8485 | -112.6867 | 110.8013 | -6.8485 | -112.6867 | 110.8013
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.3814e-10 | -3.5458e-10 | -6.4015e-11 | 8.3814e-10 | 3.5458e-10 | 6.4015e-11 | 3.3449e-10 | -4.5946e-10 | 6.2706e-10 | -3.3449e-10 | 4.5946e-10 | -6.2706e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.72912 | 0.93847 | 1.0192 | 0.72912 | 0.93847 | 1.0192 | -6.8485 | -112.6867 | 110.8013 | -6.8485 | -112.6867 | 110.8013
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.6757e-09 | -7.088e-10 | -1.2903e-10 | 1.6757e-09 | 7.088e-10 | 1.2903e-10 | 6.6946e-10 | -9.1986e-10 | 1.2546e-09 | -6.6946e-10 | 9.1986e-10 | -1.2546e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.72912 | 0.93847 | 1.0192 | 0.72912 | 0.93847 | 1.0192 | -6.8485 | -112.6867 | 110.8013 | -6.8485 | -112.6867 | 110.8013
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.3783e-10 | -3.544e-10 | -6.4514e-11 | 8.3783e-10 | 3.544e-10 | 6.4514e-11 | 3.3473e-10 | -4.5993e-10 | 6.273e-10 | -3.3473e-10 | 4.5993e-10 | -6.273e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.72912 | 0.93847 | 1.0192 | 0.72912 | 0.93847 | 1.0192 | -6.8485 | -112.6867 | 110.8013 | -6.8485 | -112.6867 | 110.8013
Line16_4_18 | 5.0202 | 0 | 0 | 5.0202 | 0 | 0 | 1.1594 | 0 | 0 | 1.1594 | 0 | 0 | 0.21002 | 2.7186e-09 | -3.3123e-09 | 6.5465e-15 | 2.2643e-10 | 1.298e-10 | 0.42004 | -1.621e-09 | 3.3941e-10 | 1.0649e-13 | 1.3203e-09 | -1.3761e-09 | -70.2834 | 0 | 0 | 109.7166 | 0 | 0 |  | 0.40507 | 0.90773 | 0.95489 | 0 | 0.90293 | 0.93166 | -6.8485 | -102.7988 | 102.1568 | 0 | -97.679 | 97.4409
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.3862e-10 | -3.5486e-10 | -6.3266e-11 | 8.3862e-10 | 3.5486e-10 | 6.3266e-11 | 3.3414e-10 | -4.5874e-10 | 6.267e-10 | -3.3414e-10 | 4.5874e-10 | -6.267e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.72912 | 0.93847 | 1.0192 | 0.72912 | 0.93847 | 1.0192 | -6.8485 | -112.6867 | 110.8013 | -6.8485 | -112.6867 | 110.8013
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.7029e-09 | -2.8354e-09 | -5.1561e-10 | 6.7029e-09 | 2.8354e-09 | 5.1561e-10 | 2.6776e-09 | -3.679e-09 | 5.0181e-09 | -2.6776e-09 | 3.679e-09 | -5.0181e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.72912 | 0.93847 | 1.0192 | 0.72912 | 0.93847 | 1.0192 | -6.8485 | -112.6867 | 110.8013 | -6.8485 | -112.6867 | 110.8013
Line2_1_4 | 3.3468 | 1.6734 | 1.6734 | 3.3468 | 1.6734 | 1.6734 | 0.77291 | 0.38646 | 0.38646 | 0.77291 | 0.38646 | 0.38646 | 0.25202 | -0.26781 | 0.39382 | -0.14001 | 0.29581 | -0.36582 | 0.50405 | 0.24457 | 0.0074564 | -0.28003 | -0.18856 | 0.048549 | -70.2834 | 109.7166 | 109.7166 | 109.7166 | -70.2834 | -70.2834 |  | 0.72912 | 0.93847 | 1.0192 | 0.40507 | 0.90773 | 0.95489 | -6.8485 | -112.6867 | 110.8013 | -6.8485 | -102.7988 | 102.1568
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.6764e-09 | -7.0925e-10 | -1.2778e-10 | 1.6764e-09 | 7.0925e-10 | 1.2778e-10 | 6.6887e-10 | -9.1867e-10 | 1.254e-09 | -6.6887e-10 | 9.1867e-10 | -1.254e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.72912 | 0.93847 | 1.0192 | 0.72912 | 0.93847 | 1.0192 | -6.8485 | -112.6867 | 110.8013 | -6.8485 | -112.6867 | 110.8013
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.1897e-09 | -1.7723e-09 | -3.2174e-10 | 4.1897e-09 | 1.7723e-09 | 3.2174e-10 | 1.6733e-09 | -2.2989e-09 | 3.1361e-09 | -1.6733e-09 | 2.2989e-09 | -3.1361e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.72912 | 0.93847 | 1.0192 | 0.72912 | 0.93847 | 1.0192 | -6.8485 | -112.6867 | 110.8013 | -6.8485 | -112.6867 | 110.8013
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.3518e-09 | -1.4179e-09 | -2.5722e-10 | 3.3518e-09 | 1.4179e-09 | 2.5722e-10 | 1.3385e-09 | -1.8389e-09 | 2.5088e-09 | -1.3385e-09 | 1.8389e-09 | -2.5088e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.72912 | 0.93847 | 1.0192 | 0.72912 | 0.93847 | 1.0192 | -6.8485 | -112.6867 | 110.8013 | -6.8485 | -112.6867 | 110.8013
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5135e-09 | -1.0632e-09 | -1.9354e-10 | 2.5135e-09 | 1.0632e-09 | 1.9354e-10 | 1.0042e-09 | -1.3798e-09 | 1.8819e-09 | -1.0042e-09 | 1.3798e-09 | -1.8819e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.72912 | 0.93847 | 1.0192 | 0.72912 | 0.93847 | 1.0192 | -6.8485 | -112.6867 | 110.8013 | -6.8485 | -112.6867 | 110.8013
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.3783e-10 | -3.544e-10 | -6.4514e-11 | 8.3783e-10 | 3.544e-10 | 6.4514e-11 | 3.3473e-10 | -4.5993e-10 | 6.273e-10 | -3.3473e-10 | 4.5993e-10 | -6.273e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.72912 | 0.93847 | 1.0192 | 0.72912 | 0.93847 | 1.0192 | -6.8485 | -112.6867 | 110.8013 | -6.8485 | -112.6867 | 110.8013
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.3783e-10 | -3.544e-10 | -6.4514e-11 | 8.3783e-10 | 3.544e-10 | 6.4514e-11 | 3.3473e-10 | -4.5993e-10 | 6.273e-10 | -3.3473e-10 | 4.5993e-10 | -6.273e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.72912 | 0.93847 | 1.0192 | 0.72912 | 0.93847 | 1.0192 | -6.8485 | -112.6867 | 110.8013 | -6.8485 | -112.6867 | 110.8013
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.8651e-09 | -2.481e-09 | -4.511e-10 | 5.8651e-09 | 2.481e-09 | 4.511e-10 | 2.3429e-09 | -3.219e-09 | 4.3908e-09 | -2.3429e-09 | 3.219e-09 | -4.3908e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.72912 | 0.93847 | 1.0192 | 0.72912 | 0.93847 | 1.0192 | -6.8485 | -112.6867 | 110.8013 | -6.8485 | -112.6867 | 110.8013

## LG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.6124e-09 | -2.3741e-09 | -4.3121e-10 | 5.6124e-09 | 2.3741e-09 | 4.3121e-10 | 2.2417e-09 | -3.137e-09 | 4.2585e-09 | -2.2417e-09 | 3.137e-09 | -4.2585e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.75279 | 0.98026 | 1.0665 | 0.75279 | 0.98026 | 1.0665 | -7.0695 | -112.3989 | 110.5019 | -7.0695 | -112.3989 | 110.5019
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.6122e-09 | -2.374e-09 | -4.3157e-10 | 5.6122e-09 | 2.374e-09 | 4.3157e-10 | 2.2418e-09 | -3.1374e-09 | 4.2587e-09 | -2.2418e-09 | 3.1374e-09 | -4.2587e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.75279 | 0.98026 | 1.0665 | 0.75279 | 0.98026 | 1.0665 | -7.0695 | -112.3989 | 110.5019 | -7.0695 | -112.3989 | 110.5019
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.6769e-09 | -1.9784e-09 | -3.5955e-10 | 4.6769e-09 | 1.9784e-09 | 3.5955e-10 | 1.8682e-09 | -2.6144e-09 | 3.5488e-09 | -1.8682e-09 | 2.6144e-09 | -3.5488e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.75279 | 0.98026 | 1.0665 | 0.75279 | 0.98026 | 1.0665 | -7.0695 | -112.3989 | 110.5019 | -7.0695 | -112.3989 | 110.5019
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.8059e-09 | -1.1869e-09 | -2.1605e-10 | 2.8059e-09 | 1.1869e-09 | 2.1605e-10 | 1.121e-09 | -1.5689e-09 | 2.1295e-09 | -1.121e-09 | 1.5689e-09 | -2.1295e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.75279 | 0.98026 | 1.0665 | 0.75279 | 0.98026 | 1.0665 | -7.0695 | -112.3989 | 110.5019 | -7.0695 | -112.3989 | 110.5019
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -9.3564e-10 | -3.9584e-10 | -7.1478e-11 | 9.3564e-10 | 3.9584e-10 | 7.1478e-11 | 3.7343e-10 | -5.2247e-10 | 7.0956e-10 | -3.7343e-10 | 5.2247e-10 | -7.0956e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.75279 | 0.98026 | 1.0665 | 0.75279 | 0.98026 | 1.0665 | -7.0695 | -112.3989 | 110.5019 | -7.0695 | -112.3989 | 110.5019
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.8706e-09 | -7.9127e-10 | -1.4403e-10 | 1.8706e-09 | 7.9127e-10 | 1.4403e-10 | 7.4736e-10 | -1.046e-09 | 1.4196e-09 | -7.4736e-10 | 1.046e-09 | -1.4196e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.75279 | 0.98026 | 1.0665 | 0.75279 | 0.98026 | 1.0665 | -7.0695 | -112.3989 | 110.5019 | -7.0695 | -112.3989 | 110.5019
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -9.353e-10 | -3.9563e-10 | -7.2017e-11 | 9.353e-10 | 3.9563e-10 | 7.2017e-11 | 3.7368e-10 | -5.2298e-10 | 7.0982e-10 | -3.7368e-10 | 5.2298e-10 | -7.0982e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.75279 | 0.98026 | 1.0665 | 0.75279 | 0.98026 | 1.0665 | -7.0695 | -112.3989 | 110.5019 | -7.0695 | -112.3989 | 110.5019
Line16_4_18 | 5.1832 | 0 | 0 | 5.1832 | 0 | 0 | 1.197 | 0 | 0 | 1.197 | 0 | 0 | 0.22388 | 2.936e-09 | -3.5806e-09 | 2.0104e-13 | 2.4731e-10 | 1.3944e-10 | 0.44775 | -1.7562e-09 | 3.9471e-10 | -2.4993e-13 | 1.4551e-09 | -1.5174e-09 | -70.5045 | 0 | 0 | 109.4955 | 0 | 0 |  | 0.41821 | 0.94984 | 1.0001 | 0 | 0.94542 | 0.97604 | -7.0695 | -102.6196 | 101.9753 | 0 | -97.5677 | 97.329
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -9.3615e-10 | -3.9614e-10 | -7.0669e-11 | 9.3615e-10 | 3.9614e-10 | 7.0669e-11 | 3.7305e-10 | -5.217e-10 | 7.0917e-10 | -3.7305e-10 | 5.217e-10 | -7.0917e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.75279 | 0.98026 | 1.0665 | 0.75279 | 0.98026 | 1.0665 | -7.0695 | -112.3989 | 110.5019 | -7.0695 | -112.3989 | 110.5019
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.4828e-09 | -3.1653e-09 | -5.756e-10 | 7.4828e-09 | 3.1653e-09 | 5.756e-10 | 2.9892e-09 | -4.1833e-09 | 5.6783e-09 | -2.9892e-09 | 4.1833e-09 | -5.6783e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.75279 | 0.98026 | 1.0665 | 0.75279 | 0.98026 | 1.0665 | -7.0695 | -112.3989 | 110.5019 | -7.0695 | -112.3989 | 110.5019
Line2_1_4 | 3.4554 | 1.7277 | 1.7277 | 3.4554 | 1.7277 | 1.7277 | 0.798 | 0.399 | 0.399 | 0.798 | 0.399 | 0.399 | 0.26865 | -0.29114 | 0.42547 | -0.14925 | 0.32099 | -0.39562 | 0.5373 | 0.26118 | 0.0074742 | -0.2985 | -0.20148 | 0.052226 | -70.5045 | 109.4955 | 109.4955 | 109.4955 | -70.5045 | -70.5045 |  | 0.75279 | 0.98026 | 1.0665 | 0.41821 | 0.94984 | 1.0001 | -7.0695 | -112.3989 | 110.5019 | -7.0695 | -102.6196 | 101.9753
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.8715e-09 | -7.9177e-10 | -1.4269e-10 | 1.8715e-09 | 7.9177e-10 | 1.4269e-10 | 7.4673e-10 | -1.0447e-09 | 1.419e-09 | -7.4673e-10 | 1.0447e-09 | -1.419e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.75279 | 0.98026 | 1.0665 | 0.75279 | 0.98026 | 1.0665 | -7.0695 | -112.3989 | 110.5019 | -7.0695 | -112.3989 | 110.5019
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.6771e-09 | -1.9785e-09 | -3.5919e-10 | 4.6771e-09 | 1.9785e-09 | 3.5919e-10 | 1.868e-09 | -2.6141e-09 | 3.5487e-09 | -1.868e-09 | 2.6141e-09 | -3.5487e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.75279 | 0.98026 | 1.0665 | 0.75279 | 0.98026 | 1.0665 | -7.0695 | -112.3989 | 110.5019 | -7.0695 | -112.3989 | 110.5019
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.7418e-09 | -1.5829e-09 | -2.8717e-10 | 3.7418e-09 | 1.5829e-09 | 2.8717e-10 | 1.4943e-09 | -2.0911e-09 | 2.8389e-09 | -1.4943e-09 | 2.0911e-09 | -2.8389e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.75279 | 0.98026 | 1.0665 | 0.75279 | 0.98026 | 1.0665 | -7.0695 | -112.3989 | 110.5019 | -7.0695 | -112.3989 | 110.5019
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.8059e-09 | -1.1869e-09 | -2.1605e-10 | 2.8059e-09 | 1.1869e-09 | 2.1605e-10 | 1.121e-09 | -1.5689e-09 | 2.1295e-09 | -1.121e-09 | 1.5689e-09 | -2.1295e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.75279 | 0.98026 | 1.0665 | 0.75279 | 0.98026 | 1.0665 | -7.0695 | -112.3989 | 110.5019 | -7.0695 | -112.3989 | 110.5019
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -9.353e-10 | -3.9563e-10 | -7.2017e-11 | 9.353e-10 | 3.9563e-10 | 7.2017e-11 | 3.7368e-10 | -5.2298e-10 | 7.0982e-10 | -3.7368e-10 | 5.2298e-10 | -7.0982e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.75279 | 0.98026 | 1.0665 | 0.75279 | 0.98026 | 1.0665 | -7.0695 | -112.3989 | 110.5019 | -7.0695 | -112.3989 | 110.5019
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -9.353e-10 | -3.9563e-10 | -7.2017e-11 | 9.353e-10 | 3.9563e-10 | 7.2017e-11 | 3.7368e-10 | -5.2298e-10 | 7.0982e-10 | -3.7368e-10 | 5.2298e-10 | -7.0982e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.75279 | 0.98026 | 1.0665 | 0.75279 | 0.98026 | 1.0665 | -7.0695 | -112.3989 | 110.5019 | -7.0695 | -112.3989 | 110.5019
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.5475e-09 | -2.7696e-09 | -5.0358e-10 | 6.5475e-09 | 2.7696e-09 | 5.0358e-10 | 2.6155e-09 | -3.6604e-09 | 4.9685e-09 | -2.6155e-09 | 3.6604e-09 | -4.9685e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.75279 | 0.98026 | 1.0665 | 0.75279 | 0.98026 | 1.0665 | -7.0695 | -112.3989 | 110.5019 | -7.0695 | -112.3989 | 110.5019

## LG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.0406e-11 | -2.4844e-11 | 4.6501e-12 | 4.0406e-11 | 2.4844e-11 | -4.6501e-12 | 3.405e-11 | -9.0241e-12 | 2.6052e-11 | -3.405e-11 | 9.0241e-12 | -2.6052e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0482 | 1.0489 | 1.0502 | 1.0482 | 1.0489 | 1.0502 | -0.080574 | -119.9786 | 119.9385 | -0.080574 | -119.9786 | 119.9385
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.0403e-11 | -2.4844e-11 | 4.6481e-12 | 4.0403e-11 | 2.4844e-11 | -4.6481e-12 | 3.4051e-11 | -9.0267e-12 | 2.6054e-11 | -3.4051e-11 | 9.0267e-12 | -2.6054e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0482 | 1.0489 | 1.0502 | 1.0482 | 1.0489 | 1.0502 | -0.080574 | -119.9786 | 119.9385 | -0.080574 | -119.9786 | 119.9385
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.367e-11 | -2.0703e-11 | 3.8739e-12 | 3.367e-11 | 2.0703e-11 | -3.8739e-12 | 2.8376e-11 | -7.5216e-12 | 2.1711e-11 | -2.8376e-11 | 7.5216e-12 | -2.1711e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0482 | 1.0489 | 1.0502 | 1.0482 | 1.0489 | 1.0502 | -0.080574 | -119.9786 | 119.9385 | -0.080574 | -119.9786 | 119.9385
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.02e-11 | -1.2423e-11 | 2.3226e-12 | 2.02e-11 | 1.2423e-11 | -2.3226e-12 | 1.7026e-11 | -4.5152e-12 | 1.3028e-11 | -1.7026e-11 | 4.5152e-12 | -1.3028e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0482 | 1.0489 | 1.0502 | 1.0482 | 1.0489 | 1.0502 | -0.080574 | -119.9786 | 119.9385 | -0.080574 | -119.9786 | 119.9385
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.7369e-12 | -4.1401e-12 | 7.771e-13 | 6.7369e-12 | 4.1401e-12 | -7.771e-13 | 5.6742e-12 | -1.5013e-12 | 4.3402e-12 | -5.6742e-12 | 1.5013e-12 | -4.3402e-12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0482 | 1.0489 | 1.0502 | 1.0482 | 1.0489 | 1.0502 | -0.080574 | -119.9786 | 119.9385 | -0.080574 | -119.9786 | 119.9385
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.3467e-11 | -8.2817e-12 | 1.5484e-12 | 1.3467e-11 | 8.2817e-12 | -1.5484e-12 | 1.1351e-11 | -3.0101e-12 | 8.6856e-12 | -1.1351e-11 | 3.0101e-12 | -8.6856e-12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0482 | 1.0489 | 1.0502 | 1.0482 | 1.0489 | 1.0502 | -0.080574 | -119.9786 | 119.9385 | -0.080574 | -119.9786 | 119.9385
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.7333e-12 | -4.1408e-12 | 7.7421e-13 | 6.7333e-12 | 4.1408e-12 | -7.7421e-13 | 5.6754e-12 | -1.5051e-12 | 4.3428e-12 | -5.6754e-12 | 1.5051e-12 | -4.3428e-12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0482 | 1.0489 | 1.0502 | 1.0482 | 1.0489 | 1.0502 | -0.080574 | -119.9786 | 119.9385 | -0.080574 | -119.9786 | 119.9385
Line16_4_18 | 0.034082 | 0 | 0 | 0.034082 | 0 | 0 | 0.0078709 | 0 | 0 | 0.0078709 | 0 | 0 | 0.0058177 | 7.2279e-12 | -2.4195e-11 | -0.005808 | 8.8587e-12 | 4.9453e-13 | 0.0058273 | -2.3735e-11 | 5.6949e-12 | -0.005808 | 5.7335e-12 | -1.0563e-11 | -45.1661 | 0 | 0 | 134.8339 | 0 | 0 |  | 1.0462 | 1.0481 | 1.05 | 1.0435 | 1.0477 | 1.0499 | -0.11851 | -119.9386 | 119.8797 | -0.16613 | -119.9186 | 119.8503
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.7424e-12 | -4.1389e-12 | 7.8146e-13 | 6.7424e-12 | 4.1389e-12 | -7.8146e-13 | 5.6723e-12 | -1.4956e-12 | 4.3364e-12 | -5.6723e-12 | 1.4956e-12 | -4.3364e-12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0482 | 1.0489 | 1.0502 | 1.0482 | 1.0489 | 1.0502 | -0.080574 | -119.9786 | 119.9385 | -0.080574 | -119.9786 | 119.9385
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.387e-11 | -3.3126e-11 | 6.1966e-12 | 5.387e-11 | 3.3126e-11 | -6.1965e-12 | 4.5402e-11 | -1.2037e-11 | 3.474e-11 | -4.5402e-11 | 1.2037e-11 | -3.474e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0482 | 1.0489 | 1.0502 | 1.0482 | 1.0489 | 1.0502 | -0.080574 | -119.9786 | 119.9385 | -0.080574 | -119.9786 | 119.9385
Line2_1_4 | 0.022721 | 0.011361 | 0.011361 | 0.022721 | 0.011361 | 0.011361 | 0.0052473 | 0.0026236 | 0.0026236 | 0.0052473 | 0.0026236 | 0.0026236 | 0.0038836 | -0.00072097 | 0.0026628 | -0.0038784 | 0.00072226 | -0.0026615 | 0.0038952 | 0.0026559 | -0.00070828 | -0.0038849 | -0.0026533 | 0.00071086 | -45.1661 | 134.8339 | 134.8339 | 134.8339 | -45.1661 | -45.1661 |  | 1.0482 | 1.0489 | 1.0502 | 1.0462 | 1.0481 | 1.05 | -0.080574 | -119.9786 | 119.9385 | -0.11851 | -119.9386 | 119.8797
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.3476e-11 | -8.2798e-12 | 1.5557e-12 | 1.3476e-11 | 8.2798e-12 | -1.5557e-12 | 1.1348e-11 | -3.0007e-12 | 8.6792e-12 | -1.1348e-11 | 3.0007e-12 | -8.6792e-12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0482 | 1.0489 | 1.0502 | 1.0482 | 1.0489 | 1.0502 | -0.080574 | -119.9786 | 119.9385 | -0.080574 | -119.9786 | 119.9385
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.3672e-11 | -2.0703e-11 | 3.8759e-12 | 3.3672e-11 | 2.0703e-11 | -3.8759e-12 | 2.8375e-11 | -7.5191e-12 | 2.171e-11 | -2.8375e-11 | 7.5191e-12 | -2.171e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0482 | 1.0489 | 1.0502 | 1.0482 | 1.0489 | 1.0502 | -0.080574 | -119.9786 | 119.9385 | -0.080574 | -119.9786 | 119.9385
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.6939e-11 | -1.6562e-11 | 3.1017e-12 | 2.6939e-11 | 1.6562e-11 | -3.1017e-12 | 2.27e-11 | -6.014e-12 | 1.7367e-11 | -2.27e-11 | 6.014e-12 | -1.7367e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0482 | 1.0489 | 1.0502 | 1.0482 | 1.0489 | 1.0502 | -0.080574 | -119.9786 | 119.9385 | -0.080574 | -119.9786 | 119.9385
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.02e-11 | -1.2423e-11 | 2.3226e-12 | 2.02e-11 | 1.2423e-11 | -2.3226e-12 | 1.7026e-11 | -4.5152e-12 | 1.3028e-11 | -1.7026e-11 | 4.5152e-12 | -1.3028e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0482 | 1.0489 | 1.0502 | 1.0482 | 1.0489 | 1.0502 | -0.080574 | -119.9786 | 119.9385 | -0.080574 | -119.9786 | 119.9385
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.7333e-12 | -4.1408e-12 | 7.7421e-13 | 6.7333e-12 | 4.1408e-12 | -7.7421e-13 | 5.6754e-12 | -1.5051e-12 | 4.3428e-12 | -5.6754e-12 | 1.5051e-12 | -4.3428e-12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0482 | 1.0489 | 1.0502 | 1.0482 | 1.0489 | 1.0502 | -0.080574 | -119.9786 | 119.9385 | -0.080574 | -119.9786 | 119.9385
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.7333e-12 | -4.1408e-12 | 7.7421e-13 | 6.7333e-12 | 4.1408e-12 | -7.7421e-13 | 5.6754e-12 | -1.5051e-12 | 4.3428e-12 | -5.6754e-12 | 1.5051e-12 | -4.3428e-12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0482 | 1.0489 | 1.0502 | 1.0482 | 1.0489 | 1.0502 | -0.080574 | -119.9786 | 119.9385 | -0.080574 | -119.9786 | 119.9385
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.7137e-11 | -2.8985e-11 | 5.4223e-12 | 4.7137e-11 | 2.8985e-11 | -5.4223e-12 | 3.9727e-11 | -1.0532e-11 | 3.0397e-11 | -3.9727e-11 | 1.0532e-11 | -3.0397e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0482 | 1.0489 | 1.0502 | 1.0482 | 1.0489 | 1.0502 | -0.080574 | -119.9786 | 119.9385 | -0.080574 | -119.9786 | 119.9385

## LG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.6433e-11 | -2.855e-11 | 5.3437e-12 | 4.6433e-11 | 2.855e-11 | -5.3437e-12 | 3.9131e-11 | -1.0373e-11 | 2.9942e-11 | -3.9131e-11 | 1.0373e-11 | -2.9942e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0981 | 1.0988 | 1.1002 | 1.0981 | 1.0988 | 1.1002 | -0.084376 | -119.9776 | 119.9356 | -0.084376 | -119.9776 | 119.9356
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.6431e-11 | -2.8551e-11 | 5.3416e-12 | 4.6431e-11 | 2.8551e-11 | -5.3416e-12 | 3.9132e-11 | -1.0376e-11 | 2.9944e-11 | -3.9132e-11 | 1.0376e-11 | -2.9944e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0981 | 1.0988 | 1.1002 | 1.0981 | 1.0988 | 1.1002 | -0.084376 | -119.9776 | 119.9356 | -0.084376 | -119.9776 | 119.9356
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.8693e-11 | -2.3792e-11 | 4.4519e-12 | 3.8693e-11 | 2.3792e-11 | -4.4519e-12 | 3.261e-11 | -8.6461e-12 | 2.4953e-11 | -3.261e-11 | 8.6461e-12 | -2.4953e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0981 | 1.0988 | 1.1002 | 1.0981 | 1.0988 | 1.1002 | -0.084376 | -119.9776 | 119.9356 | -0.084376 | -119.9776 | 119.9356
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.3213e-11 | -1.4276e-11 | 2.6692e-12 | 2.3213e-11 | 1.4276e-11 | -2.6692e-12 | 1.9567e-11 | -5.1901e-12 | 1.4973e-11 | -1.9567e-11 | 5.1901e-12 | -1.4973e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0981 | 1.0988 | 1.1002 | 1.0981 | 1.0988 | 1.1002 | -0.084376 | -119.9776 | 119.9356 | -0.084376 | -119.9776 | 119.9356
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.7418e-12 | -4.7578e-12 | 8.9292e-13 | 7.7418e-12 | 4.7578e-12 | -8.9292e-13 | 6.5208e-12 | -1.7259e-12 | 4.9883e-12 | -6.5208e-12 | 1.7259e-12 | -4.9883e-12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0981 | 1.0988 | 1.1002 | 1.0981 | 1.0988 | 1.1002 | -0.084376 | -119.9776 | 119.9356 | -0.084376 | -119.9776 | 119.9356
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.5476e-11 | -9.5173e-12 | 1.7795e-12 | 1.5476e-11 | 9.5173e-12 | -1.7795e-12 | 1.3044e-11 | -3.4601e-12 | 9.9823e-12 | -1.3044e-11 | 3.4601e-12 | -9.9823e-12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0981 | 1.0988 | 1.1002 | 1.0981 | 1.0988 | 1.1002 | -0.084376 | -119.9776 | 119.9356 | -0.084376 | -119.9776 | 119.9356
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.7378e-12 | -4.7586e-12 | 8.8974e-13 | 7.7378e-12 | 4.7586e-12 | -8.8974e-13 | 6.5222e-12 | -1.73e-12 | 4.9911e-12 | -6.5222e-12 | 1.73e-12 | -4.9911e-12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0981 | 1.0988 | 1.1002 | 1.0981 | 1.0988 | 1.1002 | -0.084376 | -119.9776 | 119.9356 | -0.084376 | -119.9776 | 119.9356
Line16_4_18 | 0.035702 | 0 | 0 | 0.035702 | 0 | 0 | 0.0082451 | 0 | 0 | 0.0082451 | 0 | 0 | 0.0063839 | 7.7194e-12 | -2.6512e-11 | -0.0063733 | 9.9351e-12 | 5.0238e-13 | 0.0063945 | -2.6124e-11 | 6.4745e-12 | -0.0063733 | 6.3708e-12 | -1.1817e-11 | -45.1699 | 0 | 0 | 134.8301 | 0 | 0 |  | 1.0959 | 1.098 | 1.1 | 1.0932 | 1.0975 | 1.0999 | -0.12231 | -119.9376 | 119.8768 | -0.16993 | -119.9175 | 119.8474
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.7478e-12 | -4.7565e-12 | 8.9769e-13 | 7.7478e-12 | 4.7565e-12 | -8.9769e-13 | 6.5188e-12 | -1.7196e-12 | 4.9841e-12 | -6.5188e-12 | 1.7196e-12 | -4.9841e-12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0981 | 1.0988 | 1.1002 | 1.0981 | 1.0988 | 1.1002 | -0.084376 | -119.9776 | 119.9356 | -0.084376 | -119.9776 | 119.9356
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.1906e-11 | -3.8068e-11 | 7.1211e-12 | 6.1906e-11 | 3.8068e-11 | -7.1211e-12 | 5.2176e-11 | -1.3836e-11 | 3.9926e-11 | -5.2176e-11 | 1.3836e-11 | -3.9926e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0981 | 1.0988 | 1.1002 | 1.0981 | 1.0988 | 1.1002 | -0.084376 | -119.9776 | 119.9356 | -0.084376 | -119.9776 | 119.9356
Line2_1_4 | 0.023802 | 0.011901 | 0.011901 | 0.023802 | 0.011901 | 0.011901 | 0.0054967 | 0.0027484 | 0.0027484 | 0.0054967 | 0.0027484 | 0.0027484 | 0.0042616 | -0.00079141 | 0.0029222 | -0.0042559 | 0.00079283 | -0.0029208 | 0.0042744 | 0.0029144 | -0.00077724 | -0.004263 | -0.0029116 | 0.00078007 | -45.1699 | 134.8301 | 134.8301 | 134.8301 | -45.1699 | -45.1699 |  | 1.0981 | 1.0988 | 1.1002 | 1.0959 | 1.098 | 1.1 | -0.084376 | -119.9776 | 119.9356 | -0.12231 | -119.9376 | 119.8768
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.5486e-11 | -9.5152e-12 | 1.7874e-12 | 1.5486e-11 | 9.5152e-12 | -1.7874e-12 | 1.3041e-11 | -3.4497e-12 | 9.9752e-12 | -1.3041e-11 | 3.4497e-12 | -9.9752e-12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0981 | 1.0988 | 1.1002 | 1.0981 | 1.0988 | 1.1002 | -0.084376 | -119.9776 | 119.9356 | -0.084376 | -119.9776 | 119.9356
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.8696e-11 | -2.3792e-11 | 4.454e-12 | 3.8696e-11 | 2.3792e-11 | -4.454e-12 | 3.2609e-11 | -8.6433e-12 | 2.4951e-11 | -3.2609e-11 | 8.6433e-12 | -2.4951e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0981 | 1.0988 | 1.1002 | 1.0981 | 1.0988 | 1.1002 | -0.084376 | -119.9776 | 119.9356 | -0.084376 | -119.9776 | 119.9356
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.0958e-11 | -1.9033e-11 | 3.5643e-12 | 3.0958e-11 | 1.9033e-11 | -3.5643e-12 | 2.6086e-11 | -6.9133e-12 | 1.996e-11 | -2.6086e-11 | 6.9133e-12 | -1.996e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0981 | 1.0988 | 1.1002 | 1.0981 | 1.0988 | 1.1002 | -0.084376 | -119.9776 | 119.9356 | -0.084376 | -119.9776 | 119.9356
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.3213e-11 | -1.4276e-11 | 2.6692e-12 | 2.3213e-11 | 1.4276e-11 | -2.6692e-12 | 1.9567e-11 | -5.1901e-12 | 1.4973e-11 | -1.9567e-11 | 5.1901e-12 | -1.4973e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0981 | 1.0988 | 1.1002 | 1.0981 | 1.0988 | 1.1002 | -0.084376 | -119.9776 | 119.9356 | -0.084376 | -119.9776 | 119.9356
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.7378e-12 | -4.7586e-12 | 8.8974e-13 | 7.7378e-12 | 4.7586e-12 | -8.8974e-13 | 6.5222e-12 | -1.73e-12 | 4.9911e-12 | -6.5222e-12 | 1.73e-12 | -4.9911e-12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0981 | 1.0988 | 1.1002 | 1.0981 | 1.0988 | 1.1002 | -0.084376 | -119.9776 | 119.9356 | -0.084376 | -119.9776 | 119.9356
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.7378e-12 | -4.7586e-12 | 8.8974e-13 | 7.7378e-12 | 4.7586e-12 | -8.8974e-13 | 6.5222e-12 | -1.73e-12 | 4.9911e-12 | -6.5222e-12 | 1.73e-12 | -4.9911e-12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0981 | 1.0988 | 1.1002 | 1.0981 | 1.0988 | 1.1002 | -0.084376 | -119.9776 | 119.9356 | -0.084376 | -119.9776 | 119.9356
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.4169e-11 | -3.331e-11 | 6.2314e-12 | 5.4169e-11 | 3.331e-11 | -6.2314e-12 | 4.5654e-11 | -1.2106e-11 | 3.4935e-11 | -4.5654e-11 | 1.2106e-11 | -3.4935e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0981 | 1.0988 | 1.1002 | 1.0981 | 1.0988 | 1.1002 | -0.084376 | -119.9776 | 119.9356 | -0.084376 | -119.9776 | 119.9356

## LG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.4129e-09 | -2.0514e-09 | 3.456e-10 | 3.4129e-09 | 2.0514e-09 | -3.456e-10 | 2.7676e-09 | -1.5233e-09 | 2.9072e-09 | -2.7676e-09 | 1.5233e-09 | -2.9072e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.71749 | 0.83464 | 0.95631 | 0.71749 | 0.83464 | 0.95631 | -10.6355 | -114.9886 | 111.6351 | -10.6355 | -114.9886 | 111.6351
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.4127e-09 | -2.0515e-09 | 3.4548e-10 | 3.4127e-09 | 2.0515e-09 | -3.4548e-10 | 2.7676e-09 | -1.5235e-09 | 2.9073e-09 | -2.7676e-09 | 1.5235e-09 | -2.9073e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.71749 | 0.83464 | 0.95631 | 0.71749 | 0.83464 | 0.95631 | -10.6355 | -114.9886 | 111.6351 | -10.6355 | -114.9886 | 111.6351
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.844e-09 | -1.7095e-09 | 2.8793e-10 | 2.844e-09 | 1.7095e-09 | -2.8793e-10 | 2.3063e-09 | -1.2696e-09 | 2.4227e-09 | -2.3063e-09 | 1.2696e-09 | -2.4227e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.71749 | 0.83464 | 0.95631 | 0.71749 | 0.83464 | 0.95631 | -10.6355 | -114.9886 | 111.6351 | -10.6355 | -114.9886 | 111.6351
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.7062e-09 | -1.0258e-09 | 1.7265e-10 | 1.7062e-09 | 1.0258e-09 | -1.7265e-10 | 1.3838e-09 | -7.6191e-10 | 1.4538e-09 | -1.3838e-09 | 7.6191e-10 | -1.4538e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.71749 | 0.83464 | 0.95631 | 0.71749 | 0.83464 | 0.95631 | -10.6355 | -114.9886 | 111.6351 | -10.6355 | -114.9886 | 111.6351
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.6899e-10 | -3.4186e-10 | 5.7736e-11 | 5.6899e-10 | 3.4186e-10 | -5.7736e-11 | 4.6126e-10 | -2.5369e-10 | 4.8433e-10 | -4.6126e-10 | 2.5369e-10 | -4.8433e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.71749 | 0.83464 | 0.95631 | 0.71749 | 0.83464 | 0.95631 | -10.6355 | -114.9886 | 111.6351 | -10.6355 | -114.9886 | 111.6351
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.1375e-09 | -6.8384e-10 | 1.151e-10 | 1.1375e-09 | 6.8384e-10 | -1.151e-10 | 9.2253e-10 | -5.0794e-10 | 9.6921e-10 | -9.2253e-10 | 5.0794e-10 | -9.6921e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.71749 | 0.83464 | 0.95631 | 0.71749 | 0.83464 | 0.95631 | -10.6355 | -114.9886 | 111.6351 | -10.6355 | -114.9886 | 111.6351
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.6874e-10 | -3.4192e-10 | 5.7548e-11 | 5.6874e-10 | 3.4192e-10 | -5.7548e-11 | 4.6127e-10 | -2.5397e-10 | 4.846e-10 | -4.6127e-10 | 2.5397e-10 | -4.846e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.71749 | 0.83464 | 0.95631 | 0.71749 | 0.83464 | 0.95631 | -10.6355 | -114.9886 | 111.6351 | -10.6355 | -114.9886 | 111.6351
Line16_4_18 | 3.9844 | 0 | 0 | 3.9844 | 0 | 0 | 0.92016 | 0 | 0 | 0.92016 | 0 | 0 | 0.25401 | 2.3798e-09 | -2.8874e-09 | -7.8172e-14 | 2.1884e-10 | 8.5683e-11 | 0.26459 | -1.1728e-09 | -3.0173e-11 | 1.3965e-13 | 1.0399e-09 | -1.1168e-09 | -56.8047 | 0 | 0 | 123.1953 | 0 | 0 |  | 0.39861 | 0.80998 | 0.88155 | 0 | 0.80923 | 0.85293 | -10.6355 | -103.9947 | 102.8383 | 0 | -98.3508 | 97.9202
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.6937e-10 | -3.4177e-10 | 5.8019e-11 | 5.6937e-10 | 3.4177e-10 | -5.8019e-11 | 4.6124e-10 | -2.5326e-10 | 4.8392e-10 | -4.6124e-10 | 2.5326e-10 | -4.8392e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.71749 | 0.83464 | 0.95631 | 0.71749 | 0.83464 | 0.95631 | -10.6355 | -114.9886 | 111.6351 | -10.6355 | -114.9886 | 111.6351
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.5502e-09 | -2.7353e-09 | 4.6058e-10 | 4.5502e-09 | 2.7353e-09 | -4.6058e-10 | 3.6901e-09 | -2.0315e-09 | 3.8766e-09 | -3.6901e-09 | 2.0315e-09 | -3.8766e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.71749 | 0.83464 | 0.95631 | 0.71749 | 0.83464 | 0.95631 | -10.6355 | -114.9886 | 111.6351 | -10.6355 | -114.9886 | 111.6351
Line2_1_4 | 2.6563 | 1.3281 | 1.3281 | 2.6563 | 1.3281 | 1.3281 | 0.61344 | 0.30672 | 0.30672 | 0.61344 | 0.30672 | 0.30672 | 0.30481 | -0.13496 | 0.28737 | -0.16934 | 0.16883 | -0.2535 | 0.31751 | 0.21754 | -0.058781 | -0.1764 | -0.18226 | 0.09406 | -56.8047 | 123.1953 | 123.1953 | 123.1953 | -56.8047 | -56.8047 |  | 0.71749 | 0.83464 | 0.95631 | 0.39861 | 0.80998 | 0.88155 | -10.6355 | -114.9886 | 111.6351 | -10.6355 | -103.9947 | 102.8383
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.1381e-09 | -6.8369e-10 | 1.1557e-10 | 1.1381e-09 | 6.8369e-10 | -1.1557e-10 | 9.2251e-10 | -5.0723e-10 | 9.6852e-10 | -9.2251e-10 | 5.0723e-10 | -9.6852e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.71749 | 0.83464 | 0.95631 | 0.71749 | 0.83464 | 0.95631 | -10.6355 | -114.9886 | 111.6351 | -10.6355 | -114.9886 | 111.6351
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.8441e-09 | -1.7095e-09 | 2.8806e-10 | 2.8441e-09 | 1.7095e-09 | -2.8806e-10 | 2.3063e-09 | -1.2694e-09 | 2.4226e-09 | -2.3063e-09 | 1.2694e-09 | -2.4226e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.71749 | 0.83464 | 0.95631 | 0.71749 | 0.83464 | 0.95631 | -10.6355 | -114.9886 | 111.6351 | -10.6355 | -114.9886 | 111.6351
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.2754e-09 | -1.3676e-09 | 2.3051e-10 | 2.2754e-09 | 1.3676e-09 | -2.3051e-10 | 1.8451e-09 | -1.0154e-09 | 1.938e-09 | -1.8451e-09 | 1.0154e-09 | -1.938e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.71749 | 0.83464 | 0.95631 | 0.71749 | 0.83464 | 0.95631 | -10.6355 | -114.9886 | 111.6351 | -10.6355 | -114.9886 | 111.6351
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.7062e-09 | -1.0258e-09 | 1.7265e-10 | 1.7062e-09 | 1.0258e-09 | -1.7265e-10 | 1.3838e-09 | -7.6191e-10 | 1.4538e-09 | -1.3838e-09 | 7.6191e-10 | -1.4538e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.71749 | 0.83464 | 0.95631 | 0.71749 | 0.83464 | 0.95631 | -10.6355 | -114.9886 | 111.6351 | -10.6355 | -114.9886 | 111.6351
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.6874e-10 | -3.4192e-10 | 5.7548e-11 | 5.6874e-10 | 3.4192e-10 | -5.7548e-11 | 4.6127e-10 | -2.5397e-10 | 4.846e-10 | -4.6127e-10 | 2.5397e-10 | -4.846e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.71749 | 0.83464 | 0.95631 | 0.71749 | 0.83464 | 0.95631 | -10.6355 | -114.9886 | 111.6351 | -10.6355 | -114.9886 | 111.6351
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.6874e-10 | -3.4192e-10 | 5.7548e-11 | 5.6874e-10 | 3.4192e-10 | -5.7548e-11 | 4.6127e-10 | -2.5397e-10 | 4.846e-10 | -4.6127e-10 | 2.5397e-10 | -4.846e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.71749 | 0.83464 | 0.95631 | 0.71749 | 0.83464 | 0.95631 | -10.6355 | -114.9886 | 111.6351 | -10.6355 | -114.9886 | 111.6351
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.9815e-09 | -2.3934e-09 | 4.0303e-10 | 3.9815e-09 | 2.3934e-09 | -4.0303e-10 | 3.2289e-09 | -1.7775e-09 | 3.3919e-09 | -3.2289e-09 | 1.7775e-09 | -3.3919e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.71749 | 0.83464 | 0.95631 | 0.71749 | 0.83464 | 0.95631 | -10.6355 | -114.9886 | 111.6351 | -10.6355 | -114.9886 | 111.6351

## LG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.0631e-09 | -1.8412e-09 | 3.1018e-10 | 3.0631e-09 | 1.8412e-09 | -3.1018e-10 | 2.4839e-09 | -1.3672e-09 | 2.6092e-09 | -2.4839e-09 | 1.3672e-09 | -2.6092e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.67973 | 0.79071 | 0.90597 | 0.67973 | 0.79071 | 0.90597 | -10.6355 | -114.9886 | 111.6351 | -10.6355 | -114.9886 | 111.6351
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.0629e-09 | -1.8412e-09 | 3.1007e-10 | 3.0629e-09 | 1.8412e-09 | -3.1007e-10 | 2.4839e-09 | -1.3674e-09 | 2.6094e-09 | -2.4839e-09 | 1.3674e-09 | -2.6094e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.67973 | 0.79071 | 0.90597 | 0.67973 | 0.79071 | 0.90597 | -10.6355 | -114.9886 | 111.6351 | -10.6355 | -114.9886 | 111.6351
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5525e-09 | -1.5343e-09 | 2.5842e-10 | 2.5525e-09 | 1.5343e-09 | -2.5842e-10 | 2.0699e-09 | -1.1394e-09 | 2.1744e-09 | -2.0699e-09 | 1.1394e-09 | -2.1744e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.67973 | 0.79071 | 0.90597 | 0.67973 | 0.79071 | 0.90597 | -10.6355 | -114.9886 | 111.6351 | -10.6355 | -114.9886 | 111.6351
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.5314e-09 | -9.2063e-10 | 1.5495e-10 | 1.5314e-09 | 9.2063e-10 | -1.5495e-10 | 1.242e-09 | -6.8382e-10 | 1.3048e-09 | -1.242e-09 | 6.8382e-10 | -1.3048e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.67973 | 0.79071 | 0.90597 | 0.67973 | 0.79071 | 0.90597 | -10.6355 | -114.9886 | 111.6351 | -10.6355 | -114.9886 | 111.6351
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.1068e-10 | -3.0682e-10 | 5.1819e-11 | 5.1068e-10 | 3.0682e-10 | -5.1819e-11 | 4.1398e-10 | -2.2768e-10 | 4.3469e-10 | -4.1398e-10 | 2.2768e-10 | -4.3469e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.67973 | 0.79071 | 0.90597 | 0.67973 | 0.79071 | 0.90597 | -10.6355 | -114.9886 | 111.6351 | -10.6355 | -114.9886 | 111.6351
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.0209e-09 | -6.1375e-10 | 1.033e-10 | 1.0209e-09 | 6.1375e-10 | -1.033e-10 | 8.2798e-10 | -4.5588e-10 | 8.6987e-10 | -8.2798e-10 | 4.5588e-10 | -8.6987e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.67973 | 0.79071 | 0.90597 | 0.67973 | 0.79071 | 0.90597 | -10.6355 | -114.9886 | 111.6351 | -10.6355 | -114.9886 | 111.6351
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.1045e-10 | -3.0688e-10 | 5.165e-11 | 5.1045e-10 | 3.0688e-10 | -5.165e-11 | 4.1399e-10 | -2.2794e-10 | 4.3493e-10 | -4.1399e-10 | 2.2794e-10 | -4.3493e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.67973 | 0.79071 | 0.90597 | 0.67973 | 0.79071 | 0.90597 | -10.6355 | -114.9886 | 111.6351 | -10.6355 | -114.9886 | 111.6351
Line16_4_18 | 3.7747 | 0 | 0 | 3.7747 | 0 | 0 | 0.87173 | 0 | 0 | 0.87173 | 0 | 0 | 0.22798 | 2.1359e-09 | -2.5914e-09 | -7.0333e-14 | 1.9641e-10 | 7.6901e-11 | 0.23747 | -1.0526e-09 | -2.708e-11 | 1.2524e-13 | 9.3335e-10 | -1.0023e-09 | -56.8047 | 0 | 0 | 123.1953 | 0 | 0 |  | 0.37763 | 0.76735 | 0.83515 | 0 | 0.76664 | 0.80804 | -10.6355 | -103.9947 | 102.8383 | 0 | -98.3508 | 97.9202
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.1101e-10 | -3.0674e-10 | 5.2073e-11 | 5.1101e-10 | 3.0674e-10 | -5.2073e-11 | 4.1397e-10 | -2.273e-10 | 4.3432e-10 | -4.1397e-10 | 2.273e-10 | -4.3432e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.67973 | 0.79071 | 0.90597 | 0.67973 | 0.79071 | 0.90597 | -10.6355 | -114.9886 | 111.6351 | -10.6355 | -114.9886 | 111.6351
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.0838e-09 | -2.455e-09 | 4.1337e-10 | 4.0838e-09 | 2.455e-09 | -4.1337e-10 | 3.3119e-09 | -1.8233e-09 | 3.4792e-09 | -3.3119e-09 | 1.8233e-09 | -3.4792e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.67973 | 0.79071 | 0.90597 | 0.67973 | 0.79071 | 0.90597 | -10.6355 | -114.9886 | 111.6351 | -10.6355 | -114.9886 | 111.6351
Line2_1_4 | 2.5165 | 1.2582 | 1.2582 | 2.5165 | 1.2582 | 1.2582 | 0.58115 | 0.29058 | 0.29058 | 0.58115 | 0.29058 | 0.29058 | 0.27357 | -0.12113 | 0.25792 | -0.15198 | 0.15153 | -0.22752 | 0.28497 | 0.19524 | -0.052756 | -0.15832 | -0.16358 | 0.084419 | -56.8047 | 123.1953 | 123.1953 | 123.1953 | -56.8047 | -56.8047 |  | 0.67973 | 0.79071 | 0.90597 | 0.37763 | 0.76735 | 0.83515 | -10.6355 | -114.9886 | 111.6351 | -10.6355 | -103.9947 | 102.8383
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.0215e-09 | -6.1362e-10 | 1.0372e-10 | 1.0215e-09 | 6.1362e-10 | -1.0372e-10 | 8.2796e-10 | -4.5524e-10 | 8.6925e-10 | -8.2796e-10 | 4.5524e-10 | -8.6925e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.67973 | 0.79071 | 0.90597 | 0.67973 | 0.79071 | 0.90597 | -10.6355 | -114.9886 | 111.6351 | -10.6355 | -114.9886 | 111.6351
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5526e-09 | -1.5343e-09 | 2.5853e-10 | 2.5526e-09 | 1.5343e-09 | -2.5853e-10 | 2.0699e-09 | -1.1393e-09 | 2.1743e-09 | -2.0699e-09 | 1.1393e-09 | -2.1743e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.67973 | 0.79071 | 0.90597 | 0.67973 | 0.79071 | 0.90597 | -10.6355 | -114.9886 | 111.6351 | -10.6355 | -114.9886 | 111.6351
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.0422e-09 | -1.2274e-09 | 2.0688e-10 | 2.0422e-09 | 1.2274e-09 | -2.0688e-10 | 1.6559e-09 | -9.1133e-10 | 1.7393e-09 | -1.6559e-09 | 9.1133e-10 | -1.7393e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.67973 | 0.79071 | 0.90597 | 0.67973 | 0.79071 | 0.90597 | -10.6355 | -114.9886 | 111.6351 | -10.6355 | -114.9886 | 111.6351
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.5314e-09 | -9.2063e-10 | 1.5495e-10 | 1.5314e-09 | 9.2063e-10 | -1.5495e-10 | 1.242e-09 | -6.8382e-10 | 1.3048e-09 | -1.242e-09 | 6.8382e-10 | -1.3048e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.67973 | 0.79071 | 0.90597 | 0.67973 | 0.79071 | 0.90597 | -10.6355 | -114.9886 | 111.6351 | -10.6355 | -114.9886 | 111.6351
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.1045e-10 | -3.0688e-10 | 5.165e-11 | 5.1045e-10 | 3.0688e-10 | -5.165e-11 | 4.1399e-10 | -2.2794e-10 | 4.3493e-10 | -4.1399e-10 | 2.2794e-10 | -4.3493e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.67973 | 0.79071 | 0.90597 | 0.67973 | 0.79071 | 0.90597 | -10.6355 | -114.9886 | 111.6351 | -10.6355 | -114.9886 | 111.6351
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.1045e-10 | -3.0688e-10 | 5.165e-11 | 5.1045e-10 | 3.0688e-10 | -5.165e-11 | 4.1399e-10 | -2.2794e-10 | 4.3493e-10 | -4.1399e-10 | 2.2794e-10 | -4.3493e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.67973 | 0.79071 | 0.90597 | 0.67973 | 0.79071 | 0.90597 | -10.6355 | -114.9886 | 111.6351 | -10.6355 | -114.9886 | 111.6351
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.5734e-09 | -2.1481e-09 | 3.6172e-10 | 3.5734e-09 | 2.1481e-09 | -3.6172e-10 | 2.8979e-09 | -1.5953e-09 | 3.0443e-09 | -2.8979e-09 | 1.5953e-09 | -3.0443e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.67973 | 0.79071 | 0.90597 | 0.67973 | 0.79071 | 0.90597 | -10.6355 | -114.9886 | 111.6351 | -10.6355 | -114.9886 | 111.6351

## LG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.4281e-11 | -2.1112e-11 | 3.9781e-12 | 3.4281e-11 | 2.1112e-11 | -3.9781e-12 | 2.8972e-11 | -7.6398e-12 | 2.2126e-11 | -2.8972e-11 | 7.6398e-12 | -2.2126e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.94836 | 0.94899 | 0.95019 | 0.94836 | 0.94899 | 0.95019 | -0.083749 | -119.9779 | 119.9362 | -0.083749 | -119.9779 | 119.9362
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.4279e-11 | -2.1113e-11 | 3.9772e-12 | 3.4279e-11 | 2.1113e-11 | -3.9772e-12 | 2.8972e-11 | -7.6413e-12 | 2.2127e-11 | -2.8972e-11 | 7.6413e-12 | -2.2127e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.94836 | 0.94899 | 0.95019 | 0.94836 | 0.94899 | 0.95019 | -0.083749 | -119.9779 | 119.9362 | -0.083749 | -119.9779 | 119.9362
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.8567e-11 | -1.7594e-11 | 3.3145e-12 | 2.8567e-11 | 1.7594e-11 | -3.3145e-12 | 2.4143e-11 | -6.3674e-12 | 1.8439e-11 | -2.4143e-11 | 6.3674e-12 | -1.8439e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.94836 | 0.94899 | 0.95019 | 0.94836 | 0.94899 | 0.95019 | -0.083749 | -119.9779 | 119.9362 | -0.083749 | -119.9779 | 119.9362
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.7138e-11 | -1.0557e-11 | 1.9879e-12 | 1.7138e-11 | 1.0557e-11 | -1.9879e-12 | 1.4486e-11 | -3.8218e-12 | 1.1065e-11 | -1.4486e-11 | 3.8218e-12 | -1.1065e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.94836 | 0.94899 | 0.95019 | 0.94836 | 0.94899 | 0.95019 | -0.083749 | -119.9779 | 119.9362 | -0.083749 | -119.9779 | 119.9362
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.7154e-12 | -3.5178e-12 | 6.6396e-13 | 5.7154e-12 | 3.5178e-12 | -6.6396e-13 | 4.8286e-12 | -1.2717e-12 | 3.686e-12 | -4.8286e-12 | 1.2717e-12 | -3.686e-12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.94836 | 0.94899 | 0.95019 | 0.94836 | 0.94899 | 0.95019 | -0.083749 | -119.9779 | 119.9362 | -0.083749 | -119.9779 | 119.9362
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.1426e-11 | -7.0381e-12 | 1.3253e-12 | 1.1426e-11 | 7.0381e-12 | -1.3253e-12 | 9.6572e-12 | -2.5478e-12 | 7.3764e-12 | -9.6572e-12 | 2.5478e-12 | -7.3764e-12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.94836 | 0.94899 | 0.95019 | 0.94836 | 0.94899 | 0.95019 | -0.083749 | -119.9779 | 119.9362 | -0.083749 | -119.9779 | 119.9362
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.7128e-12 | -3.5191e-12 | 6.6264e-13 | 5.7128e-12 | 3.5191e-12 | -6.6264e-13 | 4.8286e-12 | -1.2739e-12 | 3.6882e-12 | -4.8286e-12 | 1.2739e-12 | -3.6882e-12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.94836 | 0.94899 | 0.95019 | 0.94836 | 0.94899 | 0.95019 | -0.083749 | -119.9779 | 119.9362 | -0.083749 | -119.9779 | 119.9362
Line16_4_18 | 0.030792 | 0 | 0 | 0.030792 | 0 | 0 | 0.0071111 | 0 | 0 | 0.0071111 | 0 | 0 | 0.0047559 | 1.4155e-11 | -2.391e-11 | -0.0047408 | 6.8187e-12 | 2.4271e-12 | 0.0047566 | -1.9389e-11 | -2.4782e-12 | -0.0047408 | 6.788e-12 | -9.3235e-12 | -45.0906 | 0 | 0 | 134.9094 | 0 | 0 |  | 0.94589 | 0.94835 | 0.9496 | 0.94281 | 0.94804 | 0.9493 | -0.086777 | -119.9141 | 119.871 | -0.090584 | -119.8822 | 119.8385
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.7192e-12 | -3.516e-12 | 6.6594e-13 | 5.7192e-12 | 3.516e-12 | -6.6594e-13 | 4.8285e-12 | -1.2683e-12 | 3.6828e-12 | -4.8285e-12 | 1.2683e-12 | -3.6828e-12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.94836 | 0.94899 | 0.95019 | 0.94836 | 0.94899 | 0.95019 | -0.083749 | -119.9779 | 119.9362 | -0.083749 | -119.9779 | 119.9362
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.5705e-11 | -2.8151e-11 | 5.3025e-12 | 4.5705e-11 | 2.8151e-11 | -5.3025e-12 | 3.8629e-11 | -1.0189e-11 | 2.9504e-11 | -3.8629e-11 | 1.0189e-11 | -2.9504e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.94836 | 0.94899 | 0.95019 | 0.94836 | 0.94899 | 0.95019 | -0.083749 | -119.9779 | 119.9362 | -0.083749 | -119.9779 | 119.9362
Line2_1_4 | 0.020528 | 0.010264 | 0.010264 | 0.020528 | 0.010264 | 0.010264 | 0.0047408 | 0.0023704 | 0.0023704 | 0.0047408 | 0.0023704 | 0.0023704 | 0.0031787 | -0.00058648 | 0.0021758 | -0.0031706 | 0.0005885 | -0.0021738 | 0.0031795 | 0.0021717 | -0.00058193 | -0.0031711 | -0.0021696 | 0.00058403 | -45.0906 | 134.9094 | 134.9094 | 134.9094 | -45.0906 | -45.0906 |  | 0.94836 | 0.94899 | 0.95019 | 0.94589 | 0.94835 | 0.9496 | -0.083749 | -119.9779 | 119.9362 | -0.086777 | -119.9141 | 119.871
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.1432e-11 | -7.035e-12 | 1.3286e-12 | 1.1432e-11 | 7.035e-12 | -1.3286e-12 | 9.6571e-12 | -2.5423e-12 | 7.371e-12 | -9.6571e-12 | 2.5423e-12 | -7.371e-12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.94836 | 0.94899 | 0.95019 | 0.94836 | 0.94899 | 0.95019 | -0.083749 | -119.9779 | 119.9362 | -0.083749 | -119.9779 | 119.9362
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.8568e-11 | -1.7593e-11 | 3.3154e-12 | 2.8568e-11 | 1.7593e-11 | -3.3154e-12 | 2.4143e-11 | -6.3659e-12 | 1.8437e-11 | -2.4143e-11 | 6.3659e-12 | -1.8437e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.94836 | 0.94899 | 0.95019 | 0.94836 | 0.94899 | 0.95019 | -0.083749 | -119.9779 | 119.9362 | -0.083749 | -119.9779 | 119.9362
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.2856e-11 | -1.4074e-11 | 2.6528e-12 | 2.2856e-11 | 1.4074e-11 | -2.6528e-12 | 1.9314e-11 | -5.0919e-12 | 1.4749e-11 | -1.9314e-11 | 5.0919e-12 | -1.4749e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.94836 | 0.94899 | 0.95019 | 0.94836 | 0.94899 | 0.95019 | -0.083749 | -119.9779 | 119.9362 | -0.083749 | -119.9779 | 119.9362
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.7138e-11 | -1.0557e-11 | 1.9879e-12 | 1.7138e-11 | 1.0557e-11 | -1.9879e-12 | 1.4486e-11 | -3.8218e-12 | 1.1065e-11 | -1.4486e-11 | 3.8218e-12 | -1.1065e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.94836 | 0.94899 | 0.95019 | 0.94836 | 0.94899 | 0.95019 | -0.083749 | -119.9779 | 119.9362 | -0.083749 | -119.9779 | 119.9362
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.7128e-12 | -3.5191e-12 | 6.6264e-13 | 5.7128e-12 | 3.5191e-12 | -6.6264e-13 | 4.8286e-12 | -1.2739e-12 | 3.6882e-12 | -4.8286e-12 | 1.2739e-12 | -3.6882e-12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.94836 | 0.94899 | 0.95019 | 0.94836 | 0.94899 | 0.95019 | -0.083749 | -119.9779 | 119.9362 | -0.083749 | -119.9779 | 119.9362
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.7128e-12 | -3.5191e-12 | 6.6264e-13 | 5.7128e-12 | 3.5191e-12 | -6.6264e-13 | 4.8286e-12 | -1.2739e-12 | 3.6882e-12 | -4.8286e-12 | 1.2739e-12 | -3.6882e-12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.94836 | 0.94899 | 0.95019 | 0.94836 | 0.94899 | 0.95019 | -0.083749 | -119.9779 | 119.9362 | -0.083749 | -119.9779 | 119.9362
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.9992e-11 | -2.4632e-11 | 4.6398e-12 | 3.9992e-11 | 2.4632e-11 | -4.6398e-12 | 3.38e-11 | -8.9152e-12 | 2.5815e-11 | -3.38e-11 | 8.9152e-12 | -2.5815e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.94836 | 0.94899 | 0.95019 | 0.94836 | 0.94899 | 0.95019 | -0.083749 | -119.9779 | 119.9362 | -0.083749 | -119.9779 | 119.9362

## LG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.0768e-11 | -1.8948e-11 | 3.5703e-12 | 3.0768e-11 | 1.8948e-11 | -3.5703e-12 | 2.6002e-11 | -6.8568e-12 | 1.9858e-11 | -2.6002e-11 | 6.8568e-12 | -1.9858e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.89844 | 0.89904 | 0.90018 | 0.89844 | 0.89904 | 0.90018 | -0.083749 | -119.9779 | 119.9362 | -0.083749 | -119.9779 | 119.9362
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.0766e-11 | -1.8949e-11 | 3.5695e-12 | 3.0766e-11 | 1.8949e-11 | -3.5695e-12 | 2.6002e-11 | -6.8581e-12 | 1.9859e-11 | -2.6002e-11 | 6.8581e-12 | -1.9859e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.89844 | 0.89904 | 0.90018 | 0.89844 | 0.89904 | 0.90018 | -0.083749 | -119.9779 | 119.9362 | -0.083749 | -119.9779 | 119.9362
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5639e-11 | -1.5791e-11 | 2.9748e-12 | 2.5639e-11 | 1.5791e-11 | -2.9748e-12 | 2.1668e-11 | -5.7147e-12 | 1.6549e-11 | -2.1668e-11 | 5.7147e-12 | -1.6549e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.89844 | 0.89904 | 0.90018 | 0.89844 | 0.89904 | 0.90018 | -0.083749 | -119.9779 | 119.9362 | -0.083749 | -119.9779 | 119.9362
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.5382e-11 | -9.4751e-12 | 1.7842e-12 | 1.5382e-11 | 9.4751e-12 | -1.7842e-12 | 1.3001e-11 | -3.4301e-12 | 9.9306e-12 | -1.3001e-11 | 3.43e-12 | -9.9306e-12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.89844 | 0.89904 | 0.90018 | 0.89844 | 0.89904 | 0.90018 | -0.083749 | -119.9779 | 119.9362 | -0.083749 | -119.9779 | 119.9362
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.1296e-12 | -3.1573e-12 | 5.9591e-13 | 5.1296e-12 | 3.1573e-12 | -5.9591e-13 | 4.3337e-12 | -1.1413e-12 | 3.3082e-12 | -4.3337e-12 | 1.1413e-12 | -3.3082e-12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.89844 | 0.89904 | 0.90018 | 0.89844 | 0.89904 | 0.90018 | -0.083749 | -119.9779 | 119.9362 | -0.083749 | -119.9779 | 119.9362
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.0255e-11 | -6.3167e-12 | 1.1895e-12 | 1.0255e-11 | 6.3167e-12 | -1.1895e-12 | 8.6674e-12 | -2.2867e-12 | 6.6204e-12 | -8.6674e-12 | 2.2867e-12 | -6.6204e-12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.89844 | 0.89904 | 0.90018 | 0.89844 | 0.89904 | 0.90018 | -0.083749 | -119.9779 | 119.9362 | -0.083749 | -119.9779 | 119.9362
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.1273e-12 | -3.1584e-12 | 5.9473e-13 | 5.1273e-12 | 3.1584e-12 | -5.9473e-13 | 4.3337e-12 | -1.1433e-12 | 3.3102e-12 | -4.3337e-12 | 1.1433e-12 | -3.3102e-12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.89844 | 0.89904 | 0.90018 | 0.89844 | 0.89904 | 0.90018 | -0.083749 | -119.9779 | 119.9362 | -0.083749 | -119.9779 | 119.9362
Line16_4_18 | 0.029171 | 0 | 0 | 0.029171 | 0 | 0 | 0.0067369 | 0 | 0 | 0.0067369 | 0 | 0 | 0.0042685 | 1.2705e-11 | -2.1459e-11 | -0.0042549 | 6.1198e-12 | 2.1783e-12 | 0.0042691 | -1.7402e-11 | -2.2242e-12 | -0.0042549 | 6.0923e-12 | -8.3679e-12 | -45.0906 | 0 | 0 | 134.9094 | 0 | 0 |  | 0.89611 | 0.89844 | 0.89962 | 0.89319 | 0.89814 | 0.89934 | -0.086777 | -119.9141 | 119.871 | -0.090584 | -119.8822 | 119.8385
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.133e-12 | -3.1556e-12 | 5.9769e-13 | 5.133e-12 | 3.1556e-12 | -5.9769e-13 | 4.3336e-12 | -1.1383e-12 | 3.3053e-12 | -4.3336e-12 | 1.1383e-12 | -3.3053e-12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.89844 | 0.89904 | 0.90018 | 0.89844 | 0.89904 | 0.90018 | -0.083749 | -119.9779 | 119.9362 | -0.083749 | -119.9779 | 119.9362
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.1021e-11 | -2.5266e-11 | 4.759e-12 | 4.1021e-11 | 2.5266e-11 | -4.759e-12 | 3.467e-11 | -9.1448e-12 | 2.648e-11 | -3.467e-11 | 9.1448e-12 | -2.648e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.89844 | 0.89904 | 0.90018 | 0.89844 | 0.89904 | 0.90018 | -0.083749 | -119.9779 | 119.9362 | -0.083749 | -119.9779 | 119.9362
Line2_1_4 | 0.019448 | 0.0097238 | 0.0097238 | 0.019448 | 0.0097238 | 0.0097238 | 0.0044912 | 0.0022456 | 0.0022456 | 0.0044912 | 0.0022456 | 0.0022456 | 0.0028529 | -0.00052637 | 0.0019528 | -0.0028457 | 0.00052818 | -0.001951 | 0.0028536 | 0.0019491 | -0.00052228 | -0.002846 | -0.0019472 | 0.00052417 | -45.0906 | 134.9094 | 134.9094 | 134.9094 | -45.0906 | -45.0906 |  | 0.89844 | 0.89904 | 0.90018 | 0.89611 | 0.89844 | 0.89962 | -0.083749 | -119.9779 | 119.9362 | -0.086777 | -119.9141 | 119.871
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.026e-11 | -6.314e-12 | 1.1924e-12 | 1.026e-11 | 6.314e-12 | -1.1924e-12 | 8.6673e-12 | -2.2817e-12 | 6.6155e-12 | -8.6673e-12 | 2.2817e-12 | -6.6155e-12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.89844 | 0.89904 | 0.90018 | 0.89844 | 0.89904 | 0.90018 | -0.083749 | -119.9779 | 119.9362 | -0.083749 | -119.9779 | 119.9362
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.564e-11 | -1.579e-11 | 2.9756e-12 | 2.564e-11 | 1.579e-11 | -2.9756e-12 | 2.1668e-11 | -5.7134e-12 | 1.6548e-11 | -2.1668e-11 | 5.7134e-12 | -1.6548e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.89844 | 0.89904 | 0.90018 | 0.89844 | 0.89904 | 0.90018 | -0.083749 | -119.9779 | 119.9362 | -0.083749 | -119.9779 | 119.9362
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.0513e-11 | -1.2632e-11 | 2.3809e-12 | 2.0513e-11 | 1.2632e-11 | -2.3809e-12 | 1.7335e-11 | -4.5701e-12 | 1.3238e-11 | -1.7335e-11 | 4.5701e-12 | -1.3238e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.89844 | 0.89904 | 0.90018 | 0.89844 | 0.89904 | 0.90018 | -0.083749 | -119.9779 | 119.9362 | -0.083749 | -119.9779 | 119.9362
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.5382e-11 | -9.4751e-12 | 1.7842e-12 | 1.5382e-11 | 9.4751e-12 | -1.7842e-12 | 1.3001e-11 | -3.4301e-12 | 9.9306e-12 | -1.3001e-11 | 3.4301e-12 | -9.9306e-12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.89844 | 0.89904 | 0.90018 | 0.89844 | 0.89904 | 0.90018 | -0.083749 | -119.9779 | 119.9362 | -0.083749 | -119.9779 | 119.9362
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.1273e-12 | -3.1584e-12 | 5.9473e-13 | 5.1273e-12 | 3.1584e-12 | -5.9473e-13 | 4.3337e-12 | -1.1433e-12 | 3.3102e-12 | -4.3337e-12 | 1.1434e-12 | -3.3102e-12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.89844 | 0.89904 | 0.90018 | 0.89844 | 0.89904 | 0.90018 | -0.083749 | -119.9779 | 119.9362 | -0.083749 | -119.9779 | 119.9362
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.1273e-12 | -3.1584e-12 | 5.9473e-13 | 5.1273e-12 | 3.1584e-12 | -5.9473e-13 | 4.3337e-12 | -1.1433e-12 | 3.3102e-12 | -4.3337e-12 | 1.1434e-12 | -3.3102e-12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.89844 | 0.89904 | 0.90018 | 0.89844 | 0.89904 | 0.90018 | -0.083749 | -119.9779 | 119.9362 | -0.083749 | -119.9779 | 119.9362
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.5893e-11 | -2.2108e-11 | 4.1643e-12 | 3.5893e-11 | 2.2108e-11 | -4.1643e-12 | 3.0336e-11 | -8.0014e-12 | 2.3169e-11 | -3.0336e-11 | 8.0014e-12 | -2.3169e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.89844 | 0.89904 | 0.90018 | 0.89844 | 0.89904 | 0.90018 | -0.083749 | -119.9779 | 119.9362 | -0.083749 | -119.9779 | 119.9362

## LLG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.4285e-09 | -4.8352e-09 | -5.2405e-09 | 4.4285e-09 | 4.8352e-09 | 5.2405e-09 | 1.7703e-09 | 2.9178e-09 | 1.1066e-09 | -1.7703e-09 | -2.9178e-09 | -1.1066e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.79029 | 0.73562 | 0.71415 | 0.79029 | 0.73562 | 0.71415 | -5.5628 | -129.8908 | 116.1551 | -5.5628 | -129.8908 | 116.1551
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.4288e-09 | -4.8352e-09 | -5.2401e-09 | 4.4288e-09 | 4.8352e-09 | 5.2401e-09 | 1.7701e-09 | 2.9182e-09 | 1.1065e-09 | -1.7701e-09 | -2.9182e-09 | -1.1065e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.79029 | 0.73562 | 0.71415 | 0.79029 | 0.73562 | 0.71415 | -5.5628 | -129.8908 | 116.1551 | -5.5628 | -129.8908 | 116.1551
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.6906e-09 | -4.0294e-09 | -4.3668e-09 | 3.6906e-09 | 4.0294e-09 | 4.3668e-09 | 1.4751e-09 | 2.4317e-09 | 9.2208e-10 | -1.4751e-09 | -2.4317e-09 | -9.2208e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.79029 | 0.73562 | 0.71415 | 0.79029 | 0.73562 | 0.71415 | -5.5628 | -129.8908 | 116.1551 | -5.5628 | -129.8908 | 116.1551
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.2147e-09 | -2.4176e-09 | -2.6198e-09 | 2.2147e-09 | 2.4176e-09 | 2.6198e-09 | 8.8482e-10 | 1.4594e-09 | 5.5311e-10 | -8.8482e-10 | -1.4594e-09 | -5.5311e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.79029 | 0.73562 | 0.71415 | 0.79029 | 0.73562 | 0.71415 | -5.5628 | -129.8908 | 116.1551 | -5.5628 | -129.8908 | 116.1551
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.3767e-10 | -8.0585e-10 | -8.7384e-10 | 7.3767e-10 | 8.0585e-10 | 8.7384e-10 | 2.9536e-10 | 4.8583e-10 | 1.846e-10 | -2.9536e-10 | -4.8583e-10 | -1.846e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.79029 | 0.73562 | 0.71415 | 0.79029 | 0.73562 | 0.71415 | -5.5628 | -129.8908 | 116.1551 | -5.5628 | -129.8908 | 116.1551
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.4765e-09 | -1.6118e-09 | -1.7465e-09 | 1.4765e-09 | 1.6118e-09 | 1.7465e-09 | 5.8988e-10 | 9.7296e-10 | 3.6874e-10 | -5.8988e-10 | -9.7296e-10 | -3.6874e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.79029 | 0.73562 | 0.71415 | 0.79029 | 0.73562 | 0.71415 | -5.5628 | -129.8908 | 116.1551 | -5.5628 | -129.8908 | 116.1551
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.3824e-10 | -8.0588e-10 | -8.7325e-10 | 7.3824e-10 | 8.0588e-10 | 8.7325e-10 | 2.9494e-10 | 4.8648e-10 | 1.8437e-10 | -2.9494e-10 | -4.8648e-10 | -1.8437e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.79029 | 0.73562 | 0.71415 | 0.79029 | 0.73562 | 0.71415 | -5.5628 | -129.8908 | 116.1551 | -5.5628 | -129.8908 | 116.1551
Line16_4_18 | 0 | 5.2284 | 5.0672 | 0 | 5.2284 | 5.0672 | 0 | 1.2075 | 1.1702 | 0 | 1.2075 | 1.1702 | -1.2555e-09 | 0.13111 | 0.28798 | 9.4163e-10 | 4.9881e-14 | 4.6449e-14 | -2.7102e-09 | 0.4756 | 0.36259 | -1.4747e-10 | 7.7862e-14 | 4.2309e-14 | 0 | 147.8723 | 72.7524 | 0 | -32.1277 | -107.2476 |  | 0.52686 | 0.40858 | 0.39568 | 0.39515 | 0 | 0 | -5.5628 | -137.5402 | 124.2944 | -5.5628 | 0 | 0
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.3683e-10 | -8.0581e-10 | -8.7472e-10 | 7.3683e-10 | 8.0581e-10 | 8.7472e-10 | 2.9599e-10 | 4.8485e-10 | 1.8495e-10 | -2.9599e-10 | -4.8485e-10 | -1.8495e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.79029 | 0.73562 | 0.71415 | 0.79029 | 0.73562 | 0.71415 | -5.5628 | -129.8908 | 116.1551 | -5.5628 | -129.8908 | 116.1551
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.9053e-09 | -6.447e-09 | -6.9866e-09 | 5.9053e-09 | 6.447e-09 | 6.9866e-09 | 2.36e-09 | 3.8912e-09 | 1.4752e-09 | -2.36e-09 | -3.8912e-09 | -1.4752e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.79029 | 0.73562 | 0.71415 | 0.79029 | 0.73562 | 0.71415 | -5.5628 | -129.8908 | 116.1551 | -5.5628 | -129.8908 | 116.1551
Line2_1_4 | 2.7207 | 3.461 | 3.3802 | 2.7207 | 3.461 | 3.3802 | 0.62832 | 0.79929 | 0.78061 | 0.62832 | 0.79929 | 0.78061 | 0.22207 | 0.34481 | 0.16028 | -0.14804 | -0.22503 | -0.046026 | 0.44413 | 0.47625 | 0.53394 | -0.29609 | -0.23668 | -0.30543 | -68.9977 | 176.0143 | 42.8641 | 111.0023 | -3.9857 | -137.1359 |  | 0.79029 | 0.73562 | 0.71415 | 0.52686 | 0.40858 | 0.39568 | -5.5628 | -129.8908 | 116.1551 | -5.5628 | -137.5402 | 124.2944
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.4751e-09 | -1.6117e-09 | -1.748e-09 | 1.4751e-09 | 1.6117e-09 | 1.748e-09 | 5.9093e-10 | 9.7133e-10 | 3.6932e-10 | -5.9093e-10 | -9.7133e-10 | -3.6932e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.79029 | 0.73562 | 0.71415 | 0.79029 | 0.73562 | 0.71415 | -5.5628 | -129.8908 | 116.1551 | -5.5628 | -129.8908 | 116.1551
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.6902e-09 | -4.0293e-09 | -4.3672e-09 | 3.6902e-09 | 4.0293e-09 | 4.3672e-09 | 1.4754e-09 | 2.4313e-09 | 9.2224e-10 | -1.4754e-09 | -2.4313e-09 | -9.2224e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.79029 | 0.73562 | 0.71415 | 0.79029 | 0.73562 | 0.71415 | -5.5628 | -129.8908 | 116.1551 | -5.5628 | -129.8908 | 116.1551
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.952e-09 | -3.2235e-09 | -3.494e-09 | 2.952e-09 | 3.2235e-09 | 3.494e-09 | 1.1805e-09 | 1.9448e-09 | 7.3787e-10 | -1.1805e-09 | -1.9448e-09 | -7.3787e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.79029 | 0.73562 | 0.71415 | 0.79029 | 0.73562 | 0.71415 | -5.5628 | -129.8908 | 116.1551 | -5.5628 | -129.8908 | 116.1551
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.2147e-09 | -2.4176e-09 | -2.6198e-09 | 2.2147e-09 | 2.4176e-09 | 2.6198e-09 | 8.8482e-10 | 1.4594e-09 | 5.5311e-10 | -8.8482e-10 | -1.4594e-09 | -5.5311e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.79029 | 0.73562 | 0.71415 | 0.79029 | 0.73562 | 0.71415 | -5.5628 | -129.8908 | 116.1551 | -5.5628 | -129.8908 | 116.1551
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.3824e-10 | -8.0588e-10 | -8.7325e-10 | 7.3824e-10 | 8.0588e-10 | 8.7325e-10 | 2.9494e-10 | 4.8648e-10 | 1.8437e-10 | -2.9494e-10 | -4.8648e-10 | -1.8437e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.79029 | 0.73562 | 0.71415 | 0.79029 | 0.73562 | 0.71415 | -5.5628 | -129.8908 | 116.1551 | -5.5628 | -129.8908 | 116.1551
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.3824e-10 | -8.0588e-10 | -8.7325e-10 | 7.3824e-10 | 8.0588e-10 | 8.7325e-10 | 2.9494e-10 | 4.8648e-10 | 1.8437e-10 | -2.9494e-10 | -4.8648e-10 | -1.8437e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.79029 | 0.73562 | 0.71415 | 0.79029 | 0.73562 | 0.71415 | -5.5628 | -129.8908 | 116.1551 | -5.5628 | -129.8908 | 116.1551
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.1671e-09 | -5.6411e-09 | -6.1133e-09 | 5.1671e-09 | 5.6411e-09 | 6.1133e-09 | 2.065e-09 | 3.4047e-09 | 1.2908e-09 | -2.065e-09 | -3.4047e-09 | -1.2908e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.79029 | 0.73562 | 0.71415 | 0.79029 | 0.73562 | 0.71415 | -5.5628 | -129.8908 | 116.1551 | -5.5628 | -129.8908 | 116.1551

## LLG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.9714e-09 | -5.3964e-09 | -5.8436e-09 | 4.9714e-09 | 5.3964e-09 | 5.8436e-09 | 1.9874e-09 | 3.2585e-09 | 1.2311e-09 | -1.9874e-09 | -3.2585e-09 | -1.2311e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.81822 | 0.75969 | 0.73707 | 0.81822 | 0.75969 | 0.73707 | -5.7581 | -130.2127 | 116.0437 | -5.7581 | -130.2127 | 116.0437
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.9718e-09 | -5.3964e-09 | -5.8432e-09 | 4.9718e-09 | 5.3964e-09 | 5.8432e-09 | 1.9871e-09 | 3.2589e-09 | 1.2309e-09 | -1.9871e-09 | -3.2589e-09 | -1.2309e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.81822 | 0.75969 | 0.73707 | 0.81822 | 0.75969 | 0.73707 | -5.7581 | -130.2127 | 116.0437 | -5.7581 | -130.2127 | 116.0437
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.143e-09 | -4.497e-09 | -4.8695e-09 | 4.143e-09 | 4.497e-09 | 4.8695e-09 | 1.656e-09 | 2.7157e-09 | 1.0258e-09 | -1.656e-09 | -2.7157e-09 | -1.0258e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.81822 | 0.75969 | 0.73707 | 0.81822 | 0.75969 | 0.73707 | -5.7581 | -130.2127 | 116.0437 | -5.7581 | -130.2127 | 116.0437
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.4862e-09 | -2.6982e-09 | -2.9213e-09 | 2.4862e-09 | 2.6982e-09 | 2.9213e-09 | 9.933e-10 | 1.6298e-09 | 6.1534e-10 | -9.933e-10 | -1.6298e-09 | -6.1534e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.81822 | 0.75969 | 0.73707 | 0.81822 | 0.75969 | 0.73707 | -5.7581 | -130.2127 | 116.0437 | -5.7581 | -130.2127 | 116.0437
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.2813e-10 | -8.9937e-10 | -9.7439e-10 | 8.2813e-10 | 8.9937e-10 | 9.7439e-10 | 3.3155e-10 | 5.4257e-10 | 2.0536e-10 | -3.3155e-10 | -5.4257e-10 | -2.0536e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.81822 | 0.75969 | 0.73707 | 0.81822 | 0.75969 | 0.73707 | -5.7581 | -130.2127 | 116.0437 | -5.7581 | -130.2127 | 116.0437
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.6575e-09 | -1.7988e-09 | -1.9475e-09 | 1.6575e-09 | 1.7988e-09 | 1.9475e-09 | 6.622e-10 | 1.0865e-09 | 4.1023e-10 | -6.622e-10 | -1.0865e-09 | -4.1023e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.81822 | 0.75969 | 0.73707 | 0.81822 | 0.75969 | 0.73707 | -5.7581 | -130.2127 | 116.0437 | -5.7581 | -130.2127 | 116.0437
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.2873e-10 | -8.994e-10 | -9.7377e-10 | 8.2873e-10 | 8.994e-10 | 9.7377e-10 | 3.311e-10 | 5.4327e-10 | 2.0511e-10 | -3.311e-10 | -5.4327e-10 | -2.0511e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.81822 | 0.75969 | 0.73707 | 0.81822 | 0.75969 | 0.73707 | -5.7581 | -130.2127 | 116.0437 | -5.7581 | -130.2127 | 116.0437
Line16_4_18 | 0 | 5.4066 | 5.2369 | 0 | 5.4066 | 5.2369 | 0 | 1.2486 | 1.2094 | 0 | 1.2486 | 1.2094 | -1.3707e-09 | 0.14018 | 0.30737 | 1.0281e-09 | 3.5812e-13 | 8.7385e-14 | -2.8952e-09 | 0.50815 | 0.38694 | -1.6555e-10 | -1.6361e-13 | -3.3212e-13 | 0 | 147.556 | 72.6593 | 0 | -32.444 | -107.3407 |  | 0.54548 | 0.42218 | 0.4086 | 0.40911 | 0 | 0 | -5.7581 | -137.8658 | 124.1971 | -5.7581 | 0 | 0
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.2722e-10 | -8.9933e-10 | -9.7534e-10 | 8.2722e-10 | 8.9933e-10 | 9.7534e-10 | 3.3222e-10 | 5.4153e-10 | 2.0573e-10 | -3.3222e-10 | -5.4153e-10 | -2.0573e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.81822 | 0.75969 | 0.73707 | 0.81822 | 0.75969 | 0.73707 | -5.7581 | -130.2127 | 116.0437 | -5.7581 | -130.2127 | 116.0437
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.6292e-09 | -7.1952e-09 | -7.7908e-09 | 6.6292e-09 | 7.1952e-09 | 7.7908e-09 | 2.6493e-09 | 4.3455e-09 | 1.6411e-09 | -2.6493e-09 | -4.3455e-09 | -1.6411e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.81822 | 0.75969 | 0.73707 | 0.81822 | 0.75969 | 0.73707 | -5.7581 | -130.2127 | 116.0437 | -5.7581 | -130.2127 | 116.0437
Line2_1_4 | 2.8168 | 3.5721 | 3.4869 | 2.8168 | 3.5721 | 3.4869 | 0.65052 | 0.82494 | 0.80526 | 0.65052 | 0.82494 | 0.80526 | 0.23804 | 0.36766 | 0.17038 | -0.15869 | -0.24006 | -0.048794 | 0.47608 | 0.50752 | 0.56855 | -0.31738 | -0.25232 | -0.32539 | -69.1931 | 175.7077 | 42.7255 | 110.8069 | -4.2923 | -137.2745 |  | 0.81822 | 0.75969 | 0.73707 | 0.54548 | 0.42218 | 0.4086 | -5.7581 | -130.2127 | 116.0437 | -5.7581 | -137.8658 | 124.1971
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.6559e-09 | -1.7987e-09 | -1.9491e-09 | 1.6559e-09 | 1.7987e-09 | 1.9491e-09 | 6.6332e-10 | 1.0848e-09 | 4.1085e-10 | -6.6332e-10 | -1.0848e-09 | -4.1085e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.81822 | 0.75969 | 0.73707 | 0.81822 | 0.75969 | 0.73707 | -5.7581 | -130.2127 | 116.0437 | -5.7581 | -130.2127 | 116.0437
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.1426e-09 | -4.497e-09 | -4.8699e-09 | 4.1426e-09 | 4.497e-09 | 4.8699e-09 | 1.6563e-09 | 2.7152e-09 | 1.026e-09 | -1.6563e-09 | -2.7152e-09 | -1.026e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.81822 | 0.75969 | 0.73707 | 0.81822 | 0.75969 | 0.73707 | -5.7581 | -130.2127 | 116.0437 | -5.7581 | -130.2127 | 116.0437
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.3139e-09 | -3.5976e-09 | -3.8961e-09 | 3.3139e-09 | 3.5976e-09 | 3.8961e-09 | 1.3252e-09 | 2.1719e-09 | 8.2086e-10 | -1.3252e-09 | -2.1719e-09 | -8.2086e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.81822 | 0.75969 | 0.73707 | 0.81822 | 0.75969 | 0.73707 | -5.7581 | -130.2127 | 116.0437 | -5.7581 | -130.2127 | 116.0437
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.4862e-09 | -2.6982e-09 | -2.9213e-09 | 2.4862e-09 | 2.6982e-09 | 2.9213e-09 | 9.933e-10 | 1.6298e-09 | 6.1534e-10 | -9.933e-10 | -1.6298e-09 | -6.1534e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.81822 | 0.75969 | 0.73707 | 0.81822 | 0.75969 | 0.73707 | -5.7581 | -130.2127 | 116.0437 | -5.7581 | -130.2127 | 116.0437
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.2873e-10 | -8.994e-10 | -9.7377e-10 | 8.2873e-10 | 8.994e-10 | 9.7377e-10 | 3.311e-10 | 5.4327e-10 | 2.0511e-10 | -3.311e-10 | -5.4327e-10 | -2.0511e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.81822 | 0.75969 | 0.73707 | 0.81822 | 0.75969 | 0.73707 | -5.7581 | -130.2127 | 116.0437 | -5.7581 | -130.2127 | 116.0437
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.2873e-10 | -8.994e-10 | -9.7377e-10 | 8.2873e-10 | 8.994e-10 | 9.7377e-10 | 3.311e-10 | 5.4327e-10 | 2.0511e-10 | -3.311e-10 | -5.4327e-10 | -2.0511e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.81822 | 0.75969 | 0.73707 | 0.81822 | 0.75969 | 0.73707 | -5.7581 | -130.2127 | 116.0437 | -5.7581 | -130.2127 | 116.0437
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.8005e-09 | -6.2958e-09 | -6.817e-09 | 5.8005e-09 | 6.2958e-09 | 6.817e-09 | 2.3182e-09 | 3.8022e-09 | 1.436e-09 | -2.3182e-09 | -3.8022e-09 | -1.436e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.81822 | 0.75969 | 0.73707 | 0.81822 | 0.75969 | 0.73707 | -5.7581 | -130.2127 | 116.0437 | -5.7581 | -130.2127 | 116.0437

## LLG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.0249e-11 | -3.5755e-11 | -6.5029e-11 | 2.0249e-11 | 3.5755e-11 | 6.5029e-11 | 1.7092e-11 | 5.9929e-11 | 2.4946e-11 | -1.7092e-11 | -5.9929e-11 | -2.4946e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0491 | 1.0484 | 1.0472 | 1.0491 | 1.0484 | 1.0472 | -0.040405 | -120.1418 | 119.9409 | -0.040405 | -120.1418 | 119.9409
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.0252e-11 | -3.5755e-11 | -6.5027e-11 | 2.0252e-11 | 3.5755e-11 | 6.5027e-11 | 1.7091e-11 | 5.9932e-11 | 2.4944e-11 | -1.7091e-11 | -5.9932e-11 | -2.4944e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0491 | 1.0484 | 1.0472 | 1.0491 | 1.0484 | 1.0472 | -0.040405 | -120.1418 | 119.9409 | -0.040405 | -120.1418 | 119.9409
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.6876e-11 | -2.9796e-11 | -5.419e-11 | 1.6876e-11 | 2.9796e-11 | 5.419e-11 | 1.4243e-11 | 4.9942e-11 | 2.0787e-11 | -1.4243e-11 | -4.9942e-11 | -2.0787e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0491 | 1.0484 | 1.0472 | 1.0491 | 1.0484 | 1.0472 | -0.040405 | -120.1418 | 119.9409 | -0.040405 | -120.1418 | 119.9409
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.0128e-11 | -1.7877e-11 | -3.2512e-11 | 1.0128e-11 | 1.7877e-11 | 3.2512e-11 | 8.5451e-12 | 2.9968e-11 | 1.2471e-11 | -8.5451e-12 | -2.9968e-11 | -1.2471e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0491 | 1.0484 | 1.0472 | 1.0491 | 1.0484 | 1.0472 | -0.040405 | -120.1418 | 119.9409 | -0.040405 | -120.1418 | 119.9409
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.3722e-12 | -5.9598e-12 | -1.084e-11 | 3.3722e-12 | 5.9598e-12 | 1.084e-11 | 2.8496e-12 | 9.9854e-12 | 4.1595e-12 | -2.8496e-12 | -9.9854e-12 | -4.1595e-12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0491 | 1.0484 | 1.0472 | 1.0491 | 1.0484 | 1.0472 | -0.040405 | -120.1418 | 119.9409 | -0.040405 | -120.1418 | 119.9409
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.7518e-12 | -1.1918e-11 | -2.1675e-11 | 6.7518e-12 | 1.1918e-11 | 2.1675e-11 | 5.6967e-12 | 1.9979e-11 | 8.3138e-12 | -5.6967e-12 | -1.9979e-11 | -8.3138e-12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0491 | 1.0484 | 1.0472 | 1.0491 | 1.0484 | 1.0472 | -0.040405 | -120.1418 | 119.9409 | -0.040405 | -120.1418 | 119.9409
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.3759e-12 | -5.959e-12 | -1.0837e-11 | 3.3759e-12 | 5.959e-12 | 1.0837e-11 | 2.8484e-12 | 9.9893e-12 | 4.1569e-12 | -2.8484e-12 | -9.9893e-12 | -4.1569e-12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0491 | 1.0484 | 1.0472 | 1.0491 | 1.0484 | 1.0472 | -0.040405 | -120.1418 | 119.9409 | -0.040405 | -120.1418 | 119.9409
Line16_4_18 | 0 | 0.034078 | 0.034007 | 0 | 0.034078 | 0.034007 | 0 | 0.00787 | 0.0078537 | 0 | 0.00787 | 0.0078537 | -1.7041e-11 | 0.0058139 | 0.0057965 | 9.3969e-12 | -0.0058066 | -0.0057825 | -1.8113e-11 | 0.0058295 | 0.005802 | -4.8516e-12 | -0.0058066 | -0.0057825 | 0 | -165.3155 | 74.9156 | 0 | 14.6845 | -105.0844 |  | 1.0481 | 1.0461 | 1.0443 | 1.0476 | 1.0434 | 1.0413 | -0.059408 | -120.2384 | 119.9431 | -0.068924 | -120.3155 | 119.9156
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.3666e-12 | -5.961e-12 | -1.0845e-11 | 3.3666e-12 | 5.961e-12 | 1.0845e-11 | 2.8514e-12 | 9.9797e-12 | 4.1634e-12 | -2.8514e-12 | -9.9797e-12 | -4.1634e-12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0491 | 1.0484 | 1.0472 | 1.0491 | 1.0484 | 1.0472 | -0.040405 | -120.1418 | 119.9409 | -0.040405 | -120.1418 | 119.9409
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.7003e-11 | -4.7673e-11 | -8.6702e-11 | 2.7003e-11 | 4.7673e-11 | 8.6702e-11 | 2.2788e-11 | 7.991e-11 | 3.3258e-11 | -2.2788e-11 | -7.991e-11 | -3.3258e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0491 | 1.0484 | 1.0472 | 1.0491 | 1.0484 | 1.0472 | -0.040405 | -120.1418 | 119.9409 | -0.040405 | -120.1418 | 119.9409
Line2_1_4 | 0.011387 | 0.030006 | 0.02998 | 0.011387 | 0.030006 | 0.02998 | 0.0026298 | 0.0069296 | 0.0069235 | 0.0026298 | 0.0069296 | 0.0069235 | 0.0019489 | 0.0065284 | 0.0031523 | -0.0019476 | -0.0065194 | -0.0031434 | 0.0019528 | 0.0031884 | 0.0065289 | -0.0019502 | -0.0031704 | -0.0065109 | -45.0975 | -146.1725 | 55.7135 | 134.9025 | 33.8275 | -124.2865 |  | 1.0491 | 1.0484 | 1.0472 | 1.0481 | 1.0461 | 1.0443 | -0.040405 | -120.1418 | 119.9409 | -0.059408 | -120.2384 | 119.9431
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.7425e-12 | -1.192e-11 | -2.1682e-11 | 6.7425e-12 | 1.192e-11 | 2.1682e-11 | 5.6998e-12 | 1.9969e-11 | 8.3203e-12 | -5.6998e-12 | -1.9969e-11 | -8.3203e-12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0491 | 1.0484 | 1.0472 | 1.0491 | 1.0484 | 1.0472 | -0.040405 | -120.1418 | 119.9409 | -0.040405 | -120.1418 | 119.9409
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.6873e-11 | -2.9796e-11 | -5.4191e-11 | 1.6873e-11 | 2.9796e-11 | 5.4191e-11 | 1.4244e-11 | 4.994e-11 | 2.0789e-11 | -1.4244e-11 | -4.994e-11 | -2.0789e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0491 | 1.0484 | 1.0472 | 1.0491 | 1.0484 | 1.0472 | -0.040405 | -120.1418 | 119.9409 | -0.040405 | -120.1418 | 119.9409
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.3497e-11 | -2.3837e-11 | -4.3354e-11 | 1.3497e-11 | 2.3837e-11 | 4.3354e-11 | 1.1396e-11 | 3.9951e-11 | 1.6632e-11 | -1.1396e-11 | -3.9951e-11 | -1.6632e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0491 | 1.0484 | 1.0472 | 1.0491 | 1.0484 | 1.0472 | -0.040405 | -120.1418 | 119.9409 | -0.040405 | -120.1418 | 119.9409
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.0128e-11 | -1.7877e-11 | -3.2512e-11 | 1.0128e-11 | 1.7877e-11 | 3.2512e-11 | 8.5451e-12 | 2.9968e-11 | 1.2471e-11 | -8.5451e-12 | -2.9968e-11 | -1.2471e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0491 | 1.0484 | 1.0472 | 1.0491 | 1.0484 | 1.0472 | -0.040405 | -120.1418 | 119.9409 | -0.040405 | -120.1418 | 119.9409
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.3759e-12 | -5.959e-12 | -1.0837e-11 | 3.3759e-12 | 5.959e-12 | 1.0837e-11 | 2.8484e-12 | 9.9893e-12 | 4.1569e-12 | -2.8484e-12 | -9.9893e-12 | -4.1569e-12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0491 | 1.0484 | 1.0472 | 1.0491 | 1.0484 | 1.0472 | -0.040405 | -120.1418 | 119.9409 | -0.040405 | -120.1418 | 119.9409
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.3759e-12 | -5.959e-12 | -1.0837e-11 | 3.3759e-12 | 5.959e-12 | 1.0837e-11 | 2.8484e-12 | 9.9893e-12 | 4.1569e-12 | -2.8484e-12 | -9.9893e-12 | -4.1569e-12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0491 | 1.0484 | 1.0472 | 1.0491 | 1.0484 | 1.0472 | -0.040405 | -120.1418 | 119.9409 | -0.040405 | -120.1418 | 119.9409
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.3628e-11 | -4.1714e-11 | -7.5864e-11 | 2.3628e-11 | 4.1714e-11 | 7.5864e-11 | 1.994e-11 | 6.9921e-11 | 2.9101e-11 | -1.994e-11 | -6.9921e-11 | -2.9101e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0491 | 1.0484 | 1.0472 | 1.0491 | 1.0484 | 1.0472 | -0.040405 | -120.1418 | 119.9409 | -0.040405 | -120.1418 | 119.9409

## LLG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.3272e-11 | -4.1088e-11 | -7.4724e-11 | 2.3272e-11 | 4.1088e-11 | 7.4724e-11 | 1.9644e-11 | 6.887e-11 | 2.8662e-11 | -1.9644e-11 | -6.887e-11 | -2.8662e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.099 | 1.0983 | 1.0969 | 1.099 | 1.0983 | 1.0969 | -0.042313 | -120.1485 | 119.9381 | -0.042313 | -120.1485 | 119.9381
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.3275e-11 | -4.1088e-11 | -7.4722e-11 | 2.3275e-11 | 4.1088e-11 | 7.4722e-11 | 1.9643e-11 | 6.8873e-11 | 2.866e-11 | -1.9643e-11 | -6.8873e-11 | -2.866e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.099 | 1.0983 | 1.0969 | 1.099 | 1.0983 | 1.0969 | -0.042313 | -120.1485 | 119.9381 | -0.042313 | -120.1485 | 119.9381
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.9395e-11 | -3.424e-11 | -6.2269e-11 | 1.9395e-11 | 3.424e-11 | 6.2269e-11 | 1.6369e-11 | 5.7393e-11 | 2.3884e-11 | -1.6369e-11 | -5.7393e-11 | -2.3884e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.099 | 1.0983 | 1.0969 | 1.099 | 1.0983 | 1.0969 | -0.042313 | -120.1485 | 119.9381 | -0.042313 | -120.1485 | 119.9381
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.164e-11 | -2.0543e-11 | -3.7359e-11 | 1.164e-11 | 2.0543e-11 | 3.7359e-11 | 9.8208e-12 | 3.4438e-11 | 1.4329e-11 | -9.8208e-12 | -3.4438e-11 | -1.4329e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.099 | 1.0983 | 1.0969 | 1.099 | 1.0983 | 1.0969 | -0.042313 | -120.1485 | 119.9381 | -0.042313 | -120.1485 | 119.9381
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.8757e-12 | -6.8487e-12 | -1.2456e-11 | 3.8757e-12 | 6.8487e-12 | 1.2456e-11 | 3.2749e-12 | 1.1475e-11 | 4.7791e-12 | -3.2749e-12 | -1.1475e-11 | -4.7791e-12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.099 | 1.0983 | 1.0969 | 1.099 | 1.0983 | 1.0969 | -0.042313 | -120.1485 | 119.9381 | -0.042313 | -120.1485 | 119.9381
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.7597e-12 | -1.3696e-11 | -2.4906e-11 | 7.7597e-12 | 1.3696e-11 | 2.4906e-11 | 6.5472e-12 | 2.2959e-11 | 9.5525e-12 | -6.5472e-12 | -2.2959e-11 | -9.5525e-12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.099 | 1.0983 | 1.0969 | 1.099 | 1.0983 | 1.0969 | -0.042313 | -120.1485 | 119.9381 | -0.042313 | -120.1485 | 119.9381
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.8798e-12 | -6.8478e-12 | -1.2453e-11 | 3.8798e-12 | 6.8478e-12 | 1.2453e-11 | 3.2736e-12 | 1.1479e-11 | 4.7762e-12 | -3.2736e-12 | -1.1479e-11 | -4.7762e-12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.099 | 1.0983 | 1.0969 | 1.099 | 1.0983 | 1.0969 | -0.042313 | -120.1485 | 119.9381 | -0.042313 | -120.1485 | 119.9381
Line16_4_18 | 0 | 0.035698 | 0.035622 | 0 | 0.035698 | 0.035622 | 0 | 0.0082442 | 0.0082266 | 0 | 0.0082442 | 0.0082266 | -1.8875e-11 | 0.0063798 | 0.0063601 | 1.0487e-11 | -0.0063719 | -0.0063448 | -1.973e-11 | 0.006397 | 0.0063662 | -5.4719e-12 | -0.0063719 | -0.0063448 | 0 | -165.3222 | 74.9129 | 0 | 14.6778 | -105.0871 |  | 1.0979 | 1.0959 | 1.0939 | 1.0974 | 1.093 | 1.0907 | -0.061316 | -120.2451 | 119.9404 | -0.070832 | -120.3222 | 119.9129
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.8696e-12 | -6.85e-12 | -1.2461e-11 | 3.8696e-12 | 6.85e-12 | 1.2461e-11 | 3.2769e-12 | 1.1469e-11 | 4.7834e-12 | -3.2769e-12 | -1.1469e-11 | -4.7834e-12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.099 | 1.0983 | 1.0969 | 1.099 | 1.0983 | 1.0969 | -0.042313 | -120.1485 | 119.9381 | -0.042313 | -120.1485 | 119.9381
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.1035e-11 | -5.4783e-11 | -9.9628e-11 | 3.1035e-11 | 5.4783e-11 | 9.9628e-11 | 2.619e-11 | 9.1832e-11 | 3.8213e-11 | -2.619e-11 | -9.1832e-11 | -3.8213e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.099 | 1.0983 | 1.0969 | 1.099 | 1.0983 | 1.0969 | -0.042313 | -120.1485 | 119.9381 | -0.042313 | -120.1485 | 119.9381
Line2_1_4 | 0.011929 | 0.031432 | 0.031403 | 0.011929 | 0.031432 | 0.031403 | 0.0027549 | 0.0072589 | 0.0072522 | 0.0027549 | 0.0072589 | 0.0072522 | 0.0021388 | 0.0071637 | 0.0034586 | -0.0021374 | -0.0071538 | -0.0034487 | 0.0021431 | 0.0034987 | 0.0071638 | -0.0021402 | -0.0034789 | -0.0071441 | -45.0994 | -146.1788 | 55.7088 | 134.9006 | 33.8212 | -124.2912 |  | 1.099 | 1.0983 | 1.0969 | 1.0979 | 1.0959 | 1.0939 | -0.042313 | -120.1485 | 119.9381 | -0.061316 | -120.2451 | 119.9404
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.7495e-12 | -1.3698e-11 | -2.4914e-11 | 7.7495e-12 | 1.3698e-11 | 2.4914e-11 | 6.5506e-12 | 2.2948e-11 | 9.5596e-12 | -6.5506e-12 | -2.2948e-11 | -9.5596e-12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.099 | 1.0983 | 1.0969 | 1.099 | 1.0983 | 1.0969 | -0.042313 | -120.1485 | 119.9381 | -0.042313 | -120.1485 | 119.9381
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.9392e-11 | -3.4241e-11 | -6.2271e-11 | 1.9392e-11 | 3.4241e-11 | 6.2271e-11 | 1.637e-11 | 5.739e-11 | 2.3886e-11 | -1.637e-11 | -5.739e-11 | -2.3886e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.099 | 1.0983 | 1.0969 | 1.099 | 1.0983 | 1.0969 | -0.042313 | -120.1485 | 119.9381 | -0.042313 | -120.1485 | 119.9381
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.5513e-11 | -2.7393e-11 | -4.9818e-11 | 1.5513e-11 | 2.7393e-11 | 4.9818e-11 | 1.3097e-11 | 4.5911e-11 | 1.911e-11 | -1.3097e-11 | -4.5911e-11 | -1.911e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.099 | 1.0983 | 1.0969 | 1.099 | 1.0983 | 1.0969 | -0.042313 | -120.1485 | 119.9381 | -0.042313 | -120.1485 | 119.9381
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.164e-11 | -2.0543e-11 | -3.7359e-11 | 1.164e-11 | 2.0543e-11 | 3.7359e-11 | 9.8208e-12 | 3.4438e-11 | 1.4329e-11 | -9.8208e-12 | -3.4438e-11 | -1.4329e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.099 | 1.0983 | 1.0969 | 1.099 | 1.0983 | 1.0969 | -0.042313 | -120.1485 | 119.9381 | -0.042313 | -120.1485 | 119.9381
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.8798e-12 | -6.8478e-12 | -1.2453e-11 | 3.8798e-12 | 6.8478e-12 | 1.2453e-11 | 3.2736e-12 | 1.1479e-11 | 4.7762e-12 | -3.2736e-12 | -1.1479e-11 | -4.7762e-12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.099 | 1.0983 | 1.0969 | 1.099 | 1.0983 | 1.0969 | -0.042313 | -120.1485 | 119.9381 | -0.042313 | -120.1485 | 119.9381
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.8798e-12 | -6.8478e-12 | -1.2453e-11 | 3.8798e-12 | 6.8478e-12 | 1.2453e-11 | 3.2736e-12 | 1.1479e-11 | 4.7762e-12 | -3.2736e-12 | -1.1479e-11 | -4.7762e-12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.099 | 1.0983 | 1.0969 | 1.099 | 1.0983 | 1.0969 | -0.042313 | -120.1485 | 119.9381 | -0.042313 | -120.1485 | 119.9381
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.7155e-11 | -4.7936e-11 | -8.7175e-11 | 2.7155e-11 | 4.7936e-11 | 8.7175e-11 | 2.2917e-11 | 8.0352e-11 | 3.3437e-11 | -2.2917e-11 | -8.0352e-11 | -3.3437e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.099 | 1.0983 | 1.0969 | 1.099 | 1.0983 | 1.0969 | -0.042313 | -120.1485 | 119.9381 | -0.042313 | -120.1485 | 119.9381

## LLG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.9192e-09 | -3.1227e-09 | -3.7412e-09 | 2.9192e-09 | 3.1227e-09 | 3.7412e-09 | 2.3682e-09 | 3.4807e-09 | 2.0854e-09 | -2.3682e-09 | -3.4807e-09 | -2.0854e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.76637 | 0.73079 | 0.69581 | 0.76637 | 0.73079 | 0.69581 | -8.5024 | -133.1753 | 111.7574 | -8.5024 | -133.1753 | 111.7574
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.9195e-09 | -3.1225e-09 | -3.741e-09 | 2.9195e-09 | 3.1225e-09 | 3.741e-09 | 2.3682e-09 | 3.481e-09 | 2.0852e-09 | -2.3682e-09 | -3.481e-09 | -2.0852e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.76637 | 0.73079 | 0.69581 | 0.76637 | 0.73079 | 0.69581 | -8.5024 | -133.1753 | 111.7574 | -8.5024 | -133.1753 | 111.7574
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.4329e-09 | -2.6021e-09 | -3.1176e-09 | 2.4329e-09 | 2.6021e-09 | 3.1176e-09 | 1.9735e-09 | 2.9007e-09 | 1.7377e-09 | -1.9735e-09 | -2.9007e-09 | -1.7377e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.76637 | 0.73079 | 0.69581 | 0.76637 | 0.73079 | 0.69581 | -8.5024 | -133.1753 | 111.7574 | -8.5024 | -133.1753 | 111.7574
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.46e-09 | -1.5612e-09 | -1.8704e-09 | 1.46e-09 | 1.5612e-09 | 1.8704e-09 | 1.1841e-09 | 1.7407e-09 | 1.0424e-09 | -1.1841e-09 | -1.7407e-09 | -1.0424e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.76637 | 0.73079 | 0.69581 | 0.76637 | 0.73079 | 0.69581 | -8.5024 | -133.1753 | 111.7574 | -8.5024 | -133.1753 | 111.7574
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.8623e-10 | -5.2061e-10 | -6.2368e-10 | 4.8623e-10 | 5.2061e-10 | 6.2368e-10 | 3.9471e-10 | 5.7987e-10 | 3.4781e-10 | -3.9471e-10 | -5.7987e-10 | -3.4781e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.76637 | 0.73079 | 0.69581 | 0.76637 | 0.73079 | 0.69581 | -8.5024 | -133.1753 | 111.7574 | -8.5024 | -133.1753 | 111.7574
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -9.7332e-10 | -1.0408e-09 | -1.2469e-09 | 9.7332e-10 | 1.0408e-09 | 1.2469e-09 | 7.8938e-10 | 1.1604e-09 | 6.9496e-10 | -7.8938e-10 | -1.1604e-09 | -6.9496e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.76637 | 0.73079 | 0.69581 | 0.76637 | 0.73079 | 0.69581 | -8.5024 | -133.1753 | 111.7574 | -8.5024 | -133.1753 | 111.7574
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.8666e-10 | -5.2039e-10 | -6.2347e-10 | 4.8666e-10 | 5.2039e-10 | 6.2347e-10 | 3.9469e-10 | 5.8022e-10 | 3.4748e-10 | -3.9469e-10 | -5.8022e-10 | -3.4748e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.76637 | 0.73079 | 0.69581 | 0.76637 | 0.73079 | 0.69581 | -8.5024 | -133.1753 | 111.7574 | -8.5024 | -133.1753 | 111.7574
Line16_4_18 | 0 | 4.1639 | 3.9506 | 0 | 4.1639 | 3.9506 | 0 | 0.96161 | 0.91234 | 0 | 0.96161 | 0.91234 | -1.0423e-09 | 0.21165 | 0.29048 | 7.8171e-10 | -1.4354e-13 | -9.8821e-14 | -2.4704e-09 | 0.32709 | 0.19597 | -1.9735e-10 | 4.8844e-14 | 1.547e-13 | 0 | 162.2816 | 86.0106 | 0 | -17.7184 | -93.9894 |  | 0.51092 | 0.40514 | 0.38407 | 0.38319 | 0 | 0 | -8.5024 | -140.6241 | 120.0151 | -8.5024 | 0 | 0
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.8559e-10 | -5.2094e-10 | -6.2399e-10 | 4.8559e-10 | 5.2094e-10 | 6.2399e-10 | 3.9473e-10 | 5.7935e-10 | 3.483e-10 | -3.9473e-10 | -5.7935e-10 | -3.483e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.76637 | 0.73079 | 0.69581 | 0.76637 | 0.73079 | 0.69581 | -8.5024 | -133.1753 | 111.7574 | -8.5024 | -133.1753 | 111.7574
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.8928e-09 | -4.1633e-09 | -4.988e-09 | 3.8928e-09 | 4.1633e-09 | 4.988e-09 | 3.1576e-09 | 4.6414e-09 | 2.7802e-09 | -3.1576e-09 | -4.6414e-09 | -2.7802e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.76637 | 0.73079 | 0.69581 | 0.76637 | 0.73079 | 0.69581 | -8.5024 | -133.1753 | 111.7574 | -8.5024 | -133.1753 | 111.7574
Line2_1_4 | 2.1279 | 2.7757 | 2.6698 | 2.1279 | 2.7757 | 2.6698 | 0.49142 | 0.64103 | 0.61656 | 0.49142 | 0.64103 | 0.61656 | 0.26082 | 0.37363 | 0.2394 | -0.17388 | -0.2257 | -0.10255 | 0.27169 | 0.28258 | 0.356 | -0.18112 | -0.12848 | -0.21344 | -54.6715 | -170.2757 | 55.6776 | 125.3285 | 9.7243 | -124.3224 |  | 0.76637 | 0.73079 | 0.69581 | 0.51092 | 0.40514 | 0.38407 | -8.5024 | -133.1753 | 111.7574 | -8.5024 | -140.6241 | 120.0151
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -9.7224e-10 | -1.0413e-09 | -1.2475e-09 | 9.7224e-10 | 1.0413e-09 | 1.2475e-09 | 7.8942e-10 | 1.1596e-09 | 6.9579e-10 | -7.8942e-10 | -1.1596e-09 | -6.9579e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.76637 | 0.73079 | 0.69581 | 0.76637 | 0.73079 | 0.69581 | -8.5024 | -133.1753 | 111.7574 | -8.5024 | -133.1753 | 111.7574
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.4326e-09 | -2.6023e-09 | -3.1177e-09 | 2.4326e-09 | 2.6023e-09 | 3.1177e-09 | 1.9735e-09 | 2.9005e-09 | 1.738e-09 | -1.9735e-09 | -2.9005e-09 | -1.738e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.76637 | 0.73079 | 0.69581 | 0.76637 | 0.73079 | 0.69581 | -8.5024 | -133.1753 | 111.7574 | -8.5024 | -133.1753 | 111.7574
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.9459e-09 | -2.0819e-09 | -2.4942e-09 | 1.9459e-09 | 2.0819e-09 | 2.4942e-09 | 1.5788e-09 | 2.3203e-09 | 1.3905e-09 | -1.5788e-09 | -2.3203e-09 | -1.3905e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.76637 | 0.73079 | 0.69581 | 0.76637 | 0.73079 | 0.69581 | -8.5024 | -133.1753 | 111.7574 | -8.5024 | -133.1753 | 111.7574
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.46e-09 | -1.5612e-09 | -1.8704e-09 | 1.46e-09 | 1.5612e-09 | 1.8704e-09 | 1.1841e-09 | 1.7407e-09 | 1.0424e-09 | -1.1841e-09 | -1.7407e-09 | -1.0424e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.76637 | 0.73079 | 0.69581 | 0.76637 | 0.73079 | 0.69581 | -8.5024 | -133.1753 | 111.7574 | -8.5024 | -133.1753 | 111.7574
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.8666e-10 | -5.2039e-10 | -6.2347e-10 | 4.8666e-10 | 5.2039e-10 | 6.2347e-10 | 3.9469e-10 | 5.8022e-10 | 3.4748e-10 | -3.9469e-10 | -5.8022e-10 | -3.4748e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.76637 | 0.73079 | 0.69581 | 0.76637 | 0.73079 | 0.69581 | -8.5024 | -133.1753 | 111.7574 | -8.5024 | -133.1753 | 111.7574
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.8666e-10 | -5.2039e-10 | -6.2347e-10 | 4.8666e-10 | 5.2039e-10 | 6.2347e-10 | 3.9469e-10 | 5.8022e-10 | 3.4748e-10 | -3.9469e-10 | -5.8022e-10 | -3.4748e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.76637 | 0.73079 | 0.69581 | 0.76637 | 0.73079 | 0.69581 | -8.5024 | -133.1753 | 111.7574 | -8.5024 | -133.1753 | 111.7574
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.4062e-09 | -3.6429e-09 | -4.3645e-09 | 3.4062e-09 | 3.6429e-09 | 4.3645e-09 | 2.7629e-09 | 4.0612e-09 | 2.4327e-09 | -2.7629e-09 | -4.0612e-09 | -2.4327e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.76637 | 0.73079 | 0.69581 | 0.76637 | 0.73079 | 0.69581 | -8.5024 | -133.1753 | 111.7574 | -8.5024 | -133.1753 | 111.7574

## LLG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.62e-09 | -2.8026e-09 | -3.3577e-09 | 2.62e-09 | 2.8026e-09 | 3.3577e-09 | 2.1255e-09 | 3.124e-09 | 1.8717e-09 | -2.1255e-09 | -3.124e-09 | -1.8717e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.72604 | 0.69232 | 0.65919 | 0.72604 | 0.69232 | 0.65919 | -8.5024 | -133.1753 | 111.7574 | -8.5024 | -133.1753 | 111.7574
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.6203e-09 | -2.8025e-09 | -3.3576e-09 | 2.6203e-09 | 2.8025e-09 | 3.3576e-09 | 2.1254e-09 | 3.1242e-09 | 1.8715e-09 | -2.1254e-09 | -3.1242e-09 | -1.8715e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.72604 | 0.69232 | 0.65919 | 0.72604 | 0.69232 | 0.65919 | -8.5024 | -133.1753 | 111.7574 | -8.5024 | -133.1753 | 111.7574
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.1835e-09 | -2.3354e-09 | -2.798e-09 | 2.1835e-09 | 2.3354e-09 | 2.798e-09 | 1.7712e-09 | 2.6034e-09 | 1.5596e-09 | -1.7712e-09 | -2.6034e-09 | -1.5596e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.72604 | 0.69232 | 0.65919 | 0.72604 | 0.69232 | 0.65919 | -8.5024 | -133.1753 | 111.7574 | -8.5024 | -133.1753 | 111.7574
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.3103e-09 | -1.4011e-09 | -1.6787e-09 | 1.3103e-09 | 1.4011e-09 | 1.6787e-09 | 1.0627e-09 | 1.5622e-09 | 9.356e-10 | -1.0627e-09 | -1.5622e-09 | -9.356e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.72604 | 0.69232 | 0.65919 | 0.72604 | 0.69232 | 0.65919 | -8.5024 | -133.1753 | 111.7574 | -8.5024 | -133.1753 | 111.7574
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.3639e-10 | -4.6725e-10 | -5.5976e-10 | 4.3639e-10 | 4.6725e-10 | 5.5976e-10 | 3.5425e-10 | 5.2044e-10 | 3.1216e-10 | -3.5425e-10 | -5.2044e-10 | -3.1216e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.72604 | 0.69232 | 0.65919 | 0.72604 | 0.69232 | 0.65919 | -8.5024 | -133.1753 | 111.7574 | -8.5024 | -133.1753 | 111.7574
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.7356e-10 | -9.341e-10 | -1.1191e-09 | 8.7356e-10 | 9.341e-10 | 1.1191e-09 | 7.0848e-10 | 1.0415e-09 | 6.2373e-10 | -7.0848e-10 | -1.0415e-09 | -6.2373e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.72604 | 0.69232 | 0.65919 | 0.72604 | 0.69232 | 0.65919 | -8.5024 | -133.1753 | 111.7574 | -8.5024 | -133.1753 | 111.7574
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.3678e-10 | -4.6705e-10 | -5.5957e-10 | 4.3678e-10 | 4.6705e-10 | 5.5957e-10 | 3.5424e-10 | 5.2075e-10 | 3.1187e-10 | -3.5424e-10 | -5.2075e-10 | -3.1187e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.72604 | 0.69232 | 0.65919 | 0.72604 | 0.69232 | 0.65919 | -8.5024 | -133.1753 | 111.7574 | -8.5024 | -133.1753 | 111.7574
Line16_4_18 | 0 | 3.9447 | 3.7426 | 0 | 3.9447 | 3.7426 | 0 | 0.911 | 0.86432 | 0 | 0.911 | 0.86432 | -9.3546e-10 | 0.18996 | 0.26071 | 7.0159e-10 | -1.2903e-13 | -8.856e-14 | -2.2172e-09 | 0.29356 | 0.17588 | -1.7712e-10 | 4.3931e-14 | 1.3883e-13 | 0 | 162.2816 | 86.0106 | 0 | -17.7184 | -93.9894 |  | 0.48403 | 0.38382 | 0.36386 | 0.36302 | 0 | 0 | -8.5024 | -140.6241 | 120.0151 | -8.5024 | 0 | 0
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.3582e-10 | -4.6754e-10 | -5.6004e-10 | 4.3582e-10 | 4.6754e-10 | 5.6004e-10 | 3.5427e-10 | 5.1997e-10 | 3.1261e-10 | -3.5428e-10 | -5.1997e-10 | -3.1261e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.72604 | 0.69232 | 0.65919 | 0.72604 | 0.69232 | 0.65919 | -8.5024 | -133.1753 | 111.7574 | -8.5024 | -133.1753 | 111.7574
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.4938e-09 | -3.7366e-09 | -4.4767e-09 | 3.4938e-09 | 3.7366e-09 | 4.4767e-09 | 2.8339e-09 | 4.1657e-09 | 2.4952e-09 | -2.8339e-09 | -4.1657e-09 | -2.4952e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.72604 | 0.69232 | 0.65919 | 0.72604 | 0.69232 | 0.65919 | -8.5024 | -133.1753 | 111.7574 | -8.5024 | -133.1753 | 111.7574
Line2_1_4 | 2.0159 | 2.6296 | 2.5293 | 2.0159 | 2.6296 | 2.5293 | 0.46556 | 0.60729 | 0.58411 | 0.46556 | 0.60729 | 0.58411 | 0.23409 | 0.33534 | 0.21487 | -0.15606 | -0.20257 | -0.092041 | 0.24384 | 0.25362 | 0.31951 | -0.16256 | -0.11532 | -0.19157 | -54.6715 | -170.2757 | 55.6776 | 125.3285 | 9.7243 | -124.3224 |  | 0.72604 | 0.69232 | 0.65919 | 0.48403 | 0.38382 | 0.36386 | -8.5024 | -133.1753 | 111.7574 | -8.5024 | -140.6241 | 120.0151
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.7259e-10 | -9.3459e-10 | -1.1196e-09 | 8.7259e-10 | 9.3459e-10 | 1.1196e-09 | 7.0851e-10 | 1.0407e-09 | 6.2447e-10 | -7.0851e-10 | -1.0407e-09 | -6.2447e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.72604 | 0.69232 | 0.65919 | 0.72604 | 0.69232 | 0.65919 | -8.5024 | -133.1753 | 111.7574 | -8.5024 | -133.1753 | 111.7574
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.1833e-09 | -2.3356e-09 | -2.7982e-09 | 2.1833e-09 | 2.3356e-09 | 2.7982e-09 | 1.7712e-09 | 2.6032e-09 | 1.5598e-09 | -1.7712e-09 | -2.6032e-09 | -1.5598e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.72604 | 0.69232 | 0.65919 | 0.72604 | 0.69232 | 0.65919 | -8.5024 | -133.1753 | 111.7574 | -8.5024 | -133.1753 | 111.7574
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.7465e-09 | -1.8685e-09 | -2.2386e-09 | 1.7465e-09 | 1.8685e-09 | 2.2386e-09 | 1.417e-09 | 2.0825e-09 | 1.248e-09 | -1.417e-09 | -2.0825e-09 | -1.248e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.72604 | 0.69232 | 0.65919 | 0.72604 | 0.69232 | 0.65919 | -8.5024 | -133.1753 | 111.7574 | -8.5024 | -133.1753 | 111.7574
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.3103e-09 | -1.4011e-09 | -1.6787e-09 | 1.3103e-09 | 1.4011e-09 | 1.6787e-09 | 1.0627e-09 | 1.5622e-09 | 9.356e-10 | -1.0627e-09 | -1.5622e-09 | -9.356e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.72604 | 0.69232 | 0.65919 | 0.72604 | 0.69232 | 0.65919 | -8.5024 | -133.1753 | 111.7574 | -8.5024 | -133.1753 | 111.7574
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.3678e-10 | -4.6705e-10 | -5.5957e-10 | 4.3678e-10 | 4.6705e-10 | 5.5957e-10 | 3.5424e-10 | 5.2075e-10 | 3.1187e-10 | -3.5424e-10 | -5.2075e-10 | -3.1187e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.72604 | 0.69232 | 0.65919 | 0.72604 | 0.69232 | 0.65919 | -8.5024 | -133.1753 | 111.7574 | -8.5024 | -133.1753 | 111.7574
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.3678e-10 | -4.6705e-10 | -5.5957e-10 | 4.3678e-10 | 4.6705e-10 | 5.5957e-10 | 3.5424e-10 | 5.2075e-10 | 3.1187e-10 | -3.5424e-10 | -5.2075e-10 | -3.1187e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.72604 | 0.69232 | 0.65919 | 0.72604 | 0.69232 | 0.65919 | -8.5024 | -133.1753 | 111.7574 | -8.5024 | -133.1753 | 111.7574
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.0571e-09 | -3.2695e-09 | -3.9172e-09 | 3.0571e-09 | 3.2695e-09 | 3.9172e-09 | 2.4797e-09 | 3.6449e-09 | 2.1834e-09 | -2.4797e-09 | -3.6449e-09 | -2.1834e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.72604 | 0.69232 | 0.65919 | 0.72604 | 0.69232 | 0.65919 | -8.5024 | -133.1753 | 111.7574 | -8.5024 | -133.1753 | 111.7574

## LLG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.7197e-11 | -3.0272e-11 | -5.5176e-11 | 1.7197e-11 | 3.0272e-11 | 5.5176e-11 | 1.454e-11 | 5.0925e-11 | 2.1289e-11 | -1.454e-11 | -5.0925e-11 | -2.1289e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.94918 | 0.94855 | 0.94735 | 0.94918 | 0.94855 | 0.94735 | -0.041994 | -120.1472 | 119.9384 | -0.041994 | -120.1472 | 119.9384
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.7198e-11 | -3.0271e-11 | -5.5175e-11 | 1.7198e-11 | 3.0271e-11 | 5.5175e-11 | 1.454e-11 | 5.0927e-11 | 2.1287e-11 | -1.454e-11 | -5.0927e-11 | -2.1287e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.94918 | 0.94855 | 0.94735 | 0.94918 | 0.94855 | 0.94735 | -0.041994 | -120.1472 | 119.9384 | -0.041994 | -120.1472 | 119.9384
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.4332e-11 | -2.5226e-11 | -4.598e-11 | 1.4332e-11 | 2.5226e-11 | 4.598e-11 | 1.2117e-11 | 4.2439e-11 | 1.774e-11 | -1.2117e-11 | -4.2439e-11 | -1.774e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.94918 | 0.94855 | 0.94735 | 0.94918 | 0.94855 | 0.94735 | -0.041994 | -120.1472 | 119.9384 | -0.041994 | -120.1472 | 119.9384
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.6005e-12 | -1.5135e-11 | -2.7587e-11 | 8.6005e-12 | 1.5135e-11 | 2.7587e-11 | 7.2699e-12 | 2.5465e-11 | 1.0643e-11 | -7.2699e-12 | -2.5465e-11 | -1.0643e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.94918 | 0.94855 | 0.94735 | 0.94918 | 0.94855 | 0.94735 | -0.041994 | -120.1472 | 119.9384 | -0.041994 | -120.1472 | 119.9384
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.8643e-12 | -5.0462e-12 | -9.197e-12 | 2.8643e-12 | 5.0462e-12 | 9.197e-12 | 2.4234e-12 | 8.486e-12 | 3.5498e-12 | -2.4234e-12 | -8.486e-12 | -3.5498e-12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.94918 | 0.94855 | 0.94735 | 0.94918 | 0.94855 | 0.94735 | -0.041994 | -120.1472 | 119.9384 | -0.041994 | -120.1472 | 119.9384
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.7337e-12 | -1.009e-11 | -1.8391e-11 | 5.7337e-12 | 1.009e-11 | 1.8391e-11 | 4.8466e-12 | 1.6976e-11 | 7.0951e-12 | -4.8466e-12 | -1.6976e-11 | -7.0951e-12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.94918 | 0.94855 | 0.94735 | 0.94918 | 0.94855 | 0.94735 | -0.041994 | -120.1472 | 119.9384 | -0.041994 | -120.1472 | 119.9384
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.8668e-12 | -5.045e-12 | -9.1956e-12 | 2.8668e-12 | 5.045e-12 | 9.1956e-12 | 2.4233e-12 | 8.4882e-12 | 3.5475e-12 | -2.4233e-12 | -8.4882e-12 | -3.5475e-12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.94918 | 0.94855 | 0.94735 | 0.94918 | 0.94855 | 0.94735 | -0.041994 | -120.1472 | 119.9384 | -0.041994 | -120.1472 | 119.9384
Line16_4_18 | 0 | 0.03077 | 0.030729 | 0 | 0.03077 | 0.030729 | 0 | 0.0071059 | 0.0070965 | 0 | 0.0071059 | 0.0070965 | -9.8034e-12 | 0.0047478 | 0.0047406 | 9.298e-12 | -0.0047338 | -0.0047213 | -2.1976e-11 | 0.0047538 | 0.0047359 | -2.5498e-12 | -0.0047338 | -0.0047213 | 0 | -165.2519 | 75.0274 | 0 | 14.7481 | -104.9726 |  | 0.94794 | 0.9455 | 0.94426 | 0.94732 | 0.94212 | 0.94087 | -0.043512 | -120.2154 | 119.9992 | -0.044273 | -120.2519 | 120.0274
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.8604e-12 | -5.0481e-12 | -9.1989e-12 | 2.8604e-12 | 5.0481e-12 | 9.1989e-12 | 2.4234e-12 | 8.4826e-12 | 3.5531e-12 | -2.4234e-12 | -8.4826e-12 | -3.5531e-12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.94918 | 0.94855 | 0.94735 | 0.94918 | 0.94855 | 0.94735 | -0.041994 | -120.1472 | 119.9384 | -0.041994 | -120.1472 | 119.9384
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.2932e-11 | -4.0361e-11 | -7.3566e-11 | 2.2932e-11 | 4.0361e-11 | 7.3566e-11 | 1.9387e-11 | 6.7903e-11 | 2.8383e-11 | -1.9387e-11 | -6.7903e-11 | -2.8383e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.94918 | 0.94855 | 0.94735 | 0.94918 | 0.94855 | 0.94735 | -0.041994 | -120.1472 | 119.9384 | -0.041994 | -120.1472 | 119.9384
Line2_1_4 | 0.010293 | 0.027093 | 0.027078 | 0.010293 | 0.027093 | 0.027078 | 0.0023771 | 0.0062569 | 0.0062533 | 0.0023771 | 0.0062569 | 0.0062533 | 0.0015953 | 0.0053372 | 0.0025861 | -0.0015932 | -0.0053231 | -0.0025721 | 0.0015955 | 0.0025959 | 0.0053298 | -0.0015934 | -0.0025812 | -0.0053151 | -45.0466 | -146.0845 | 55.8221 | 134.9534 | 33.9155 | -124.1779 |  | 0.94918 | 0.94855 | 0.94735 | 0.94794 | 0.9455 | 0.94426 | -0.041994 | -120.1472 | 119.9384 | -0.043512 | -120.2154 | 119.9992
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.7272e-12 | -1.0093e-11 | -1.8395e-11 | 5.7272e-12 | 1.0093e-11 | 1.8395e-11 | 4.8467e-12 | 1.6971e-11 | 7.1006e-12 | -4.8467e-12 | -1.6971e-11 | -7.1006e-12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.94918 | 0.94855 | 0.94735 | 0.94918 | 0.94855 | 0.94735 | -0.041994 | -120.1472 | 119.9384 | -0.041994 | -120.1472 | 119.9384
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.433e-11 | -2.5227e-11 | -4.598e-11 | 1.433e-11 | 2.5227e-11 | 4.598e-11 | 1.2117e-11 | 4.2437e-11 | 1.7741e-11 | -1.2117e-11 | -4.2437e-11 | -1.7741e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.94918 | 0.94855 | 0.94735 | 0.94918 | 0.94855 | 0.94735 | -0.041994 | -120.1472 | 119.9384 | -0.041994 | -120.1472 | 119.9384
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.1463e-11 | -2.0182e-11 | -3.6785e-11 | 1.1463e-11 | 2.0182e-11 | 3.6785e-11 | 9.6933e-12 | 3.3949e-11 | 1.4194e-11 | -9.6933e-12 | -3.3949e-11 | -1.4194e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.94918 | 0.94855 | 0.94735 | 0.94918 | 0.94855 | 0.94735 | -0.041994 | -120.1472 | 119.9384 | -0.041994 | -120.1472 | 119.9384
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.6005e-12 | -1.5135e-11 | -2.7587e-11 | 8.6005e-12 | 1.5135e-11 | 2.7587e-11 | 7.2699e-12 | 2.5465e-11 | 1.0643e-11 | -7.2699e-12 | -2.5465e-11 | -1.0643e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.94918 | 0.94855 | 0.94735 | 0.94918 | 0.94855 | 0.94735 | -0.041994 | -120.1472 | 119.9384 | -0.041994 | -120.1472 | 119.9384
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.8668e-12 | -5.045e-12 | -9.1956e-12 | 2.8668e-12 | 5.045e-12 | 9.1956e-12 | 2.4233e-12 | 8.4882e-12 | 3.5475e-12 | -2.4233e-12 | -8.4882e-12 | -3.5475e-12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.94918 | 0.94855 | 0.94735 | 0.94918 | 0.94855 | 0.94735 | -0.041994 | -120.1472 | 119.9384 | -0.041994 | -120.1472 | 119.9384
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.8668e-12 | -5.045e-12 | -9.1956e-12 | 2.8668e-12 | 5.045e-12 | 9.1956e-12 | 2.4233e-12 | 8.4882e-12 | 3.5475e-12 | -2.4233e-12 | -8.4882e-12 | -3.5475e-12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.94918 | 0.94855 | 0.94735 | 0.94918 | 0.94855 | 0.94735 | -0.041994 | -120.1472 | 119.9384 | -0.041994 | -120.1472 | 119.9384
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.0065e-11 | -3.5316e-11 | -6.4371e-11 | 2.0065e-11 | 3.5316e-11 | 6.4371e-11 | 1.6963e-11 | 5.9415e-11 | 2.4835e-11 | -1.6963e-11 | -5.9415e-11 | -2.4835e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.94918 | 0.94855 | 0.94735 | 0.94918 | 0.94855 | 0.94735 | -0.041994 | -120.1472 | 119.9384 | -0.041994 | -120.1472 | 119.9384

## LLG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.5434e-11 | -2.7169e-11 | -4.9521e-11 | 1.5434e-11 | 2.7169e-11 | 4.9521e-11 | 1.305e-11 | 4.5706e-11 | 1.9107e-11 | -1.305e-11 | -4.5706e-11 | -1.9107e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.89922 | 0.89862 | 0.89749 | 0.89922 | 0.89862 | 0.89749 | -0.041994 | -120.1472 | 119.9384 | -0.041994 | -120.1472 | 119.9384
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.5436e-11 | -2.7169e-11 | -4.952e-11 | 1.5436e-11 | 2.7169e-11 | 4.952e-11 | 1.305e-11 | 4.5707e-11 | 1.9106e-11 | -1.305e-11 | -4.5707e-11 | -1.9106e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.89922 | 0.89862 | 0.89749 | 0.89922 | 0.89862 | 0.89749 | -0.041994 | -120.1472 | 119.9384 | -0.041994 | -120.1472 | 119.9384
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.2863e-11 | -2.2641e-11 | -4.1267e-11 | 1.2863e-11 | 2.2641e-11 | 4.1267e-11 | 1.0875e-11 | 3.8089e-11 | 1.5922e-11 | -1.0875e-11 | -3.8089e-11 | -1.5922e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.89922 | 0.89862 | 0.89749 | 0.89922 | 0.89862 | 0.89749 | -0.041994 | -120.1472 | 119.9384 | -0.041994 | -120.1472 | 119.9384
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.719e-12 | -1.3584e-11 | -2.4759e-11 | 7.719e-12 | 1.3584e-11 | 2.4759e-11 | 6.5248e-12 | 2.2855e-11 | 9.5518e-12 | -6.5248e-12 | -2.2855e-11 | -9.5518e-12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.89922 | 0.89862 | 0.89749 | 0.89922 | 0.89862 | 0.89749 | -0.041994 | -120.1472 | 119.9384 | -0.041994 | -120.1472 | 119.9384
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5707e-12 | -4.529e-12 | -8.2543e-12 | 2.5707e-12 | 4.529e-12 | 8.2543e-12 | 2.175e-12 | 7.6162e-12 | 3.1859e-12 | -2.175e-12 | -7.6162e-12 | -3.1859e-12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.89922 | 0.89862 | 0.89749 | 0.89922 | 0.89862 | 0.89749 | -0.041994 | -120.1472 | 119.9384 | -0.041994 | -120.1472 | 119.9384
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.146e-12 | -9.0558e-12 | -1.6506e-11 | 5.146e-12 | 9.0558e-12 | 1.6506e-11 | 4.3499e-12 | 1.5236e-11 | 6.3679e-12 | -4.3499e-12 | -1.5236e-11 | -6.3679e-12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.89922 | 0.89862 | 0.89749 | 0.89922 | 0.89862 | 0.89749 | -0.041994 | -120.1472 | 119.9384 | -0.041994 | -120.1472 | 119.9384
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.573e-12 | -4.5279e-12 | -8.2532e-12 | 2.573e-12 | 4.5279e-12 | 8.2532e-12 | 2.1749e-12 | 7.6182e-12 | 3.1839e-12 | -2.1749e-12 | -7.6182e-12 | -3.1839e-12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.89922 | 0.89862 | 0.89749 | 0.89922 | 0.89862 | 0.89749 | -0.041994 | -120.1472 | 119.9384 | -0.041994 | -120.1472 | 119.9384
Line16_4_18 | 0 | 0.02915 | 0.029111 | 0 | 0.02915 | 0.029111 | 0 | 0.0067319 | 0.006723 | 0 | 0.0067319 | 0.006723 | -8.7986e-12 | 0.0042611 | 0.0042547 | 8.345e-12 | -0.0042487 | -0.0042374 | -1.9724e-11 | 0.0042666 | 0.0042505 | -2.2885e-12 | -0.0042487 | -0.0042374 | 0 | -165.2519 | 75.0274 | 0 | 14.7481 | -104.9726 |  | 0.89805 | 0.89573 | 0.89456 | 0.89746 | 0.89254 | 0.89135 | -0.043512 | -120.2154 | 119.9992 | -0.044273 | -120.2519 | 120.0274
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5672e-12 | -4.5307e-12 | -8.2561e-12 | 2.5672e-12 | 4.5307e-12 | 8.2561e-12 | 2.175e-12 | 7.6132e-12 | 3.1889e-12 | -2.175e-12 | -7.6132e-12 | -3.1889e-12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.89922 | 0.89862 | 0.89749 | 0.89922 | 0.89862 | 0.89749 | -0.041994 | -120.1472 | 119.9384 | -0.041994 | -120.1472 | 119.9384
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.0582e-11 | -3.6224e-11 | -6.6026e-11 | 2.0582e-11 | 3.6224e-11 | 6.6026e-11 | 1.74e-11 | 6.0944e-11 | 2.5474e-11 | -1.74e-11 | -6.0944e-11 | -2.5474e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.89922 | 0.89862 | 0.89749 | 0.89922 | 0.89862 | 0.89749 | -0.041994 | -120.1472 | 119.9384 | -0.041994 | -120.1472 | 119.9384
Line2_1_4 | 0.0097512 | 0.025667 | 0.025653 | 0.0097512 | 0.025667 | 0.025653 | 0.002252 | 0.0059276 | 0.0059242 | 0.002252 | 0.0059276 | 0.0059242 | 0.0014318 | 0.0047901 | 0.0023211 | -0.00143 | -0.0047775 | -0.0023084 | 0.001432 | 0.0023298 | 0.0047835 | -0.0014301 | -0.0023166 | -0.0047704 | -45.0466 | -146.0845 | 55.8221 | 134.9534 | 33.9155 | -124.1779 |  | 0.89922 | 0.89862 | 0.89749 | 0.89805 | 0.89573 | 0.89456 | -0.041994 | -120.1472 | 119.9384 | -0.043512 | -120.2154 | 119.9992
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.1402e-12 | -9.0586e-12 | -1.6509e-11 | 5.1402e-12 | 9.0586e-12 | 1.6509e-11 | 4.35e-12 | 1.5231e-11 | 6.3729e-12 | -4.35e-12 | -1.5231e-11 | -6.3729e-12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.89922 | 0.89862 | 0.89749 | 0.89922 | 0.89862 | 0.89749 | -0.041994 | -120.1472 | 119.9384 | -0.041994 | -120.1472 | 119.9384
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.2861e-11 | -2.2641e-11 | -4.1268e-11 | 1.2861e-11 | 2.2641e-11 | 4.1268e-11 | 1.0875e-11 | 3.8088e-11 | 1.5923e-11 | -1.0875e-11 | -3.8088e-11 | -1.5923e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.89922 | 0.89862 | 0.89749 | 0.89922 | 0.89862 | 0.89749 | -0.041994 | -120.1472 | 119.9384 | -0.041994 | -120.1472 | 119.9384
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.0288e-11 | -1.8114e-11 | -3.3015e-11 | 1.0288e-11 | 1.8114e-11 | 3.3015e-11 | 8.6998e-12 | 3.047e-11 | 1.2739e-11 | -8.6998e-12 | -3.047e-11 | -1.2739e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.89922 | 0.89862 | 0.89749 | 0.89922 | 0.89862 | 0.89749 | -0.041994 | -120.1472 | 119.9384 | -0.041994 | -120.1472 | 119.9384
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.719e-12 | -1.3584e-11 | -2.4759e-11 | 7.719e-12 | 1.3584e-11 | 2.4759e-11 | 6.5248e-12 | 2.2855e-11 | 9.5518e-12 | -6.5248e-12 | -2.2855e-11 | -9.5518e-12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.89922 | 0.89862 | 0.89749 | 0.89922 | 0.89862 | 0.89749 | -0.041994 | -120.1472 | 119.9384 | -0.041994 | -120.1472 | 119.9384
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.573e-12 | -4.5279e-12 | -8.2532e-12 | 2.573e-12 | 4.5279e-12 | 8.2532e-12 | 2.1749e-12 | 7.6182e-12 | 3.1839e-12 | -2.1749e-12 | -7.6182e-12 | -3.1839e-12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.89922 | 0.89862 | 0.89749 | 0.89922 | 0.89862 | 0.89749 | -0.041994 | -120.1472 | 119.9384 | -0.041994 | -120.1472 | 119.9384
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.573e-12 | -4.5279e-12 | -8.2532e-12 | 2.573e-12 | 4.5279e-12 | 8.2532e-12 | 2.1749e-12 | 7.6182e-12 | 3.1839e-12 | -2.1749e-12 | -7.6182e-12 | -3.1839e-12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.89922 | 0.89862 | 0.89749 | 0.89922 | 0.89862 | 0.89749 | -0.041994 | -120.1472 | 119.9384 | -0.041994 | -120.1472 | 119.9384
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.8009e-11 | -3.1696e-11 | -5.7773e-11 | 1.8009e-11 | 3.1696e-11 | 5.7773e-11 | 1.5225e-11 | 5.3326e-11 | 2.229e-11 | -1.5225e-11 | -5.3326e-11 | -2.229e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.89922 | 0.89862 | 0.89749 | 0.89922 | 0.89862 | 0.89749 | -0.041994 | -120.1472 | 119.9384 | -0.041994 | -120.1472 | 119.9384