## LLL_max
name | pf_ikss_ka | pf_skss_mw | pf_rk_ohm | pf_xk_ohm | pf_vm_pu | pf_va_degree
Bus_0 | 5.2486 | 1000.0001 | 1.3244 | 13.2439 | 0 | 84.2894
Bus_1 | 5.4963 | 190.3978 | 0.10773 | 2.3084 | 0 | 87.328
Bus_2 | 4.283 | 148.3662 | 0.62773 | 2.8984 | 0 | 77.7798
Bus_3(1) | 3.4587 | 119.8128 | 1.1477 | 3.4884 | 0 | 71.7883
Bus_4 | 3.4587 | 119.8128 | 1.1477 | 3.4884 | 0 | 71.7883

## LLL_max_branch
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_vm_pu
Line_0 | 0 | 4.283 | 0 | 9.2778 | 0 | 148.3662 | 6.297e-19 | -1e-07 | -4.9284e-19 | -1e-07
Line_1 | 3.4587 | 0 | 6.7756 | 0 | 119.8128 | 0 | -1e-07 | 1.6014e-19 | -1e-07 | -1.2512e-19
Line_2 | 3.4587 | 0 | 6.7756 | 0 | 119.8128 | 0 | -1e-07 | 1.6014e-19 | -1e-07 | -1.2512e-19

## LLL_max_fault
name | pf_ikss_ka | pf_skss_mw | pf_rk_ohm | pf_xk_ohm | pf_vm_pu | pf_va_degree
Bus_0 | 3.618 | 689.314 | 1.3244 | 13.2439 | 0.40283 | 45
Bus_1 | 1.4245 | 49.3473 | 0.10773 | 2.3084 | 0.87234 | 45
Bus_2 | 1.3097 | 45.3689 | 0.62773 | 2.8984 | 0.80202 | 45
Bus_3(1) | 1.2119 | 41.9813 | 1.1477 | 3.4884 | 0.74213 | 45
Bus_4 | 1.2119 | 41.9813 | 1.1477 | 3.4884 | 0.74213 | 45

## LLL_max_fault_branch
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_vm_pu
Line_0 | 0 | 1.3097 | 0 | 2.8371 | 0 | 45.3689 | -6.0676e-09 | -25.7292 | 5.5265e-09 | -25.7292
Line_1 | 1.2119 | 0 | 2.3741 | 0 | 41.9813 | 0 | -22.0304 | -2.495e-09 | -22.0304 | 1.6066e-09
Line_2 | 1.2119 | 0 | 2.3741 | 0 | 41.9813 | 0 | -22.0304 | -2.495e-09 | -22.0304 | 1.6066e-09

## LLL_min
name | pf_ikss_ka | pf_skss_mw | pf_rk_ohm | pf_xk_ohm | pf_vm_pu | pf_va_degree
Bus_0 | 4.1989 | 800 | 1.505 | 15.0499 | 0 | 84.2894
Bus_1 | 4.7732 | 165.3474 | 0.11535 | 2.4164 | 0 | 87.2669
Bus_2 | 3.6016 | 124.7634 | 1.1138 | 3.0064 | 0 | 69.6723
Bus_3(1) | 2.7686 | 95.9057 | 2.1122 | 3.5964 | 0 | 59.5744
Bus_4 | 2.7686 | 95.9057 | 2.1122 | 3.5964 | 0 | 59.5744

## LLL_min_branch
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_vm_pu
Line_0 | 0 | 3.6016 | 0 | 6.8381 | 0 | 124.7634 | 7.2789e-20 | -1e-07 | 2.6702e-19 | -1e-07
Line_1 | 2.7686 | 0 | 4.6525 | 0 | 95.9057 | 0 | -1e-07 | 1.7283e-20 | -1e-07 | 6.3218e-20
Line_2 | 2.7686 | 0 | 4.6525 | 0 | 95.9057 | 0 | -1e-07 | 1.7283e-20 | -1e-07 | 6.3218e-20

## LLL_min_fault
name | pf_ikss_ka | pf_skss_mw | pf_rk_ohm | pf_xk_ohm | pf_vm_pu | pf_va_degree
Bus_0 | 3.0129 | 574.037 | 1.505 | 15.0499 | 0.33546 | 45
Bus_1 | 1.2817 | 44.3979 | 0.11535 | 2.4164 | 0.78485 | 45
Bus_2 | 1.1462 | 39.7072 | 1.1138 | 3.0064 | 0.70193 | 45
Bus_3(1) | 1.0349 | 35.8516 | 2.1122 | 3.5964 | 0.63377 | 45
Bus_4 | 1.0349 | 35.8516 | 2.1122 | 3.5964 | 0.63377 | 45

## LLL_min_fault_branch
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_vm_pu
Line_0 | 0 | 1.1462 | 0 | 2.1763 | 0 | 39.7072 | -5.1465e-09 | -19.7082 | 4.6774e-09 | -19.7082
Line_1 | 1.0349 | 0 | 1.7392 | 0 | 35.8516 | 0 | -16.0667 | -2.233e-09 | -16.0667 | 1.0258e-09
Line_2 | 1.0349 | 0 | 1.7392 | 0 | 35.8516 | 0 | -16.0667 | -2.233e-09 | -16.0667 | 1.0258e-09

## LL_max
name | pf_ikss_a_ka | pf_ikss_b_ka | pf_ikss_c_ka | pf_skss_a_mw | pf_skss_b_mw | pf_skss_c_mw | pf_rk0_ohm | pf_xk0_ohm | pf_rk1_ohm | pf_xk1_ohm | pf_rk2_ohm | pf_xk2_ohm | pf_vm_a_pu | pf_vm_b_pu | pf_vm_c_pu | pf_va_a_degree | pf_va_b_degree | pf_va_c_degree
Bus_0 | 0 | 4.5455 | 4.5455 | 0 | 288.6752 | 288.6752 | 0.50157 | 8.1756 | 1.3244 | 13.2439 | 1.3244 | 13.2439 | 0.95263 | 0 | 0.95263 | -8.6936e-11 | 0 | -180
Bus_1 | 0 | 4.7599 | 4.7599 | 0 | 54.9631 | 54.9631 | 0.022433 | 69.8413 | 0.10773 | 2.3084 | 0.10773 | 2.3084 | 0.95263 | 0 | 0.95263 | -4.0482e-12 | 0 | -180
Bus_2 | 0 | 3.7092 | 3.7092 | 0 | 42.8296 | 42.8296 | 4.285 | 71.5159 | 0.62773 | 2.8984 | 0.62773 | 2.8984 | 0.95263 | 0 | 0.95263 | -1.2545e-11 | 0 | -180
Bus_3(1) | 0 | 2.9953 | 2.9953 | 0 | 34.587 | 34.587 | 8.0984 | 73.0216 | 1.1477 | 3.4884 | 1.1477 | 3.4884 | 0.95263 | 0 | 0.95263 | -1.4656e-11 | 0 | -180
Bus_4 | 0 | 2.9953 | 2.9953 | 0 | 34.587 | 34.587 | 8.0984 | 73.0216 | 1.1477 | 3.4884 | 1.1477 | 3.4884 | 0.95263 | 0 | 0.95263 | -1.4688e-11 | 0 | -180

## LL_max_branch
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mw | pf_q_b_from_mw | pf_q_c_from_mw | pf_q_a_to_mw | pf_q_b_to_mw | pf_q_c_to_mw
Line_0 | 0 | 0 | 0 | 0 | 3.7092 | 3.7092 | 0 | 0 | 0 | 0 | 42.8296 | 42.8296 | 5.2106e-15 | 7.816e-15 | -1.0421e-14 | -2.6053e-14 | -23.0225 | 23.0225 | 2.0843e-14 | 5.7634e-09 | -5.7634e-09 | -2.0843e-14 | 4.9861 | -4.9861
Line_1 | 0 | 2.9953 | 2.9953 | 0 | 0 | 0 | 0 | 34.587 | 34.587 | 0 | 0 | 0 | -1.0421e-14 | -18.0699 | 18.0699 | -5.2106e-15 | 1.3027e-14 | -1.5632e-14 | 1.0421e-14 | 5.9452 | -5.9452 | -5.0689e-29 | 1.9211e-09 | -1.9211e-09
Line_2 | 0 | 2.9953 | 2.9953 | 0 | 0 | 0 | 0 | 34.587 | 34.587 | 0 | 0 | 0 | -1.5632e-14 | -18.0699 | 18.0699 | 5.2106e-15 | 2.3448e-14 | -1.5632e-14 | 5.2106e-15 | 5.9452 | -5.9452 | -5.2106e-15 | 1.9211e-09 | -1.9211e-09

## LL_max_fault
name | pf_ikss_a_ka | pf_ikss_b_ka | pf_ikss_c_ka | pf_skss_a_mw | pf_skss_b_mw | pf_skss_c_mw | pf_rk0_ohm | pf_xk0_ohm | pf_rk1_ohm | pf_xk1_ohm | pf_rk2_ohm | pf_xk2_ohm | pf_vm_a_pu | pf_vm_b_pu | pf_vm_c_pu | pf_va_a_degree | pf_va_b_degree | pf_va_c_degree
Bus_0 | 0 | 3.7342 | 3.7342 | 0 | 237.1508 | 237.1508 | 0.50157 | 8.1756 | 1.3244 | 13.2439 | 1.3244 | 13.2439 | 1.0202 | 0.24004 | 0.89607 | 5.7662 | -121.3466 | 173.4316
Bus_1 | 0 | 2.011 | 2.011 | 0 | 23.2205 | 23.2205 | 0.022433 | 69.8413 | 0.10773 | 2.3084 | 0.10773 | 2.3084 | 1.1075 | 0.71098 | 0.91717 | 17.922 | -106.528 | 158.1868
Bus_2 | 0 | 1.7631 | 1.7631 | 0 | 20.3584 | 20.3584 | 4.285 | 71.5159 | 0.62773 | 2.8984 | 0.62773 | 2.8984 | 1.0759 | 0.62335 | 0.92294 | 16.2567 | -104.913 | 160.9544
Bus_3(1) | 0 | 1.5688 | 1.5688 | 0 | 18.1144 | 18.1144 | 8.0984 | 73.0216 | 1.1477 | 3.4884 | 1.1477 | 3.4884 | 1.0531 | 0.55464 | 0.92719 | 14.8259 | -103.6532 | 163.1035
Bus_4 | 0 | 1.5688 | 1.5688 | 0 | 18.1144 | 18.1144 | 8.0984 | 73.0216 | 1.1477 | 3.4884 | 1.1477 | 3.4884 | 1.0531 | 0.55464 | 0.92719 | 14.8259 | -103.6532 | 163.1035

## LL_max_fault_branch
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mw | pf_q_b_from_mw | pf_q_c_from_mw | pf_q_a_to_mw | pf_q_b_to_mw | pf_q_c_to_mw
Line_0 | 0 | 0 | 0 | 0 | 1.7631 | 1.7631 | 0 | 0 | 0 | 0 | 20.3584 | 20.3584 | -2.5857e-29 | -9.5548e-10 | -3.0749e-09 | 6.528e-29 | -17.4596 | 1.9173 | 5.2106e-15 | 4.0277e-09 | -3.5664e-10 | -1.3027e-14 | -2.1579 | -13.3845
Line_1 | 0 | 1.5688 | 1.5688 | 0 | 0 | 0 | 0 | 18.1144 | 18.1144 | 0 | 0 | 0 | 2.6053e-15 | -14.6611 | 2.3562 | -7.816e-15 | -4.7338e-10 | -1.0337e-09 | -2.6053e-15 | -0.96958 | -11.3353 | -7.816e-15 | 1.3544e-09 | -3.8386e-10
Line_2 | 0 | 1.5688 | 1.5688 | 0 | 0 | 0 | 0 | 18.1144 | 18.1144 | 0 | 0 | 0 | -2.6053e-15 | -14.6611 | 2.3562 | 7.816e-15 | -4.7339e-10 | -1.0337e-09 | -1.4906e-29 | -0.96958 | -11.3353 | -7.816e-15 | 1.3544e-09 | -3.8387e-10

## LL_min
name | pf_ikss_a_ka | pf_ikss_b_ka | pf_ikss_c_ka | pf_skss_a_mw | pf_skss_b_mw | pf_skss_c_mw | pf_rk0_ohm | pf_xk0_ohm | pf_rk1_ohm | pf_xk1_ohm | pf_rk2_ohm | pf_xk2_ohm | pf_vm_a_pu | pf_vm_b_pu | pf_vm_c_pu | pf_va_a_degree | pf_va_b_degree | pf_va_c_degree
Bus_0 | 0 | 3.6364 | 3.6364 | 0 | 230.9401 | 230.9401 | 0.52544 | 8.9215 | 1.505 | 15.0499 | 1.505 | 15.0499 | 0.86603 | 0 | 0.86603 | 1.72e-10 | 0 | 180
Bus_1 | 0 | 4.1337 | 4.1337 | 0 | 47.7317 | 47.7317 | 0.043071 | 69.8435 | 0.11535 | 2.4164 | 0.11535 | 2.4164 | 0.86603 | 0 | 0.86603 | 3.0762e-11 | 0 | 180
Bus_2 | 0 | 3.1191 | 3.1191 | 0 | 36.0161 | 36.0161 | 8.2268 | 71.4687 | 1.1138 | 3.0064 | 1.1138 | 3.0064 | 0.86603 | 0 | 0.86603 | 1.7234e-10 | 0 | 180
Bus_3(1) | 0 | 2.3976 | 2.3976 | 0 | 27.6856 | 27.6856 | 15.5483 | 72.9479 | 2.1122 | 3.5964 | 2.1122 | 3.5964 | 0.86603 | 0 | 0.86603 | 1.9336e-10 | 0 | 180
Bus_4 | 0 | 2.3976 | 2.3976 | 0 | 27.6856 | 27.6856 | 15.5483 | 72.9479 | 2.1122 | 3.5964 | 2.1122 | 3.5964 | 0.86603 | 0 | 0.86603 | 1.9336e-10 | 0 | 180

## LL_min_branch
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mw | pf_q_b_from_mw | pf_q_c_from_mw | pf_q_a_to_mw | pf_q_b_to_mw | pf_q_c_to_mw
Line_0 | 0 | 0 | 0 | 0 | 3.1191 | 3.1191 | 0 | 0 | 0 | 0 | 36.0161 | 36.0161 | -1.6579e-14 | 1.5395e-14 | -2.3685e-15 | 2.3685e-15 | -16.8865 | 16.8865 | -2.3685e-14 | 4.7631e-09 | -4.7631e-09 | 2.8422e-14 | 6.2558 | -6.2558
Line_1 | 0 | 2.3976 | 2.3976 | 0 | 0 | 0 | 0 | 27.6856 | 27.6856 | 0 | 0 | 0 | -3.5527e-15 | -11.9365 | 11.9365 | -7.1054e-15 | -1.1843e-15 | 2.3685e-15 | -3.1772e-29 | 7.0103 | -7.0103 | -4.737e-15 | 1.5877e-09 | -1.5877e-09
Line_2 | 0 | 2.3976 | 2.3976 | 0 | 0 | 0 | 0 | 27.6856 | 27.6856 | 0 | 0 | 0 | -5.9212e-15 | -11.9365 | 11.9365 | -2.3685e-15 | 3.5527e-15 | -2.3685e-15 | 1.4211e-14 | 7.0103 | -7.0103 | -4.737e-15 | 1.5877e-09 | -1.5877e-09

## LL_min_fault
name | pf_ikss_a_ka | pf_ikss_b_ka | pf_ikss_c_ka | pf_skss_a_mw | pf_skss_b_mw | pf_skss_c_mw | pf_rk0_ohm | pf_xk0_ohm | pf_rk1_ohm | pf_xk1_ohm | pf_rk2_ohm | pf_xk2_ohm | pf_vm_a_pu | pf_vm_b_pu | pf_vm_c_pu | pf_va_a_degree | pf_va_b_degree | pf_va_c_degree
Bus_0 | 0 | 3.0554 | 3.0554 | 0 | 194.0418 | 194.0418 | 0.52544 | 8.9215 | 1.505 | 15.0499 | 1.505 | 15.0499 | 0.92203 | 0.19641 | 0.81801 | 5.174 | -122.1449 | 174.1659
Bus_1 | 0 | 1.7957 | 1.7957 | 0 | 20.7353 | 20.7353 | 0.043071 | 69.8435 | 0.11535 | 2.4164 | 0.11535 | 2.4164 | 1.0057 | 0.63489 | 0.83074 | 17.5701 | -106.9886 | 158.5648
Bus_2 | 0 | 1.5183 | 1.5183 | 0 | 17.5318 | 17.5318 | 8.2268 | 71.4687 | 1.1138 | 3.0064 | 1.1138 | 3.0064 | 0.95734 | 0.5368 | 0.85298 | 15.9329 | -101.7238 | 162.0554
Bus_3(1) | 0 | 1.3081 | 1.3081 | 0 | 15.105 | 15.105 | 15.5483 | 72.9479 | 2.1122 | 3.5964 | 2.1122 | 3.5964 | 0.92653 | 0.4625 | 0.86515 | 14.3131 | -97.8911 | 164.6473
Bus_4 | 0 | 1.3081 | 1.3081 | 0 | 15.105 | 15.105 | 15.5483 | 72.9479 | 2.1122 | 3.5964 | 2.1122 | 3.5964 | 0.92653 | 0.4625 | 0.86515 | 14.3131 | -97.8911 | 164.6473

## LL_min_fault_branch
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mw | pf_q_b_from_mw | pf_q_c_from_mw | pf_q_a_to_mw | pf_q_b_to_mw | pf_q_c_to_mw
Line_0 | 0 | 0 | 0 | 0 | 1.5183 | 1.5183 | 0 | 0 | 0 | 0 | 17.5318 | 17.5318 | -4.4409e-15 | -8.0026e-10 | -2.5674e-09 | 1.7764e-15 | -13.0917 | 1.5655 | -1.1842e-14 | 3.4014e-09 | -3.4065e-10 | 1.4211e-14 | -0.95344 | -10.5727
Line_1 | 0 | 1.3081 | 1.3081 | 0 | 0 | 0 | 0 | 15.105 | 15.105 | 0 | 0 | 0 | -3.5527e-15 | -10.3011 | 1.745 | -1.1842e-15 | -4.7981e-10 | -8.2616e-10 | 4.737e-15 | 0.27863 | -8.8347 | -6.1482e-30 | 1.0532e-09 | -4.5326e-10
Line_2 | 0 | 1.3081 | 1.3081 | 0 | 0 | 0 | 0 | 15.105 | 15.105 | 0 | 0 | 0 | -1.7764e-15 | -10.3011 | 1.745 | -1.7764e-15 | -4.798e-10 | -8.2615e-10 | -6.5697e-30 | 0.27863 | -8.8347 | -9.2223e-30 | 1.0532e-09 | -4.5326e-10

## LLG_max
name | pf_ikss_a_ka | pf_ikss_b_ka | pf_ikss_c_ka | pf_skss_a_mw | pf_skss_b_mw | pf_skss_c_mw | pf_rk0_ohm | pf_xk0_ohm | pf_rk1_ohm | pf_xk1_ohm | pf_rk2_ohm | pf_xk2_ohm | pf_vm_a_pu | pf_vm_b_pu | pf_vm_c_pu | pf_va_a_degree | pf_va_b_degree | pf_va_c_degree
Bus_0 | 0 | 5.6957 | 5.8138 | 0 | 361.7272 | 369.2287 | 0.50157 | 8.1756 | 1.3244 | 13.2439 | 1.3244 | 13.2439 | 0.52569 | 0 | 0.52569 | 0.98614 | 0 | -179.0139
Bus_1 | 0 | 4.7557 | 4.7679 | 0 | 54.9144 | 55.0554 | 0.022433 | 69.8413 | 0.10773 | 2.3084 | 0.10773 | 2.3084 | 0.93714 | 0 | 0.93714 | 0.043172 | 0 | -179.9568
Bus_2 | 0 | 3.6919 | 3.7309 | 0 | 42.6302 | 43.0807 | 4.285 | 71.5159 | 0.62773 | 2.8984 | 0.62773 | 2.8984 | 0.93353 | 0 | 0.93353 | 0.17761 | 0 | -179.8224
Bus_3(1) | 0 | 2.9725 | 3.0233 | 0 | 34.3231 | 34.9101 | 8.0984 | 73.0216 | 1.1477 | 3.4884 | 1.1477 | 3.4884 | 0.92987 | 0 | 0.92987 | 0.28783 | 0 | -179.7122
Bus_4 | 0 | 2.9725 | 3.0233 | 0 | 34.3231 | 34.9101 | 8.0984 | 73.0216 | 1.1477 | 3.4884 | 1.1477 | 3.4884 | 0.92987 | 0 | 0.92987 | 0.28783 | 0 | -179.7122

## LLG_max_branch
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mw | pf_q_b_from_mw | pf_q_c_from_mw | pf_q_a_to_mw | pf_q_b_to_mw | pf_q_c_to_mw
Line_0 | 0.0080458 | 0.0080458 | 0.0080458 | 0.0053365 | 3.691 | 3.7322 | 0.092905 | 0.092905 | 0.092905 | 0.061621 | 42.6195 | 43.0957 | 0.00053852 | -3.9204e-14 | -3.9009e-14 | -3.9482e-05 | 7.419e-11 | 7.7312e-11 | -0.1508 | -7.386e-14 | 6.939e-14 | 0.099636 | -4.4338e-11 | 3.4385e-11
Line_1 | 0 | 2.9725 | 3.0233 | 0.0026683 | 0.0026683 | 0.0026683 | 0 | 34.3231 | 34.9101 | 0.03081 | 0.03081 | 0.03081 | -3.0154e-09 | 6.4711e-11 | 7.4482e-11 | 1.974e-05 | -2.2269e-14 | -3.7327e-14 | 3.2642e-11 | -4.6676e-11 | 2.5369e-11 | -0.049818 | -5.8378e-14 | 4.7604e-14
Line_2 | 0 | 2.9725 | 3.0233 | 0.0026683 | 0.0026683 | 0.0026683 | 0 | 34.3231 | 34.9101 | 0.03081 | 0.03081 | 0.03081 | -3.0154e-09 | 6.4644e-11 | 7.4531e-11 | 1.974e-05 | -2.2269e-14 | -3.7327e-14 | 3.2612e-11 | -4.6578e-11 | 2.5289e-11 | -0.049818 | -5.8378e-14 | 4.7604e-14

## LLG_max_fault
name | pf_ikss_a_ka | pf_ikss_b_ka | pf_ikss_c_ka | pf_skss_a_mw | pf_skss_b_mw | pf_skss_c_mw | pf_rk0_ohm | pf_xk0_ohm | pf_rk1_ohm | pf_xk1_ohm | pf_rk2_ohm | pf_xk2_ohm | pf_vm_a_pu | pf_vm_b_pu | pf_vm_c_pu | pf_va_a_degree | pf_va_b_degree | pf_va_c_degree
Bus_0 | 0 | 3.8886 | 3.7561 | 0 | 246.9567 | 238.5425 | 0.50157 | 8.1756 | 1.3244 | 13.2439 | 1.3244 | 13.2439 | 0.7929 | 0.40283 | 0.65946 | 7.9952 | -115.8808 | 157.5213
Bus_1 | 0 | 1.179 | 1.2973 | 0 | 13.6141 | 14.9802 | 0.022433 | 69.8413 | 0.10773 | 2.3084 | 0.10773 | 2.3084 | 1.1017 | 0.87234 | 0.96388 | 22.9055 | -100.051 | 153.4941
Bus_2 | 0 | 1.0862 | 1.1918 | 0 | 12.5429 | 13.7618 | 4.285 | 71.5159 | 0.62773 | 2.8984 | 0.62773 | 2.8984 | 1.0773 | 0.80202 | 0.95422 | 21.5993 | -99.5297 | 155.5887
Bus_3(1) | 0 | 1.0072 | 1.102 | 0 | 11.63 | 12.725 | 8.0984 | 73.0216 | 1.1477 | 3.4884 | 1.1477 | 3.4884 | 1.057 | 0.74213 | 0.94608 | 20.4311 | -99.0862 | 157.383
Bus_4 | 0 | 1.0072 | 1.102 | 0 | 11.63 | 12.725 | 8.0984 | 73.0216 | 1.1477 | 3.4884 | 1.1477 | 3.4884 | 1.057 | 0.74213 | 0.94608 | 20.4311 | -99.0862 | 157.383

## LLG_max_fault_branch
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mw | pf_q_b_from_mw | pf_q_c_from_mw | pf_q_a_to_mw | pf_q_b_to_mw | pf_q_c_to_mw
Line_0 | 0.0072434 | 0.0072434 | 0.0072434 | 0.0047948 | 1.0842 | 1.1946 | 0.08364 | 0.08364 | 0.08364 | 0.055366 | 12.5197 | 13.7939 | -0.0082794 | -0.056578 | 0.065294 | 0.0052335 | -5.8651 | -7.1418 | -0.13101 | 0.021109 | -0.012325 | 0.086376 | -5.9123 | -7.0953
Line_1 | 0 | 1.0072 | 1.102 | 0.0023974 | 0.0023974 | 0.0023974 | 0 | 11.63 | 12.725 | 0.027683 | 0.027683 | 0.027683 | -2.6112e-09 | -5.0721 | -6.0722 | -0.0026167 | -0.017288 | 0.019921 | 1.744e-10 | -5.0721 | -6.0722 | -0.043188 | 0.0063415 | -0.0033708
Line_2 | 0 | 1.0072 | 1.102 | 0.0023974 | 0.0023974 | 0.0023974 | 0 | 11.63 | 12.725 | 0.027683 | 0.027683 | 0.027683 | -2.6112e-09 | -5.0721 | -6.0722 | -0.0026167 | -0.017288 | 0.019921 | 1.7442e-10 | -5.0721 | -6.0722 | -0.043188 | 0.0063415 | -0.0033708

## LLG_min
name | pf_ikss_a_ka | pf_ikss_b_ka | pf_ikss_c_ka | pf_skss_a_mw | pf_skss_b_mw | pf_skss_c_mw | pf_rk0_ohm | pf_xk0_ohm | pf_rk1_ohm | pf_xk1_ohm | pf_rk2_ohm | pf_xk2_ohm | pf_vm_a_pu | pf_vm_b_pu | pf_vm_c_pu | pf_va_a_degree | pf_va_b_degree | pf_va_c_degree
Bus_0 | 0 | 4.593 | 4.6931 | 0 | 291.6968 | 298.0505 | 0.52544 | 8.9215 | 1.505 | 15.0499 | 1.505 | 15.0499 | 0.46918 | 0 | 0.46918 | 1.0725 | 0 | -178.9275
Bus_1 | 0 | 4.1298 | 4.1411 | 0 | 47.6873 | 47.8175 | 0.043071 | 69.8435 | 0.11535 | 2.4164 | 0.11535 | 2.4164 | 0.8513 | 0 | 0.8513 | 0.045909 | 0 | -179.9541
Bus_2 | 0 | 3.0938 | 3.1486 | 0 | 35.7238 | 36.357 | 8.2268 | 71.4687 | 1.1138 | 3.0064 | 1.1138 | 3.0064 | 0.84767 | 0 | 0.84767 | 0.29726 | 0 | -179.7027
Bus_3(1) | 0 | 2.3653 | 2.4348 | 0 | 27.3124 | 28.1145 | 15.5483 | 72.9479 | 2.1122 | 3.5964 | 2.1122 | 3.5964 | 0.84361 | 0 | 0.84361 | 0.4924 | 0 | -179.5076
Bus_4 | 0 | 2.3653 | 2.4348 | 0 | 27.3124 | 28.1145 | 15.5483 | 72.9479 | 2.1122 | 3.5964 | 2.1122 | 3.5964 | 0.84361 | 0 | 0.84361 | 0.4924 | 0 | -179.5076

## LLG_min_branch
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mw | pf_q_b_from_mw | pf_q_c_from_mw | pf_q_a_to_mw | pf_q_b_to_mw | pf_q_c_to_mw
Line_0 | 0.0073086 | 0.0073086 | 0.0073086 | 0.0048457 | 3.0923 | 3.1504 | 0.084393 | 0.084393 | 0.084393 | 0.055953 | 35.7066 | 36.3781 | 0.00085317 | -7.7768e-14 | 8.0734e-14 | -6.2495e-05 | -1.3496e-10 | 3.3673e-11 | -0.12443 | 4.4766e-14 | 4.4142e-14 | 0.082151 | -1.345e-10 | -1.9183e-10
Line_1 | 0 | 2.3653 | 2.4348 | 0.0024228 | 0.0024228 | 0.0024228 | 0 | 27.3124 | 28.1145 | 0.027977 | 0.027977 | 0.027977 | -2.471e-09 | -1.3283e-10 | -1.1498e-12 | 3.1246e-05 | -1.3274e-13 | 1.2675e-13 | 4.6029e-11 | -9.4169e-11 | -1.6803e-10 | -0.041075 | 6.8317e-14 | 7.981e-14
Line_2 | 0 | 2.3653 | 2.4348 | 0.0024228 | 0.0024228 | 0.0024228 | 0 | 27.3124 | 28.1145 | 0.027977 | 0.027977 | 0.027977 | -2.471e-09 | -1.3282e-10 | -1.1719e-12 | 3.1246e-05 | -1.3274e-13 | 1.2675e-13 | 4.6043e-11 | -9.3973e-11 | -1.6823e-10 | -0.041075 | 6.8317e-14 | 7.981e-14

## LLG_min_fault
name | pf_ikss_a_ka | pf_ikss_b_ka | pf_ikss_c_ka | pf_skss_a_mw | pf_skss_b_mw | pf_skss_c_mw | pf_rk0_ohm | pf_xk0_ohm | pf_rk1_ohm | pf_xk1_ohm | pf_rk2_ohm | pf_xk2_ohm | pf_vm_a_pu | pf_vm_b_pu | pf_vm_c_pu | pf_va_a_degree | pf_va_b_degree | pf_va_c_degree
Bus_0 | 0 | 3.2654 | 3.1511 | 0 | 207.3791 | 200.121 | 0.52544 | 8.9215 | 1.505 | 15.0499 | 1.505 | 15.0499 | 0.69879 | 0.33546 | 0.58166 | 7.0251 | -117.0249 | 158.4803
Bus_1 | 0 | 1.061 | 1.1672 | 0 | 12.2511 | 13.4778 | 0.043071 | 69.8435 | 0.11535 | 2.4164 | 0.11535 | 2.4164 | 1.0008 | 0.78485 | 0.87226 | 22.6451 | -100.4046 | 153.6892
Bus_2 | 0 | 0.9513 | 1.0431 | 0 | 10.9847 | 12.0449 | 8.2268 | 71.4687 | 1.1138 | 3.0064 | 1.1138 | 3.0064 | 0.96205 | 0.70193 | 0.87379 | 21.3639 | -97.6343 | 156.7273
Bus_3(1) | 0 | 0.86139 | 0.9408 | 0 | 9.9465 | 10.8634 | 15.5483 | 72.9479 | 2.1122 | 3.5964 | 2.1122 | 3.5964 | 0.93226 | 0.63377 | 0.87282 | 20.1151 | -95.3977 | 159.1714
Bus_4 | 0 | 0.86139 | 0.9408 | 0 | 9.9465 | 10.8634 | 15.5483 | 72.9479 | 2.1122 | 3.5964 | 2.1122 | 3.5964 | 0.93226 | 0.63377 | 0.87282 | 20.1151 | -95.3977 | 159.1714

## LLG_min_fault_branch
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mw | pf_q_b_from_mw | pf_q_c_from_mw | pf_q_a_to_mw | pf_q_b_to_mw | pf_q_c_to_mw
Line_0 | 0.0065801 | 0.0065801 | 0.0065801 | 0.0043379 | 0.94935 | 1.0458 | 0.07598 | 0.07598 | 0.07598 | 0.050089 | 10.9622 | 12.0756 | -0.0064751 | -0.046182 | 0.053348 | 0.0039684 | -4.4972 | -5.4722 | -0.10814 | 0.017441 | -0.010167 | 0.070906 | -4.534 | -5.4365
Line_1 | 0 | 0.86139 | 0.9408 | 0.0021689 | 0.0021689 | 0.0021689 | 0 | 9.9465 | 10.8634 | 0.025045 | 0.025045 | 0.025045 | -2.1272e-09 | -3.71 | -4.4255 | -0.0019842 | -0.013861 | 0.01587 | 1.414e-10 | -3.71 | -4.4255 | -0.035453 | 0.0045537 | -0.0020178
Line_2 | 0 | 0.86139 | 0.9408 | 0.0021689 | 0.0021689 | 0.0021689 | 0 | 9.9465 | 10.8634 | 0.025045 | 0.025045 | 0.025045 | -2.1272e-09 | -3.71 | -4.4255 | -0.0019842 | -0.013861 | 0.01587 | 1.4141e-10 | -3.71 | -4.4255 | -0.035453 | 0.0045537 | -0.0020178

## LG_max
name | pf_ikss_a_ka | pf_ikss_b_ka | pf_ikss_c_ka | pf_skss_a_mw | pf_skss_b_mw | pf_skss_c_mw | pf_rk0_ohm | pf_xk0_ohm | pf_rk1_ohm | pf_xk1_ohm | pf_rk2_ohm | pf_xk2_ohm | pf_vm_a_pu | pf_vm_b_pu | pf_vm_c_pu | pf_va_a_degree | pf_va_b_degree | pf_va_c_degree
Bus_0 | 6.0213 | 0 | 0 | 382.4016 | 0 | 0 | 0.50157 | 8.1756 | 1.3244 | 13.2439 | 1.3244 | 13.2439 | 0.6 | 1.1 | 0.58781 | 68.0698 | -90 | 112.4094
Bus_1 | 0.51176 | 0 | 0 | 5.9093 | 0 | 0 | 0.022433 | 69.8413 | 0.10773 | 2.3084 | 0.10773 | 2.3084 | 1.0506 | 1.1 | 1.0479 | 31.7325 | -90 | 148.5064
Bus_2 | 0.49161 | 0 | 0 | 5.6766 | 0 | 0 | 4.285 | 71.5159 | 0.62773 | 2.8984 | 0.62773 | 2.8984 | 1.0436 | 1.1 | 1.0327 | 32.4714 | -90 | 148.4927
Bus_3(1) | 0.47235 | 0 | 0 | 5.4543 | 0 | 0 | 8.0984 | 73.0216 | 1.1477 | 3.4884 | 1.1477 | 3.4884 | 1.0359 | 1.1 | 1.0185 | 33.1367 | -90 | 148.3959
Bus_4 | 0.47235 | 0 | 0 | 5.4543 | 0 | 0 | 8.0984 | 73.0216 | 1.1477 | 3.4884 | 1.1477 | 3.4884 | 1.0359 | 1.1 | 1.0185 | 33.1367 | -90 | 148.3959

## LG_max_branch
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mw | pf_q_b_from_mw | pf_q_c_from_mw | pf_q_a_to_mw | pf_q_b_to_mw | pf_q_c_to_mw
Line_0 | 0.015343 | 0.015343 | 0.015343 | 0.50166 | 0.010067 | 0.010067 | 0.17717 | 0.17717 | 0.17717 | 5.7926 | 0.11624 | 0.11624 | -2.364e-13 | 0.16975 | -0.1678 | 7.2086e-12 | -0.1108 | 0.11066 | 7.1629e-14 | -0.27408 | -0.27432 | -2.7579e-12 | 0.17854 | 0.17603
Line_1 | 0.47235 | 0 | 0 | 0.0050335 | 0.0050335 | 0.0050335 | 5.4543 | 0 | 0 | 0.058122 | 0.058122 | 0.058122 | 6.3081e-12 | -5.3482e-09 | -5.1514e-09 | -7.3836e-14 | 0.0554 | -0.05533 | -2.842e-12 | -3.27e-09 | 3.3837e-09 | 2.3356e-14 | -0.089268 | -0.088017
Line_2 | 0.47235 | 0 | 0 | 0.0050335 | 0.0050335 | 0.0050335 | 5.4543 | 0 | 0 | 0.058122 | 0.058122 | 0.058122 | 6.3101e-12 | -5.3482e-09 | -5.1515e-09 | -7.3836e-14 | 0.0554 | -0.05533 | -2.8398e-12 | -3.27e-09 | 3.3837e-09 | 2.3356e-14 | -0.089268 | -0.088017

## LG_max_fault
name | pf_ikss_a_ka | pf_ikss_b_ka | pf_ikss_c_ka | pf_skss_a_mw | pf_skss_b_mw | pf_skss_c_mw | pf_rk0_ohm | pf_xk0_ohm | pf_rk1_ohm | pf_xk1_ohm | pf_rk2_ohm | pf_xk2_ohm | pf_vm_a_pu | pf_vm_b_pu | pf_vm_c_pu | pf_va_a_degree | pf_va_b_degree | pf_va_c_degree
Bus_0 | 3.9636 | 0 | 0 | 251.7199 | 0 | 0 | 0.50157 | 8.1756 | 1.3244 | 13.2439 | 1.3244 | 13.2439 | 0.65111 | 1.1 | 0.82808 | 41.4499 | -90 | 126.1111
Bus_1 | 0.41991 | 0 | 0 | 4.8487 | 0 | 0 | 0.022433 | 69.8413 | 0.10773 | 2.3084 | 0.10773 | 2.3084 | 1.0555 | 1.1 | 1.0616 | 31.0294 | -90 | 148.4241
Bus_2 | 0.40293 | 0 | 0 | 4.6526 | 0 | 0 | 4.285 | 71.5159 | 0.62773 | 2.8984 | 0.62773 | 2.8984 | 1.0485 | 1.1 | 1.0489 | 31.6166 | -90 | 148.3519
Bus_3(1) | 0.38751 | 0 | 0 | 4.4746 | 0 | 0 | 8.0984 | 73.0216 | 1.1477 | 3.4884 | 1.1477 | 3.4884 | 1.0412 | 1.1 | 1.037 | 32.1471 | -90 | 148.2299
Bus_4 | 0.38751 | 0 | 0 | 4.4746 | 0 | 0 | 8.0984 | 73.0216 | 1.1477 | 3.4884 | 1.1477 | 3.4884 | 1.0412 | 1.1 | 1.037 | 32.1471 | -90 | 148.2299

## LG_max_fault_branch
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mw | pf_q_b_from_mw | pf_q_c_from_mw | pf_q_a_to_mw | pf_q_b_to_mw | pf_q_c_to_mw
Line_0 | 0.012589 | 0.012589 | 0.012589 | 0.41117 | 0.0082511 | 0.0082511 | 0.14537 | 0.14537 | 0.14537 | 4.7477 | 0.095275 | 0.095275 | 0.026329 | 0.1241 | -0.14911 | -0.82735 | -0.081872 | 0.09737 | 0.026534 | -0.22059 | -0.17515 | -0.82935 | 0.14223 | 0.11355
Line_1 | 0.38751 | 0 | 0 | 0.0041255 | 0.0041255 | 0.0041255 | 4.4746 | 0 | 0 | 0.047637 | 0.047637 | 0.047637 | -0.75081 | -4.2357e-09 | -3.3572e-09 | 0.007796 | 0.040936 | -0.048685 | -0.75081 | -2.4413e-09 | 2.9485e-09 | 0.0087968 | -0.071117 | -0.056773
Line_2 | 0.38751 | 0 | 0 | 0.0041255 | 0.0041255 | 0.0041255 | 4.4746 | 0 | 0 | 0.047637 | 0.047637 | 0.047637 | -0.75081 | -4.2357e-09 | -3.3572e-09 | 0.007796 | 0.040936 | -0.048685 | -0.75081 | -2.4413e-09 | 2.9485e-09 | 0.0087968 | -0.071117 | -0.056773

## LG_min
name | pf_ikss_a_ka | pf_ikss_b_ka | pf_ikss_c_ka | pf_skss_a_mw | pf_skss_b_mw | pf_skss_c_mw | pf_rk0_ohm | pf_xk0_ohm | pf_rk1_ohm | pf_xk1_ohm | pf_rk2_ohm | pf_xk2_ohm | pf_vm_a_pu | pf_vm_b_pu | pf_vm_c_pu | pf_va_a_degree | pf_va_b_degree | pf_va_c_degree
Bus_0 | 4.8627 | 0 | 0 | 308.8215 | 0 | 0 | 0.52544 | 8.9215 | 1.505 | 15.0499 | 1.505 | 15.0499 | 0.54337 | 1 | 0.53178 | 68.6934 | -90 | 111.7941
Bus_1 | 0.46388 | 0 | 0 | 5.3564 | 0 | 0 | 0.043071 | 69.8435 | 0.11535 | 2.4164 | 0.11535 | 2.4164 | 0.95317 | 1 | 0.95057 | 31.8137 | -90 | 148.4394
Bus_2 | 0.44307 | 0 | 0 | 5.1162 | 0 | 0 | 8.2268 | 71.4687 | 1.1138 | 3.0064 | 1.1138 | 3.0064 | 0.94897 | 1 | 0.93245 | 32.9063 | -90 | 148.6979
Bus_3(1) | 0.41967 | 0 | 0 | 4.8459 | 0 | 0 | 15.5483 | 72.9479 | 2.1122 | 3.5964 | 2.1122 | 3.5964 | 0.94198 | 1 | 0.9151 | 33.8685 | -90 | 148.7269
Bus_4 | 0.41967 | 0 | 0 | 4.8459 | 0 | 0 | 15.5483 | 72.9479 | 2.1122 | 3.5964 | 2.1122 | 3.5964 | 0.94198 | 1 | 0.9151 | 33.8685 | -90 | 148.7269

## LG_min_branch
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mw | pf_q_b_from_mw | pf_q_c_from_mw | pf_q_a_to_mw | pf_q_b_to_mw | pf_q_c_to_mw
Line_0 | 0.013908 | 0.013908 | 0.013908 | 0.45212 | 0.0091107 | 0.0091107 | 0.16059 | 0.16059 | 0.16059 | 5.2207 | 0.1052 | 0.1052 | 9.8229e-14 | 0.14062 | -0.13753 | -3.3607e-12 | -0.091201 | 0.09098 | 8.0428e-14 | -0.22476 | -0.22582 | -2.0353e-12 | 0.14691 | 0.14349
Line_1 | 0.41967 | 0 | 0 | 0.0045553 | 0.0045553 | 0.0045553 | 4.8459 | 0 | 0 | 0.0526 | 0.0526 | 0.0526 | -3.0929e-12 | -4.3896e-09 | -4.1152e-09 | 3.1331e-14 | 0.0456 | -0.04549 | -1.4086e-12 | -2.6348e-09 | 2.7933e-09 | 2.4195e-14 | -0.073454 | -0.071746
Line_2 | 0.41967 | 0 | 0 | 0.0045553 | 0.0045553 | 0.0045553 | 4.8459 | 0 | 0 | 0.0526 | 0.0526 | 0.0526 | -3.0942e-12 | -4.3897e-09 | -4.1152e-09 | 3.1331e-14 | 0.0456 | -0.04549 | -1.4082e-12 | -2.6348e-09 | 2.7933e-09 | 2.4195e-14 | -0.073454 | -0.071746

## LG_min_fault
name | pf_ikss_a_ka | pf_ikss_b_ka | pf_ikss_c_ka | pf_skss_a_mw | pf_skss_b_mw | pf_skss_c_mw | pf_rk0_ohm | pf_xk0_ohm | pf_rk1_ohm | pf_xk1_ohm | pf_rk2_ohm | pf_xk2_ohm | pf_vm_a_pu | pf_vm_b_pu | pf_vm_c_pu | pf_va_a_degree | pf_va_b_degree | pf_va_c_degree
Bus_0 | 3.336 | 0 | 0 | 211.8615 | 0 | 0 | 0.52544 | 8.9215 | 1.505 | 15.0499 | 1.505 | 15.0499 | 0.57623 | 1 | 0.73617 | 43.2803 | -90 | 124.739
Bus_1 | 0.38081 | 0 | 0 | 4.3972 | 0 | 0 | 0.043071 | 69.8435 | 0.11535 | 2.4164 | 0.11535 | 2.4164 | 0.95779 | 1 | 0.96358 | 31.0797 | -90 | 148.354
Bus_2 | 0.36114 | 0 | 0 | 4.1701 | 0 | 0 | 8.2268 | 71.4687 | 1.1138 | 3.0064 | 1.1138 | 3.0064 | 0.95312 | 1 | 0.94788 | 31.9935 | -90 | 148.5175
Bus_3(1) | 0.34198 | 0 | 0 | 3.9488 | 0 | 0 | 15.5483 | 72.9479 | 2.1122 | 3.5964 | 2.1122 | 3.5964 | 0.94678 | 1 | 0.93315 | 32.7953 | -90 | 148.5273
Bus_4 | 0.34198 | 0 | 0 | 3.9488 | 0 | 0 | 15.5483 | 72.9479 | 2.1122 | 3.5964 | 2.1122 | 3.5964 | 0.94678 | 1 | 0.93315 | 32.7953 | -90 | 148.5273

## LG_min_fault_branch
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mw | pf_q_b_from_mw | pf_q_c_from_mw | pf_q_a_to_mw | pf_q_b_to_mw | pf_q_c_to_mw
Line_0 | 0.011417 | 0.011417 | 0.011417 | 0.36852 | 0.007426 | 0.007426 | 0.13183 | 0.13183 | 0.13183 | 4.2553 | 0.085748 | 0.085748 | 0.021575 | 0.10294 | -0.12244 | -0.6639 | -0.067575 | 0.079205 | 0.0219 | -0.1811 | -0.14445 | -0.66699 | 0.11523 | 0.092565
Line_1 | 0.34198 | 0 | 0 | 0.003713 | 0.003713 | 0.003713 | 3.9488 | 0 | 0 | 0.042874 | 0.042874 | 0.042874 | -0.58475 | -3.3963e-09 | -2.6949e-09 | 0.0058883 | 0.033787 | -0.039602 | -0.58475 | -1.984e-09 | 2.389e-09 | 0.0074318 | -0.057616 | -0.046282
Line_2 | 0.34198 | 0 | 0 | 0.003713 | 0.003713 | 0.003713 | 3.9488 | 0 | 0 | 0.042874 | 0.042874 | 0.042874 | -0.58475 | -3.3963e-09 | -2.6949e-09 | 0.0058883 | 0.033787 | -0.039602 | -0.58475 | -1.984e-09 | 2.389e-09 | 0.0074318 | -0.057616 | -0.046282