## LLL_max_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 4.283 | 4.283 | 0 | 9.2778 | 148.3662 | 148.3662 | 28.6163 | -1e-07 | 32.4685 | -1e-07 | -77.7798 | 102.2202 | 0.29171 | 0 | -29.1714 | 0
Line_1 | 0.78635 | 0.78635 | 0 | 1.5487 | 27.2398 | 27.2398 | 0.96461 | -1e-07 | 1.0945 | -1e-07 | -72.1353 | 107.8647 | 0.053557 | 0 | -23.5269 | 0
Line_2 | 0.78635 | 0.78635 | 0 | 1.5487 | 27.2398 | 27.2398 | 0.96461 | -1e-07 | 1.0945 | -1e-07 | -72.1353 | 107.8647 | 0.053557 | 0 | -23.5269 | 0

## LLL_max_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 4.283 | 4.283 | 0 | 9.2778 | 148.3662 | 148.3662 | 28.6163 | -1e-07 | 32.4685 | -1e-07 | -77.7798 | 102.2202 | 0.29171 | 0 | -29.1714 | 0
Line_1 | 0.78635 | 0.78635 | 0 | 1.5487 | 27.2398 | 27.2398 | 0.96461 | -1e-07 | 1.0945 | -1e-07 | -72.1353 | 107.8647 | 0.053557 | 0 | -23.5269 | 0
Line_2 | 0.78635 | 0.78635 | 0 | 1.5487 | 27.2398 | 27.2398 | 0.96461 | -1e-07 | 1.0945 | -1e-07 | -72.1353 | 107.8647 | 0.053557 | 0 | -23.5269 | 0

## LLL_max_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 1.0335 | 1.0335 | 0 | 2.2388 | 35.8013 | 35.8013 | 22.9639 | -21.2976 | 24.3455 | -22.4549 | -53.7095 | 126.2905 | 0.9348 | 0.86445 | -7.0367 | -7.1943
Line_1 | 0.18975 | 0.18975 | 0 | 0.37371 | 6.5731 | 6.5731 | 4.3529 | -4.2967 | 3.7818 | -3.7181 | -48.065 | 131.935 | 0.87726 | 0.86445 | -7.0807 | -7.1943
Line_2 | 0.18975 | 0.18975 | 0 | 0.37371 | 6.5731 | 6.5731 | 4.3529 | -4.2967 | 3.7818 | -3.7181 | -48.065 | 131.935 | 0.87726 | 0.86445 | -7.0807 | -7.1943

## LLL_max_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 1.0335 | 1.0335 | 0 | 2.2388 | 35.8013 | 35.8013 | 22.9639 | -21.2976 | 24.3455 | -22.4549 | -53.7095 | 126.2905 | 0.9348 | 0.86445 | -7.0367 | -7.1943
Line_1 | 0.18975 | 0.18975 | 0 | 0.37371 | 6.5731 | 6.5731 | 4.3529 | -4.2967 | 3.7818 | -3.7181 | -48.065 | 131.935 | 0.87726 | 0.86445 | -7.0807 | -7.1943
Line_2 | 0.18975 | 0.18975 | 0 | 0.37371 | 6.5731 | 6.5731 | 4.3529 | -4.2967 | 3.7818 | -3.7181 | -48.065 | 131.935 | 0.87726 | 0.86445 | -7.0807 | -7.1943

## LLL_min_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 3.6016 | 3.6016 | 0 | 6.8381 | 124.7634 | 124.7634 | 38.8525 | -1e-07 | 22.9597 | -1e-07 | -69.6723 | 110.3277 | 0.36172 | 0 | -39.0915 | 0
Line_1 | 0.77473 | 0.77473 | 0 | 1.4838 | 26.8374 | 26.8374 | 1.7977 | -1e-07 | 1.0624 | -1e-07 | -70.2749 | 109.7251 | 0.077808 | 0 | -39.6941 | 0
Line_2 | 0.77473 | 0.77473 | 0 | 1.4838 | 26.8374 | 26.8374 | 1.7977 | -1e-07 | 1.0624 | -1e-07 | -70.2749 | 109.7251 | 0.077808 | 0 | -39.6941 | 0

## LLL_min_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 3.6016 | 3.6016 | 0 | 6.8381 | 124.7634 | 124.7634 | 38.8525 | -1e-07 | 22.9597 | -1e-07 | -69.6723 | 110.3277 | 0.36172 | 0 | -39.0915 | 0
Line_1 | 0.77473 | 0.77473 | 0 | 1.4838 | 26.8374 | 26.8374 | 1.7977 | -1e-07 | 1.0624 | -1e-07 | -70.2749 | 109.7251 | 0.077808 | 0 | -39.6941 | 0
Line_2 | 0.77473 | 0.77473 | 0 | 1.4838 | 26.8374 | 26.8374 | 1.7977 | -1e-07 | 1.0624 | -1e-07 | -70.2749 | 109.7251 | 0.077808 | 0 | -39.6941 | 0

## LLL_min_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.88201 | 0.88201 | 0 | 1.6746 | 30.5537 | 30.5537 | 19.072 | -16.7419 | 18.0132 | -16.6363 | -50.7266 | 129.2734 | 0.85861 | 0.77248 | -7.3619 | -5.9079
Line_1 | 0.18973 | 0.18973 | 0 | 0.36337 | 6.5723 | 6.5723 | 3.6713 | -3.5635 | 3.68 | -3.6162 | -51.3292 | 128.6708 | 0.79091 | 0.77248 | -6.2614 | -5.9079
Line_2 | 0.18973 | 0.18973 | 0 | 0.36337 | 6.5723 | 6.5723 | 3.6713 | -3.5635 | 3.68 | -3.6162 | -51.3292 | 128.6708 | 0.79091 | 0.77248 | -6.2614 | -5.9079

## LLL_min_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.88201 | 0.88201 | 0 | 1.6746 | 30.5537 | 30.5537 | 19.072 | -16.7419 | 18.0132 | -16.6363 | -50.7266 | 129.2734 | 0.85861 | 0.77248 | -7.3619 | -5.9079
Line_1 | 0.18973 | 0.18973 | 0 | 0.36337 | 6.5723 | 6.5723 | 3.6713 | -3.5635 | 3.68 | -3.6162 | -51.3292 | 128.6708 | 0.79091 | 0.77248 | -6.2614 | -5.9079
Line_2 | 0.18973 | 0.18973 | 0 | 0.36337 | 6.5723 | 6.5723 | 3.6713 | -3.5635 | 3.68 | -3.6162 | -51.3292 | 128.6708 | 0.79091 | 0.77248 | -6.2614 | -5.9079

## LL_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.16904 | 3.6325 | 3.7862 | 0.16904 | 3.6325 | 3.7862 | 1.952 | 41.9444 | 43.7187 | 1.952 | 41.9444 | 43.7187 | -2.1001 | 29.9127 | -16.6546 | 2.115 | -23.0513 | 24.1088 | -0.52717 | 3.407 | 12.5637 | 0.54403 | 4.3781 | -4.1061 | 167.5964 | -167.2244 | 11.6872 | -12.4036 | 12.7756 | -168.3128 | 1.1093 | 0.71776 | 0.47719 | 1.1188 | 0.55939 | 0.55939 | 1.6876 | -160.7266 | 154.6575 | 2.0217 | -177.9783 | -177.9783
Line_1 | 0.084522 | 0.67821 | 0.60008 | 0.084522 | 0.67821 | 0.60008 | 0.97598 | 7.8313 | 6.9291 | 0.97598 | 7.8313 | 6.9291 | 1.0612 | 4.5909 | -3.6358 | -1.0575 | -4.3518 | 3.823 | 0.27623 | -0.232 | 0.85185 | -0.27202 | 0.50338 | -0.63939 | -12.4036 | -171.3801 | 11.5164 | 167.5964 | 8.6199 | -168.4836 | 1.1236 | 0.58698 | 0.53892 | 1.1188 | 0.55939 | 0.55939 | 2.1866 | -174.273 | 178.33 | 2.0217 | -177.9783 | -177.9783
Line_2 | 0.084522 | 0.67821 | 0.60008 | 0.084522 | 0.67821 | 0.60008 | 0.97598 | 7.8313 | 6.9291 | 0.97598 | 7.8313 | 6.9291 | 1.0612 | 4.5909 | -3.6358 | -1.0575 | -4.3518 | 3.823 | 0.27623 | -0.232 | 0.85185 | -0.27202 | 0.50338 | -0.63939 | -12.4036 | -171.3801 | 11.5164 | 167.5964 | 8.6199 | -168.4836 | 1.1236 | 0.58698 | 0.53892 | 1.1188 | 0.55939 | 0.55939 | 2.1866 | -174.273 | 178.33 | 2.0217 | -177.9783 | -177.9783

## LL_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.16904 | 3.6325 | 3.7862 | 0.16904 | 3.6325 | 3.7862 | 1.952 | 41.9444 | 43.7187 | 1.952 | 41.9444 | 43.7187 | -2.1001 | 29.9127 | -16.6546 | 2.115 | -23.0513 | 24.1088 | -0.52717 | 3.407 | 12.5637 | 0.54403 | 4.3781 | -4.1061 | 167.5964 | -167.2244 | 11.6872 | -12.4036 | 12.7756 | -168.3128 | 1.1093 | 0.71776 | 0.47719 | 1.1188 | 0.55939 | 0.55939 | 1.6876 | -160.7266 | 154.6575 | 2.0217 | -177.9783 | -177.9783
Line_1 | 0.084522 | 0.67821 | 0.60008 | 0.084522 | 0.67821 | 0.60008 | 0.97598 | 7.8313 | 6.9291 | 0.97598 | 7.8313 | 6.9291 | 1.0612 | 4.5909 | -3.6358 | -1.0575 | -4.3518 | 3.823 | 0.27623 | -0.232 | 0.85185 | -0.27202 | 0.50338 | -0.63939 | -12.4036 | -171.3801 | 11.5164 | 167.5964 | 8.6199 | -168.4836 | 1.1236 | 0.58698 | 0.53892 | 1.1188 | 0.55939 | 0.55939 | 2.1866 | -174.273 | 178.33 | 2.0217 | -177.9783 | -177.9783
Line_2 | 0.084522 | 0.67821 | 0.60008 | 0.084522 | 0.67821 | 0.60008 | 0.97598 | 7.8313 | 6.9291 | 0.97598 | 7.8313 | 6.9291 | 1.0612 | 4.5909 | -3.6358 | -1.0575 | -4.3518 | 3.823 | 0.27623 | -0.232 | 0.85185 | -0.27202 | 0.50338 | -0.63939 | -12.4036 | -171.3801 | 11.5164 | 167.5964 | 8.6199 | -168.4836 | 1.1236 | 0.58698 | 0.53892 | 1.1188 | 0.55939 | 0.55939 | 2.1866 | -174.273 | 178.33 | 2.0217 | -177.9783 | -177.9783

## LL_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.06764 | 1.4535 | 1.515 | 0.06764 | 1.4535 | 1.515 | 0.78104 | 16.7833 | 17.4932 | 0.78104 | 16.7833 | 17.4932 | -0.85077 | 16.2829 | 0.53583 | 0.85314 | -15.1844 | 0.65762 | 0.11259 | 3.3836 | 13.9285 | -0.10989 | -2.1372 | -12.5744 | -171.7585 | -146.5792 | 32.3323 | 8.2415 | 33.4208 | -147.6677 | 1.0988 | 0.99091 | 0.79681 | 1.1013 | 0.91365 | 0.7198 | 0.70258 | -134.8402 | 120.1292 | 0.90162 | -138.5676 | 125.3261
Line_1 | 0.03382 | 0.27137 | 0.24011 | 0.03382 | 0.27137 | 0.24011 | 0.39052 | 3.1335 | 2.7726 | 0.39052 | 3.1335 | 2.7726 | 0.42717 | 2.8369 | -0.08019 | -0.42657 | -2.7987 | 0.11017 | -0.054272 | 0.64687 | 2.0267 | 0.054947 | -0.60342 | -1.9926 | 8.2415 | -150.7349 | 32.1615 | -171.7585 | 29.2651 | -147.8385 | 1.1026 | 0.92858 | 0.73154 | 1.1013 | 0.91365 | 0.7198 | 1.0008 | -137.8902 | 124.4274 | 0.90162 | -138.5676 | 125.3261
Line_2 | 0.03382 | 0.27137 | 0.24011 | 0.03382 | 0.27137 | 0.24011 | 0.39052 | 3.1335 | 2.7726 | 0.39052 | 3.1335 | 2.7726 | 0.42717 | 2.8369 | -0.08019 | -0.42657 | -2.7987 | 0.11017 | -0.054272 | 0.64687 | 2.0267 | 0.054947 | -0.60342 | -1.9926 | 8.2415 | -150.7349 | 32.1615 | -171.7585 | 29.2651 | -147.8385 | 1.1026 | 0.92858 | 0.73154 | 1.1013 | 0.91365 | 0.7198 | 1.0008 | -137.8902 | 124.4274 | 0.90162 | -138.5676 | 125.3261

## LL_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.06764 | 1.4535 | 1.515 | 0.06764 | 1.4535 | 1.515 | 0.78104 | 16.7833 | 17.4932 | 0.78104 | 16.7833 | 17.4932 | -0.85077 | 16.2829 | 0.53583 | 0.85314 | -15.1844 | 0.65762 | 0.11259 | 3.3836 | 13.9285 | -0.10989 | -2.1372 | -12.5744 | -171.7585 | -146.5792 | 32.3323 | 8.2415 | 33.4208 | -147.6677 | 1.0988 | 0.99091 | 0.79681 | 1.1013 | 0.91365 | 0.7198 | 0.70258 | -134.8402 | 120.1292 | 0.90162 | -138.5676 | 125.3261
Line_1 | 0.03382 | 0.27137 | 0.24011 | 0.03382 | 0.27137 | 0.24011 | 0.39052 | 3.1335 | 2.7726 | 0.39052 | 3.1335 | 2.7726 | 0.42717 | 2.8369 | -0.08019 | -0.42657 | -2.7987 | 0.11017 | -0.054272 | 0.64687 | 2.0267 | 0.054947 | -0.60342 | -1.9926 | 8.2415 | -150.7349 | 32.1615 | -171.7585 | 29.2651 | -147.8385 | 1.1026 | 0.92858 | 0.73154 | 1.1013 | 0.91365 | 0.7198 | 1.0008 | -137.8902 | 124.4274 | 0.90162 | -138.5676 | 125.3261
Line_2 | 0.03382 | 0.27137 | 0.24011 | 0.03382 | 0.27137 | 0.24011 | 0.39052 | 3.1335 | 2.7726 | 0.39052 | 3.1335 | 2.7726 | 0.42717 | 2.8369 | -0.08019 | -0.42657 | -2.7987 | 0.11017 | -0.054272 | 0.64687 | 2.0267 | 0.054947 | -0.60342 | -1.9926 | 8.2415 | -150.7349 | 32.1615 | -171.7585 | 29.2651 | -147.8385 | 1.1026 | 0.92858 | 0.73154 | 1.1013 | 0.91365 | 0.7198 | 1.0008 | -137.8902 | 124.4274 | 0.90162 | -138.5676 | 125.3261

## LL_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.15892 | 3.0486 | 3.19 | 0.15892 | 3.0486 | 3.19 | 1.8351 | 35.2024 | 36.8347 | 1.8351 | 35.2024 | 36.8347 | -1.8248 | 26.2892 | -7.7754 | 1.8501 | -17.01 | 17.935 | -0.28017 | -0.30937 | 11.6491 | 0.29507 | 5.7929 | -5.6453 | 173.1413 | -158.99 | 19.6756 | -6.8587 | 21.01 | -160.3244 | 1.0061 | 0.74685 | 0.38023 | 1.0209 | 0.51046 | 0.51046 | 1.8699 | -159.6642 | 143.3972 | 2.2033 | -177.7967 | -177.7967
Line_1 | 0.079461 | 0.67052 | 0.59523 | 0.079461 | 0.67052 | 0.59523 | 0.91753 | 7.7425 | 6.8731 | 0.91753 | 7.7425 | 6.8731 | 0.93133 | 4.3581 | -3.093 | -0.92503 | -3.9093 | 3.4467 | 0.15126 | -0.3159 | 0.86397 | -0.14754 | 0.58117 | -0.65493 | -6.8587 | -169.3408 | 12.9622 | 173.1413 | 10.6592 | -167.0378 | 1.0283 | 0.56436 | 0.46725 | 1.0209 | 0.51046 | 0.51046 | 2.3664 | -173.4866 | 177.3556 | 2.2033 | -177.7967 | -177.7967
Line_2 | 0.079461 | 0.67052 | 0.59523 | 0.079461 | 0.67052 | 0.59523 | 0.91753 | 7.7425 | 6.8731 | 0.91753 | 7.7425 | 6.8731 | 0.93133 | 4.3581 | -3.093 | -0.92503 | -3.9093 | 3.4467 | 0.15126 | -0.3159 | 0.86397 | -0.14754 | 0.58117 | -0.65493 | -6.8587 | -169.3408 | 12.9622 | 173.1413 | 10.6592 | -167.0378 | 1.0283 | 0.56436 | 0.46725 | 1.0209 | 0.51046 | 0.51046 | 2.3664 | -173.4866 | 177.3556 | 2.2033 | -177.7967 | -177.7967

## LL_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.15892 | 3.0486 | 3.19 | 0.15892 | 3.0486 | 3.19 | 1.8351 | 35.2024 | 36.8347 | 1.8351 | 35.2024 | 36.8347 | -1.8248 | 26.2892 | -7.7754 | 1.8501 | -17.01 | 17.935 | -0.28017 | -0.30937 | 11.6491 | 0.29507 | 5.7929 | -5.6453 | 173.1413 | -158.99 | 19.6756 | -6.8587 | 21.01 | -160.3244 | 1.0061 | 0.74685 | 0.38023 | 1.0209 | 0.51046 | 0.51046 | 1.8699 | -159.6642 | 143.3972 | 2.2033 | -177.7967 | -177.7967
Line_1 | 0.079461 | 0.67052 | 0.59523 | 0.079461 | 0.67052 | 0.59523 | 0.91753 | 7.7425 | 6.8731 | 0.91753 | 7.7425 | 6.8731 | 0.93133 | 4.3581 | -3.093 | -0.92503 | -3.9093 | 3.4467 | 0.15126 | -0.3159 | 0.86397 | -0.14754 | 0.58117 | -0.65493 | -6.8587 | -169.3408 | 12.9622 | 173.1413 | 10.6592 | -167.0378 | 1.0283 | 0.56436 | 0.46725 | 1.0209 | 0.51046 | 0.51046 | 2.3664 | -173.4866 | 177.3556 | 2.2033 | -177.7967 | -177.7967
Line_2 | 0.079461 | 0.67052 | 0.59523 | 0.079461 | 0.67052 | 0.59523 | 0.91753 | 7.7425 | 6.8731 | 0.91753 | 7.7425 | 6.8731 | 0.93133 | 4.3581 | -3.093 | -0.92503 | -3.9093 | 3.4467 | 0.15126 | -0.3159 | 0.86397 | -0.14754 | 0.58117 | -0.65493 | -6.8587 | -169.3408 | 12.9622 | 173.1413 | 10.6592 | -167.0378 | 1.0283 | 0.56436 | 0.46725 | 1.0209 | 0.51046 | 0.51046 | 2.3664 | -173.4866 | 177.3556 | 2.2033 | -177.7967 | -177.7967

## LL_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.064112 | 1.2299 | 1.2869 | 0.064112 | 1.2299 | 1.2869 | 0.7403 | 14.2014 | 14.8599 | 0.7403 | 14.2014 | 14.8599 | -0.73023 | 12.9507 | 1.4179 | 0.73434 | -11.4405 | 0.23553 | 0.11457 | 1.7681 | 10.7707 | -0.11214 | -0.87564 | -9.7936 | -170.3183 | -142.4496 | 36.216 | 9.6817 | 37.5504 | -143.784 | 0.99846 | 0.92039 | 0.73107 | 1.0034 | 0.80795 | 0.65925 | 0.76513 | -134.6755 | 118.7162 | 0.99898 | -138.0728 | 127.5936
Line_1 | 0.032056 | 0.2705 | 0.24013 | 0.032056 | 0.2705 | 0.24013 | 0.37015 | 3.1235 | 2.7727 | 0.37015 | 3.1235 | 2.7727 | 0.36819 | 2.5137 | -0.19971 | -0.36717 | -2.4407 | 0.25728 | -0.055465 | 0.68473 | 1.8438 | 0.056071 | -0.64156 | -1.8097 | 9.6817 | -152.8004 | 29.5025 | -170.3183 | 27.1996 | -150.4975 | 1.0059 | 0.83411 | 0.66885 | 1.0034 | 0.80795 | 0.65925 | 1.115 | -137.563 | 125.6845 | 0.99898 | -138.0728 | 127.5936
Line_2 | 0.032056 | 0.2705 | 0.24013 | 0.032056 | 0.2705 | 0.24013 | 0.37015 | 3.1235 | 2.7727 | 0.37015 | 3.1235 | 2.7727 | 0.36819 | 2.5137 | -0.19971 | -0.36717 | -2.4407 | 0.25728 | -0.055465 | 0.68473 | 1.8438 | 0.056071 | -0.64156 | -1.8097 | 9.6817 | -152.8004 | 29.5025 | -170.3183 | 27.1996 | -150.4975 | 1.0059 | 0.83411 | 0.66885 | 1.0034 | 0.80795 | 0.65925 | 1.115 | -137.563 | 125.6845 | 0.99898 | -138.0728 | 127.5936

## LL_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.064112 | 1.2299 | 1.2869 | 0.064112 | 1.2299 | 1.2869 | 0.7403 | 14.2014 | 14.8599 | 0.7403 | 14.2014 | 14.8599 | -0.73023 | 12.9507 | 1.4179 | 0.73434 | -11.4405 | 0.23553 | 0.11457 | 1.7681 | 10.7707 | -0.11214 | -0.87564 | -9.7936 | -170.3183 | -142.4496 | 36.216 | 9.6817 | 37.5504 | -143.784 | 0.99846 | 0.92039 | 0.73107 | 1.0034 | 0.80795 | 0.65925 | 0.76513 | -134.6755 | 118.7162 | 0.99898 | -138.0728 | 127.5936
Line_1 | 0.032056 | 0.2705 | 0.24013 | 0.032056 | 0.2705 | 0.24013 | 0.37015 | 3.1235 | 2.7727 | 0.37015 | 3.1235 | 2.7727 | 0.36819 | 2.5137 | -0.19971 | -0.36717 | -2.4407 | 0.25728 | -0.055465 | 0.68473 | 1.8438 | 0.056071 | -0.64156 | -1.8097 | 9.6817 | -152.8004 | 29.5025 | -170.3183 | 27.1996 | -150.4975 | 1.0059 | 0.83411 | 0.66885 | 1.0034 | 0.80795 | 0.65925 | 1.115 | -137.563 | 125.6845 | 0.99898 | -138.0728 | 127.5936
Line_2 | 0.032056 | 0.2705 | 0.24013 | 0.032056 | 0.2705 | 0.24013 | 0.37015 | 3.1235 | 2.7727 | 0.37015 | 3.1235 | 2.7727 | 0.36819 | 2.5137 | -0.19971 | -0.36717 | -2.4407 | 0.25728 | -0.055465 | 0.68473 | 1.8438 | 0.056071 | -0.64156 | -1.8097 | 9.6817 | -152.8004 | 29.5025 | -170.3183 | 27.1996 | -150.4975 | 1.0059 | 0.83411 | 0.66885 | 1.0034 | 0.80795 | 0.65925 | 1.115 | -137.563 | 125.6845 | 0.99898 | -138.0728 | 127.5936

## LG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 3.8476 | 0.55014 | 0.36881 | 3.8467 | 0.5513 | 0.36995 | 44.4284 | 6.3524 | 4.2587 | 44.4177 | 6.3659 | 4.2718 | 20.0427 | -6.1352 | 3.2727 | 2.9103e-10 | 5.6502 | -3.4896 | 15.0738 | 0.46533 | 3.1616 | -2.3209e-10 | -2.166 | -4.3941 | -62.4847 | 73.9363 | 66.5703 | 117.526 | -106.051 | -113.3879 | 0.56447 | 0.96858 | 1.0685 | 0 | 0.95056 | 1.3135 | -25.5385 | -110.401 | 110.581 | 0 | -127.0248 | 118.1568
Line_1 | 0.90994 | 0.27749 | 0.18677 | 0.90822 | 0.27565 | 0.18497 | 10.5071 | 3.2041 | 2.1566 | 10.4872 | 3.1829 | 2.1359 | 1.7516 | 3.2235 | -1.5401 | 8.1229e-11 | -2.8251 | 1.7448 | 0.61259 | -0.82806 | -2.0187 | -3.3556e-11 | 1.083 | 2.1971 | -78.6414 | -106.0088 | -113.2539 | 101.4004 | 73.949 | 66.6121 | 0.17661 | 1.0387 | 1.1773 | 0 | 0.95056 | 1.3135 | -59.3652 | -120.4156 | 119.4054 | 0 | -127.0248 | 118.1568
Line_2 | 0.90994 | 0.27749 | 0.18677 | 0.90822 | 0.27565 | 0.18497 | 10.5071 | 3.2041 | 2.1566 | 10.4872 | 3.1829 | 2.1359 | 1.7516 | 3.2235 | -1.5401 | 8.1229e-11 | -2.8251 | 1.7448 | 0.61259 | -0.82806 | -2.0187 | -3.3556e-11 | 1.083 | 2.1971 | -78.6414 | -106.0088 | -113.2539 | 101.4004 | 73.949 | 66.6121 | 0.17661 | 1.0387 | 1.1773 | 0 | 0.95056 | 1.3135 | -59.3652 | -120.4156 | 119.4054 | 0 | -127.0248 | 118.1568

## LG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 3.8476 | 0.55014 | 0.36881 | 3.8467 | 0.5513 | 0.36995 | 44.4284 | 6.3524 | 4.2587 | 44.4177 | 6.3659 | 4.2718 | 20.0427 | -6.1352 | 3.2727 | 2.9103e-10 | 5.6502 | -3.4896 | 15.0738 | 0.46533 | 3.1616 | -2.3209e-10 | -2.166 | -4.3941 | -62.4847 | 73.9363 | 66.5703 | 117.526 | -106.051 | -113.3879 | 0.56447 | 0.96858 | 1.0685 | 0 | 0.95056 | 1.3135 | -25.5385 | -110.401 | 110.581 | 0 | -127.0248 | 118.1568
Line_1 | 0.90994 | 0.27749 | 0.18677 | 0.90822 | 0.27565 | 0.18497 | 10.5071 | 3.2041 | 2.1566 | 10.4872 | 3.1829 | 2.1359 | 1.7516 | 3.2235 | -1.5401 | 8.1229e-11 | -2.8251 | 1.7448 | 0.61259 | -0.82806 | -2.0187 | -3.3556e-11 | 1.083 | 2.1971 | -78.6414 | -106.0088 | -113.2539 | 101.4004 | 73.949 | 66.6121 | 0.17661 | 1.0387 | 1.1773 | 0 | 0.95056 | 1.3135 | -59.3652 | -120.4156 | 119.4054 | 0 | -127.0248 | 118.1568
Line_2 | 0.90994 | 0.27749 | 0.18677 | 0.90822 | 0.27565 | 0.18497 | 10.5071 | 3.2041 | 2.1566 | 10.4872 | 3.1829 | 2.1359 | 1.7516 | 3.2235 | -1.5401 | 8.1229e-11 | -2.8251 | 1.7448 | 0.61259 | -0.82806 | -2.0187 | -3.3556e-11 | 1.083 | 2.1971 | -78.6414 | -106.0088 | -113.2539 | 101.4004 | 73.949 | 66.6121 | 0.17661 | 1.0387 | 1.1773 | 0 | 0.95056 | 1.3135 | -59.3652 | -120.4156 | 119.4054 | 0 | -127.0248 | 118.1568

## LG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.94611 | 0.13528 | 0.090689 | 0.94588 | 0.13556 | 0.090968 | 10.9247 | 1.562 | 1.0472 | 10.9221 | 1.5653 | 1.0504 | 8.3019 | -1.4316 | 0.95831 | -7.0894 | 1.4043 | -0.97411 | 6.8302 | 0.81485 | 0.64448 | -5.916 | -0.91957 | -0.71984 | -45.2842 | 91.1368 | 83.7708 | 134.7265 | -88.8505 | -96.1874 | 0.98405 | 1.0546 | 1.1028 | 0.84541 | 1.0724 | 1.1531 | -5.8392 | -118.5114 | 117.692 | -5.4291 | -122.0678 | 120.276
Line_1 | 0.22375 | 0.068232 | 0.045926 | 0.22333 | 0.067781 | 0.045484 | 2.5836 | 0.78788 | 0.5303 | 2.5787 | 0.78267 | 0.52521 | 1.3269 | 0.7295 | -0.47891 | -1.22 | -0.70217 | 0.48705 | 1.8481 | -0.44739 | -0.35044 | -1.8067 | 0.45979 | 0.35992 | -61.4409 | -88.8083 | -96.0534 | 118.6009 | 91.1495 | 83.8126 | 0.88059 | 1.0862 | 1.119 | 0.84541 | 1.0724 | 1.1531 | -7.1193 | -120.3285 | 120.1408 | -5.4291 | -122.0678 | 120.276
Line_2 | 0.22375 | 0.068232 | 0.045926 | 0.22333 | 0.067781 | 0.045484 | 2.5836 | 0.78788 | 0.5303 | 2.5787 | 0.78267 | 0.52521 | 1.3269 | 0.7295 | -0.47891 | -1.22 | -0.70217 | 0.48705 | 1.8481 | -0.44739 | -0.35044 | -1.8067 | 0.45979 | 0.35992 | -61.4409 | -88.8083 | -96.0534 | 118.6009 | 91.1495 | 83.8126 | 0.88059 | 1.0862 | 1.119 | 0.84541 | 1.0724 | 1.1531 | -7.1193 | -120.3285 | 120.1408 | -5.4291 | -122.0678 | 120.276

## LG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.94611 | 0.13528 | 0.090689 | 0.94588 | 0.13556 | 0.090968 | 10.9247 | 1.562 | 1.0472 | 10.9221 | 1.5653 | 1.0504 | 8.3019 | -1.4316 | 0.95831 | -7.0894 | 1.4043 | -0.97411 | 6.8302 | 0.81485 | 0.64448 | -5.916 | -0.91957 | -0.71984 | -45.2842 | 91.1368 | 83.7708 | 134.7265 | -88.8505 | -96.1874 | 0.98405 | 1.0546 | 1.1028 | 0.84541 | 1.0724 | 1.1531 | -5.8392 | -118.5114 | 117.692 | -5.4291 | -122.0678 | 120.276
Line_1 | 0.22375 | 0.068232 | 0.045926 | 0.22333 | 0.067781 | 0.045484 | 2.5836 | 0.78788 | 0.5303 | 2.5787 | 0.78267 | 0.52521 | 1.3269 | 0.7295 | -0.47891 | -1.22 | -0.70217 | 0.48705 | 1.8481 | -0.44739 | -0.35044 | -1.8067 | 0.45979 | 0.35992 | -61.4409 | -88.8083 | -96.0534 | 118.6009 | 91.1495 | 83.8126 | 0.88059 | 1.0862 | 1.119 | 0.84541 | 1.0724 | 1.1531 | -7.1193 | -120.3285 | 120.1408 | -5.4291 | -122.0678 | 120.276
Line_2 | 0.22375 | 0.068232 | 0.045926 | 0.22333 | 0.067781 | 0.045484 | 2.5836 | 0.78788 | 0.5303 | 2.5787 | 0.78267 | 0.52521 | 1.3269 | 0.7295 | -0.47891 | -1.22 | -0.70217 | 0.48705 | 1.8481 | -0.44739 | -0.35044 | -1.8067 | 0.45979 | 0.35992 | -61.4409 | -88.8083 | -96.0534 | 118.6009 | 91.1495 | 83.8126 | 0.88059 | 1.0862 | 1.119 | 0.84541 | 1.0724 | 1.1531 | -7.1193 | -120.3285 | 120.1408 | -5.4291 | -122.0678 | 120.276

## LG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 2.8071 | 0.53547 | 0.37207 | 2.8064 | 0.53656 | 0.37316 | 32.4139 | 6.1831 | 4.2963 | 32.4056 | 6.1957 | 4.3088 | 19.0243 | -4.505 | 4.2404 | -8.3472e-11 | 3.3744 | -5.1155 | 8.9115 | 2.7672 | 0.90474 | -3.9868e-12 | -4.38 | -2.0617 | -50.937 | 98.7634 | 99.1844 | 129.0819 | -81.2832 | -80.8838 | 0.64812 | 0.85509 | 1.0092 | 0 | 0.89241 | 1.28 | -25.8374 | -112.7971 | 111.2285 | 0 | -133.6718 | 121.067
Line_1 | 0.87188 | 0.27001 | 0.18831 | 0.87029 | 0.26828 | 0.18658 | 10.0677 | 3.1178 | 2.1744 | 10.0493 | 3.0978 | 2.1544 | 3.1164 | 2.4742 | -2.0547 | -2.4364e-11 | -1.6872 | 2.5577 | 0.60153 | -1.9455 | -0.87983 | -8.8311e-12 | 2.19 | 1.0308 | -68.1598 | -81.371 | -81.0135 | 111.8926 | 98.7168 | 99.1162 | 0.31526 | 1.0095 | 1.0279 | 0 | 0.89241 | 1.28 | -57.2348 | -119.5499 | 122.1678 | 0 | -133.6718 | 121.067
Line_2 | 0.87188 | 0.27001 | 0.18831 | 0.87029 | 0.26828 | 0.18658 | 10.0677 | 3.1178 | 2.1744 | 10.0493 | 3.0978 | 2.1544 | 3.1164 | 2.4742 | -2.0547 | -2.4364e-11 | -1.6872 | 2.5577 | 0.60153 | -1.9455 | -0.87983 | -8.8311e-12 | 2.19 | 1.0308 | -68.1598 | -81.371 | -81.0135 | 111.8926 | 98.7168 | 99.1162 | 0.31526 | 1.0095 | 1.0279 | 0 | 0.89241 | 1.28 | -57.2348 | -119.5499 | 122.1678 | 0 | -133.6718 | 121.067

## LG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 2.8071 | 0.53547 | 0.37207 | 2.8064 | 0.53656 | 0.37316 | 32.4139 | 6.1831 | 4.2963 | 32.4056 | 6.1957 | 4.3088 | 19.0243 | -4.505 | 4.2404 | -8.3472e-11 | 3.3744 | -5.1155 | 8.9115 | 2.7672 | 0.90474 | -3.9868e-12 | -4.38 | -2.0617 | -50.937 | 98.7634 | 99.1844 | 129.0819 | -81.2832 | -80.8838 | 0.64812 | 0.85509 | 1.0092 | 0 | 0.89241 | 1.28 | -25.8374 | -112.7971 | 111.2285 | 0 | -133.6718 | 121.067
Line_1 | 0.87188 | 0.27001 | 0.18831 | 0.87029 | 0.26828 | 0.18658 | 10.0677 | 3.1178 | 2.1744 | 10.0493 | 3.0978 | 2.1544 | 3.1164 | 2.4742 | -2.0547 | -2.4364e-11 | -1.6872 | 2.5577 | 0.60153 | -1.9455 | -0.87983 | -8.8311e-12 | 2.19 | 1.0308 | -68.1598 | -81.371 | -81.0135 | 111.8926 | 98.7168 | 99.1162 | 0.31526 | 1.0095 | 1.0279 | 0 | 0.89241 | 1.28 | -57.2348 | -119.5499 | 122.1678 | 0 | -133.6718 | 121.067
Line_2 | 0.87188 | 0.27001 | 0.18831 | 0.87029 | 0.26828 | 0.18658 | 10.0677 | 3.1178 | 2.1744 | 10.0493 | 3.0978 | 2.1544 | 3.1164 | 2.4742 | -2.0547 | -2.4364e-11 | -1.6872 | 2.5577 | 0.60153 | -1.9455 | -0.87983 | -8.8311e-12 | 2.19 | 1.0308 | -68.1598 | -81.371 | -81.0135 | 111.8926 | 98.7168 | 99.1162 | 0.31526 | 1.0095 | 1.0279 | 0 | 0.89241 | 1.28 | -57.2348 | -119.5499 | 122.1678 | 0 | -133.6718 | 121.067

## LG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.75107 | 0.14327 | 0.099549 | 0.75087 | 0.14356 | 0.099841 | 8.6726 | 1.6543 | 1.1495 | 8.6703 | 1.6577 | 1.1529 | 6.368 | -1.0858 | 1.1419 | -5.0061 | 1.0072 | -1.2069 | 4.6133 | 1.149 | 0.18754 | -3.9727 | -1.2658 | -0.27173 | -41.7689 | 107.9316 | 108.3525 | 138.2501 | -72.115 | -71.7157 | 0.9067 | 0.95562 | 1.0067 | 0.73709 | 0.97583 | 1.073 | -5.8473 | -118.6896 | 117.6795 | -3.3156 | -123.6063 | 120.9731
Line_1 | 0.23328 | 0.072244 | 0.050383 | 0.23285 | 0.071781 | 0.04992 | 2.6937 | 0.8342 | 0.58177 | 2.6888 | 0.82885 | 0.57643 | 1.3427 | 0.56314 | -0.57117 | -1.119 | -0.50359 | 0.60343 | 1.6828 | -0.61789 | -0.12659 | -1.6357 | 0.63291 | 0.13586 | -58.9917 | -72.2028 | -71.8453 | 121.0607 | 107.885 | 108.2843 | 0.79921 | 1.0022 | 1.0056 | 0.73709 | 0.97583 | 1.073 | -7.5768 | -119.8572 | 120.6512 | -3.3156 | -123.6063 | 120.9731
Line_2 | 0.23328 | 0.072244 | 0.050383 | 0.23285 | 0.071781 | 0.04992 | 2.6937 | 0.8342 | 0.58177 | 2.6888 | 0.82885 | 0.57643 | 1.3427 | 0.56314 | -0.57117 | -1.119 | -0.50359 | 0.60343 | 1.6828 | -0.61789 | -0.12659 | -1.6357 | 0.63291 | 0.13586 | -58.9917 | -72.2028 | -71.8453 | 121.0607 | 107.885 | 108.2843 | 0.79921 | 1.0022 | 1.0056 | 0.73709 | 0.97583 | 1.073 | -7.5768 | -119.8572 | 120.6512 | -3.3156 | -123.6063 | 120.9731

## LG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.75107 | 0.14327 | 0.099549 | 0.75087 | 0.14356 | 0.099841 | 8.6726 | 1.6543 | 1.1495 | 8.6703 | 1.6577 | 1.1529 | 6.368 | -1.0858 | 1.1419 | -5.0061 | 1.0072 | -1.2069 | 4.6133 | 1.149 | 0.18754 | -3.9727 | -1.2658 | -0.27173 | -41.7689 | 107.9316 | 108.3525 | 138.2501 | -72.115 | -71.7157 | 0.9067 | 0.95562 | 1.0067 | 0.73709 | 0.97583 | 1.073 | -5.8473 | -118.6896 | 117.6795 | -3.3156 | -123.6063 | 120.9731
Line_1 | 0.23328 | 0.072244 | 0.050383 | 0.23285 | 0.071781 | 0.04992 | 2.6937 | 0.8342 | 0.58177 | 2.6888 | 0.82885 | 0.57643 | 1.3427 | 0.56314 | -0.57117 | -1.119 | -0.50359 | 0.60343 | 1.6828 | -0.61789 | -0.12659 | -1.6357 | 0.63291 | 0.13586 | -58.9917 | -72.2028 | -71.8453 | 121.0607 | 107.885 | 108.2843 | 0.79921 | 1.0022 | 1.0056 | 0.73709 | 0.97583 | 1.073 | -7.5768 | -119.8572 | 120.6512 | -3.3156 | -123.6063 | 120.9731
Line_2 | 0.23328 | 0.072244 | 0.050383 | 0.23285 | 0.071781 | 0.04992 | 2.6937 | 0.8342 | 0.58177 | 2.6888 | 0.82885 | 0.57643 | 1.3427 | 0.56314 | -0.57117 | -1.119 | -0.50359 | 0.60343 | 1.6828 | -0.61789 | -0.12659 | -1.6357 | 0.63291 | 0.13586 | -58.9917 | -72.2028 | -71.8453 | 121.0607 | 107.885 | 108.2843 | 0.79921 | 1.0022 | 1.0056 | 0.73709 | 0.97583 | 1.073 | -7.5768 | -119.8572 | 120.6512 | -3.3156 | -123.6063 | 120.9731

## LLG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.45932 | 4.7616 | 3.1925 | 0.46029 | 4.7614 | 3.1918 | 5.3038 | 54.9819 | 36.8634 | 5.315 | 54.9803 | 36.8557 | -2.15 | 27.447 | 0.046792 | 2.4031 | 1.6176e-10 | 1.4136e-10 | 4.4804 | 8.1441 | 15.7557 | -5.9572 | -2.0232e-10 | -9.8854e-11 | -118.6381 | 175.0911 | 38.2784 | 61.4329 | -4.8955 | -141.7378 | 0.93698 | 0.52071 | 0.42741 | 1.2086 | 0 | 0 | -3.003 | -168.3822 | 128.1083 | -6.5982 | 0 | 0
Line_1 | 0.23167 | 0.90799 | 0.78579 | 0.23014 | 0.90719 | 0.78433 | 2.6751 | 10.4846 | 9.0735 | 2.6575 | 10.4753 | 9.0567 | 1.4026 | 1.45 | 0.85087 | -1.2016 | 4.2026e-11 | 2.4904e-11 | -2.6991 | -0.27302 | 1.33 | 2.9786 | -2.5878e-11 | -3.43e-11 | 61.6575 | 155.2717 | 57.3881 | -118.5671 | -24.6284 | -122.686 | 1.1371 | 0.14073 | 0.17401 | 1.2086 | 0 | 0 | -0.88347 | 144.6087 | 114.7782 | -6.5982 | 0 | 0
Line_2 | 0.23167 | 0.90799 | 0.78579 | 0.23014 | 0.90719 | 0.78433 | 2.6751 | 10.4846 | 9.0735 | 2.6575 | 10.4753 | 9.0567 | 1.4026 | 1.45 | 0.85087 | -1.2016 | 4.2026e-11 | 2.4904e-11 | -2.6991 | -0.27302 | 1.33 | 2.9786 | -2.5878e-11 | -3.43e-11 | 61.6575 | 155.2717 | 57.3881 | -118.5671 | -24.6284 | -122.686 | 1.1371 | 0.14073 | 0.17401 | 1.2086 | 0 | 0 | -0.88347 | 144.6087 | 114.7782 | -6.5982 | 0 | 0

## LLG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.45932 | 4.7616 | 3.1925 | 0.46029 | 4.7614 | 3.1918 | 5.3038 | 54.9819 | 36.8634 | 5.315 | 54.9803 | 36.8557 | -2.15 | 27.447 | 0.046792 | 2.4031 | 1.6176e-10 | 1.4136e-10 | 4.4804 | 8.1441 | 15.7557 | -5.9572 | -2.0232e-10 | -9.8854e-11 | -118.6381 | 175.0911 | 38.2784 | 61.4329 | -4.8955 | -141.7378 | 0.93698 | 0.52071 | 0.42741 | 1.2086 | 0 | 0 | -3.003 | -168.3822 | 128.1083 | -6.5982 | 0 | 0
Line_1 | 0.23167 | 0.90799 | 0.78579 | 0.23014 | 0.90719 | 0.78433 | 2.6751 | 10.4846 | 9.0735 | 2.6575 | 10.4753 | 9.0567 | 1.4026 | 1.45 | 0.85087 | -1.2016 | 4.2026e-11 | 2.4904e-11 | -2.6991 | -0.27302 | 1.33 | 2.9786 | -2.5878e-11 | -3.43e-11 | 61.6575 | 155.2717 | 57.3881 | -118.5671 | -24.6284 | -122.686 | 1.1371 | 0.14073 | 0.17401 | 1.2086 | 0 | 0 | -0.88347 | 144.6087 | 114.7782 | -6.5982 | 0 | 0
Line_2 | 0.23167 | 0.90799 | 0.78579 | 0.23014 | 0.90719 | 0.78433 | 2.6751 | 10.4846 | 9.0735 | 2.6575 | 10.4753 | 9.0567 | 1.4026 | 1.45 | 0.85087 | -1.2016 | 4.2026e-11 | 2.4904e-11 | -2.6991 | -0.27302 | 1.33 | 2.9786 | -2.5878e-11 | -3.43e-11 | 61.6575 | 155.2717 | 57.3881 | -118.5671 | -24.6284 | -122.686 | 1.1371 | 0.14073 | 0.17401 | 1.2086 | 0 | 0 | -0.88347 | 144.6087 | 114.7782 | -6.5982 | 0 | 0

## LLG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.12573 | 1.0785 | 0.9045 | 0.12598 | 1.0785 | 0.90427 | 1.4518 | 12.4531 | 10.4442 | 1.4547 | 12.4534 | 10.4416 | -0.44539 | 9.9376 | 5.9526 | 0.45763 | -8.5322 | -5.6735 | 1.4712 | 7.1919 | 7.7108 | -1.5742 | -6.9815 | -6.4584 | -107.826 | -164.5644 | 63.7074 | 72.2334 | 15.4504 | -116.3031 | 1.0588 | 0.98506 | 0.93268 | 1.127 | 0.88526 | 0.82329 | -0.9822 | -128.6708 | 116.0399 | -1.5572 | -125.2576 | 112.3986
Line_1 | 0.06338 | 0.19393 | 0.22335 | 0.062989 | 0.19381 | 0.22295 | 0.73185 | 2.2394 | 2.579 | 0.72733 | 2.2379 | 2.5743 | 0.24268 | 1.0213 | 1.7605 | -0.22881 | -0.95848 | -1.682 | -0.77236 | 1.7097 | 1.3813 | 0.7871 | -1.7338 | -1.2895 | 72.4218 | 173.5513 | 74.9708 | -107.7666 | -6.3232 | -105.0779 | 1.1062 | 0.88932 | 0.86767 | 1.127 | 0.88526 | 0.82329 | -0.13523 | -127.3011 | 113.0879 | -1.5572 | -125.2576 | 112.3986
Line_2 | 0.06338 | 0.19393 | 0.22335 | 0.062989 | 0.19381 | 0.22295 | 0.73185 | 2.2394 | 2.579 | 0.72733 | 2.2379 | 2.5743 | 0.24268 | 1.0213 | 1.7605 | -0.22881 | -0.95848 | -1.682 | -0.77236 | 1.7097 | 1.3813 | 0.7871 | -1.7338 | -1.2895 | 72.4218 | 173.5513 | 74.9708 | -107.7666 | -6.3232 | -105.0779 | 1.1062 | 0.88932 | 0.86767 | 1.127 | 0.88526 | 0.82329 | -0.13523 | -127.3011 | 113.0879 | -1.5572 | -125.2576 | 112.3986

## LLG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.12573 | 1.0785 | 0.9045 | 0.12598 | 1.0785 | 0.90427 | 1.4518 | 12.4531 | 10.4442 | 1.4547 | 12.4534 | 10.4416 | -0.44539 | 9.9376 | 5.9526 | 0.45763 | -8.5322 | -5.6735 | 1.4712 | 7.1919 | 7.7108 | -1.5742 | -6.9815 | -6.4584 | -107.826 | -164.5644 | 63.7074 | 72.2334 | 15.4504 | -116.3031 | 1.0588 | 0.98506 | 0.93268 | 1.127 | 0.88526 | 0.82329 | -0.9822 | -128.6708 | 116.0399 | -1.5572 | -125.2576 | 112.3986
Line_1 | 0.06338 | 0.19393 | 0.22335 | 0.062989 | 0.19381 | 0.22295 | 0.73185 | 2.2394 | 2.579 | 0.72733 | 2.2379 | 2.5743 | 0.24268 | 1.0213 | 1.7605 | -0.22881 | -0.95848 | -1.682 | -0.77236 | 1.7097 | 1.3813 | 0.7871 | -1.7338 | -1.2895 | 72.4218 | 173.5513 | 74.9708 | -107.7666 | -6.3232 | -105.0779 | 1.1062 | 0.88932 | 0.86767 | 1.127 | 0.88526 | 0.82329 | -0.13523 | -127.3011 | 113.0879 | -1.5572 | -125.2576 | 112.3986
Line_2 | 0.06338 | 0.19393 | 0.22335 | 0.062989 | 0.19381 | 0.22295 | 0.73185 | 2.2394 | 2.579 | 0.72733 | 2.2379 | 2.5743 | 0.24268 | 1.0213 | 1.7605 | -0.22881 | -0.95848 | -1.682 | -0.77236 | 1.7097 | 1.3813 | 0.7871 | -1.7338 | -1.2895 | 72.4218 | 173.5513 | 74.9708 | -107.7666 | -6.3232 | -105.0779 | 1.1062 | 0.88932 | 0.86767 | 1.127 | 0.88526 | 0.82329 | -0.13523 | -127.3011 | 113.0879 | -1.5572 | -125.2576 | 112.3986

## LLG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.35192 | 3.7855 | 2.6664 | 0.35296 | 3.7856 | 2.6658 | 4.0636 | 43.7109 | 30.7889 | 4.0756 | 43.7125 | 30.7816 | 0.19312 | 27.1861 | 1.3227 | -0.42511 | -1.4343e-10 | -5.6657e-11 | 3.6248 | 2.5633 | 12.3285 | -4.834 | -9.1819e-11 | -1.0671e-10 | -91.0108 | -172.0282 | 38.0132 | 88.9934 | 7.9873 | -142.0044 | 0.89327 | 0.62471 | 0.40272 | 1.1907 | 0 | 0 | -4.0605 | -166.642 | 121.8897 | -6.0323 | 0 | 0
Line_1 | 0.17802 | 0.94611 | 0.64413 | 0.17648 | 0.94546 | 0.6429 | 2.0556 | 10.9247 | 7.4378 | 2.0378 | 10.9172 | 7.4235 | 0.13903 | 2.7356 | 0.98912 | 0.21255 | -2.3568e-11 | -2.2598e-11 | -2.1471 | -0.77138 | 1.6678 | 2.417 | -3.5406e-11 | -1.8393e-11 | 89.0784 | 164.1773 | 60.9722 | -91.0066 | -15.7363 | -119.1132 | 1.0467 | 0.26017 | 0.2607 | 1.1907 | 0 | 0 | 2.7833 | 148.43 | 120.3008 | -6.0323 | 0 | 0
Line_2 | 0.17802 | 0.94611 | 0.64413 | 0.17648 | 0.94546 | 0.6429 | 2.0556 | 10.9247 | 7.4378 | 2.0378 | 10.9172 | 7.4235 | 0.13903 | 2.7356 | 0.98912 | 0.21255 | -2.3568e-11 | -2.2598e-11 | -2.1471 | -0.77138 | 1.6678 | 2.417 | -3.5406e-11 | -1.8393e-11 | 89.0784 | 164.1773 | 60.9722 | -91.0066 | -15.7363 | -119.1132 | 1.0467 | 0.26017 | 0.2607 | 1.1907 | 0 | 0 | 2.7833 | 148.43 | 120.3008 | -6.0323 | 0 | 0

## LLG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.35192 | 3.7855 | 2.6664 | 0.35296 | 3.7856 | 2.6658 | 4.0636 | 43.7109 | 30.7889 | 4.0756 | 43.7125 | 30.7816 | 0.19312 | 27.1861 | 1.3227 | -0.42511 | -1.4343e-10 | -5.6657e-11 | 3.6248 | 2.5633 | 12.3285 | -4.834 | -9.1819e-11 | -1.0671e-10 | -91.0108 | -172.0282 | 38.0132 | 88.9934 | 7.9873 | -142.0044 | 0.89327 | 0.62471 | 0.40272 | 1.1907 | 0 | 0 | -4.0605 | -166.642 | 121.8897 | -6.0323 | 0 | 0
Line_1 | 0.17802 | 0.94611 | 0.64413 | 0.17648 | 0.94546 | 0.6429 | 2.0556 | 10.9247 | 7.4378 | 2.0378 | 10.9172 | 7.4235 | 0.13903 | 2.7356 | 0.98912 | 0.21255 | -2.3568e-11 | -2.2598e-11 | -2.1471 | -0.77138 | 1.6678 | 2.417 | -3.5406e-11 | -1.8393e-11 | 89.0784 | 164.1773 | 60.9722 | -91.0066 | -15.7363 | -119.1132 | 1.0467 | 0.26017 | 0.2607 | 1.1907 | 0 | 0 | 2.7833 | 148.43 | 120.3008 | -6.0323 | 0 | 0
Line_2 | 0.17802 | 0.94611 | 0.64413 | 0.17648 | 0.94546 | 0.6429 | 2.0556 | 10.9247 | 7.4378 | 2.0378 | 10.9172 | 7.4235 | 0.13903 | 2.7356 | 0.98912 | 0.21255 | -2.3568e-11 | -2.2598e-11 | -2.1471 | -0.77138 | 1.6678 | 2.417 | -3.5406e-11 | -1.8393e-11 | 89.0784 | 164.1773 | 60.9722 | -91.0066 | -15.7363 | -119.1132 | 1.0467 | 0.26017 | 0.2607 | 1.1907 | 0 | 0 | 2.7833 | 148.43 | 120.3008 | -6.0323 | 0 | 0

## LLG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.11748 | 0.89384 | 0.7594 | 0.11778 | 0.89395 | 0.75913 | 1.3566 | 10.3212 | 8.7688 | 1.3601 | 10.3225 | 8.7657 | 0.075033 | 8.1728 | 4.4757 | -0.10389 | -6.6206 | -4.041 | 1.307 | 4.6285 | 5.9881 | -1.4231 | -4.7664 | -4.8332 | -87.867 | -158.3954 | 62.7043 | 92.1268 | 21.6225 | -117.3061 | 0.96505 | 0.91002 | 0.85256 | 1.0491 | 0.7903 | 0.7187 | -1.1526 | -128.8714 | 115.9291 | -2.0487 | -122.6259 | 112.7948
Line_1 | 0.059345 | 0.2165 | 0.21189 | 0.058892 | 0.21638 | 0.21147 | 0.68526 | 2.5 | 2.4467 | 0.68003 | 2.4986 | 2.4418 | -0.016173 | 1.004 | 1.5634 | 0.051947 | -0.85356 | -1.4231 | -0.69065 | 1.7057 | 1.169 | 0.71154 | -1.7806 | -1.027 | 92.1719 | 172.8687 | 77.0217 | -87.8732 | -7.0149 | -103.0225 | 1.0082 | 0.79172 | 0.79785 | 1.0491 | 0.7903 | 0.7187 | 0.83046 | -127.6144 | 113.8074 | -2.0487 | -122.6259 | 112.7948
Line_2 | 0.059345 | 0.2165 | 0.21189 | 0.058892 | 0.21638 | 0.21147 | 0.68526 | 2.5 | 2.4467 | 0.68003 | 2.4986 | 2.4418 | -0.016173 | 1.004 | 1.5634 | 0.051947 | -0.85356 | -1.4231 | -0.69065 | 1.7057 | 1.169 | 0.71154 | -1.7806 | -1.027 | 92.1719 | 172.8687 | 77.0217 | -87.8732 | -7.0149 | -103.0225 | 1.0082 | 0.79172 | 0.79785 | 1.0491 | 0.7903 | 0.7187 | 0.83046 | -127.6144 | 113.8074 | -2.0487 | -122.6259 | 112.7948

## LLG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.11748 | 0.89384 | 0.7594 | 0.11778 | 0.89395 | 0.75913 | 1.3566 | 10.3212 | 8.7688 | 1.3601 | 10.3225 | 8.7657 | 0.075033 | 8.1728 | 4.4757 | -0.10389 | -6.6206 | -4.041 | 1.307 | 4.6285 | 5.9881 | -1.4231 | -4.7664 | -4.8332 | -87.867 | -158.3954 | 62.7043 | 92.1268 | 21.6225 | -117.3061 | 0.96505 | 0.91002 | 0.85256 | 1.0491 | 0.7903 | 0.7187 | -1.1526 | -128.8714 | 115.9291 | -2.0487 | -122.6259 | 112.7948
Line_1 | 0.059345 | 0.2165 | 0.21189 | 0.058892 | 0.21638 | 0.21147 | 0.68526 | 2.5 | 2.4467 | 0.68003 | 2.4986 | 2.4418 | -0.016173 | 1.004 | 1.5634 | 0.051947 | -0.85356 | -1.4231 | -0.69065 | 1.7057 | 1.169 | 0.71154 | -1.7806 | -1.027 | 92.1719 | 172.8687 | 77.0217 | -87.8732 | -7.0149 | -103.0225 | 1.0082 | 0.79172 | 0.79785 | 1.0491 | 0.7903 | 0.7187 | 0.83046 | -127.6144 | 113.8074 | -2.0487 | -122.6259 | 112.7948
Line_2 | 0.059345 | 0.2165 | 0.21189 | 0.058892 | 0.21638 | 0.21147 | 0.68526 | 2.5 | 2.4467 | 0.68003 | 2.4986 | 2.4418 | -0.016173 | 1.004 | 1.5634 | 0.051947 | -0.85356 | -1.4231 | -0.69065 | 1.7057 | 1.169 | 0.71154 | -1.7806 | -1.027 | 92.1719 | 172.8687 | 77.0217 | -87.8732 | -7.0149 | -103.0225 | 1.0082 | 0.79172 | 0.79785 | 1.0491 | 0.7903 | 0.7187 | 0.83046 | -127.6144 | 113.8074 | -2.0487 | -122.6259 | 112.7948