## LLL_max_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 1.4429 | 1.4429 | 3.6121 | 0 | 49.9825 | 49.9825 | -1e-07 | 3.2477 | -1e-07 | 3.6849 | 109.9084 | -70.0916 | 0 | 0.098271 | 0 | -21.4832
Line_1 | 0.72143 | 0.72143 | 0 | 0 | 24.9912 | 24.9912 | 2.4358 | -1.6239 | 2.7637 | -1.8425 | -70.0916 | 109.9084 | 0.14741 | 0.098271 | -21.4832 | -21.4832
Line_2 | 0.72143 | 0.72143 | 0 | 0 | 24.9912 | 24.9912 | 2.4358 | -1.6239 | 2.7637 | -1.8425 | -70.0916 | 109.9084 | 0.14741 | 0.098271 | -21.4832 | -21.4832
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14741 | 0.14741 | -21.4832 | -21.4832

## LLL_max_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 1.4429 | 1.4429 | 3.6121 | 0 | 49.9825 | 49.9825 | -1e-07 | 3.2477 | -1e-07 | 3.6849 | 109.9084 | -70.0916 | 0 | 0.098271 | 0 | -21.4832
Line_1 | 0.72143 | 0.72143 | 0 | 0 | 24.9912 | 24.9912 | 2.4358 | -1.6239 | 2.7637 | -1.8425 | -70.0916 | 109.9084 | 0.14741 | 0.098271 | -21.4832 | -21.4832
Line_2 | 0.72143 | 0.72143 | 0 | 0 | 24.9912 | 24.9912 | 2.4358 | -1.6239 | 2.7637 | -1.8425 | -70.0916 | 109.9084 | 0.14741 | 0.098271 | -21.4832 | -21.4832
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14741 | 0.14741 | -21.4832 | -21.4832

## LLL_max_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.30987 | 0.30987 | 0.77573 | 0 | 10.7343 | 10.7343 | -8.3062 | 8.456 | -5.0547 | 5.2247 | 140.949 | -39.051 | 0.90582 | 0.92599 | -7.7285 | -7.3405
Line_1 | 0.15494 | 0.15494 | 0 | 0 | 5.3671 | 5.3671 | 4.2654 | -4.228 | 2.6548 | -2.6123 | -39.051 | 140.949 | 0.93609 | 0.92599 | -7.1528 | -7.3405
Line_2 | 0.15494 | 0.15494 | 0 | 0 | 5.3671 | 5.3671 | 4.2654 | -4.228 | 2.6548 | -2.6123 | -39.051 | 140.949 | 0.93609 | 0.92599 | -7.1528 | -7.3405
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.93609 | 0.93609 | -7.1528 | -7.1528

## LLL_max_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.30987 | 0.30987 | 0.77573 | 0 | 10.7343 | 10.7343 | -8.3062 | 8.456 | -5.0547 | 5.2247 | 140.949 | -39.051 | 0.90582 | 0.92599 | -7.7285 | -7.3405
Line_1 | 0.15494 | 0.15494 | 0 | 0 | 5.3671 | 5.3671 | 4.2654 | -4.228 | 2.6548 | -2.6123 | -39.051 | 140.949 | 0.93609 | 0.92599 | -7.1528 | -7.3405
Line_2 | 0.15494 | 0.15494 | 0 | 0 | 5.3671 | 5.3671 | 4.2654 | -4.228 | 2.6548 | -2.6123 | -39.051 | 140.949 | 0.93609 | 0.92599 | -7.1528 | -7.3405
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.93609 | 0.93609 | -7.1528 | -7.1528

## LLL_min_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 1.3783 | 1.3783 | 3.412 | 0 | 47.7473 | 47.7473 | -1e-07 | 5.6904 | -1e-07 | 3.3627 | 114.7975 | -65.2025 | 0 | 0.13843 | 0 | -34.6217
Line_1 | 0.68917 | 0.68917 | 0 | 0 | 23.8737 | 23.8737 | 4.2678 | -2.8452 | 2.522 | -1.6814 | -65.2025 | 114.7975 | 0.20765 | 0.13843 | -34.6217 | -34.6217
Line_2 | 0.68917 | 0.68917 | 0 | 0 | 23.8737 | 23.8737 | 4.2678 | -2.8452 | 2.522 | -1.6814 | -65.2025 | 114.7975 | 0.20765 | 0.13843 | -34.6217 | -34.6217
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.20765 | 0.20765 | -34.6217 | -34.6217

## LLL_min_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 1.3783 | 1.3783 | 3.412 | 0 | 47.7473 | 47.7473 | -1e-07 | 5.6904 | -1e-07 | 3.3627 | 114.7975 | -65.2025 | 0 | 0.13843 | 0 | -34.6217
Line_1 | 0.68917 | 0.68917 | 0 | 0 | 23.8737 | 23.8737 | 4.2678 | -2.8452 | 2.522 | -1.6814 | -65.2025 | 114.7975 | 0.20765 | 0.13843 | -34.6217 | -34.6217
Line_2 | 0.68917 | 0.68917 | 0 | 0 | 23.8737 | 23.8737 | 4.2678 | -2.8452 | 2.522 | -1.6814 | -65.2025 | 114.7975 | 0.20765 | 0.13843 | -34.6217 | -34.6217
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.20765 | 0.20765 | -34.6217 | -34.6217

## LLL_min_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.30266 | 0.30266 | 0.74922 | 0 | 10.4846 | 10.4846 | -7.5715 | 7.8458 | -3.9965 | 4.1586 | 144.5132 | -35.4868 | 0.81658 | 0.84694 | -7.6601 | -7.5613
Line_1 | 0.15133 | 0.15133 | 0 | 0 | 5.2423 | 5.2423 | 3.9915 | -3.9229 | 2.1199 | -2.0793 | -35.4868 | 144.5132 | 0.86212 | 0.84694 | -7.5145 | -7.5613
Line_2 | 0.15133 | 0.15133 | 0 | 0 | 5.2423 | 5.2423 | 3.9915 | -3.9229 | 2.1199 | -2.0793 | -35.4868 | 144.5132 | 0.86212 | 0.84694 | -7.5145 | -7.5613
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.86212 | 0.86212 | -7.5145 | -7.5145

## LLL_min_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.30266 | 0.30266 | 0.74922 | 0 | 10.4846 | 10.4846 | -7.5715 | 7.8458 | -3.9965 | 4.1586 | 144.5132 | -35.4868 | 0.81658 | 0.84694 | -7.6601 | -7.5613
Line_1 | 0.15133 | 0.15133 | 0 | 0 | 5.2423 | 5.2423 | 3.9915 | -3.9229 | 2.1199 | -2.0793 | -35.4868 | 144.5132 | 0.86212 | 0.84694 | -7.5145 | -7.5613
Line_2 | 0.15133 | 0.15133 | 0 | 0 | 5.2423 | 5.2423 | 3.9915 | -3.9229 | 2.1199 | -2.0793 | -35.4868 | 144.5132 | 0.86212 | 0.84694 | -7.5145 | -7.5613
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.86212 | 0.86212 | -7.5145 | -7.5145

## LL_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.15666 | 1.2571 | 1.1123 | 0.15666 | 1.2571 | 1.1123 | 1.809 | 14.5155 | 12.8433 | 1.809 | 14.5155 | 12.8433 | -1.9631 | -7.9243 | 6.9428 | 1.9758 | 8.746 | -6.2995 | -0.3979 | 1.3354 | -1.5343 | 0.41239 | -0.40301 | 2.2642 | 170.1256 | 11.1492 | -165.9544 | -9.8744 | -168.8508 | 14.0456 | 1.1072 | 0.55362 | 0.55362 | 1.1158 | 0.60317 | 0.52121 | 1.5839 | -178.4161 | -178.4161 | 1.9148 | -171.4891 | 174.2757
Line_1 | 0.078332 | 0.62854 | 0.55613 | 0.078332 | 0.62854 | 0.55613 | 0.9045 | 7.2578 | 6.4217 | 0.9045 | 7.2578 | 6.4217 | 0.99111 | 4.5785 | -2.9889 | -0.98792 | -4.373 | 3.1497 | 0.20981 | 0.031582 | 1.3146 | -0.20619 | 0.20151 | -1.1321 | -9.8744 | -168.8508 | 14.0456 | 170.1256 | 11.1492 | -165.9544 | 1.12 | 0.63085 | 0.50847 | 1.1158 | 0.60317 | 0.52121 | 2.0784 | -168.4556 | 170.3047 | 1.9148 | -171.4891 | 174.2757
Line_2 | 0.078332 | 0.62854 | 0.55613 | 0.078332 | 0.62854 | 0.55613 | 0.9045 | 7.2578 | 6.4217 | 0.9045 | 7.2578 | 6.4217 | 0.99111 | 4.5785 | -2.9889 | -0.98792 | -4.373 | 3.1497 | 0.20981 | 0.031582 | 1.3146 | -0.20619 | 0.20151 | -1.1321 | -9.8744 | -168.8508 | 14.0456 | 170.1256 | 11.1492 | -165.9544 | 1.12 | 0.63085 | 0.50847 | 1.1158 | 0.60317 | 0.52121 | 2.0784 | -168.4556 | 170.3047 | 1.9148 | -171.4891 | 174.2757
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0717e-15 | -1.7318e-15 | 1.1811e-14 | -1.1181e-14 | 9.3192e-15 | -6.2518e-15 | -2.1016e-14 | -6.4538e-15 | -1.6679e-14 | 1.5521e-14 | 1.4104e-14 | 2.0616e-14 | 0 | 0 | 0 | 0 | 0 | 0 | 1.12 | 0.63085 | 0.50847 | 1.12 | 0.63085 | 0.50847 | 2.0784 | -168.4556 | 170.3047 | 2.0784 | -168.4556 | 170.3047

## LL_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.15666 | 1.2571 | 1.1123 | 0.15666 | 1.2571 | 1.1123 | 1.809 | 14.5155 | 12.8433 | 1.809 | 14.5155 | 12.8433 | -1.9631 | -7.9243 | 6.9428 | 1.9758 | 8.746 | -6.2995 | -0.3979 | 1.3354 | -1.5343 | 0.41239 | -0.40301 | 2.2642 | 170.1256 | 11.1492 | -165.9544 | -9.8744 | -168.8508 | 14.0456 | 1.1072 | 0.55362 | 0.55362 | 1.1158 | 0.60317 | 0.52121 | 1.5839 | -178.4161 | -178.4161 | 1.9148 | -171.4891 | 174.2757
Line_1 | 0.078332 | 0.62854 | 0.55613 | 0.078332 | 0.62854 | 0.55613 | 0.9045 | 7.2578 | 6.4217 | 0.9045 | 7.2578 | 6.4217 | 0.99111 | 4.5785 | -2.9889 | -0.98792 | -4.373 | 3.1497 | 0.20981 | 0.031582 | 1.3146 | -0.20619 | 0.20151 | -1.1321 | -9.8744 | -168.8508 | 14.0456 | 170.1256 | 11.1492 | -165.9544 | 1.12 | 0.63085 | 0.50847 | 1.1158 | 0.60317 | 0.52121 | 2.0784 | -168.4556 | 170.3047 | 1.9148 | -171.4891 | 174.2757
Line_2 | 0.078332 | 0.62854 | 0.55613 | 0.078332 | 0.62854 | 0.55613 | 0.9045 | 7.2578 | 6.4217 | 0.9045 | 7.2578 | 6.4217 | 0.99111 | 4.5785 | -2.9889 | -0.98792 | -4.373 | 3.1497 | 0.20981 | 0.031582 | 1.3146 | -0.20619 | 0.20151 | -1.1321 | -9.8744 | -168.8508 | 14.0456 | 170.1256 | 11.1492 | -165.9544 | 1.12 | 0.63085 | 0.50847 | 1.1158 | 0.60317 | 0.52121 | 2.0784 | -168.4556 | 170.3047 | 1.9148 | -171.4891 | 174.2757
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0717e-15 | -1.7318e-15 | 1.1811e-14 | -1.1181e-14 | 9.3192e-15 | -6.2518e-15 | -2.1016e-14 | -6.4538e-15 | -1.6679e-14 | 1.5521e-14 | 1.4104e-14 | 2.0616e-14 | 0 | 0 | 0 | 0 | 0 | 0 | 1.12 | 0.63085 | 0.50847 | 1.12 | 0.63085 | 0.50847 | 2.0784 | -168.4556 | 170.3047 | 2.0784 | -168.4556 | 170.3047

## LL_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.057064 | 0.45788 | 0.40513 | 0.057064 | 0.45788 | 0.40513 | 0.65892 | 5.2872 | 4.6781 | 0.65892 | 5.2872 | 4.6781 | -0.69404 | -5.045 | -0.55581 | 0.69573 | 5.154 | 0.64116 | 0.2026 | -0.41812 | -3.4566 | -0.20068 | 0.54182 | 3.5535 | -163.1487 | 37.8749 | -139.2287 | 16.8513 | -142.1251 | 40.7713 | 1.0973 | 0.95747 | 0.74839 | 1.0989 | 0.98019 | 0.77186 | 0.57819 | -137.3873 | 121.6367 | 0.76166 | -136.1239 | 120.5435
Line_1 | 0.028532 | 0.22894 | 0.20257 | 0.028532 | 0.22894 | 0.20257 | 0.32946 | 2.6436 | 2.339 | 0.32946 | 2.6436 | 2.339 | 0.34829 | 2.6043 | 0.34192 | -0.34787 | -2.577 | -0.32058 | -0.099858 | 0.30183 | 1.8009 | 0.10034 | -0.27091 | -1.7767 | 16.8513 | -142.1251 | 40.7713 | -163.1487 | 37.8749 | -139.2287 | 1.0997 | 0.99172 | 0.7837 | 1.0989 | 0.98019 | 0.77186 | 0.85319 | -135.514 | 120.0215 | 0.76166 | -136.1239 | 120.5435
Line_2 | 0.028532 | 0.22894 | 0.20257 | 0.028532 | 0.22894 | 0.20257 | 0.32946 | 2.6436 | 2.339 | 0.32946 | 2.6436 | 2.339 | 0.34829 | 2.6043 | 0.34192 | -0.34787 | -2.577 | -0.32058 | -0.099858 | 0.30183 | 1.8009 | 0.10034 | -0.27091 | -1.7767 | 16.8513 | -142.1251 | 40.7713 | -163.1487 | 37.8749 | -139.2287 | 1.0997 | 0.99172 | 0.7837 | 1.0989 | 0.98019 | 0.77186 | 0.85319 | -135.514 | 120.0215 | 0.76166 | -136.1239 | 120.5435
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.682e-15 | 0 | -4.5712e-15 | 3.8785e-17 | 1.0803e-14 | 1.7851e-15 | 5.1701e-15 | 0 | -6.9291e-15 | -2.6044e-15 | 7.3357e-16 | 1.1751e-14 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0997 | 0.99172 | 0.7837 | 1.0997 | 0.99172 | 0.7837 | 0.85319 | -135.514 | 120.0215 | 0.85319 | -135.514 | 120.0215

## LL_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.057064 | 0.45788 | 0.40513 | 0.057064 | 0.45788 | 0.40513 | 0.65892 | 5.2872 | 4.6781 | 0.65892 | 5.2872 | 4.6781 | -0.69404 | -5.045 | -0.55581 | 0.69573 | 5.154 | 0.64116 | 0.2026 | -0.41812 | -3.4566 | -0.20068 | 0.54182 | 3.5535 | -163.1487 | 37.8749 | -139.2287 | 16.8513 | -142.1251 | 40.7713 | 1.0973 | 0.95747 | 0.74839 | 1.0989 | 0.98019 | 0.77186 | 0.57819 | -137.3873 | 121.6367 | 0.76166 | -136.1239 | 120.5435
Line_1 | 0.028532 | 0.22894 | 0.20257 | 0.028532 | 0.22894 | 0.20257 | 0.32946 | 2.6436 | 2.339 | 0.32946 | 2.6436 | 2.339 | 0.34829 | 2.6043 | 0.34192 | -0.34787 | -2.577 | -0.32058 | -0.099858 | 0.30183 | 1.8009 | 0.10034 | -0.27091 | -1.7767 | 16.8513 | -142.1251 | 40.7713 | -163.1487 | 37.8749 | -139.2287 | 1.0997 | 0.99172 | 0.7837 | 1.0989 | 0.98019 | 0.77186 | 0.85319 | -135.514 | 120.0215 | 0.76166 | -136.1239 | 120.5435
Line_2 | 0.028532 | 0.22894 | 0.20257 | 0.028532 | 0.22894 | 0.20257 | 0.32946 | 2.6436 | 2.339 | 0.32946 | 2.6436 | 2.339 | 0.34829 | 2.6043 | 0.34192 | -0.34787 | -2.577 | -0.32058 | -0.099858 | 0.30183 | 1.8009 | 0.10034 | -0.27091 | -1.7767 | 16.8513 | -142.1251 | 40.7713 | -163.1487 | 37.8749 | -139.2287 | 1.0997 | 0.99172 | 0.7837 | 1.0989 | 0.98019 | 0.77186 | 0.85319 | -135.514 | 120.0215 | 0.76166 | -136.1239 | 120.5435
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.682e-15 | 0 | -4.5712e-15 | 3.8785e-17 | 1.0803e-14 | 1.7851e-15 | 5.1701e-15 | 0 | -6.9291e-15 | -2.6044e-15 | 7.3357e-16 | 1.1751e-14 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0997 | 0.99172 | 0.7837 | 1.0997 | 0.99172 | 0.7837 | 0.85319 | -135.514 | 120.0215 | 0.85319 | -135.514 | 120.0215

## LL_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.14393 | 1.2145 | 1.0782 | 0.14393 | 1.2145 | 1.0782 | 1.662 | 14.0243 | 12.4494 | 1.662 | 14.0243 | 12.4494 | -1.664 | -6.8035 | 5.9715 | 1.6847 | 8.2762 | -4.811 | -0.085413 | 1.7696 | -1.8123 | 0.097635 | -0.89926 | 2.4981 | 178.781 | 16.2989 | -161.3982 | -1.219 | -163.7011 | 18.6018 | 1.0025 | 0.50126 | 0.50126 | 1.0154 | 0.59361 | 0.43543 | 1.7195 | -178.2805 | -178.2805 | 2.0979 | -169.9023 | 171.1612
Line_1 | 0.071965 | 0.60727 | 0.53908 | 0.071965 | 0.60727 | 0.53908 | 0.83098 | 7.0121 | 6.2247 | 0.83098 | 7.0121 | 6.2247 | 0.8475 | 4.5063 | -2.1153 | -0.84233 | -4.1381 | 2.4055 | 0.051873 | -0.23205 | 1.4205 | -0.048818 | 0.44963 | -1.2491 | -1.219 | -163.7011 | 18.6018 | 178.781 | 16.2989 | -161.3982 | 1.0218 | 0.6435 | 0.40934 | 1.0154 | 0.59361 | 0.43543 | 2.2836 | -166.649 | 164.7195 | 2.0979 | -169.9023 | 171.1612
Line_2 | 0.071965 | 0.60727 | 0.53908 | 0.071965 | 0.60727 | 0.53908 | 0.83098 | 7.0121 | 6.2247 | 0.83098 | 7.0121 | 6.2247 | 0.8475 | 4.5063 | -2.1153 | -0.84233 | -4.1381 | 2.4055 | 0.051873 | -0.23205 | 1.4205 | -0.048818 | 0.44963 | -1.2491 | -1.219 | -163.7011 | 18.6018 | 178.781 | 16.2989 | -161.3982 | 1.0218 | 0.6435 | 0.40934 | 1.0154 | 0.59361 | 0.43543 | 2.2836 | -166.649 | 164.7195 | 2.0979 | -169.9023 | 171.1612
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.611e-15 | 3.5946e-15 | -2.8925e-15 | -4.8363e-15 | 1.4078e-15 | 3.741e-15 | -4.7399e-15 | -8.5455e-15 | -3.2299e-15 | -1.9286e-16 | -5.9317e-15 | -1.022e-15 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218 | 0.6435 | 0.40934 | 1.0218 | 0.6435 | 0.40934 | 2.2836 | -166.649 | 164.7195 | 2.2836 | -166.649 | 164.7195

## LL_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.14393 | 1.2145 | 1.0782 | 0.14393 | 1.2145 | 1.0782 | 1.662 | 14.0243 | 12.4494 | 1.662 | 14.0243 | 12.4494 | -1.664 | -6.8035 | 5.9715 | 1.6847 | 8.2762 | -4.811 | -0.085413 | 1.7696 | -1.8123 | 0.097635 | -0.89926 | 2.4981 | 178.781 | 16.2989 | -161.3982 | -1.219 | -163.7011 | 18.6018 | 1.0025 | 0.50126 | 0.50126 | 1.0154 | 0.59361 | 0.43543 | 1.7195 | -178.2805 | -178.2805 | 2.0979 | -169.9023 | 171.1612
Line_1 | 0.071965 | 0.60727 | 0.53908 | 0.071965 | 0.60727 | 0.53908 | 0.83098 | 7.0121 | 6.2247 | 0.83098 | 7.0121 | 6.2247 | 0.8475 | 4.5063 | -2.1153 | -0.84233 | -4.1381 | 2.4055 | 0.051873 | -0.23205 | 1.4205 | -0.048818 | 0.44963 | -1.2491 | -1.219 | -163.7011 | 18.6018 | 178.781 | 16.2989 | -161.3982 | 1.0218 | 0.6435 | 0.40934 | 1.0154 | 0.59361 | 0.43543 | 2.2836 | -166.649 | 164.7195 | 2.0979 | -169.9023 | 171.1612
Line_2 | 0.071965 | 0.60727 | 0.53908 | 0.071965 | 0.60727 | 0.53908 | 0.83098 | 7.0121 | 6.2247 | 0.83098 | 7.0121 | 6.2247 | 0.8475 | 4.5063 | -2.1153 | -0.84233 | -4.1381 | 2.4055 | 0.051873 | -0.23205 | 1.4205 | -0.048818 | 0.44963 | -1.2491 | -1.219 | -163.7011 | 18.6018 | 178.781 | 16.2989 | -161.3982 | 1.0218 | 0.6435 | 0.40934 | 1.0154 | 0.59361 | 0.43543 | 2.2836 | -166.649 | 164.7195 | 2.0979 | -169.9023 | 171.1612
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.611e-15 | 3.5946e-15 | -2.8925e-15 | -4.8363e-15 | 1.4078e-15 | 3.741e-15 | -4.7399e-15 | -8.5455e-15 | -3.2299e-15 | -1.9286e-16 | -5.9317e-15 | -1.022e-15 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0218 | 0.6435 | 0.40934 | 1.0218 | 0.6435 | 0.40934 | 2.2836 | -166.649 | 164.7195 | 2.2836 | -166.649 | 164.7195

## LL_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.053172 | 0.44869 | 0.3983 | 0.053172 | 0.44869 | 0.3983 | 0.61398 | 5.181 | 4.5992 | 0.61398 | 5.181 | 4.5992 | -0.55942 | -4.4702 | -0.65138 | 0.56224 | 4.6712 | 0.80977 | 0.2469 | -0.04336 | -3.0398 | -0.24523 | 0.16214 | 3.1334 | -155.5905 | 41.9274 | -135.7696 | 24.4095 | -138.0726 | 44.2304 | 0.99594 | 0.86284 | 0.67595 | 0.99906 | 0.90214 | 0.70368 | 0.59555 | -137.5168 | 122.1359 | 0.84456 | -136.0846 | 119.7405
Line_1 | 0.026586 | 0.22434 | 0.19915 | 0.026586 | 0.22434 | 0.19915 | 0.30699 | 2.5905 | 2.2996 | 0.30699 | 2.5905 | 2.2996 | 0.28183 | 2.3858 | 0.44448 | -0.28112 | -2.3356 | -0.40488 | -0.1222 | 0.11076 | 1.5901 | 0.12261 | -0.081069 | -1.5667 | 24.4095 | -138.0726 | 44.2304 | -155.5905 | 41.9274 | -135.7696 | 1.0006 | 0.92199 | 0.71798 | 0.99906 | 0.90214 | 0.70368 | 0.96848 | -135.4145 | 118.6132 | 0.84456 | -136.0846 | 119.7405
Line_2 | 0.026586 | 0.22434 | 0.19915 | 0.026586 | 0.22434 | 0.19915 | 0.30699 | 2.5905 | 2.2996 | 0.30699 | 2.5905 | 2.2996 | 0.28183 | 2.3858 | 0.44448 | -0.28112 | -2.3356 | -0.40488 | -0.1222 | 0.11076 | 1.5901 | 0.12261 | -0.081069 | -1.5667 | 24.4095 | -138.0726 | 44.2304 | -155.5905 | 41.9274 | -135.7696 | 1.0006 | 0.92199 | 0.71798 | 0.99906 | 0.90214 | 0.70368 | 0.96848 | -135.4145 | 118.6132 | 0.84456 | -136.0846 | 119.7405
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2269e-15 | 4.6434e-15 | -9.1617e-16 | -4.5432e-15 | -8.4645e-15 | 1.4252e-15 | -4.6691e-15 | 1.5106e-15 | 1.6795e-15 | 5.8489e-15 | 3.9216e-15 | -2.6125e-15 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0006 | 0.92199 | 0.71798 | 1.0006 | 0.92199 | 0.71798 | 0.96848 | -135.4145 | 118.6132 | 0.96848 | -135.4145 | 118.6132

## LL_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.053172 | 0.44869 | 0.3983 | 0.053172 | 0.44869 | 0.3983 | 0.61398 | 5.181 | 4.5992 | 0.61398 | 5.181 | 4.5992 | -0.55942 | -4.4702 | -0.65138 | 0.56224 | 4.6712 | 0.80977 | 0.2469 | -0.04336 | -3.0398 | -0.24523 | 0.16214 | 3.1334 | -155.5905 | 41.9274 | -135.7696 | 24.4095 | -138.0726 | 44.2304 | 0.99594 | 0.86284 | 0.67595 | 0.99906 | 0.90214 | 0.70368 | 0.59555 | -137.5168 | 122.1359 | 0.84456 | -136.0846 | 119.7405
Line_1 | 0.026586 | 0.22434 | 0.19915 | 0.026586 | 0.22434 | 0.19915 | 0.30699 | 2.5905 | 2.2996 | 0.30699 | 2.5905 | 2.2996 | 0.28183 | 2.3858 | 0.44448 | -0.28112 | -2.3356 | -0.40488 | -0.1222 | 0.11076 | 1.5901 | 0.12261 | -0.081069 | -1.5667 | 24.4095 | -138.0726 | 44.2304 | -155.5905 | 41.9274 | -135.7696 | 1.0006 | 0.92199 | 0.71798 | 0.99906 | 0.90214 | 0.70368 | 0.96848 | -135.4145 | 118.6132 | 0.84456 | -136.0846 | 119.7405
Line_2 | 0.026586 | 0.22434 | 0.19915 | 0.026586 | 0.22434 | 0.19915 | 0.30699 | 2.5905 | 2.2996 | 0.30699 | 2.5905 | 2.2996 | 0.28183 | 2.3858 | 0.44448 | -0.28112 | -2.3356 | -0.40488 | -0.1222 | 0.11076 | 1.5901 | 0.12261 | -0.081069 | -1.5667 | 24.4095 | -138.0726 | 44.2304 | -155.5905 | 41.9274 | -135.7696 | 1.0006 | 0.92199 | 0.71798 | 0.99906 | 0.90214 | 0.70368 | 0.96848 | -135.4145 | 118.6132 | 0.84456 | -136.0846 | 119.7405
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2269e-15 | 4.6434e-15 | -9.1617e-16 | -4.5432e-15 | -8.4645e-15 | 1.4252e-15 | -4.6691e-15 | 1.5106e-15 | 1.6795e-15 | 5.8489e-15 | 3.9216e-15 | -2.6125e-15 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0006 | 0.92199 | 0.71798 | 1.0006 | 0.92199 | 0.71798 | 0.96848 | -135.4145 | 118.6132 | 0.96848 | -135.4145 | 118.6132

## LG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.3633 | 0.2305 | 0.4524 | 1.364 | 0.22973 | 0.45163 | 15.7416 | 2.6616 | 5.2238 | 15.7507 | 2.6526 | 5.2149 | 2.1393e-10 | 2.5971 | -4.7552 | 1.9286 | -2.6606 | 4.6671 | -9.068e-11 | -0.46291 | -2.3507 | 1.8116 | 0.31502 | 2.1186 | 107.6866 | -96.1695 | -97.8641 | -72.3198 | 83.7864 | 82.1106 | 0 | 0.99115 | 1.0154 | 0.16799 | 1.01 | 0.98283 | 0 | -106.2756 | 108.441 | -29.1115 | -102.9662 | 106.5259
Line_1 | 0.68257 | 0.1144 | 0.22536 | 0.68202 | 0.11486 | 0.22581 | 7.8817 | 1.321 | 2.6022 | 7.8753 | 1.3263 | 2.6075 | 1.449 | -1.3433 | 2.3074 | -0.96428 | 1.3303 | -2.3335 | 1.3601 | 0.11712 | 1.0028 | -0.90578 | -0.15751 | -1.0593 | -72.3116 | 83.63 | 82.0278 | 107.6802 | -96.2136 | -97.8894 | 0.25214 | 1.0207 | 0.96682 | 0.16799 | 1.01 | 0.98283 | -29.1242 | -101.3528 | 105.5165 | -29.1115 | -102.9662 | 106.5259
Line_2 | 0.68257 | 0.1144 | 0.22536 | 0.68202 | 0.11486 | 0.22581 | 7.8817 | 1.321 | 2.6022 | 7.8753 | 1.3263 | 2.6075 | 1.449 | -1.3433 | 2.3074 | -0.96428 | 1.3303 | -2.3335 | 1.3601 | 0.11712 | 1.0028 | -0.90578 | -0.15751 | -1.0593 | -72.3116 | 83.63 | 82.0278 | 107.6802 | -96.2136 | -97.8894 | 0.25214 | 1.0207 | 0.96682 | 0.16799 | 1.01 | 0.98283 | -29.1242 | -101.3528 | 105.5165 | -29.1115 | -102.9662 | 106.5259
Line_3 | 0.00025307 | 0.00025307 | 0.00025307 | 0.00025307 | 0.00025307 | 0.00025307 | 0.0029222 | 0.0029222 | 0.0029222 | 0.0029222 | 0.0029222 | 0.0029222 | 0.00068242 | 0.0019141 | -0.0025966 | 0.00068242 | 0.0019141 | -0.0025966 | 0.00027778 | -0.0022876 | 0.0011134 | 0.00027778 | -0.0022876 | 0.0011134 | -51.2733 | -51.2733 | -51.2733 | -51.2733 | -51.2733 | -51.2733 | 0.25214 | 1.0207 | 0.96682 | 0.25214 | 1.0207 | 0.96682 | -29.1242 | -101.3528 | 105.5165 | -29.1242 | -101.3528 | 105.5165

## LG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.3633 | 0.2305 | 0.4524 | 1.364 | 0.22973 | 0.45163 | 15.7416 | 2.6616 | 5.2238 | 15.7507 | 2.6526 | 5.2149 | 2.1393e-10 | 2.5971 | -4.7552 | 1.9286 | -2.6606 | 4.6671 | -9.068e-11 | -0.46291 | -2.3507 | 1.8116 | 0.31502 | 2.1186 | 107.6866 | -96.1695 | -97.8641 | -72.3198 | 83.7864 | 82.1106 | 0 | 0.99115 | 1.0154 | 0.16799 | 1.01 | 0.98283 | 0 | -106.2756 | 108.441 | -29.1115 | -102.9662 | 106.5259
Line_1 | 0.68257 | 0.1144 | 0.22536 | 0.68202 | 0.11486 | 0.22581 | 7.8817 | 1.321 | 2.6022 | 7.8753 | 1.3263 | 2.6075 | 1.449 | -1.3433 | 2.3074 | -0.96428 | 1.3303 | -2.3335 | 1.3601 | 0.11712 | 1.0028 | -0.90578 | -0.15751 | -1.0593 | -72.3116 | 83.63 | 82.0278 | 107.6802 | -96.2136 | -97.8894 | 0.25214 | 1.0207 | 0.96682 | 0.16799 | 1.01 | 0.98283 | -29.1242 | -101.3528 | 105.5165 | -29.1115 | -102.9662 | 106.5259
Line_2 | 0.68257 | 0.1144 | 0.22536 | 0.68202 | 0.11486 | 0.22581 | 7.8817 | 1.321 | 2.6022 | 7.8753 | 1.3263 | 2.6075 | 1.449 | -1.3433 | 2.3074 | -0.96428 | 1.3303 | -2.3335 | 1.3601 | 0.11712 | 1.0028 | -0.90578 | -0.15751 | -1.0593 | -72.3116 | 83.63 | 82.0278 | 107.6802 | -96.2136 | -97.8894 | 0.25214 | 1.0207 | 0.96682 | 0.16799 | 1.01 | 0.98283 | -29.1242 | -101.3528 | 105.5165 | -29.1115 | -102.9662 | 106.5259
Line_3 | 0.00025307 | 0.00025307 | 0.00025307 | 0.00025307 | 0.00025307 | 0.00025307 | 0.0029222 | 0.0029222 | 0.0029222 | 0.0029222 | 0.0029222 | 0.0029222 | 0.00068242 | 0.0019141 | -0.0025966 | 0.00068242 | 0.0019141 | -0.0025966 | 0.00027778 | -0.0022876 | 0.0011134 | 0.00027778 | -0.0022876 | 0.0011134 | -51.2733 | -51.2733 | -51.2733 | -51.2733 | -51.2733 | -51.2733 | 0.25214 | 1.0207 | 0.96682 | 0.25214 | 1.0207 | 0.96682 | -29.1242 | -101.3528 | 105.5165 | -29.1242 | -101.3528 | 105.5165

## LG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.24863 | 0.042039 | 0.082509 | 0.24878 | 0.041898 | 0.082368 | 2.871 | 0.48543 | 0.95273 | 2.8726 | 0.48379 | 0.95111 | -2.2813 | 0.28654 | -1.0521 | 2.3466 | -0.28829 | 1.0476 | -1.4362 | -0.4249 | -0.042958 | 1.4975 | 0.41845 | 0.035692 | 141.0584 | -62.7977 | -64.4923 | -38.948 | 117.1582 | 115.4824 | 0.93897 | 1.0558 | 1.1052 | 0.96906 | 1.0503 | 1.1021 | -6.7495 | -118.8029 | 117.8459 | -6.4035 | -118.2766 | 117.4337
Line_1 | 0.12449 | 0.020865 | 0.041102 | 0.12439 | 0.020949 | 0.041184 | 1.4375 | 0.24092 | 0.4746 | 1.4363 | 0.2419 | 0.47555 | 1.1905 | -0.14473 | 0.52207 | -1.1733 | 0.14415 | -0.52381 | 0.76429 | 0.20679 | 0.016644 | -0.74877 | -0.20922 | -0.017846 | -38.9398 | 117.0018 | 115.3995 | 141.052 | -62.8418 | -64.5176 | 0.98415 | 1.0477 | 1.1006 | 0.96906 | 1.0503 | 1.1021 | -6.2388 | -118.0098 | 117.2256 | -6.4035 | -118.2766 | 117.4337
Line_2 | 0.12449 | 0.020865 | 0.041102 | 0.12439 | 0.020949 | 0.041184 | 1.4375 | 0.24092 | 0.4746 | 1.4363 | 0.2419 | 0.47555 | 1.1905 | -0.14473 | 0.52207 | -1.1733 | 0.14415 | -0.52381 | 0.76429 | 0.20679 | 0.016644 | -0.74877 | -0.20922 | -0.017846 | -38.9398 | 117.0018 | 115.3995 | 141.052 | -62.8418 | -64.5176 | 0.98415 | 1.0477 | 1.1006 | 0.96906 | 1.0503 | 1.1021 | -6.2388 | -118.0098 | 117.2256 | -6.4035 | -118.2766 | 117.4337
Line_3 | 4.6155e-05 | 4.6155e-05 | 4.6155e-05 | 4.6155e-05 | 4.6155e-05 | 4.6155e-05 | 0.00053295 | 0.00053295 | 0.00053295 | 0.00053295 | 0.00053295 | 0.00053295 | 0.00051368 | -9.7996e-05 | -0.00041568 | 0.00051368 | -9.7996e-05 | -0.00041568 | 0.00010603 | -0.00054969 | 0.00041384 | 0.00010603 | -0.00054969 | 0.00041384 | -17.9015 | -17.9015 | -17.9015 | -17.9015 | -17.9015 | -17.9015 | 0.98415 | 1.0477 | 1.1006 | 0.98415 | 1.0477 | 1.1006 | -6.2388 | -118.0098 | 117.2256 | -6.2388 | -118.0098 | 117.2256

## LG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.24863 | 0.042039 | 0.082509 | 0.24878 | 0.041898 | 0.082368 | 2.871 | 0.48543 | 0.95273 | 2.8726 | 0.48379 | 0.95111 | -2.2813 | 0.28654 | -1.0521 | 2.3466 | -0.28829 | 1.0476 | -1.4362 | -0.4249 | -0.042958 | 1.4975 | 0.41845 | 0.035692 | 141.0584 | -62.7977 | -64.4923 | -38.948 | 117.1582 | 115.4824 | 0.93897 | 1.0558 | 1.1052 | 0.96906 | 1.0503 | 1.1021 | -6.7495 | -118.8029 | 117.8459 | -6.4035 | -118.2766 | 117.4337
Line_1 | 0.12449 | 0.020865 | 0.041102 | 0.12439 | 0.020949 | 0.041184 | 1.4375 | 0.24092 | 0.4746 | 1.4363 | 0.2419 | 0.47555 | 1.1905 | -0.14473 | 0.52207 | -1.1733 | 0.14415 | -0.52381 | 0.76429 | 0.20679 | 0.016644 | -0.74877 | -0.20922 | -0.017846 | -38.9398 | 117.0018 | 115.3995 | 141.052 | -62.8418 | -64.5176 | 0.98415 | 1.0477 | 1.1006 | 0.96906 | 1.0503 | 1.1021 | -6.2388 | -118.0098 | 117.2256 | -6.4035 | -118.2766 | 117.4337
Line_2 | 0.12449 | 0.020865 | 0.041102 | 0.12439 | 0.020949 | 0.041184 | 1.4375 | 0.24092 | 0.4746 | 1.4363 | 0.2419 | 0.47555 | 1.1905 | -0.14473 | 0.52207 | -1.1733 | 0.14415 | -0.52381 | 0.76429 | 0.20679 | 0.016644 | -0.74877 | -0.20922 | -0.017846 | -38.9398 | 117.0018 | 115.3995 | 141.052 | -62.8418 | -64.5176 | 0.98415 | 1.0477 | 1.1006 | 0.96906 | 1.0503 | 1.1021 | -6.2388 | -118.0098 | 117.2256 | -6.4035 | -118.2766 | 117.4337
Line_3 | 4.6155e-05 | 4.6155e-05 | 4.6155e-05 | 4.6155e-05 | 4.6155e-05 | 4.6155e-05 | 0.00053295 | 0.00053295 | 0.00053295 | 0.00053295 | 0.00053295 | 0.00053295 | 0.00051368 | -9.7996e-05 | -0.00041568 | 0.00051368 | -9.7996e-05 | -0.00041568 | 0.00010603 | -0.00054969 | 0.00041384 | 0.00010603 | -0.00054969 | 0.00041384 | -17.9015 | -17.9015 | -17.9015 | -17.9015 | -17.9015 | -17.9015 | 0.98415 | 1.0477 | 1.1006 | 0.98415 | 1.0477 | 1.1006 | -6.2388 | -118.0098 | 117.2256 | -6.2388 | -118.0098 | 117.2256

## LG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.2072 | 0.31556 | 0.51626 | 1.2079 | 0.31486 | 0.51556 | 13.9398 | 3.6437 | 5.9612 | 13.9475 | 3.6357 | 5.9532 | -5.3104e-11 | 3.1346 | -5.1903 | 2.426 | -3.1696 | 5.2257 | -4.0839e-11 | -1.0432 | -1.8476 | 1.8054 | 0.7751 | 1.4697 | 113.2603 | -88.9768 | -89.808 | -66.7491 | 91.0101 | 90.1828 | 0 | 0.90665 | 0.9242 | 0.21682 | 0.89749 | 0.91186 | 0 | -107.3842 | 109.7864 | -30.0932 | -102.7315 | 105.8914
Line_1 | 0.60431 | 0.15713 | 0.25749 | 0.60395 | 0.15743 | 0.25778 | 6.9779 | 1.8144 | 2.9732 | 6.9738 | 1.8178 | 2.9766 | 1.8223 | -1.593 | 2.6194 | -1.213 | 1.5848 | -2.6129 | 1.3549 | 0.31825 | 0.64197 | -0.9027 | -0.38755 | -0.73486 | -66.7407 | 90.9306 | 90.1334 | 113.2509 | -88.9899 | -89.8172 | 0.32543 | 0.89531 | 0.90709 | 0.21682 | 0.89749 | 0.91186 | -30.1099 | -100.3674 | 103.9039 | -30.0932 | -102.7315 | 105.8914
Line_2 | 0.60431 | 0.15713 | 0.25749 | 0.60395 | 0.15743 | 0.25778 | 6.9779 | 1.8144 | 2.9732 | 6.9738 | 1.8178 | 2.9766 | 1.8223 | -1.593 | 2.6194 | -1.213 | 1.5848 | -2.6129 | 1.3549 | 0.31825 | 0.64197 | -0.9027 | -0.38755 | -0.73486 | -66.7407 | 90.9306 | 90.1334 | 113.2509 | -88.9899 | -89.8172 | 0.32543 | 0.89531 | 0.90709 | 0.21682 | 0.89749 | 0.91186 | -30.1099 | -100.3674 | 103.9039 | -30.0932 | -102.7315 | 105.8914
Line_3 | 0.00015703 | 0.00015703 | 0.00015703 | 0.00015703 | 0.00015703 | 0.00015703 | 0.0018132 | 0.0018132 | 0.0018132 | 0.0018132 | 0.0018132 | 0.0018132 | 0.00059001 | 0.00056777 | -0.0011578 | 0.00059001 | 0.00056777 | -0.0011578 | 7.5125e-06 | -0.0015208 | 0.0011682 | 7.5125e-06 | -0.0015208 | 0.0011682 | -30.8394 | -30.8394 | -30.8394 | -30.8394 | -30.8394 | -30.8394 | 0.32543 | 0.89531 | 0.90709 | 0.32543 | 0.89531 | 0.90709 | -30.1099 | -100.3674 | 103.9039 | -30.1099 | -100.3674 | 103.9039

## LG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.2072 | 0.31556 | 0.51626 | 1.2079 | 0.31486 | 0.51556 | 13.9398 | 3.6437 | 5.9612 | 13.9475 | 3.6357 | 5.9532 | -5.3104e-11 | 3.1346 | -5.1903 | 2.426 | -3.1696 | 5.2257 | -4.0839e-11 | -1.0432 | -1.8476 | 1.8054 | 0.7751 | 1.4697 | 113.2603 | -88.9768 | -89.808 | -66.7491 | 91.0101 | 90.1828 | 0 | 0.90665 | 0.9242 | 0.21682 | 0.89749 | 0.91186 | 0 | -107.3842 | 109.7864 | -30.0932 | -102.7315 | 105.8914
Line_1 | 0.60431 | 0.15713 | 0.25749 | 0.60395 | 0.15743 | 0.25778 | 6.9779 | 1.8144 | 2.9732 | 6.9738 | 1.8178 | 2.9766 | 1.8223 | -1.593 | 2.6194 | -1.213 | 1.5848 | -2.6129 | 1.3549 | 0.31825 | 0.64197 | -0.9027 | -0.38755 | -0.73486 | -66.7407 | 90.9306 | 90.1334 | 113.2509 | -88.9899 | -89.8172 | 0.32543 | 0.89531 | 0.90709 | 0.21682 | 0.89749 | 0.91186 | -30.1099 | -100.3674 | 103.9039 | -30.0932 | -102.7315 | 105.8914
Line_2 | 0.60431 | 0.15713 | 0.25749 | 0.60395 | 0.15743 | 0.25778 | 6.9779 | 1.8144 | 2.9732 | 6.9738 | 1.8178 | 2.9766 | 1.8223 | -1.593 | 2.6194 | -1.213 | 1.5848 | -2.6129 | 1.3549 | 0.31825 | 0.64197 | -0.9027 | -0.38755 | -0.73486 | -66.7407 | 90.9306 | 90.1334 | 113.2509 | -88.9899 | -89.8172 | 0.32543 | 0.89531 | 0.90709 | 0.21682 | 0.89749 | 0.91186 | -30.1099 | -100.3674 | 103.9039 | -30.0932 | -102.7315 | 105.8914
Line_3 | 0.00015703 | 0.00015703 | 0.00015703 | 0.00015703 | 0.00015703 | 0.00015703 | 0.0018132 | 0.0018132 | 0.0018132 | 0.0018132 | 0.0018132 | 0.0018132 | 0.00059001 | 0.00056777 | -0.0011578 | 0.00059001 | 0.00056777 | -0.0011578 | 7.5125e-06 | -0.0015208 | 0.0011682 | 7.5125e-06 | -0.0015208 | 0.0011682 | -30.8394 | -30.8394 | -30.8394 | -30.8394 | -30.8394 | -30.8394 | 0.32543 | 0.89531 | 0.90709 | 0.32543 | 0.89531 | 0.90709 | -30.1099 | -100.3674 | 103.9039 | -30.1099 | -100.3674 | 103.9039

## LG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.22777 | 0.059538 | 0.097405 | 0.2279 | 0.059406 | 0.097274 | 2.6301 | 0.68749 | 1.1247 | 2.6316 | 0.68597 | 1.1232 | -1.97 | 0.31038 | -1.1244 | 2.0573 | -0.31131 | 1.1244 | -1.0361 | -0.58394 | 0.086247 | 1.1013 | 0.57314 | -0.099345 | 145.4393 | -56.7977 | -57.629 | -34.5701 | 123.1891 | 122.3618 | 0.84629 | 0.96191 | 1.0026 | 0.88673 | 0.95082 | 1.005 | -6.819 | -118.806 | 117.9848 | -6.4098 | -118.3017 | 117.3128
Line_1 | 0.11402 | 0.029647 | 0.048581 | 0.11395 | 0.029703 | 0.048637 | 1.3166 | 0.34233 | 0.56097 | 1.3158 | 0.34298 | 0.56161 | 1.051 | -0.15613 | 0.56198 | -1.0286 | 0.15565 | -0.56221 | 0.56689 | 0.28345 | -0.052488 | -0.55063 | -0.28657 | 0.049672 | -34.5616 | 123.1096 | 122.3124 | 145.4299 | -56.8109 | -57.6382 | 0.90701 | 0.9453 | 1.0062 | 0.88673 | 0.95082 | 1.005 | -6.2197 | -118.0426 | 116.9765 | -6.4098 | -118.3017 | 117.3128
Line_2 | 0.11402 | 0.029647 | 0.048581 | 0.11395 | 0.029703 | 0.048637 | 1.3166 | 0.34233 | 0.56097 | 1.3158 | 0.34298 | 0.56161 | 1.051 | -0.15613 | 0.56198 | -1.0286 | 0.15565 | -0.56221 | 0.56689 | 0.28345 | -0.052488 | -0.55063 | -0.28657 | 0.049672 | -34.5616 | 123.1096 | 122.3124 | 145.4299 | -56.8109 | -57.6382 | 0.90701 | 0.9453 | 1.0062 | 0.88673 | 0.95082 | 1.005 | -6.2197 | -118.0426 | 116.9765 | -6.4098 | -118.3017 | 117.3128
Line_3 | 2.9627e-05 | 2.9627e-05 | 2.9627e-05 | 2.9627e-05 | 2.9627e-05 | 2.9627e-05 | 0.00034211 | 0.00034211 | 0.00034211 | 0.00034211 | 0.00034211 | 0.00034211 | 0.0003076 | -0.00015867 | -0.00014893 | 0.0003076 | -0.00015867 | -0.00014893 | -4.082e-05 | -0.00028179 | 0.00031033 | -4.082e-05 | -0.00028179 | 0.00031033 | 1.3396 | 1.3396 | 1.3396 | 1.3396 | 1.3396 | 1.3396 | 0.90701 | 0.9453 | 1.0062 | 0.90701 | 0.9453 | 1.0062 | -6.2197 | -118.0426 | 116.9765 | -6.2197 | -118.0426 | 116.9765

## LG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.22777 | 0.059538 | 0.097405 | 0.2279 | 0.059406 | 0.097274 | 2.6301 | 0.68749 | 1.1247 | 2.6316 | 0.68597 | 1.1232 | -1.97 | 0.31038 | -1.1244 | 2.0573 | -0.31131 | 1.1244 | -1.0361 | -0.58394 | 0.086247 | 1.1013 | 0.57314 | -0.099345 | 145.4393 | -56.7977 | -57.629 | -34.5701 | 123.1891 | 122.3618 | 0.84629 | 0.96191 | 1.0026 | 0.88673 | 0.95082 | 1.005 | -6.819 | -118.806 | 117.9848 | -6.4098 | -118.3017 | 117.3128
Line_1 | 0.11402 | 0.029647 | 0.048581 | 0.11395 | 0.029703 | 0.048637 | 1.3166 | 0.34233 | 0.56097 | 1.3158 | 0.34298 | 0.56161 | 1.051 | -0.15613 | 0.56198 | -1.0286 | 0.15565 | -0.56221 | 0.56689 | 0.28345 | -0.052488 | -0.55063 | -0.28657 | 0.049672 | -34.5616 | 123.1096 | 122.3124 | 145.4299 | -56.8109 | -57.6382 | 0.90701 | 0.9453 | 1.0062 | 0.88673 | 0.95082 | 1.005 | -6.2197 | -118.0426 | 116.9765 | -6.4098 | -118.3017 | 117.3128
Line_2 | 0.11402 | 0.029647 | 0.048581 | 0.11395 | 0.029703 | 0.048637 | 1.3166 | 0.34233 | 0.56097 | 1.3158 | 0.34298 | 0.56161 | 1.051 | -0.15613 | 0.56198 | -1.0286 | 0.15565 | -0.56221 | 0.56689 | 0.28345 | -0.052488 | -0.55063 | -0.28657 | 0.049672 | -34.5616 | 123.1096 | 122.3124 | 145.4299 | -56.8109 | -57.6382 | 0.90701 | 0.9453 | 1.0062 | 0.88673 | 0.95082 | 1.005 | -6.2197 | -118.0426 | 116.9765 | -6.4098 | -118.3017 | 117.3128
Line_3 | 2.9627e-05 | 2.9627e-05 | 2.9627e-05 | 2.9627e-05 | 2.9627e-05 | 2.9627e-05 | 0.00034211 | 0.00034211 | 0.00034211 | 0.00034211 | 0.00034211 | 0.00034211 | 0.0003076 | -0.00015867 | -0.00014893 | 0.0003076 | -0.00015867 | -0.00014893 | -4.082e-05 | -0.00028179 | 0.00031033 | -4.082e-05 | -0.00028179 | 0.00031033 | 1.3396 | 1.3396 | 1.3396 | 1.3396 | 1.3396 | 1.3396 | 0.90701 | 0.9453 | 1.0062 | 0.90701 | 0.9453 | 1.0062 | -6.2197 | -118.0426 | 116.9765 | -6.2197 | -118.0426 | 116.9765

## LLG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.48127 | 1.5873 | 1.2397 | 0.48024 | 1.5877 | 1.2404 | 5.5572 | 18.329 | 14.3149 | 5.5453 | 18.3329 | 14.323 | -0.96497 | 1.2668e-10 | 9.2667e-11 | 0.67912 | 2.9756 | 0.68843 | -4.229 | -2.0726e-10 | -1.6535e-10 | 3.9845 | 0.76345 | 2.3217 | 103.7134 | -10.1914 | -128.2734 | -76.2757 | 169.7732 | 51.7616 | 0.78055 | 0 | 0 | 0.72889 | 0.16757 | 0.16907 | 0.85977 | 0 | 0 | 4.0517 | -175.837 | 125.2455
Line_1 | 0.23942 | 0.79431 | 0.62048 | 0.24012 | 0.79384 | 0.62021 | 2.7646 | 9.1719 | 7.1647 | 2.7726 | 9.1664 | 7.1615 | 0.2655 | 2.2342 | 0.51868 | -0.33956 | -1.4878 | -0.34421 | 1.9277 | 0.57332 | 1.743 | -1.9922 | -0.38172 | -1.1608 | -76.3239 | 169.733 | 51.8239 | 103.7243 | -10.2268 | -128.2384 | 0.70388 | 0.25148 | 0.25382 | 0.72889 | 0.16757 | 0.16907 | 5.8342 | -175.8746 | 125.2517 | 4.0517 | -175.837 | 125.2455
Line_2 | 0.23942 | 0.79431 | 0.62048 | 0.24012 | 0.79384 | 0.62021 | 2.7646 | 9.1719 | 7.1647 | 2.7726 | 9.1664 | 7.1615 | 0.2655 | 2.2342 | 0.51868 | -0.33956 | -1.4878 | -0.34421 | 1.9277 | 0.57332 | 1.743 | -1.9922 | -0.38172 | -1.1608 | -76.3239 | 169.733 | 51.8239 | 103.7243 | -10.2268 | -128.2384 | 0.70388 | 0.25148 | 0.25382 | 0.72889 | 0.16757 | 0.16907 | 5.8342 | -175.8746 | 125.2517 | 4.0517 | -175.837 | 125.2455
Line_3 | 0.00032971 | 0.00032971 | 0.00032971 | 0.00032971 | 0.00032971 | 0.00032971 | 0.0038072 | 0.0038072 | 0.0038072 | 0.0038072 | 0.0038072 | 0.0038072 | -0.0015327 | 0.00057079 | 0.00096193 | -0.0015327 | 0.00057079 | 0.00096193 | -0.0021982 | 0.0007687 | -9.21e-05 | -0.0021982 | 0.0007687 | -9.21e-05 | 130.7208 | 130.7208 | 130.7208 | 130.7208 | 130.7208 | 130.7208 | 0.70388 | 0.25148 | 0.25382 | 0.70388 | 0.25148 | 0.25382 | 5.8342 | -175.8746 | 125.2517 | 5.8342 | -175.8746 | 125.2517

## LLG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.48127 | 1.5873 | 1.2397 | 0.48024 | 1.5877 | 1.2404 | 5.5572 | 18.329 | 14.3149 | 5.5453 | 18.3329 | 14.323 | -0.96497 | 1.2668e-10 | 9.2667e-11 | 0.67912 | 2.9756 | 0.68843 | -4.229 | -2.0726e-10 | -1.6535e-10 | 3.9845 | 0.76345 | 2.3217 | 103.7134 | -10.1914 | -128.2734 | -76.2757 | 169.7732 | 51.7616 | 0.78055 | 0 | 0 | 0.72889 | 0.16757 | 0.16907 | 0.85977 | 0 | 0 | 4.0517 | -175.837 | 125.2455
Line_1 | 0.23942 | 0.79431 | 0.62048 | 0.24012 | 0.79384 | 0.62021 | 2.7646 | 9.1719 | 7.1647 | 2.7726 | 9.1664 | 7.1615 | 0.2655 | 2.2342 | 0.51868 | -0.33956 | -1.4878 | -0.34421 | 1.9277 | 0.57332 | 1.743 | -1.9922 | -0.38172 | -1.1608 | -76.3239 | 169.733 | 51.8239 | 103.7243 | -10.2268 | -128.2384 | 0.70388 | 0.25148 | 0.25382 | 0.72889 | 0.16757 | 0.16907 | 5.8342 | -175.8746 | 125.2517 | 4.0517 | -175.837 | 125.2455
Line_2 | 0.23942 | 0.79431 | 0.62048 | 0.24012 | 0.79384 | 0.62021 | 2.7646 | 9.1719 | 7.1647 | 2.7726 | 9.1664 | 7.1615 | 0.2655 | 2.2342 | 0.51868 | -0.33956 | -1.4878 | -0.34421 | 1.9277 | 0.57332 | 1.743 | -1.9922 | -0.38172 | -1.1608 | -76.3239 | 169.733 | 51.8239 | 103.7243 | -10.2268 | -128.2384 | 0.70388 | 0.25148 | 0.25382 | 0.72889 | 0.16757 | 0.16907 | 5.8342 | -175.8746 | 125.2517 | 4.0517 | -175.837 | 125.2455
Line_3 | 0.00032971 | 0.00032971 | 0.00032971 | 0.00032971 | 0.00032971 | 0.00032971 | 0.0038072 | 0.0038072 | 0.0038072 | 0.0038072 | 0.0038072 | 0.0038072 | -0.0015327 | 0.00057079 | 0.00096193 | -0.0015327 | 0.00057079 | 0.00096193 | -0.0021982 | 0.0007687 | -9.21e-05 | -0.0021982 | 0.0007687 | -9.21e-05 | 130.7208 | 130.7208 | 130.7208 | 130.7208 | 130.7208 | 130.7208 | 0.70388 | 0.25148 | 0.25382 | 0.70388 | 0.25148 | 0.25382 | 5.8342 | -175.8746 | 125.2517 | 5.8342 | -175.8746 | 125.2517

## LLG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.075395 | 0.31631 | 0.24451 | 0.075249 | 0.31635 | 0.24458 | 0.87059 | 3.6525 | 2.8233 | 0.8689 | 3.6529 | 2.8242 | -0.76116 | -3.1651 | -1.888 | 0.75265 | 3.2629 | 1.9088 | -0.5217 | -1.3671 | -1.7079 | 0.51657 | 1.4028 | 1.7814 | 144.4013 | 27.8283 | -107.5939 | -35.5737 | -152.198 | 72.4363 | 1.06 | 0.94395 | 0.90173 | 1.0506 | 0.97229 | 0.92448 | -1.1718 | -128.8114 | 114.5398 | -1.1109 | -128.9334 | 115.46
Line_1 | 0.03752 | 0.15824 | 0.12231 | 0.037624 | 0.15817 | 0.12229 | 0.43325 | 1.8271 | 1.4123 | 0.43445 | 1.8264 | 1.4121 | 0.37336 | 1.6562 | 0.96012 | -0.37633 | -1.6314 | -0.95438 | 0.25677 | 0.71109 | 0.90857 | -0.25828 | -0.70142 | -0.89072 | -35.5974 | -152.2292 | 72.4849 | 144.4263 | 27.802 | -107.5637 | 1.0459 | 0.98648 | 0.93597 | 1.0506 | 0.97229 | 0.92448 | -1.0797 | -128.9934 | 115.9048 | -1.1109 | -128.9334 | 115.46
Line_2 | 0.03752 | 0.15824 | 0.12231 | 0.037624 | 0.15817 | 0.12229 | 0.43325 | 1.8271 | 1.4123 | 0.43445 | 1.8264 | 1.4121 | 0.37336 | 1.6562 | 0.96012 | -0.37633 | -1.6314 | -0.95438 | 0.25677 | 0.71109 | 0.90857 | -0.25828 | -0.70142 | -0.89072 | -35.5974 | -152.2292 | 72.4849 | 144.4263 | 27.802 | -107.5637 | 1.0459 | 0.98648 | 0.93597 | 1.0506 | 0.97229 | 0.92448 | -1.0797 | -128.9934 | 115.9048 | -1.1109 | -128.9334 | 115.46
Line_3 | 4.7673e-05 | 4.7673e-05 | 4.7673e-05 | 4.7673e-05 | 4.7673e-05 | 4.7673e-05 | 0.00055048 | 0.00055048 | 0.00055048 | 0.00055048 | 0.00055048 | 0.00055048 | -0.00055591 | 0.00021069 | 0.00034522 | -0.00055591 | 0.00021069 | 0.00034522 | -0.00014984 | 0.00050051 | -0.00038247 | -0.00014984 | 0.00050051 | -0.00038247 | 163.8351 | 163.8351 | 163.8351 | 163.8351 | 163.8351 | 163.8351 | 1.0459 | 0.98648 | 0.93597 | 1.0459 | 0.98648 | 0.93597 | -1.0797 | -128.9934 | 115.9048 | -1.0797 | -128.9934 | 115.9048

## LLG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.075395 | 0.31631 | 0.24451 | 0.075249 | 0.31635 | 0.24458 | 0.87059 | 3.6525 | 2.8233 | 0.8689 | 3.6529 | 2.8242 | -0.76116 | -3.1651 | -1.888 | 0.75265 | 3.2629 | 1.9088 | -0.5217 | -1.3671 | -1.7079 | 0.51657 | 1.4028 | 1.7814 | 144.4013 | 27.8283 | -107.5939 | -35.5737 | -152.198 | 72.4363 | 1.06 | 0.94395 | 0.90173 | 1.0506 | 0.97229 | 0.92448 | -1.1718 | -128.8114 | 114.5398 | -1.1109 | -128.9334 | 115.46
Line_1 | 0.03752 | 0.15824 | 0.12231 | 0.037624 | 0.15817 | 0.12229 | 0.43325 | 1.8271 | 1.4123 | 0.43445 | 1.8264 | 1.4121 | 0.37336 | 1.6562 | 0.96012 | -0.37633 | -1.6314 | -0.95438 | 0.25677 | 0.71109 | 0.90857 | -0.25828 | -0.70142 | -0.89072 | -35.5974 | -152.2292 | 72.4849 | 144.4263 | 27.802 | -107.5637 | 1.0459 | 0.98648 | 0.93597 | 1.0506 | 0.97229 | 0.92448 | -1.0797 | -128.9934 | 115.9048 | -1.1109 | -128.9334 | 115.46
Line_2 | 0.03752 | 0.15824 | 0.12231 | 0.037624 | 0.15817 | 0.12229 | 0.43325 | 1.8271 | 1.4123 | 0.43445 | 1.8264 | 1.4121 | 0.37336 | 1.6562 | 0.96012 | -0.37633 | -1.6314 | -0.95438 | 0.25677 | 0.71109 | 0.90857 | -0.25828 | -0.70142 | -0.89072 | -35.5974 | -152.2292 | 72.4849 | 144.4263 | 27.802 | -107.5637 | 1.0459 | 0.98648 | 0.93597 | 1.0506 | 0.97229 | 0.92448 | -1.0797 | -128.9934 | 115.9048 | -1.1109 | -128.9334 | 115.46
Line_3 | 4.7673e-05 | 4.7673e-05 | 4.7673e-05 | 4.7673e-05 | 4.7673e-05 | 4.7673e-05 | 0.00055048 | 0.00055048 | 0.00055048 | 0.00055048 | 0.00055048 | 0.00055048 | -0.00055591 | 0.00021069 | 0.00034522 | -0.00055591 | 0.00021069 | 0.00034522 | -0.00014984 | 0.00050051 | -0.00038247 | -0.00014984 | 0.00050051 | -0.00038247 | 163.8351 | 163.8351 | 163.8351 | 163.8351 | 163.8351 | 163.8351 | 1.0459 | 0.98648 | 0.93597 | 1.0459 | 0.98648 | 0.93597 | -1.0797 | -128.9934 | 115.9048 | -1.0797 | -128.9934 | 115.9048

## LLG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.55222 | 1.4738 | 1.1043 | 0.55134 | 1.474 | 1.1049 | 6.3765 | 17.0183 | 12.751 | 6.3664 | 17.0199 | 12.7578 | -1.3015 | -1.5286e-10 | -1.1391e-10 | 1.1215 | 4.1289 | 0.71191 | -4.527 | 1.8492e-12 | -1.73e-11 | 4.0837 | 0.55543 | 2.2026 | 107.4901 | -0.23672 | -129.5184 | -72.496 | 179.7292 | 50.516 | 0.73871 | 0 | 0 | 0.6652 | 0.24478 | 0.18144 | 1.45 | 0 | 0 | 2.1473 | -172.6091 | 122.6046
Line_1 | 0.27524 | 0.73728 | 0.55252 | 0.27567 | 0.73698 | 0.55243 | 3.1781 | 8.5134 | 6.38 | 3.1832 | 8.51 | 6.3789 | 0.51315 | 3.0991 | 0.53584 | -0.56076 | -2.0644 | -0.35596 | 1.9299 | 0.41637 | 1.6535 | -2.0419 | -0.27771 | -1.1013 | -72.5317 | 179.7011 | 50.5635 | 107.504 | -0.27078 | -129.484 | 0.62834 | 0.3673 | 0.27244 | 0.6652 | 0.24478 | 0.18144 | 2.5781 | -172.647 | 122.608 | 2.1473 | -172.6091 | 122.6046
Line_2 | 0.27524 | 0.73728 | 0.55252 | 0.27567 | 0.73698 | 0.55243 | 3.1781 | 8.5134 | 6.38 | 3.1832 | 8.51 | 6.3789 | 0.51315 | 3.0991 | 0.53584 | -0.56076 | -2.0644 | -0.35596 | 1.9299 | 0.41637 | 1.6535 | -2.0419 | -0.27771 | -1.1013 | -72.5317 | 179.7011 | 50.5635 | 107.504 | -0.27078 | -129.484 | 0.62834 | 0.3673 | 0.27244 | 0.6652 | 0.24478 | 0.18144 | 2.5781 | -172.647 | 122.608 | 2.1473 | -172.6091 | 122.6046
Line_3 | 0.00019871 | 0.00019871 | 0.00019871 | 0.00019871 | 0.00019871 | 0.00019871 | 0.0022945 | 0.0022945 | 0.0022945 | 0.0022945 | 0.0022945 | 0.0022945 | -0.0012288 | 0.00067912 | 0.0005497 | -0.0012288 | 0.00067912 | 0.0005497 | -0.00075406 | 0.00049904 | -0.00029766 | -0.00075406 | 0.00049904 | -0.00029766 | 151.043 | 151.043 | 151.043 | 151.043 | 151.043 | 151.043 | 0.62834 | 0.3673 | 0.27244 | 0.62834 | 0.3673 | 0.27244 | 2.5781 | -172.647 | 122.608 | 2.5781 | -172.647 | 122.608

## LLG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.55222 | 1.4738 | 1.1043 | 0.55134 | 1.474 | 1.1049 | 6.3765 | 17.0183 | 12.751 | 6.3664 | 17.0199 | 12.7578 | -1.3015 | -1.5286e-10 | -1.1391e-10 | 1.1215 | 4.1289 | 0.71191 | -4.527 | 1.8492e-12 | -1.73e-11 | 4.0837 | 0.55543 | 2.2026 | 107.4901 | -0.23672 | -129.5184 | -72.496 | 179.7292 | 50.516 | 0.73871 | 0 | 0 | 0.6652 | 0.24478 | 0.18144 | 1.45 | 0 | 0 | 2.1473 | -172.6091 | 122.6046
Line_1 | 0.27524 | 0.73728 | 0.55252 | 0.27567 | 0.73698 | 0.55243 | 3.1781 | 8.5134 | 6.38 | 3.1832 | 8.51 | 6.3789 | 0.51315 | 3.0991 | 0.53584 | -0.56076 | -2.0644 | -0.35596 | 1.9299 | 0.41637 | 1.6535 | -2.0419 | -0.27771 | -1.1013 | -72.5317 | 179.7011 | 50.5635 | 107.504 | -0.27078 | -129.484 | 0.62834 | 0.3673 | 0.27244 | 0.6652 | 0.24478 | 0.18144 | 2.5781 | -172.647 | 122.608 | 2.1473 | -172.6091 | 122.6046
Line_2 | 0.27524 | 0.73728 | 0.55252 | 0.27567 | 0.73698 | 0.55243 | 3.1781 | 8.5134 | 6.38 | 3.1832 | 8.51 | 6.3789 | 0.51315 | 3.0991 | 0.53584 | -0.56076 | -2.0644 | -0.35596 | 1.9299 | 0.41637 | 1.6535 | -2.0419 | -0.27771 | -1.1013 | -72.5317 | 179.7011 | 50.5635 | 107.504 | -0.27078 | -129.484 | 0.62834 | 0.3673 | 0.27244 | 0.6652 | 0.24478 | 0.18144 | 2.5781 | -172.647 | 122.608 | 2.1473 | -172.6091 | 122.6046
Line_3 | 0.00019871 | 0.00019871 | 0.00019871 | 0.00019871 | 0.00019871 | 0.00019871 | 0.0022945 | 0.0022945 | 0.0022945 | 0.0022945 | 0.0022945 | 0.0022945 | -0.0012288 | 0.00067912 | 0.0005497 | -0.0012288 | 0.00067912 | 0.0005497 | -0.00075406 | 0.00049904 | -0.00029766 | -0.00075406 | 0.00049904 | -0.00029766 | 151.043 | 151.043 | 151.043 | 151.043 | 151.043 | 151.043 | 0.62834 | 0.3673 | 0.27244 | 0.62834 | 0.3673 | 0.27244 | 2.5781 | -172.647 | 122.608 | 2.5781 | -172.647 | 122.608

## LLG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.089057 | 0.30621 | 0.23176 | 0.088925 | 0.30623 | 0.23183 | 1.0283 | 3.5359 | 2.6761 | 1.0268 | 3.536 | 2.6769 | -0.82251 | -2.8806 | -1.6038 | 0.81597 | 3.0352 | 1.6339 | -0.55281 | -0.84553 | -1.4763 | 0.54236 | 0.87548 | 1.5517 | 145.0869 | 34.8875 | -108.1748 | -34.8913 | -145.1379 | 71.8541 | 0.9637 | 0.84906 | 0.81457 | 0.95419 | 0.89336 | 0.84175 | -1.0081 | -128.7544 | 114.4547 | -1.2803 | -129.048 | 115.3756
Line_1 | 0.044393 | 0.15316 | 0.11592 | 0.044463 | 0.15311 | 0.11591 | 0.51261 | 1.7685 | 1.3385 | 0.51341 | 1.768 | 1.3385 | 0.40583 | 1.5566 | 0.82466 | -0.40799 | -1.5176 | -0.81695 | 0.26861 | 0.44555 | 0.79432 | -0.27118 | -0.43774 | -0.77584 | -34.9165 | -145.1596 | 71.8896 | 145.1087 | 34.8621 | -108.1459 | 0.9494 | 0.91553 | 0.85545 | 0.95419 | 0.89336 | 0.84175 | -1.4175 | -129.1867 | 115.8159 | -1.2803 | -129.048 | 115.3756
Line_2 | 0.044393 | 0.15316 | 0.11592 | 0.044463 | 0.15311 | 0.11591 | 0.51261 | 1.7685 | 1.3385 | 0.51341 | 1.768 | 1.3385 | 0.40583 | 1.5566 | 0.82466 | -0.40799 | -1.5176 | -0.81695 | 0.26861 | 0.44555 | 0.79432 | -0.27118 | -0.43774 | -0.77584 | -34.9165 | -145.1596 | 71.8896 | 145.1087 | 34.8621 | -108.1459 | 0.9494 | 0.91553 | 0.85545 | 0.95419 | 0.89336 | 0.84175 | -1.4175 | -129.1867 | 115.8159 | -1.2803 | -129.048 | 115.3756
Line_3 | 3.0539e-05 | 3.0539e-05 | 3.0539e-05 | 3.0539e-05 | 3.0539e-05 | 3.0539e-05 | 0.00035263 | 0.00035263 | 0.00035263 | 0.00035263 | 0.00035263 | 0.00035263 | -0.00033382 | 0.00021655 | 0.00011727 | -0.00033382 | 0.00021655 | 0.00011727 | 2.543e-05 | 0.00023945 | -0.00027793 | 2.543e-05 | 0.00023945 | -0.00027793 | -177.0612 | -177.0612 | -177.0612 | -177.0612 | -177.0612 | -177.0612 | 0.9494 | 0.91553 | 0.85545 | 0.9494 | 0.91553 | 0.85545 | -1.4175 | -129.1867 | 115.8159 | -1.4175 | -129.1867 | 115.8159

## LLG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.089057 | 0.30621 | 0.23176 | 0.088925 | 0.30623 | 0.23183 | 1.0283 | 3.5359 | 2.6761 | 1.0268 | 3.536 | 2.6769 | -0.82251 | -2.8806 | -1.6038 | 0.81597 | 3.0352 | 1.6339 | -0.55281 | -0.84553 | -1.4763 | 0.54236 | 0.87548 | 1.5517 | 145.0869 | 34.8875 | -108.1748 | -34.8913 | -145.1379 | 71.8541 | 0.9637 | 0.84906 | 0.81457 | 0.95419 | 0.89336 | 0.84175 | -1.0081 | -128.7544 | 114.4547 | -1.2803 | -129.048 | 115.3756
Line_1 | 0.044393 | 0.15316 | 0.11592 | 0.044463 | 0.15311 | 0.11591 | 0.51261 | 1.7685 | 1.3385 | 0.51341 | 1.768 | 1.3385 | 0.40583 | 1.5566 | 0.82466 | -0.40799 | -1.5176 | -0.81695 | 0.26861 | 0.44555 | 0.79432 | -0.27118 | -0.43774 | -0.77584 | -34.9165 | -145.1596 | 71.8896 | 145.1087 | 34.8621 | -108.1459 | 0.9494 | 0.91553 | 0.85545 | 0.95419 | 0.89336 | 0.84175 | -1.4175 | -129.1867 | 115.8159 | -1.2803 | -129.048 | 115.3756
Line_2 | 0.044393 | 0.15316 | 0.11592 | 0.044463 | 0.15311 | 0.11591 | 0.51261 | 1.7685 | 1.3385 | 0.51341 | 1.768 | 1.3385 | 0.40583 | 1.5566 | 0.82466 | -0.40799 | -1.5176 | -0.81695 | 0.26861 | 0.44555 | 0.79432 | -0.27118 | -0.43774 | -0.77584 | -34.9165 | -145.1596 | 71.8896 | 145.1087 | 34.8621 | -108.1459 | 0.9494 | 0.91553 | 0.85545 | 0.95419 | 0.89336 | 0.84175 | -1.4175 | -129.1867 | 115.8159 | -1.2803 | -129.048 | 115.3756
Line_3 | 3.0539e-05 | 3.0539e-05 | 3.0539e-05 | 3.0539e-05 | 3.0539e-05 | 3.0539e-05 | 0.00035263 | 0.00035263 | 0.00035263 | 0.00035263 | 0.00035263 | 0.00035263 | -0.00033382 | 0.00021655 | 0.00011727 | -0.00033382 | 0.00021655 | 0.00011727 | 2.543e-05 | 0.00023945 | -0.00027793 | 2.543e-05 | 0.00023945 | -0.00027793 | -177.0612 | -177.0612 | -177.0612 | -177.0612 | -177.0612 | -177.0612 | 0.9494 | 0.91553 | 0.85545 | 0.9494 | 0.91553 | 0.85545 | -1.4175 | -129.1867 | 115.8159 | -1.4175 | -129.1867 | 115.8159