## LLL_max_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 3.6473 | 3.6473 | 0 | 0 | 126.3464 | 126.3464 | 35.9247 | -15.1722 | 40.9065 | -17.3604 | -73.1767 | 106.8233 | 0.43089 | 0.18248 | -24.4668 | -24.3287
Line_1 | 2.6793 | 2.6793 | 5.3365 | 0 | 92.8137 | 92.8137 | -1e-07 | 11.1987 | -1e-07 | 12.7062 | 107.0629 | -72.9371 | 0 | 0.18248 | 0 | -24.3287
Line_2 | 0.96809 | 0.96809 | 0 | 0 | 33.5358 | 33.5358 | -2.5115 | 3.9735 | -2.9954 | 4.6542 | 106.1604 | -73.8396 | 0.11656 | 0.18248 | -23.8181 | -24.3287
Line_3 | 1.7114 | 1.7114 | 3.4087 | 0 | 59.2845 | 59.2845 | -1e-07 | 4.569 | -1e-07 | 5.1841 | 107.5734 | -72.4266 | 0 | 0.11656 | 0 | -23.8181

## LLL_max_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 3.6473 | 3.6473 | 0 | 0 | 126.3464 | 126.3464 | 35.9247 | -15.1722 | 40.9065 | -17.3604 | -73.1767 | 106.8233 | 0.43089 | 0.18248 | -24.4668 | -24.3287
Line_1 | 2.6793 | 2.6793 | 5.3365 | 0 | 92.8137 | 92.8137 | -1e-07 | 11.1987 | -1e-07 | 12.7062 | 107.0629 | -72.9371 | 0 | 0.18248 | 0 | -24.3287
Line_2 | 0.96809 | 0.96809 | 0 | 0 | 33.5358 | 33.5358 | -2.5115 | 3.9735 | -2.9954 | 4.6542 | 106.1604 | -73.8396 | 0.11656 | 0.18248 | -23.8181 | -24.3287
Line_3 | 1.7114 | 1.7114 | 3.4087 | 0 | 59.2845 | 59.2845 | -1e-07 | 4.569 | -1e-07 | 5.1841 | 107.5734 | -72.4266 | 0 | 0.11656 | 0 | -23.8181

## LLL_max_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.95594 | 0.95594 | 0 | 0 | 33.1147 | 33.1147 | 21.9414 | -20.5158 | 22.5228 | -20.9053 | -52.3773 | 127.6227 | 0.94954 | 0.88451 | -6.6281 | -6.8385
Line_1 | 0.70223 | 0.70223 | 1.3987 | 0 | 24.326 | 24.326 | -14.3657 | 15.1349 | -14.421 | 15.2938 | 127.8623 | -52.1377 | 0.83677 | 0.88451 | -7.0275 | -6.8385
Line_2 | 0.25373 | 0.25373 | 0 | 0 | 8.7895 | 8.7895 | -5.2804 | 5.3809 | -5.4975 | 5.6115 | 126.9598 | -53.0402 | 0.86725 | 0.88451 | -6.8864 | -6.8385
Line_3 | 0.44855 | 0.44855 | 0.8934 | 0 | 15.5381 | 15.5381 | -9.2577 | 9.5716 | -9.1293 | 9.4854 | 128.3728 | -51.6272 | 0.83677 | 0.86725 | -7.0275 | -6.8864

## LLL_max_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.95594 | 0.95594 | 0 | 0 | 33.1147 | 33.1147 | 21.9414 | -20.5158 | 22.5228 | -20.9053 | -52.3773 | 127.6227 | 0.94954 | 0.88451 | -6.6281 | -6.8385
Line_1 | 0.70223 | 0.70223 | 1.3987 | 0 | 24.326 | 24.326 | -14.3657 | 15.1349 | -14.421 | 15.2938 | 127.8623 | -52.1377 | 0.83677 | 0.88451 | -7.0275 | -6.8385
Line_2 | 0.25373 | 0.25373 | 0 | 0 | 8.7895 | 8.7895 | -5.2804 | 5.3809 | -5.4975 | 5.6115 | 126.9598 | -53.0402 | 0.86725 | 0.88451 | -6.8864 | -6.8385
Line_3 | 0.44855 | 0.44855 | 0.8934 | 0 | 15.5381 | 15.5381 | -9.2577 | 9.5716 | -9.1293 | 9.4854 | 128.3728 | -51.6272 | 0.83677 | 0.86725 | -7.0275 | -6.8864

## LLL_min_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 2.9516 | 2.9516 | 0 | 0 | 102.2474 | 102.2474 | 45.756 | -19.6615 | 26.7104 | -11.29 | -61.5111 | 118.4889 | 0.51817 | 0.22174 | -31.2365 | -31.6459
Line_1 | 2.2078 | 2.2078 | 3.9682 | 0 | 76.4821 | 76.4821 | -1e-07 | 14.6004 | -1e-07 | 8.628 | 117.7734 | -62.2266 | 0 | 0.22174 | 0 | -31.6459
Line_2 | 0.74446 | 0.74446 | 0 | 0 | 25.7889 | 25.7889 | -3.4011 | 5.0611 | -1.681 | 2.6619 | 120.6115 | -59.3885 | 0.14711 | 0.22174 | -33.0879 | -31.6459
Line_3 | 1.4648 | 1.4648 | 2.6326 | 0 | 50.7409 | 50.7409 | -1e-07 | 6.4263 | -1e-07 | 3.7976 | 116.3313 | -63.6687 | 0 | 0.14711 | 0 | -33.0879

## LLL_min_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 2.9516 | 2.9516 | 0 | 0 | 102.2474 | 102.2474 | 45.756 | -19.6615 | 26.7104 | -11.29 | -61.5111 | 118.4889 | 0.51817 | 0.22174 | -31.2365 | -31.6459
Line_1 | 2.2078 | 2.2078 | 3.9682 | 0 | 76.4821 | 76.4821 | -1e-07 | 14.6004 | -1e-07 | 8.628 | 117.7734 | -62.2266 | 0 | 0.22174 | 0 | -31.6459
Line_2 | 0.74446 | 0.74446 | 0 | 0 | 25.7889 | 25.7889 | -3.4011 | 5.0611 | -1.681 | 2.6619 | 120.6115 | -59.3885 | 0.14711 | 0.22174 | -33.0879 | -31.6459
Line_3 | 1.4648 | 1.4648 | 2.6326 | 0 | 50.7409 | 50.7409 | -1e-07 | 6.4263 | -1e-07 | 3.7976 | 116.3313 | -63.6687 | 0 | 0.14711 | 0 | -33.0879

## LLL_min_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.79717 | 0.79717 | 0 | 0 | 27.6148 | 27.6148 | 18.6059 | -16.7025 | 15.5964 | -14.4716 | -47.0211 | 132.9789 | 0.87917 | 0.80029 | -7.0497 | -6.1144
Line_1 | 0.59629 | 0.59629 | 1.0717 | 0 | 20.6561 | 20.6561 | -11.2925 | 12.3575 | -10.3507 | 10.9801 | 132.2633 | -47.7367 | 0.7416 | 0.80029 | -5.2282 | -6.1144
Line_2 | 0.20106 | 0.20106 | 0 | 0 | 6.965 | 6.965 | -4.2239 | 4.345 | -3.4199 | 3.4915 | 135.1015 | -44.8985 | 0.78031 | 0.80029 | -5.9028 | -6.1144
Line_3 | 0.3956 | 0.3956 | 0.71101 | 0 | 13.704 | 13.704 | -7.3166 | 7.7854 | -7.0534 | 7.3304 | 130.8213 | -49.1787 | 0.7416 | 0.78031 | -5.2282 | -5.9028

## LLL_min_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.79717 | 0.79717 | 0 | 0 | 27.6148 | 27.6148 | 18.6059 | -16.7025 | 15.5964 | -14.4716 | -47.0211 | 132.9789 | 0.87917 | 0.80029 | -7.0497 | -6.1144
Line_1 | 0.59629 | 0.59629 | 1.0717 | 0 | 20.6561 | 20.6561 | -11.2925 | 12.3575 | -10.3507 | 10.9801 | 132.2633 | -47.7367 | 0.7416 | 0.80029 | -5.2282 | -6.1144
Line_2 | 0.20106 | 0.20106 | 0 | 0 | 6.965 | 6.965 | -4.2239 | 4.345 | -3.4199 | 3.4915 | 135.1015 | -44.8985 | 0.78031 | 0.80029 | -5.9028 | -6.1144
Line_3 | 0.3956 | 0.3956 | 0.71101 | 0 | 13.704 | 13.704 | -7.3166 | 7.7854 | -7.0534 | 7.3304 | 130.8213 | -49.1787 | 0.7416 | 0.78031 | -5.2282 | -5.9028

## LL_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.16767 | 3.0916 | 3.2377 | 0.16767 | 3.0916 | 3.2377 | 1.9361 | 35.6989 | 37.3862 | 1.9361 | 35.6989 | 37.3862 | -2.0827 | 27.9998 | -10.9539 | 2.0973 | -23.0296 | 16.405 | -0.52411 | 4.3805 | 15.7348 | 0.5407 | 1.2588 | -9.5499 | 167.548 | -162.3322 | 16.1787 | -12.452 | 17.6678 | -163.8213 | 1.1092 | 0.79387 | 0.51281 | 1.1187 | 0.64607 | 0.50773 | 1.6735 | -153.4406 | 141.0226 | 2.0047 | -165.4608 | 165.9736
Line_1 | 0.085685 | 2.2727 | 2.3472 | 0.085685 | 2.2727 | 2.3472 | 0.9894 | 26.2428 | 27.1034 | 0.9894 | 26.2428 | 27.1034 | 1.0722 | -14.2537 | 14.7898 | -1.0684 | 16.9395 | -11.9249 | 0.29329 | 3.7641 | -3.6175 | -0.28895 | -0.7167 | 6.8681 | -13.1289 | 16.9619 | -164.0868 | 166.8711 | -163.0381 | 15.9132 | 1.1235 | 0.56177 | 0.56177 | 1.1187 | 0.64607 | 0.50773 | 2.1688 | -177.8312 | -177.8312 | 2.0047 | -165.4608 | 165.9736
Line_2 | 0.082 | 0.81957 | 0.89061 | 0.082 | 0.81957 | 0.89061 | 0.94685 | 9.4636 | 10.2839 | 0.94685 | 9.4636 | 10.2839 | 1.0323 | -5.7408 | 4.8926 | -1.0289 | 6.0901 | -4.4801 | 0.25571 | 0.93837 | -2.2138 | -0.25175 | -0.54207 | 2.6818 | -11.7447 | 19.6256 | -163.1216 | 168.2553 | -160.3744 | 16.8784 | 1.1232 | 0.61467 | 0.52219 | 1.1187 | 0.64607 | 0.50773 | 2.1675 | -169.6577 | 172.5323 | 2.0047 | -165.4608 | 165.9736
Line_3 | 0.0042047 | 1.4545 | 1.4568 | 0.0042047 | 1.4545 | 1.4568 | 0.048552 | 16.7952 | 16.8219 | 0.048552 | 16.7952 | 16.8219 | 0.039633 | -9.1822 | 9.202 | -0.039624 | 10.2823 | -8.0984 | 0.037482 | 2.1693 | -2.1506 | -0.037472 | -0.92111 | 3.4027 | -41.2335 | 15.4613 | -164.6769 | 138.7665 | -164.5387 | 15.3231 | 1.1235 | 0.56177 | 0.56177 | 1.1232 | 0.61467 | 0.52219 | 2.1688 | -177.8312 | -177.8312 | 2.1675 | -169.6577 | 172.5323

## LL_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.16767 | 3.0916 | 3.2377 | 0.16767 | 3.0916 | 3.2377 | 1.9361 | 35.6989 | 37.3862 | 1.9361 | 35.6989 | 37.3862 | -2.0827 | 27.9998 | -10.9539 | 2.0973 | -23.0296 | 16.405 | -0.52411 | 4.3805 | 15.7348 | 0.5407 | 1.2588 | -9.5499 | 167.548 | -162.3322 | 16.1787 | -12.452 | 17.6678 | -163.8213 | 1.1092 | 0.79387 | 0.51281 | 1.1187 | 0.64607 | 0.50773 | 1.6735 | -153.4406 | 141.0226 | 2.0047 | -165.4608 | 165.9736
Line_1 | 0.085685 | 2.2727 | 2.3472 | 0.085685 | 2.2727 | 2.3472 | 0.9894 | 26.2428 | 27.1034 | 0.9894 | 26.2428 | 27.1034 | 1.0722 | -14.2537 | 14.7898 | -1.0684 | 16.9395 | -11.9249 | 0.29329 | 3.7641 | -3.6175 | -0.28895 | -0.7167 | 6.8681 | -13.1289 | 16.9619 | -164.0868 | 166.8711 | -163.0381 | 15.9132 | 1.1235 | 0.56177 | 0.56177 | 1.1187 | 0.64607 | 0.50773 | 2.1688 | -177.8312 | -177.8312 | 2.0047 | -165.4608 | 165.9736
Line_2 | 0.082 | 0.81957 | 0.89061 | 0.082 | 0.81957 | 0.89061 | 0.94685 | 9.4636 | 10.2839 | 0.94685 | 9.4636 | 10.2839 | 1.0323 | -5.7408 | 4.8926 | -1.0289 | 6.0901 | -4.4801 | 0.25571 | 0.93837 | -2.2138 | -0.25175 | -0.54207 | 2.6818 | -11.7447 | 19.6256 | -163.1216 | 168.2553 | -160.3744 | 16.8784 | 1.1232 | 0.61467 | 0.52219 | 1.1187 | 0.64607 | 0.50773 | 2.1675 | -169.6577 | 172.5323 | 2.0047 | -165.4608 | 165.9736
Line_3 | 0.0042047 | 1.4545 | 1.4568 | 0.0042047 | 1.4545 | 1.4568 | 0.048552 | 16.7952 | 16.8219 | 0.048552 | 16.7952 | 16.8219 | 0.039633 | -9.1822 | 9.202 | -0.039624 | 10.2823 | -8.0984 | 0.037482 | 2.1693 | -2.1506 | -0.037472 | -0.92111 | 3.4027 | -41.2335 | 15.4613 | -164.6769 | 138.7665 | -164.5387 | 15.3231 | 1.1235 | 0.56177 | 0.56177 | 1.1232 | 0.61467 | 0.52219 | 2.1688 | -177.8312 | -177.8312 | 2.1675 | -169.6577 | 172.5323

## LL_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.071598 | 1.3201 | 1.3825 | 0.071598 | 1.3201 | 1.3825 | 0.82674 | 15.2438 | 15.9643 | 0.82674 | 15.2438 | 15.9643 | -0.90611 | 15.0577 | 0.99002 | 0.90878 | -14.1515 | 0.0039296 | 0.071765 | 2.9587 | 13.1075 | -0.06874 | -1.9304 | -11.9797 | -174.7256 | -144.6058 | 33.905 | 5.2744 | 35.3942 | -146.095 | 1.0994 | 1.0067 | 0.82339 | 1.1024 | 0.93694 | 0.75041 | 0.74599 | -133.4895 | 119.5857 | 0.94877 | -136.8379 | 123.9238
Line_1 | 0.036588 | 0.97046 | 1.0023 | 0.036588 | 0.97046 | 1.0023 | 0.42248 | 11.2059 | 11.5734 | 0.42248 | 11.2059 | 11.5734 | 0.46549 | -9.895 | 0.56547 | -0.46479 | 10.3847 | -0.043093 | -0.028849 | -0.99149 | -8.092 | 0.029639 | 1.5471 | 8.6847 | 4.5975 | 34.6883 | -146.3605 | -175.4025 | -145.3117 | 33.6395 | 1.1039 | 0.88743 | 0.70089 | 1.1024 | 0.93694 | 0.75041 | 1.051 | -139.5897 | 127.6369 | 0.94877 | -136.8379 | 123.9238
Line_2 | 0.035015 | 0.34997 | 0.3803 | 0.035015 | 0.34997 | 0.3803 | 0.40431 | 4.041 | 4.3913 | 0.40431 | 4.041 | 4.3913 | 0.44463 | -3.7031 | 0.036043 | -0.44399 | 3.7668 | 0.039163 | -0.038378 | -0.31102 | -3.2097 | 0.039101 | 0.38328 | 3.2951 | 5.9817 | 37.352 | -145.3952 | -174.0183 | -142.648 | 34.6048 | 1.1038 | 0.9196 | 0.73097 | 1.1024 | 0.93694 | 0.75041 | 1.0485 | -137.847 | 125.2482 | 0.94877 | -136.8379 | 123.9238
Line_3 | 0.0017955 | 0.62109 | 0.62207 | 0.0017955 | 0.62109 | 0.62207 | 0.020732 | 7.1717 | 7.1831 | 0.020732 | 7.1717 | 7.1831 | 0.020816 | -6.3139 | 0.40267 | -0.020814 | 6.5145 | -0.20144 | 0.0095119 | -0.80016 | -5.0185 | -0.00951 | 1.0278 | 5.2468 | -23.5071 | 33.1877 | -146.9505 | 156.4929 | -146.8123 | 33.0495 | 1.1039 | 0.88743 | 0.70089 | 1.1038 | 0.9196 | 0.73097 | 1.051 | -139.5897 | 127.6369 | 1.0485 | -137.847 | 125.2482

## LL_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.071598 | 1.3201 | 1.3825 | 0.071598 | 1.3201 | 1.3825 | 0.82674 | 15.2438 | 15.9643 | 0.82674 | 15.2438 | 15.9643 | -0.90611 | 15.0577 | 0.99002 | 0.90878 | -14.1515 | 0.0039296 | 0.071765 | 2.9587 | 13.1075 | -0.06874 | -1.9304 | -11.9797 | -174.7256 | -144.6058 | 33.905 | 5.2744 | 35.3942 | -146.095 | 1.0994 | 1.0067 | 0.82339 | 1.1024 | 0.93694 | 0.75041 | 0.74599 | -133.4895 | 119.5857 | 0.94877 | -136.8379 | 123.9238
Line_1 | 0.036588 | 0.97046 | 1.0023 | 0.036588 | 0.97046 | 1.0023 | 0.42248 | 11.2059 | 11.5734 | 0.42248 | 11.2059 | 11.5734 | 0.46549 | -9.895 | 0.56547 | -0.46479 | 10.3847 | -0.043093 | -0.028849 | -0.99149 | -8.092 | 0.029639 | 1.5471 | 8.6847 | 4.5975 | 34.6883 | -146.3605 | -175.4025 | -145.3117 | 33.6395 | 1.1039 | 0.88743 | 0.70089 | 1.1024 | 0.93694 | 0.75041 | 1.051 | -139.5897 | 127.6369 | 0.94877 | -136.8379 | 123.9238
Line_2 | 0.035015 | 0.34997 | 0.3803 | 0.035015 | 0.34997 | 0.3803 | 0.40431 | 4.041 | 4.3913 | 0.40431 | 4.041 | 4.3913 | 0.44463 | -3.7031 | 0.036043 | -0.44399 | 3.7668 | 0.039163 | -0.038378 | -0.31102 | -3.2097 | 0.039101 | 0.38328 | 3.2951 | 5.9817 | 37.352 | -145.3952 | -174.0183 | -142.648 | 34.6048 | 1.1038 | 0.9196 | 0.73097 | 1.1024 | 0.93694 | 0.75041 | 1.0485 | -137.847 | 125.2482 | 0.94877 | -136.8379 | 123.9238
Line_3 | 0.0017955 | 0.62109 | 0.62207 | 0.0017955 | 0.62109 | 0.62207 | 0.020732 | 7.1717 | 7.1831 | 0.020732 | 7.1717 | 7.1831 | 0.020816 | -6.3139 | 0.40267 | -0.020814 | 6.5145 | -0.20144 | 0.0095119 | -0.80016 | -5.0185 | -0.00951 | 1.0278 | 5.2468 | -23.5071 | 33.1877 | -146.9505 | 156.4929 | -146.8123 | 33.0495 | 1.1039 | 0.88743 | 0.70089 | 1.1038 | 0.9196 | 0.73097 | 1.051 | -139.5897 | 127.6369 | 1.0485 | -137.847 | 125.2482

## LL_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.1573 | 2.5018 | 2.6288 | 0.1573 | 2.5018 | 2.6288 | 1.8163 | 28.8882 | 30.3543 | 1.8163 | 28.8882 | 30.3543 | -1.8033 | 24.2039 | -2.0881 | 1.828 | -17.955 | 8.9874 | -0.29968 | -0.52181 | 13.6286 | 0.31428 | 4.2146 | -9.5515 | 172.4103 | -150.363 | 27.5625 | -7.5897 | 29.637 | -152.4375 | 1.0064 | 0.83804 | 0.45422 | 1.0212 | 0.63843 | 0.43207 | 1.8461 | -151.598 | 126.2732 | 2.1658 | -163.5729 | 160.8196
Line_1 | 0.080807 | 1.868 | 1.9334 | 0.080807 | 1.868 | 1.9334 | 0.93307 | 21.5701 | 22.3245 | 0.93307 | 21.5701 | 22.3245 | 0.9414 | -10.0168 | 10.4875 | -0.93488 | 13.5007 | -6.7556 | 0.18797 | 4.7735 | -4.6795 | -0.18412 | -2.7146 | 6.8848 | -8.9755 | 27.7962 | -153.6375 | 171.0245 | -152.2038 | 26.3625 | 1.0288 | 0.51442 | 0.51442 | 1.0212 | 0.63843 | 0.43207 | 2.3162 | -177.6838 | -177.6838 | 2.1658 | -163.5729 | 160.8196
Line_2 | 0.07654 | 0.63756 | 0.697 | 0.07654 | 0.63756 | 0.697 | 0.88381 | 7.3619 | 8.0483 | 0.88381 | 7.3619 | 8.0483 | 0.89894 | -4.0484 | 2.7169 | -0.89309 | 4.4543 | -2.2318 | 0.13362 | 1.7398 | -2.3801 | -0.13017 | -1.4999 | 2.6667 | -6.1266 | 35.0378 | -149.1073 | 173.8734 | -144.9622 | 30.8927 | 1.0283 | 0.59855 | 0.44878 | 1.0212 | 0.63843 | 0.43207 | 2.3283 | -168.2174 | 169.6733 | 2.1658 | -163.5729 | 160.8196
Line_3 | 0.0057872 | 1.2382 | 1.2398 | 0.0057872 | 1.2382 | 1.2398 | 0.066825 | 14.2971 | 14.3155 | 0.066825 | 14.2971 | 14.3155 | 0.041958 | -6.8307 | 6.8517 | -0.041925 | 8.3613 | -5.3171 | 0.054463 | 2.7263 | -2.6991 | -0.054444 | -1.8218 | 3.6059 | -50.0733 | 24.0746 | -156.1827 | 129.9267 | -155.9254 | 23.8173 | 1.0288 | 0.51442 | 0.51442 | 1.0283 | 0.59855 | 0.44878 | 2.3162 | -177.6838 | -177.6838 | 2.3283 | -168.2174 | 169.6733

## LL_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.1573 | 2.5018 | 2.6288 | 0.1573 | 2.5018 | 2.6288 | 1.8163 | 28.8882 | 30.3543 | 1.8163 | 28.8882 | 30.3543 | -1.8033 | 24.2039 | -2.0881 | 1.828 | -17.955 | 8.9874 | -0.29968 | -0.52181 | 13.6286 | 0.31428 | 4.2146 | -9.5515 | 172.4103 | -150.363 | 27.5625 | -7.5897 | 29.637 | -152.4375 | 1.0064 | 0.83804 | 0.45422 | 1.0212 | 0.63843 | 0.43207 | 1.8461 | -151.598 | 126.2732 | 2.1658 | -163.5729 | 160.8196
Line_1 | 0.080807 | 1.868 | 1.9334 | 0.080807 | 1.868 | 1.9334 | 0.93307 | 21.5701 | 22.3245 | 0.93307 | 21.5701 | 22.3245 | 0.9414 | -10.0168 | 10.4875 | -0.93488 | 13.5007 | -6.7556 | 0.18797 | 4.7735 | -4.6795 | -0.18412 | -2.7146 | 6.8848 | -8.9755 | 27.7962 | -153.6375 | 171.0245 | -152.2038 | 26.3625 | 1.0288 | 0.51442 | 0.51442 | 1.0212 | 0.63843 | 0.43207 | 2.3162 | -177.6838 | -177.6838 | 2.1658 | -163.5729 | 160.8196
Line_2 | 0.07654 | 0.63756 | 0.697 | 0.07654 | 0.63756 | 0.697 | 0.88381 | 7.3619 | 8.0483 | 0.88381 | 7.3619 | 8.0483 | 0.89894 | -4.0484 | 2.7169 | -0.89309 | 4.4543 | -2.2318 | 0.13362 | 1.7398 | -2.3801 | -0.13017 | -1.4999 | 2.6667 | -6.1266 | 35.0378 | -149.1073 | 173.8734 | -144.9622 | 30.8927 | 1.0283 | 0.59855 | 0.44878 | 1.0212 | 0.63843 | 0.43207 | 2.3283 | -168.2174 | 169.6733 | 2.1658 | -163.5729 | 160.8196
Line_3 | 0.0057872 | 1.2382 | 1.2398 | 0.0057872 | 1.2382 | 1.2398 | 0.066825 | 14.2971 | 14.3155 | 0.066825 | 14.2971 | 14.3155 | 0.041958 | -6.8307 | 6.8517 | -0.041925 | 8.3613 | -5.3171 | 0.054463 | 2.7263 | -2.6991 | -0.054444 | -1.8218 | 3.6059 | -50.0733 | 24.0746 | -156.1827 | 129.9267 | -155.9254 | 23.8173 | 1.0288 | 0.51442 | 0.51442 | 1.0283 | 0.59855 | 0.44878 | 2.3162 | -177.6838 | -177.6838 | 2.3283 | -168.2174 | 169.6733

## LL_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.068597 | 1.091 | 1.1464 | 0.068597 | 1.091 | 1.1464 | 0.79209 | 12.5981 | 13.2375 | 0.79209 | 12.5981 | 13.2375 | -0.78949 | 11.8666 | 2.206 | 0.79419 | -10.6782 | -0.89388 | 0.059138 | 0.94684 | 9.8501 | -0.056362 | -0.24454 | -9.0747 | -174.893 | -137.6663 | 40.2592 | 5.107 | 42.3337 | -139.7408 | 0.99951 | 0.94493 | 0.76254 | 1.0052 | 0.84783 | 0.68885 | 0.82315 | -133.1043 | 117.6357 | 1.0476 | -136.3544 | 124.6336
Line_1 | 0.03524 | 0.81464 | 0.84313 | 0.03524 | 0.81464 | 0.84313 | 0.40691 | 9.4067 | 9.7357 | 0.40691 | 9.4067 | 9.7357 | 0.40981 | -7.3006 | 0.19224 | -0.40857 | 7.9632 | 0.5175 | -0.018346 | -0.047078 | -6.267 | 0.019079 | 0.43863 | 6.6864 | 3.7212 | 40.4929 | -140.9408 | -176.2788 | -139.5071 | 39.0592 | 1.0081 | 0.77612 | 0.64402 | 1.0052 | 0.84783 | 0.68885 | 1.1579 | -139.1377 | 130.8161 | 1.0476 | -136.3544 | 124.6336
Line_2 | 0.033379 | 0.27804 | 0.30396 | 0.033379 | 0.27804 | 0.30396 | 0.38543 | 3.2105 | 3.5098 | 0.38543 | 3.2105 | 3.5098 | 0.38673 | -2.6378 | -0.28414 | -0.38562 | 2.715 | 0.37638 | -0.036626 | 0.23969 | -2.3338 | 0.037283 | -0.19408 | 2.3883 | 6.5701 | 47.7344 | -136.4106 | -173.4299 | -132.2656 | 43.5894 | 1.0079 | 0.82502 | 0.66983 | 1.0052 | 0.84783 | 0.68885 | 1.1599 | -137.4576 | 126.6478 | 1.0476 | -136.3544 | 124.6336
Line_3 | 0.0025238 | 0.53996 | 0.54066 | 0.0025238 | 0.53996 | 0.54066 | 0.029142 | 6.2349 | 6.243 | 0.029142 | 6.2349 | 6.243 | 0.022981 | -4.8268 | 0.30161 | -0.022975 | 5.1178 | -0.0097645 | 0.018303 | -0.34522 | -4.0093 | -0.018299 | 0.51724 | 4.1817 | -37.3766 | 36.7713 | -143.486 | 142.6234 | -143.2287 | 36.514 | 1.0081 | 0.77612 | 0.64402 | 1.0079 | 0.82502 | 0.66983 | 1.1579 | -139.1377 | 130.8161 | 1.1599 | -137.4576 | 126.6478

## LL_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.068597 | 1.091 | 1.1464 | 0.068597 | 1.091 | 1.1464 | 0.79209 | 12.5981 | 13.2375 | 0.79209 | 12.5981 | 13.2375 | -0.78949 | 11.8666 | 2.206 | 0.79419 | -10.6782 | -0.89388 | 0.059138 | 0.94684 | 9.8501 | -0.056362 | -0.24454 | -9.0747 | -174.893 | -137.6663 | 40.2592 | 5.107 | 42.3337 | -139.7408 | 0.99951 | 0.94493 | 0.76254 | 1.0052 | 0.84783 | 0.68885 | 0.82315 | -133.1043 | 117.6357 | 1.0476 | -136.3544 | 124.6336
Line_1 | 0.03524 | 0.81464 | 0.84313 | 0.03524 | 0.81464 | 0.84313 | 0.40691 | 9.4067 | 9.7357 | 0.40691 | 9.4067 | 9.7357 | 0.40981 | -7.3006 | 0.19224 | -0.40857 | 7.9632 | 0.5175 | -0.018346 | -0.047078 | -6.267 | 0.019079 | 0.43863 | 6.6864 | 3.7212 | 40.4929 | -140.9408 | -176.2788 | -139.5071 | 39.0592 | 1.0081 | 0.77612 | 0.64402 | 1.0052 | 0.84783 | 0.68885 | 1.1579 | -139.1377 | 130.8161 | 1.0476 | -136.3544 | 124.6336
Line_2 | 0.033379 | 0.27804 | 0.30396 | 0.033379 | 0.27804 | 0.30396 | 0.38543 | 3.2105 | 3.5098 | 0.38543 | 3.2105 | 3.5098 | 0.38673 | -2.6378 | -0.28414 | -0.38562 | 2.715 | 0.37638 | -0.036626 | 0.23969 | -2.3338 | 0.037283 | -0.19408 | 2.3883 | 6.5701 | 47.7344 | -136.4106 | -173.4299 | -132.2656 | 43.5894 | 1.0079 | 0.82502 | 0.66983 | 1.0052 | 0.84783 | 0.68885 | 1.1599 | -137.4576 | 126.6478 | 1.0476 | -136.3544 | 124.6336
Line_3 | 0.0025238 | 0.53996 | 0.54066 | 0.0025238 | 0.53996 | 0.54066 | 0.029142 | 6.2349 | 6.243 | 0.029142 | 6.2349 | 6.243 | 0.022981 | -4.8268 | 0.30161 | -0.022975 | 5.1178 | -0.0097645 | 0.018303 | -0.34522 | -4.0093 | -0.018299 | 0.51724 | 4.1817 | -37.3766 | 36.7713 | -143.486 | 142.6234 | -143.2287 | 36.514 | 1.0081 | 0.77612 | 0.64402 | 1.0079 | 0.82502 | 0.66983 | 1.1579 | -139.1377 | 130.8161 | 1.1599 | -137.4576 | 126.6478

## LG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 2.0464 | 0.92886 | 0.79414 | 2.0441 | 0.93115 | 0.79643 | 23.6296 | 10.7256 | 9.1699 | 23.6032 | 10.752 | 9.1963 | 6.3071 | -9.572 | 9.5965 | -3.4415 | 9.7381 | -9.5644 | 5.36 | 10.3209 | 5.0232 | -2.6527 | -9.96 | -4.7463 | -76.3879 | 100.6634 | 105.6462 | 103.6107 | -79.3261 | -74.3558 | 0.35028 | 1.3124 | 1.1812 | 0.18409 | 1.2955 | 1.161 | -36.0285 | -126.4928 | 133.2755 | -38.7642 | -124.9717 | 132.0369
Line_1 | 1.6764 | 0.4822 | 0.41161 | 1.6788 | 0.47976 | 0.40918 | 19.3574 | 5.5679 | 4.7529 | 19.3855 | 5.5397 | 4.7248 | 9.3613e-11 | 5.0656 | -5.0207 | 2.8349 | -5.2936 | 4.7494 | -6.5688e-11 | -4.9222 | -2.7984 | 2.1678 | 4.8462 | 2.745 | 103.84 | -82.4947 | -78.0123 | -76.1683 | 97.5019 | 102.0104 | 0 | 1.2685 | 1.2093 | 0.18409 | 1.2955 | 1.161 | 0 | -126.6717 | 131.1218 | -38.7642 | -124.9717 | 132.0369
Line_2 | 0.36307 | 0.45517 | 0.3912 | 0.36533 | 0.4529 | 0.38894 | 4.1923 | 5.2559 | 4.5172 | 4.2185 | 5.2297 | 4.4911 | -0.71103 | 4.7977 | -4.564 | 0.60658 | -4.4444 | 4.8149 | -0.47725 | -4.9322 | -1.8692 | 0.48494 | 5.1138 | 2.0013 | 102.5739 | -75.9565 | -70.5533 | -77.4054 | 104.0341 | 109.4673 | 0.20427 | 1.3092 | 1.0918 | 0.18409 | 1.2955 | 1.161 | -43.5562 | -121.7489 | 131.7187 | -38.7642 | -124.9717 | 132.0369
Line_3 | 1.3123 | 0.060237 | 0.056402 | 1.3147 | 0.059176 | 0.055361 | 15.1537 | 0.69555 | 0.65128 | 15.181 | 0.6833 | 0.63925 | 7.2972e-11 | 0.85318 | 0.041558 | 2.6222 | -0.83099 | -0.070585 | -5.1864e-11 | 0.22497 | -0.78652 | 1.6553 | -0.33117 | 0.69437 | 104.1858 | -141.4434 | -141.9028 | -75.8201 | 36.5229 | 35.9143 | 0 | 1.2685 | 1.2093 | 0.20427 | 1.3092 | 1.0918 | 0 | -126.6717 | 131.1218 | -43.5562 | -121.7489 | 131.7187

## LG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 2.0464 | 0.92886 | 0.79414 | 2.0441 | 0.93115 | 0.79643 | 23.6296 | 10.7256 | 9.1699 | 23.6032 | 10.752 | 9.1963 | 6.3071 | -9.572 | 9.5965 | -3.4415 | 9.7381 | -9.5644 | 5.36 | 10.3209 | 5.0232 | -2.6527 | -9.96 | -4.7463 | -76.3879 | 100.6634 | 105.6462 | 103.6107 | -79.3261 | -74.3558 | 0.35028 | 1.3124 | 1.1812 | 0.18409 | 1.2955 | 1.161 | -36.0285 | -126.4928 | 133.2755 | -38.7642 | -124.9717 | 132.0369
Line_1 | 1.6764 | 0.4822 | 0.41161 | 1.6788 | 0.47976 | 0.40918 | 19.3574 | 5.5679 | 4.7529 | 19.3855 | 5.5397 | 4.7248 | 9.3613e-11 | 5.0656 | -5.0207 | 2.8349 | -5.2936 | 4.7494 | -6.5688e-11 | -4.9222 | -2.7984 | 2.1678 | 4.8462 | 2.745 | 103.84 | -82.4947 | -78.0123 | -76.1683 | 97.5019 | 102.0104 | 0 | 1.2685 | 1.2093 | 0.18409 | 1.2955 | 1.161 | 0 | -126.6717 | 131.1218 | -38.7642 | -124.9717 | 132.0369
Line_2 | 0.36307 | 0.45517 | 0.3912 | 0.36533 | 0.4529 | 0.38894 | 4.1923 | 5.2559 | 4.5172 | 4.2185 | 5.2297 | 4.4911 | -0.71103 | 4.7977 | -4.564 | 0.60658 | -4.4444 | 4.8149 | -0.47725 | -4.9322 | -1.8692 | 0.48494 | 5.1138 | 2.0013 | 102.5739 | -75.9565 | -70.5533 | -77.4054 | 104.0341 | 109.4673 | 0.20427 | 1.3092 | 1.0918 | 0.18409 | 1.2955 | 1.161 | -43.5562 | -121.7489 | 131.7187 | -38.7642 | -124.9717 | 132.0369
Line_3 | 1.3123 | 0.060237 | 0.056402 | 1.3147 | 0.059176 | 0.055361 | 15.1537 | 0.69555 | 0.65128 | 15.181 | 0.6833 | 0.63925 | 7.2972e-11 | 0.85318 | 0.041558 | 2.6222 | -0.83099 | -0.070585 | -5.1864e-11 | 0.22497 | -0.78652 | 1.6553 | -0.33117 | 0.69437 | 104.1858 | -141.4434 | -141.9028 | -75.8201 | 36.5229 | 35.9143 | 0 | 1.2685 | 1.2093 | 0.20427 | 1.3092 | 1.0918 | 0 | -126.6717 | 131.1218 | -43.5562 | -121.7489 | 131.7187

## LG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.65061 | 0.29532 | 0.25248 | 0.64988 | 0.29604 | 0.25321 | 7.5126 | 3.41 | 2.9154 | 7.5042 | 3.4184 | 2.9238 | 4.9994 | -1.7007 | 3.1489 | -4.7048 | 1.7188 | -3.152 | 4.5829 | 3.6407 | -0.25189 | -4.3048 | -3.6108 | 0.28199 | -52.9401 | 124.1111 | 129.0939 | 127.0584 | -55.8784 | -50.9081 | 0.90276 | 1.1784 | 1.0835 | 0.84979 | 1.1698 | 1.0823 | -10.4292 | -120.8499 | 124.5204 | -10.4835 | -120.4226 | 123.9796
Line_1 | 0.53298 | 0.15331 | 0.13087 | 0.53375 | 0.15253 | 0.13009 | 6.1543 | 1.7702 | 1.5111 | 6.1633 | 1.7613 | 1.5022 | -3.5864 | 0.96635 | -1.6597 | 3.8777 | -0.98718 | 1.6253 | -3.2962 | -1.8229 | 0.038004 | 3.5206 | 1.8085 | -0.041952 | 127.2877 | -59.0469 | -54.5646 | -52.7205 | 120.9497 | 125.4582 | 0.79148 | 1.1655 | 1.0986 | 0.84979 | 1.1698 | 1.0823 | -10.1265 | -121.1185 | 124.1237 | -10.4835 | -120.4226 | 123.9796
Line_2 | 0.11543 | 0.14471 | 0.12438 | 0.11615 | 0.14399 | 0.12366 | 1.3329 | 1.671 | 1.4362 | 1.3412 | 1.6627 | 1.4278 | -0.83263 | 0.76856 | -1.5075 | 0.82708 | -0.73165 | 1.5267 | -0.77911 | -1.7904 | 0.25558 | 0.78417 | 1.8022 | -0.24004 | 126.0216 | -52.5088 | -47.1056 | -53.9577 | 127.4818 | 132.915 | 0.85552 | 1.166 | 1.0647 | 0.84979 | 1.1698 | 1.0823 | -10.8804 | -119.2762 | 123.272 | -10.4835 | -120.4226 | 123.9796
Line_3 | 0.41724 | 0.019151 | 0.017932 | 0.41799 | 0.018814 | 0.017601 | 4.8178 | 0.22114 | 0.20706 | 4.8265 | 0.21724 | 0.20324 | -2.8231 | 0.25736 | -0.10476 | 3.093 | -0.25328 | 0.09516 | -2.5634 | -0.014041 | -0.20192 | 2.7356 | -0.0033296 | 0.19433 | 127.6335 | -117.9957 | -118.455 | -52.3723 | 59.9706 | 59.362 | 0.79148 | 1.1655 | 1.0986 | 0.85552 | 1.166 | 1.0647 | -10.1265 | -121.1185 | 124.1237 | -10.8804 | -119.2762 | 123.272

## LG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.65061 | 0.29532 | 0.25248 | 0.64988 | 0.29604 | 0.25321 | 7.5126 | 3.41 | 2.9154 | 7.5042 | 3.4184 | 2.9238 | 4.9994 | -1.7007 | 3.1489 | -4.7048 | 1.7188 | -3.152 | 4.5829 | 3.6407 | -0.25189 | -4.3048 | -3.6108 | 0.28199 | -52.9401 | 124.1111 | 129.0939 | 127.0584 | -55.8784 | -50.9081 | 0.90276 | 1.1784 | 1.0835 | 0.84979 | 1.1698 | 1.0823 | -10.4292 | -120.8499 | 124.5204 | -10.4835 | -120.4226 | 123.9796
Line_1 | 0.53298 | 0.15331 | 0.13087 | 0.53375 | 0.15253 | 0.13009 | 6.1543 | 1.7702 | 1.5111 | 6.1633 | 1.7613 | 1.5022 | -3.5864 | 0.96635 | -1.6597 | 3.8777 | -0.98718 | 1.6253 | -3.2962 | -1.8229 | 0.038004 | 3.5206 | 1.8085 | -0.041952 | 127.2877 | -59.0469 | -54.5646 | -52.7205 | 120.9497 | 125.4582 | 0.79148 | 1.1655 | 1.0986 | 0.84979 | 1.1698 | 1.0823 | -10.1265 | -121.1185 | 124.1237 | -10.4835 | -120.4226 | 123.9796
Line_2 | 0.11543 | 0.14471 | 0.12438 | 0.11615 | 0.14399 | 0.12366 | 1.3329 | 1.671 | 1.4362 | 1.3412 | 1.6627 | 1.4278 | -0.83263 | 0.76856 | -1.5075 | 0.82708 | -0.73165 | 1.5267 | -0.77911 | -1.7904 | 0.25558 | 0.78417 | 1.8022 | -0.24004 | 126.0216 | -52.5088 | -47.1056 | -53.9577 | 127.4818 | 132.915 | 0.85552 | 1.166 | 1.0647 | 0.84979 | 1.1698 | 1.0823 | -10.8804 | -119.2762 | 123.272 | -10.4835 | -120.4226 | 123.9796
Line_3 | 0.41724 | 0.019151 | 0.017932 | 0.41799 | 0.018814 | 0.017601 | 4.8178 | 0.22114 | 0.20706 | 4.8265 | 0.21724 | 0.20324 | -2.8231 | 0.25736 | -0.10476 | 3.093 | -0.25328 | 0.09516 | -2.5634 | -0.014041 | -0.20192 | 2.7356 | -0.0033296 | 0.19433 | 127.6335 | -117.9957 | -118.455 | -52.3723 | 59.9706 | 59.362 | 0.79148 | 1.1655 | 1.0986 | 0.85552 | 1.166 | 1.0647 | -10.1265 | -121.1185 | 124.1237 | -10.8804 | -119.2762 | 123.272

## LG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.7148 | 0.78992 | 0.66828 | 1.713 | 0.79175 | 0.67012 | 19.8007 | 9.1212 | 7.7167 | 19.7795 | 9.1424 | 7.7379 | 8.5164 | -6.3471 | 7.5618 | -4.6935 | 6.5849 | -7.4835 | 4.0602 | 8.6641 | 1.9198 | -2.1198 | -8.4386 | -1.7237 | -65.3297 | 110.6514 | 117.5497 | 114.6695 | -69.3376 | -62.4562 | 0.47648 | 1.1775 | 1.011 | 0.26037 | 1.1708 | 0.99245 | -39.8404 | -123.123 | 131.7954 | -41.0238 | -121.3714 | 130.5144
Line_1 | 1.4254 | 0.42104 | 0.35447 | 1.4274 | 0.419 | 0.35245 | 16.4587 | 4.8617 | 4.0931 | 16.4817 | 4.8382 | 4.0698 | -4.0812e-11 | 3.6445 | -4.1314 | 3.9066 | -3.9617 | 3.7833 | 1.7694e-13 | -4.2288 | -1.5307 | 1.7759 | 4.0486 | 1.4145 | 114.5479 | -75.7581 | -70.029 | -65.4692 | 104.2503 | 110.014 | 0 | 1.1483 | 1.0764 | 0.26037 | 1.1708 | 0.99245 | 0 | -125.003 | 130.301 | -41.0238 | -121.3714 | 130.5144
Line_2 | 0.28383 | 0.38007 | 0.32579 | 0.28562 | 0.37828 | 0.32401 | 3.2774 | 4.3887 | 3.7619 | 3.2981 | 4.368 | 3.7414 | -0.93365 | 3.095 | -3.3362 | 0.78683 | -2.6232 | 3.7003 | -0.37153 | -4.2356 | -0.21194 | 0.34398 | 4.39 | 0.30913 | 115.3477 | -62.2319 | -54.3049 | -64.6372 | 117.7682 | 125.7389 | 0.3066 | 1.1953 | 0.88862 | 0.26037 | 1.1708 | 0.99245 | -42.9529 | -116.0759 | 129.3302 | -41.0238 | -121.3714 | 130.5144
Line_3 | 1.1407 | 0.10289 | 0.097452 | 1.1426 | 0.10203 | 0.09658 | 13.1718 | 1.1881 | 1.1253 | 13.1939 | 1.1782 | 1.1152 | -3.2662e-11 | 1.3427 | -0.10588 | 3.7314 | -1.3227 | 0.085908 | 2.3852e-14 | 0.24136 | -1.2066 | 1.5622 | -0.48352 | 0.98727 | 114.3413 | -135.1933 | -134.6842 | -65.6696 | 43.8439 | 44.3033 | 0 | 1.1483 | 1.0764 | 0.3066 | 1.1953 | 0.88862 | 0 | -125.003 | 130.301 | -42.9529 | -116.0759 | 129.3302

## LG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.7148 | 0.78992 | 0.66828 | 1.713 | 0.79175 | 0.67012 | 19.8007 | 9.1212 | 7.7167 | 19.7795 | 9.1424 | 7.7379 | 8.5164 | -6.3471 | 7.5618 | -4.6935 | 6.5849 | -7.4835 | 4.0602 | 8.6641 | 1.9198 | -2.1198 | -8.4386 | -1.7237 | -65.3297 | 110.6514 | 117.5497 | 114.6695 | -69.3376 | -62.4562 | 0.47648 | 1.1775 | 1.011 | 0.26037 | 1.1708 | 0.99245 | -39.8404 | -123.123 | 131.7954 | -41.0238 | -121.3714 | 130.5144
Line_1 | 1.4254 | 0.42104 | 0.35447 | 1.4274 | 0.419 | 0.35245 | 16.4587 | 4.8617 | 4.0931 | 16.4817 | 4.8382 | 4.0698 | -4.0812e-11 | 3.6445 | -4.1314 | 3.9066 | -3.9617 | 3.7833 | 1.7694e-13 | -4.2288 | -1.5307 | 1.7759 | 4.0486 | 1.4145 | 114.5479 | -75.7581 | -70.029 | -65.4692 | 104.2503 | 110.014 | 0 | 1.1483 | 1.0764 | 0.26037 | 1.1708 | 0.99245 | 0 | -125.003 | 130.301 | -41.0238 | -121.3714 | 130.5144
Line_2 | 0.28383 | 0.38007 | 0.32579 | 0.28562 | 0.37828 | 0.32401 | 3.2774 | 4.3887 | 3.7619 | 3.2981 | 4.368 | 3.7414 | -0.93365 | 3.095 | -3.3362 | 0.78683 | -2.6232 | 3.7003 | -0.37153 | -4.2356 | -0.21194 | 0.34398 | 4.39 | 0.30913 | 115.3477 | -62.2319 | -54.3049 | -64.6372 | 117.7682 | 125.7389 | 0.3066 | 1.1953 | 0.88862 | 0.26037 | 1.1708 | 0.99245 | -42.9529 | -116.0759 | 129.3302 | -41.0238 | -121.3714 | 130.5144
Line_3 | 1.1407 | 0.10289 | 0.097452 | 1.1426 | 0.10203 | 0.09658 | 13.1718 | 1.1881 | 1.1253 | 13.1939 | 1.1782 | 1.1152 | -3.2662e-11 | 1.3427 | -0.10588 | 3.7314 | -1.3227 | 0.085908 | 2.3852e-14 | 0.24136 | -1.2066 | 1.5622 | -0.48352 | 0.98727 | 114.3413 | -135.1933 | -134.6842 | -65.6696 | 43.8439 | 44.3033 | 0 | 1.1483 | 1.0764 | 0.3066 | 1.1953 | 0.88862 | 0 | -125.003 | 130.301 | -42.9529 | -116.0759 | 129.3302

## LG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.54767 | 0.25229 | 0.21344 | 0.54709 | 0.25287 | 0.21402 | 6.324 | 2.9132 | 2.4646 | 6.3172 | 2.9199 | 2.4713 | 4.3269 | -1.1093 | 2.3572 | -3.9332 | 1.1343 | -2.3536 | 3.2148 | 2.881 | -0.50613 | -3.0139 | -2.8627 | 0.5279 | -47.1457 | 128.8354 | 135.7337 | 132.8535 | -51.1536 | -44.2722 | 0.85237 | 1.0597 | 0.97821 | 0.78438 | 1.0545 | 0.97602 | -10.534 | -120.1053 | 123.6152 | -9.6843 | -119.5389 | 123.0858
Line_1 | 0.45524 | 0.13447 | 0.11321 | 0.45587 | 0.13382 | 0.11257 | 5.2566 | 1.5527 | 1.3073 | 5.264 | 1.5452 | 1.2998 | -2.8695 | 0.73524 | -1.3043 | 3.2713 | -0.76569 | 1.2636 | -2.3341 | -1.4617 | 0.10201 | 2.5193 | 1.4384 | -0.11305 | 132.7319 | -57.5741 | -51.8449 | -47.2852 | 122.4343 | 128.198 | 0.70366 | 1.0538 | 1.0008 | 0.78438 | 1.0545 | 0.97602 | -8.143 | -120.8724 | 123.6833 | -9.6843 | -119.5389 | 123.0858
Line_2 | 0.090652 | 0.12139 | 0.10405 | 0.091224 | 0.12082 | 0.10348 | 1.0468 | 1.4017 | 1.2015 | 1.0534 | 1.3951 | 1.1949 | -0.67307 | 0.41717 | -1.0571 | 0.66186 | -0.36857 | 1.09 | -0.49466 | -1.4131 | 0.42667 | 0.49458 | 1.4242 | -0.41486 | 133.5317 | -44.0479 | -36.1209 | -46.4532 | 135.9522 | 143.9229 | 0.79798 | 1.0512 | 0.9488 | 0.78438 | 1.0545 | 0.97602 | -10.1551 | -117.6005 | 121.899 | -9.6843 | -119.5389 | 123.0858
Line_3 | 0.36432 | 0.032861 | 0.031124 | 0.36493 | 0.032588 | 0.030846 | 4.2068 | 0.37945 | 0.35939 | 4.2139 | 0.37629 | 0.35618 | -2.2897 | 0.39894 | -0.17884 | 2.6738 | -0.39554 | 0.17197 | -1.8762 | -0.026939 | -0.31207 | 2.0391 | -0.0025647 | 0.29092 | 132.5253 | -117.0093 | -116.5002 | -47.4856 | 62.0279 | 62.4873 | 0.70366 | 1.0538 | 1.0008 | 0.79798 | 1.0512 | 0.9488 | -8.143 | -120.8724 | 123.6833 | -10.1551 | -117.6005 | 121.899

## LG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.54767 | 0.25229 | 0.21344 | 0.54709 | 0.25287 | 0.21402 | 6.324 | 2.9132 | 2.4646 | 6.3172 | 2.9199 | 2.4713 | 4.3269 | -1.1093 | 2.3572 | -3.9332 | 1.1343 | -2.3536 | 3.2148 | 2.881 | -0.50613 | -3.0139 | -2.8627 | 0.5279 | -47.1457 | 128.8354 | 135.7337 | 132.8535 | -51.1536 | -44.2722 | 0.85237 | 1.0597 | 0.97821 | 0.78438 | 1.0545 | 0.97602 | -10.534 | -120.1053 | 123.6152 | -9.6843 | -119.5389 | 123.0858
Line_1 | 0.45524 | 0.13447 | 0.11321 | 0.45587 | 0.13382 | 0.11257 | 5.2566 | 1.5527 | 1.3073 | 5.264 | 1.5452 | 1.2998 | -2.8695 | 0.73524 | -1.3043 | 3.2713 | -0.76569 | 1.2636 | -2.3341 | -1.4617 | 0.10201 | 2.5193 | 1.4384 | -0.11305 | 132.7319 | -57.5741 | -51.8449 | -47.2852 | 122.4343 | 128.198 | 0.70366 | 1.0538 | 1.0008 | 0.78438 | 1.0545 | 0.97602 | -8.143 | -120.8724 | 123.6833 | -9.6843 | -119.5389 | 123.0858
Line_2 | 0.090652 | 0.12139 | 0.10405 | 0.091224 | 0.12082 | 0.10348 | 1.0468 | 1.4017 | 1.2015 | 1.0534 | 1.3951 | 1.1949 | -0.67307 | 0.41717 | -1.0571 | 0.66186 | -0.36857 | 1.09 | -0.49466 | -1.4131 | 0.42667 | 0.49458 | 1.4242 | -0.41486 | 133.5317 | -44.0479 | -36.1209 | -46.4532 | 135.9522 | 143.9229 | 0.79798 | 1.0512 | 0.9488 | 0.78438 | 1.0545 | 0.97602 | -10.1551 | -117.6005 | 121.899 | -9.6843 | -119.5389 | 123.0858
Line_3 | 0.36432 | 0.032861 | 0.031124 | 0.36493 | 0.032588 | 0.030846 | 4.2068 | 0.37945 | 0.35939 | 4.2139 | 0.37629 | 0.35618 | -2.2897 | 0.39894 | -0.17884 | 2.6738 | -0.39554 | 0.17197 | -1.8762 | -0.026939 | -0.31207 | 2.0391 | -0.0025647 | 0.29092 | 132.5253 | -117.0093 | -116.5002 | -47.4856 | 62.0279 | 62.4873 | 0.70366 | 1.0538 | 1.0008 | 0.79798 | 1.0512 | 0.9488 | -8.143 | -120.8724 | 123.6833 | -10.1551 | -117.6005 | 121.899

## LLG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.67507 | 3.0981 | 3.2947 | 0.67694 | 3.0979 | 3.2943 | 7.795 | 35.7743 | 38.0435 | 7.8166 | 35.7718 | 38.0395 | -0.9385 | 10.3945 | 8.9675 | 1.0008 | -5.0271 | -3.446 | 10.2551 | 6.7087 | 14.7214 | -10.1237 | -1.8882 | -7.3419 | -90.2446 | -171.6549 | 24.9223 | 89.7981 | 8.3807 | -155.1109 | 1.3211 | 0.34582 | 0.4531 | 1.3015 | 0.15012 | 0.21321 | 4.9843 | -138.8163 | 83.5748 | 5.4436 | -151.0333 | 89.7456
Line_1 | 0.35454 | 2.318 | 2.4143 | 0.35251 | 2.3181 | 2.415 | 4.0939 | 26.7659 | 27.8776 | 4.0705 | 26.7675 | 27.886 | 0.69065 | 7.3091e-11 | 1.0055e-10 | -0.83387 | 3.6445 | 2.8654 | -5.3477 | -6.6888e-11 | -1.3347e-11 | 5.2316 | 1.6924 | 5.2095 | 86.4549 | 4.1086 | -151.4879 | -93.6127 | -175.9424 | 28.5581 | 1.3171 | 0 | 0 | 1.3015 | 0.15012 | 0.21321 | 3.8139 | 0 | 0 | 5.4436 | -151.0333 | 89.7456
Line_2 | 0.3276 | 0.80574 | 0.89771 | 0.32573 | 0.80557 | 0.89768 | 3.7828 | 9.3039 | 10.3658 | 3.7612 | 9.3019 | 10.3655 | 0.34237 | -1.1315 | -0.020067 | -0.16689 | 1.3826 | 0.58057 | -4.7814 | 0.53949 | -2.0344 | 4.8922 | 0.19574 | 2.1324 | 93.5613 | 21.0447 | -165.1464 | -86.5102 | -159.0912 | 14.9761 | 1.2672 | 0.13473 | 0.19627 | 1.3015 | 0.15012 | 0.21321 | 7.657 | 175.5534 | 104.2885 | 5.4436 | -151.0333 | 89.7456
Line_3 | 0.050326 | 1.5645 | 1.5562 | 0.049588 | 1.5651 | 1.557 | 0.58112 | 18.0656 | 17.9692 | 0.57259 | 18.0717 | 17.9792 | 0.66496 | 5.5526e-11 | 6.3045e-11 | -0.66438 | 2.4349 | 1.3268 | -0.37904 | -3.7267e-11 | -1.7313e-11 | 0.29168 | 0.0046942 | 3.2699 | 33.4981 | -4.4863 | -143.6931 | -148.6405 | 175.4429 | 36.3735 | 1.3171 | 0 | 0 | 1.2672 | 0.13473 | 0.19627 | 3.8139 | 0 | 0 | 7.657 | 175.5534 | 104.2885

## LLG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.67507 | 3.0981 | 3.2947 | 0.67694 | 3.0979 | 3.2943 | 7.795 | 35.7743 | 38.0435 | 7.8166 | 35.7718 | 38.0395 | -0.9385 | 10.3945 | 8.9675 | 1.0008 | -5.0271 | -3.446 | 10.2551 | 6.7087 | 14.7214 | -10.1237 | -1.8882 | -7.3419 | -90.2446 | -171.6549 | 24.9223 | 89.7981 | 8.3807 | -155.1109 | 1.3211 | 0.34582 | 0.4531 | 1.3015 | 0.15012 | 0.21321 | 4.9843 | -138.8163 | 83.5748 | 5.4436 | -151.0333 | 89.7456
Line_1 | 0.35454 | 2.318 | 2.4143 | 0.35251 | 2.3181 | 2.415 | 4.0939 | 26.7659 | 27.8776 | 4.0705 | 26.7675 | 27.886 | 0.69065 | 7.3091e-11 | 1.0055e-10 | -0.83387 | 3.6445 | 2.8654 | -5.3477 | -6.6888e-11 | -1.3347e-11 | 5.2316 | 1.6924 | 5.2095 | 86.4549 | 4.1086 | -151.4879 | -93.6127 | -175.9424 | 28.5581 | 1.3171 | 0 | 0 | 1.3015 | 0.15012 | 0.21321 | 3.8139 | 0 | 0 | 5.4436 | -151.0333 | 89.7456
Line_2 | 0.3276 | 0.80574 | 0.89771 | 0.32573 | 0.80557 | 0.89768 | 3.7828 | 9.3039 | 10.3658 | 3.7612 | 9.3019 | 10.3655 | 0.34237 | -1.1315 | -0.020067 | -0.16689 | 1.3826 | 0.58057 | -4.7814 | 0.53949 | -2.0344 | 4.8922 | 0.19574 | 2.1324 | 93.5613 | 21.0447 | -165.1464 | -86.5102 | -159.0912 | 14.9761 | 1.2672 | 0.13473 | 0.19627 | 1.3015 | 0.15012 | 0.21321 | 7.657 | 175.5534 | 104.2885 | 5.4436 | -151.0333 | 89.7456
Line_3 | 0.050326 | 1.5645 | 1.5562 | 0.049588 | 1.5651 | 1.557 | 0.58112 | 18.0656 | 17.9692 | 0.57259 | 18.0717 | 17.9792 | 0.66496 | 5.5526e-11 | 6.3045e-11 | -0.66438 | 2.4349 | 1.3268 | -0.37904 | -3.7267e-11 | -1.7313e-11 | 0.29168 | 0.0046942 | 3.2699 | 33.4981 | -4.4863 | -143.6931 | -148.6405 | 175.4429 | 36.3735 | 1.3171 | 0 | 0 | 1.2672 | 0.13473 | 0.19627 | 3.8139 | 0 | 0 | 7.657 | 175.5534 | 104.2885

## LLG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.24441 | 0.82819 | 0.88398 | 0.24508 | 0.82807 | 0.88382 | 2.8222 | 9.5631 | 10.2073 | 2.83 | 9.5618 | 10.2055 | 1.2323 | 7.5364 | 5.0308 | -1.2291 | -7.1412 | -4.6251 | 3.0275 | 3.8651 | 8.5139 | -3.0126 | -3.5326 | -7.9611 | -64.6925 | -152.8672 | 49.7873 | 115.3399 | 27.1799 | -130.2564 | 1.1582 | 0.88567 | 0.96883 | 1.1497 | 0.83323 | 0.90217 | 3.1594 | -125.7157 | 109.2089 | 3.1448 | -126.4996 | 109.5883
Line_1 | 0.12795 | 0.62657 | 0.65347 | 0.12723 | 0.62667 | 0.65378 | 1.4775 | 7.235 | 7.5456 | 1.4691 | 7.2362 | 7.5491 | -0.56699 | -4.8345 | -3.685 | 0.54321 | 5.1284 | 3.9101 | -1.6172 | -3.0687 | -5.1541 | 1.5993 | 3.1707 | 5.5763 | 111.9526 | 21.8405 | -125.4326 | -68.0945 | -158.2262 | 54.6262 | 1.1599 | 0.79146 | 0.83968 | 1.1497 | 0.83323 | 0.90217 | 2.6318 | -125.7537 | 109.0042 | 3.1448 | -126.4996 | 109.5883
Line_2 | 0.11901 | 0.21262 | 0.23901 | 0.11833 | 0.21255 | 0.23899 | 1.3742 | 2.4551 | 2.7598 | 1.3664 | 2.4544 | 2.7596 | -0.66696 | -1.9989 | -0.66509 | 0.6859 | 2.0128 | 0.71505 | -1.4036 | -0.29599 | -2.3888 | 1.4133 | 0.3619 | 2.3847 | 119.0831 | 43.4909 | -143.8846 | -60.9674 | -136.6927 | 36.2795 | 1.1308 | 0.82304 | 0.89849 | 1.1497 | 0.83323 | 0.90217 | 3.667 | -128.0861 | 110.5572 | 3.1448 | -126.4996 | 109.5883
Line_3 | 0.017851 | 0.43589 | 0.43327 | 0.017574 | 0.43616 | 0.43365 | 0.20613 | 5.0333 | 5.003 | 0.20293 | 5.0363 | 5.0073 | 0.14021 | -2.9262 | -3.0001 | -0.14465 | 3.1526 | 3.131 | -0.19365 | -2.7032 | -2.9405 | 0.17815 | 2.6913 | 3.2307 | 56.7253 | 11.515 | -115.421 | -125.408 | -168.5725 | 64.6594 | 1.1599 | 0.79146 | 0.83968 | 1.1308 | 0.82304 | 0.89849 | 2.6318 | -125.7537 | 109.0042 | 3.667 | -128.0861 | 110.5572

## LLG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.24441 | 0.82819 | 0.88398 | 0.24508 | 0.82807 | 0.88382 | 2.8222 | 9.5631 | 10.2073 | 2.83 | 9.5618 | 10.2055 | 1.2323 | 7.5364 | 5.0308 | -1.2291 | -7.1412 | -4.6251 | 3.0275 | 3.8651 | 8.5139 | -3.0126 | -3.5326 | -7.9611 | -64.6925 | -152.8672 | 49.7873 | 115.3399 | 27.1799 | -130.2564 | 1.1582 | 0.88567 | 0.96883 | 1.1497 | 0.83323 | 0.90217 | 3.1594 | -125.7157 | 109.2089 | 3.1448 | -126.4996 | 109.5883
Line_1 | 0.12795 | 0.62657 | 0.65347 | 0.12723 | 0.62667 | 0.65378 | 1.4775 | 7.235 | 7.5456 | 1.4691 | 7.2362 | 7.5491 | -0.56699 | -4.8345 | -3.685 | 0.54321 | 5.1284 | 3.9101 | -1.6172 | -3.0687 | -5.1541 | 1.5993 | 3.1707 | 5.5763 | 111.9526 | 21.8405 | -125.4326 | -68.0945 | -158.2262 | 54.6262 | 1.1599 | 0.79146 | 0.83968 | 1.1497 | 0.83323 | 0.90217 | 2.6318 | -125.7537 | 109.0042 | 3.1448 | -126.4996 | 109.5883
Line_2 | 0.11901 | 0.21262 | 0.23901 | 0.11833 | 0.21255 | 0.23899 | 1.3742 | 2.4551 | 2.7598 | 1.3664 | 2.4544 | 2.7596 | -0.66696 | -1.9989 | -0.66509 | 0.6859 | 2.0128 | 0.71505 | -1.4036 | -0.29599 | -2.3888 | 1.4133 | 0.3619 | 2.3847 | 119.0831 | 43.4909 | -143.8846 | -60.9674 | -136.6927 | 36.2795 | 1.1308 | 0.82304 | 0.89849 | 1.1497 | 0.83323 | 0.90217 | 3.667 | -128.0861 | 110.5572 | 3.1448 | -126.4996 | 109.5883
Line_3 | 0.017851 | 0.43589 | 0.43327 | 0.017574 | 0.43616 | 0.43365 | 0.20613 | 5.0333 | 5.003 | 0.20293 | 5.0363 | 5.0073 | 0.14021 | -2.9262 | -3.0001 | -0.14465 | 3.1526 | 3.131 | -0.19365 | -2.7032 | -2.9405 | 0.17815 | 2.6913 | 3.2307 | 56.7253 | 11.515 | -115.421 | -125.408 | -168.5725 | 64.6594 | 1.1599 | 0.79146 | 0.83968 | 1.1308 | 0.82304 | 0.89849 | 2.6318 | -125.7537 | 109.0042 | 3.667 | -128.0861 | 110.5572

## LLG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.57165 | 2.4993 | 2.6834 | 0.57319 | 2.4991 | 2.683 | 6.6008 | 28.8589 | 30.985 | 6.6187 | 28.8572 | 30.9811 | 0.37054 | 12.6997 | 12.0986 | -0.28379 | -6.1195 | -4.9118 | 7.5998 | 2.1477 | 12.1119 | -7.5494 | 0.44273 | -6.6298 | -80.5953 | -160.2678 | 36.7778 | 99.4473 | 19.7688 | -143.2556 | 1.1527 | 0.44631 | 0.55251 | 1.1414 | 0.21262 | 0.26633 | 6.6134 | -150.6689 | 81.8093 | 7.2945 | -164.3692 | 90.2111
Line_1 | 0.3127 | 1.9169 | 1.9873 | 0.31094 | 1.9168 | 1.9882 | 3.6107 | 22.134 | 22.9479 | 3.5905 | 22.1332 | 22.9575 | 0.13937 | -6.7679e-11 | -3.1979e-11 | -0.33759 | 4.7043 | 3.8963 | -4.2829 | -4.7107e-11 | -8.0419e-11 | 4.0843 | 0.12015 | 4.7119 | 92.6226 | 14.2209 | -140.247 | -87.4306 | -165.8323 | 39.7983 | 1.1868 | 0 | 0 | 1.1414 | 0.21262 | 0.26633 | 4.4864 | 0 | 0 | 7.2945 | -164.3692 | 90.2111
Line_2 | 0.26864 | 0.62063 | 0.70566 | 0.2671 | 0.62035 | 0.70568 | 3.102 | 7.1664 | 8.1483 | 3.0842 | 7.1632 | 8.1485 | -0.37412 | -1.076 | -0.3753 | 0.62138 | 1.4152 | 1.0155 | -3.3545 | 1.2585 | -2.1387 | 3.4651 | -0.56289 | 1.9179 | 107.5174 | 37.4631 | -152.0153 | -72.5389 | -142.679 | 28.1116 | 1.0881 | 0.23105 | 0.26648 | 1.1414 | 0.21262 | 0.26633 | 11.1536 | 167.993 | 108.0318 | 7.2945 | -164.3692 | 90.2111
Line_3 | 0.087185 | 1.3683 | 1.3043 | 0.086533 | 1.3687 | 1.3051 | 1.0067 | 15.7999 | 15.0611 | 0.99919 | 15.8044 | 15.0704 | 0.96433 | -4.1534e-11 | -2.6655e-11 | -0.95552 | 3.5123 | 1.8908 | -0.70535 | -4.1709e-11 | -5.0157e-11 | 0.51872 | -0.9991 | 3.543 | 40.6694 | 3.9403 | -133.9452 | -140.3506 | -176.128 | 46.1194 | 1.1868 | 0 | 0 | 1.0881 | 0.23105 | 0.26648 | 4.4864 | 0 | 0 | 11.1536 | 167.993 | 108.0318

## LLG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.57165 | 2.4993 | 2.6834 | 0.57319 | 2.4991 | 2.683 | 6.6008 | 28.8589 | 30.985 | 6.6187 | 28.8572 | 30.9811 | 0.37054 | 12.6997 | 12.0986 | -0.28379 | -6.1195 | -4.9118 | 7.5998 | 2.1477 | 12.1119 | -7.5494 | 0.44273 | -6.6298 | -80.5953 | -160.2678 | 36.7778 | 99.4473 | 19.7688 | -143.2556 | 1.1527 | 0.44631 | 0.55251 | 1.1414 | 0.21262 | 0.26633 | 6.6134 | -150.6689 | 81.8093 | 7.2945 | -164.3692 | 90.2111
Line_1 | 0.3127 | 1.9169 | 1.9873 | 0.31094 | 1.9168 | 1.9882 | 3.6107 | 22.134 | 22.9479 | 3.5905 | 22.1332 | 22.9575 | 0.13937 | -6.7679e-11 | -3.1979e-11 | -0.33759 | 4.7043 | 3.8963 | -4.2829 | -4.7107e-11 | -8.0419e-11 | 4.0843 | 0.12015 | 4.7119 | 92.6226 | 14.2209 | -140.247 | -87.4306 | -165.8323 | 39.7983 | 1.1868 | 0 | 0 | 1.1414 | 0.21262 | 0.26633 | 4.4864 | 0 | 0 | 7.2945 | -164.3692 | 90.2111
Line_2 | 0.26864 | 0.62063 | 0.70566 | 0.2671 | 0.62035 | 0.70568 | 3.102 | 7.1664 | 8.1483 | 3.0842 | 7.1632 | 8.1485 | -0.37412 | -1.076 | -0.3753 | 0.62138 | 1.4152 | 1.0155 | -3.3545 | 1.2585 | -2.1387 | 3.4651 | -0.56289 | 1.9179 | 107.5174 | 37.4631 | -152.0153 | -72.5389 | -142.679 | 28.1116 | 1.0881 | 0.23105 | 0.26648 | 1.1414 | 0.21262 | 0.26633 | 11.1536 | 167.993 | 108.0318 | 7.2945 | -164.3692 | 90.2111
Line_3 | 0.087185 | 1.3683 | 1.3043 | 0.086533 | 1.3687 | 1.3051 | 1.0067 | 15.7999 | 15.0611 | 0.99919 | 15.8044 | 15.0704 | 0.96433 | -4.1534e-11 | -2.6655e-11 | -0.95552 | 3.5123 | 1.8908 | -0.70535 | -4.1709e-11 | -5.0157e-11 | 0.51872 | -0.9991 | 3.543 | 40.6694 | 3.9403 | -133.9452 | -140.3506 | -176.128 | 46.1194 | 1.1868 | 0 | 0 | 1.0881 | 0.23105 | 0.26648 | 4.4864 | 0 | 0 | 11.1536 | 167.993 | 108.0318

## LLG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.20297 | 0.69384 | 0.73888 | 0.20351 | 0.69374 | 0.73876 | 2.3436 | 8.0117 | 8.5318 | 2.35 | 8.0107 | 8.5304 | 1.1083 | 6.2444 | 4.4426 | -1.1012 | -5.723 | -3.8917 | 2.162 | 2.3003 | 6.2775 | -2.1564 | -2.1154 | -5.838 | -59.6945 | -147.2339 | 55.0469 | 120.3386 | 32.8118 | -124.9956 | 1.0366 | 0.83061 | 0.90139 | 1.0303 | 0.76166 | 0.8225 | 3.1655 | -127.0111 | 109.76 | 3.2863 | -126.9021 | 111.3167
Line_1 | 0.11035 | 0.53942 | 0.5494 | 0.10973 | 0.53945 | 0.54971 | 1.2743 | 6.2286 | 6.344 | 1.2671 | 6.229 | 6.3475 | -0.47681 | -3.8313 | -2.8961 | 0.44777 | 4.2399 | 3.2057 | -1.2526 | -2.1445 | -3.7126 | 1.2264 | 2.129 | 4.1208 | 113.3789 | 26.5019 | -120.8596 | -66.6559 | -153.5642 | 59.1969 | 1.0518 | 0.7049 | 0.74221 | 1.0303 | 0.76166 | 0.8225 | 2.5386 | -124.2607 | 111.1836 | 3.2863 | -126.9021 | 111.3167
Line_2 | 0.096081 | 0.16872 | 0.19472 | 0.095536 | 0.16863 | 0.19471 | 1.1094 | 1.9482 | 2.2485 | 1.1032 | 1.9472 | 2.2483 | -0.6251 | -1.4606 | -0.62772 | 0.65345 | 1.483 | 0.68601 | -0.91987 | 0.079286 | -1.7459 | 0.93002 | -0.013542 | 1.7173 | 128.4151 | 53.805 | -137.0686 | -51.6211 | -126.3789 | 43.0926 | 1.0024 | 0.75085 | 0.82513 | 1.0303 | 0.76166 | 0.8225 | 4.2168 | -129.3021 | 113.1554 | 3.2863 | -126.9021 | 111.3167
Line_3 | 0.030526 | 0.39695 | 0.3664 | 0.030289 | 0.39715 | 0.36672 | 0.35248 | 4.5836 | 4.2308 | 0.34975 | 4.5859 | 4.2345 | 0.20461 | -2.4589 | -2.2758 | -0.20703 | 2.8038 | 2.4513 | -0.30916 | -2.096 | -2.1637 | 0.28295 | 1.9987 | 2.4899 | 59.0406 | 15.2948 | -112.3698 | -121.9746 | -164.7852 | 67.7075 | 1.0518 | 0.7049 | 0.74221 | 1.0024 | 0.75085 | 0.82513 | 2.5386 | -124.2607 | 111.1836 | 4.2168 | -129.3021 | 113.1554

## LLG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.20297 | 0.69384 | 0.73888 | 0.20351 | 0.69374 | 0.73876 | 2.3436 | 8.0117 | 8.5318 | 2.35 | 8.0107 | 8.5304 | 1.1083 | 6.2444 | 4.4426 | -1.1012 | -5.723 | -3.8917 | 2.162 | 2.3003 | 6.2775 | -2.1564 | -2.1154 | -5.838 | -59.6945 | -147.2339 | 55.0469 | 120.3386 | 32.8118 | -124.9956 | 1.0366 | 0.83061 | 0.90139 | 1.0303 | 0.76166 | 0.8225 | 3.1655 | -127.0111 | 109.76 | 3.2863 | -126.9021 | 111.3167
Line_1 | 0.11035 | 0.53942 | 0.5494 | 0.10973 | 0.53945 | 0.54971 | 1.2743 | 6.2286 | 6.344 | 1.2671 | 6.229 | 6.3475 | -0.47681 | -3.8313 | -2.8961 | 0.44777 | 4.2399 | 3.2057 | -1.2526 | -2.1445 | -3.7126 | 1.2264 | 2.129 | 4.1208 | 113.3789 | 26.5019 | -120.8596 | -66.6559 | -153.5642 | 59.1969 | 1.0518 | 0.7049 | 0.74221 | 1.0303 | 0.76166 | 0.8225 | 2.5386 | -124.2607 | 111.1836 | 3.2863 | -126.9021 | 111.3167
Line_2 | 0.096081 | 0.16872 | 0.19472 | 0.095536 | 0.16863 | 0.19471 | 1.1094 | 1.9482 | 2.2485 | 1.1032 | 1.9472 | 2.2483 | -0.6251 | -1.4606 | -0.62772 | 0.65345 | 1.483 | 0.68601 | -0.91987 | 0.079286 | -1.7459 | 0.93002 | -0.013542 | 1.7173 | 128.4151 | 53.805 | -137.0686 | -51.6211 | -126.3789 | 43.0926 | 1.0024 | 0.75085 | 0.82513 | 1.0303 | 0.76166 | 0.8225 | 4.2168 | -129.3021 | 113.1554 | 3.2863 | -126.9021 | 111.3167
Line_3 | 0.030526 | 0.39695 | 0.3664 | 0.030289 | 0.39715 | 0.36672 | 0.35248 | 4.5836 | 4.2308 | 0.34975 | 4.5859 | 4.2345 | 0.20461 | -2.4589 | -2.2758 | -0.20703 | 2.8038 | 2.4513 | -0.30916 | -2.096 | -2.1637 | 0.28295 | 1.9987 | 2.4899 | 59.0406 | 15.2948 | -112.3698 | -121.9746 | -164.7852 | 67.7075 | 1.0518 | 0.7049 | 0.74221 | 1.0024 | 0.75085 | 0.82513 | 2.5386 | -124.2607 | 111.1836 | 4.2168 | -129.3021 | 113.1554