## LLL_max_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 3.4587 | 3.4587 | 0 | 0 | 119.8128 | 119.8128 | 37.3233 | -18.6616 | 42.3476 | -21.1738 | -71.7883 | 108.2117 | 0.47113 | 0.23557 | -23.1798 | -23.1798
Line_1 | 3.4587 | 3.4587 | 6.7756 | 0 | 119.8128 | 119.8128 | -1e-07 | 18.6616 | -1e-07 | 21.1738 | 108.2117 | -71.7883 | 0 | 0.23557 | 0 | -23.1798
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23557 | 0.23557 | -23.1798 | -23.1798

## LLL_max_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 3.4587 | 3.4587 | 0 | 0 | 119.8128 | 119.8128 | 37.3233 | -18.6616 | 42.3476 | -21.1738 | -71.7883 | 108.2117 | 0.47113 | 0.23557 | -23.1798 | -23.1798
Line_1 | 3.4587 | 3.4587 | 6.7756 | 0 | 119.8128 | 119.8128 | -1e-07 | 18.6616 | -1e-07 | 21.1738 | 108.2117 | -71.7883 | 0 | 0.23557 | 0 | -23.1798
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23557 | 0.23557 | -23.1798 | -23.1798

## LLL_max_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 1.2119 | 1.2119 | 0 | 0 | 41.9813 | 41.9813 | 26.6127 | -24.3216 | 27.2296 | -24.63 | -54.0862 | 125.9138 | 0.90694 | 0.82453 | -8.4298 | -8.7252
Line_1 | 1.2119 | 1.2119 | 2.3741 | 0 | 41.9813 | 41.9813 | -22.0304 | 24.3216 | -22.0304 | 24.63 | 125.9138 | -54.0862 | 0.74213 | 0.82453 | -9.0862 | -8.7252
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.82453 | 0.82453 | -8.7252 | -8.7252

## LLL_max_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 1.2119 | 1.2119 | 0 | 0 | 41.9813 | 41.9813 | 26.6127 | -24.3216 | 27.2296 | -24.63 | -54.0862 | 125.9138 | 0.90694 | 0.82453 | -8.4298 | -8.7252
Line_1 | 1.2119 | 1.2119 | 2.3741 | 0 | 41.9813 | 41.9813 | -22.0304 | 24.3216 | -22.0304 | 24.63 | 125.9138 | -54.0862 | 0.74213 | 0.82453 | -9.0862 | -8.7252
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.82453 | 0.82453 | -8.7252 | -8.7252

## LLL_min_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 2.7686 | 2.7686 | 0 | 0 | 95.9057 | 95.9057 | 45.916 | -22.958 | 27.1338 | -13.5669 | -59.5744 | 120.4256 | 0.55611 | 0.27805 | -28.9937 | -28.9937
Line_1 | 2.7686 | 2.7686 | 4.6525 | 0 | 95.9057 | 95.9057 | -1e-07 | 22.958 | -1e-07 | 13.5669 | 120.4256 | -59.5744 | 0 | 0.27805 | 0 | -28.9937
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27805 | 0.27805 | -28.9937 | -28.9937

## LLL_min_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 2.7686 | 2.7686 | 0 | 0 | 95.9057 | 95.9057 | 45.916 | -22.958 | 27.1338 | -13.5669 | -59.5744 | 120.4256 | 0.55611 | 0.27805 | -28.9937 | -28.9937
Line_1 | 2.7686 | 2.7686 | 4.6525 | 0 | 95.9057 | 95.9057 | -1e-07 | 22.958 | -1e-07 | 13.5669 | 120.4256 | -59.5744 | 0 | 0.27805 | 0 | -28.9937
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27805 | 0.27805 | -28.9937 | -28.9937

## LLL_min_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 1.0349 | 1.0349 | 0 | 0 | 35.8516 | 35.8516 | 22.4832 | -19.2749 | 19.8585 | -17.9626 | -50.3977 | 129.6023 | 0.83671 | 0.7349 | -8.9447 | -7.416
Line_1 | 1.0349 | 1.0349 | 1.7392 | 0 | 35.8516 | 35.8516 | -16.0667 | 19.2749 | -16.0667 | 17.9626 | 129.6023 | -50.3977 | 0.63377 | 0.7349 | -5.3977 | -7.416
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7349 | 0.7349 | -7.416 | -7.416

## LLL_min_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 1.0349 | 1.0349 | 0 | 0 | 35.8516 | 35.8516 | 22.4832 | -19.2749 | 19.8585 | -17.9626 | -50.3977 | 129.6023 | 0.83671 | 0.7349 | -8.9447 | -7.416
Line_1 | 1.0349 | 1.0349 | 1.7392 | 0 | 35.8516 | 35.8516 | -16.0667 | 19.2749 | -16.0667 | 17.9626 | 129.6023 | -50.3977 | 0.63377 | 0.7349 | -5.3977 | -7.416
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7349 | 0.7349 | -7.416 | -7.416

## LL_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 2.9953 | 2.9953 | 0 | 2.9953 | 2.9953 | 0 | 34.587 | 34.587 | 0 | 34.587 | 34.587 | -2.0843e-14 | 27.4008 | -8.7391 | 1.0421e-14 | -22.7354 | 13.4045 | -5.2106e-15 | 4.6417 | 16.5321 | 5.2106e-15 | 0.65175 | -11.2386 | 0 | -161.7883 | 18.2117 | 0 | 18.2117 | -161.7883 | 1.1 | 0.80351 | 0.54066 | 1.1 | 0.65761 | 0.50575 | 4.2602e-13 | -152.1736 | 136.0734 | 4.1751e-13 | -163.4303 | 158.2346
Line_1 | 0 | 2.9953 | 2.9953 | 0 | 2.9953 | 2.9953 | 0 | 34.587 | 34.587 | 0 | 34.587 | 34.587 | -1.0421e-14 | -18.0699 | 18.0699 | 7.594e-29 | 22.7354 | -13.4045 | 1.0421e-14 | 5.9452 | -5.9452 | -1.0421e-14 | -0.65175 | 11.2386 | 0 | 18.2117 | -161.7883 | 0 | -161.7883 | 18.2117 | 1.1 | 0.55 | 0.55 | 1.1 | 0.65761 | 0.50575 | 4.0773e-13 | 180 | -180 | 4.1751e-13 | -163.4303 | 158.2346
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.2106e-15 | 3.4051e-10 | 6.6441e-10 | 5.2106e-15 | -3.4051e-10 | -6.644e-10 | 1.0421e-14 | -1.8234e-09 | 1.2624e-09 | -5.2106e-15 | 1.8234e-09 | -1.2624e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.65761 | 0.50575 | 1.1 | 0.65761 | 0.50575 | 4.1883e-13 | -163.4303 | 158.2346 | 4.1751e-13 | -163.4303 | 158.2346

## LL_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 2.9953 | 2.9953 | 0 | 2.9953 | 2.9953 | 0 | 34.587 | 34.587 | 0 | 34.587 | 34.587 | -2.0843e-14 | 27.4008 | -8.7391 | 1.0421e-14 | -22.7354 | 13.4045 | -5.2106e-15 | 4.6417 | 16.5321 | 5.2106e-15 | 0.65175 | -11.2386 | 0 | -161.7883 | 18.2117 | 0 | 18.2117 | -161.7883 | 1.1 | 0.80351 | 0.54066 | 1.1 | 0.65761 | 0.50575 | 4.2602e-13 | -152.1736 | 136.0734 | 4.1751e-13 | -163.4303 | 158.2346
Line_1 | 0 | 2.9953 | 2.9953 | 0 | 2.9953 | 2.9953 | 0 | 34.587 | 34.587 | 0 | 34.587 | 34.587 | -1.0421e-14 | -18.0699 | 18.0699 | 7.594e-29 | 22.7354 | -13.4045 | 1.0421e-14 | 5.9452 | -5.9452 | -1.0421e-14 | -0.65175 | 11.2386 | 0 | 18.2117 | -161.7883 | 0 | -161.7883 | 18.2117 | 1.1 | 0.55 | 0.55 | 1.1 | 0.65761 | 0.50575 | 4.0773e-13 | 180 | -180 | 4.1751e-13 | -163.4303 | 158.2346
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.2106e-15 | 3.4051e-10 | 6.6441e-10 | 5.2106e-15 | -3.4051e-10 | -6.644e-10 | 1.0421e-14 | -1.8234e-09 | 1.2624e-09 | -5.2106e-15 | 1.8234e-09 | -1.2624e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.65761 | 0.50575 | 1.1 | 0.65761 | 0.50575 | 4.1883e-13 | -163.4303 | 158.2346 | 4.1751e-13 | -163.4303 | 158.2346

## LL_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 1.5688 | 1.5688 | 0 | 1.5688 | 1.5688 | 0 | 18.1144 | 18.1144 | 0 | 18.1144 | 18.1144 | -2.6053e-15 | 17.2205 | 0.20321 | -2.6053e-15 | -15.9408 | 1.0765 | -1.3027e-14 | 3.8735 | 14.2393 | 1.3027e-14 | -2.4216 | -12.7873 | 0 | -148.6532 | 31.3468 | 0 | 31.3468 | -148.6532 | 1.1 | 0.97441 | 0.78616 | 1.1 | 0.89011 | 0.70842 | 1.9811e-13 | -135.9762 | 120.5292 | 1.9112e-13 | -140.0155 | 126.1589
Line_1 | 0 | 1.5688 | 1.5688 | 0 | 1.5688 | 1.5688 | 0 | 18.1144 | 18.1144 | 0 | 18.1144 | 18.1144 | -5.2106e-15 | -14.6611 | 2.3562 | 8.6906e-30 | 15.9408 | -1.0765 | 2.6053e-15 | -0.96958 | -11.3353 | -2.6053e-15 | 2.4216 | 12.7873 | 0 | 31.3468 | -148.6532 | 0 | -148.6532 | 31.3468 | 1.1 | 0.81113 | 0.63914 | 1.1 | 0.89011 | 0.70842 | 1.8664e-13 | -144.8696 | 133.0893 | 1.9112e-13 | -140.0155 | 126.1589
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.6053e-15 | 4.6819e-10 | 1.0007e-09 | -5.2106e-15 | -4.6818e-10 | -1.0006e-09 | -5.2106e-15 | -1.2288e-09 | 3.0653e-10 | 2.6053e-15 | 1.2288e-09 | -3.0653e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.89011 | 0.70842 | 1.1 | 0.89011 | 0.70842 | 1.9218e-13 | -140.0155 | 126.1589 | 1.9112e-13 | -140.0155 | 126.1589

## LL_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 1.5688 | 1.5688 | 0 | 1.5688 | 1.5688 | 0 | 18.1144 | 18.1144 | 0 | 18.1144 | 18.1144 | -2.6053e-15 | 17.2205 | 0.20321 | -2.6053e-15 | -15.9408 | 1.0765 | -1.3027e-14 | 3.8735 | 14.2393 | 1.3027e-14 | -2.4216 | -12.7873 | 0 | -148.6532 | 31.3468 | 0 | 31.3468 | -148.6532 | 1.1 | 0.97441 | 0.78616 | 1.1 | 0.89011 | 0.70842 | 1.9811e-13 | -135.9762 | 120.5292 | 1.9112e-13 | -140.0155 | 126.1589
Line_1 | 0 | 1.5688 | 1.5688 | 0 | 1.5688 | 1.5688 | 0 | 18.1144 | 18.1144 | 0 | 18.1144 | 18.1144 | -5.2106e-15 | -14.6611 | 2.3562 | 8.6906e-30 | 15.9408 | -1.0765 | 2.6053e-15 | -0.96958 | -11.3353 | -2.6053e-15 | 2.4216 | 12.7873 | 0 | 31.3468 | -148.6532 | 0 | -148.6532 | 31.3468 | 1.1 | 0.81113 | 0.63914 | 1.1 | 0.89011 | 0.70842 | 1.8664e-13 | -144.8696 | 133.0893 | 1.9112e-13 | -140.0155 | 126.1589
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.6053e-15 | 4.6819e-10 | 1.0007e-09 | -5.2106e-15 | -4.6818e-10 | -1.0006e-09 | -5.2106e-15 | -1.2288e-09 | 3.0653e-10 | 2.6053e-15 | 1.2288e-09 | -3.0653e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.89011 | 0.70842 | 1.1 | 0.89011 | 0.70842 | 1.9218e-13 | -140.0155 | 126.1589 | 1.9112e-13 | -140.0155 | 126.1589

## LL_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 2.3976 | 2.3976 | 0 | 2.3976 | 2.3976 | 0 | 27.6856 | 27.6856 | 0 | 27.6856 | 27.6856 | 8.2897e-15 | 23.4155 | -0.45749 | -1.0658e-14 | -17.676 | 6.197 | -1.4211e-14 | -0.22679 | 13.7937 | 1.6579e-14 | 3.6185 | -10.402 | 0 | -149.5744 | 30.4256 | 0 | 30.4256 | -149.5744 | 1 | 0.8458 | 0.4985 | 1 | 0.65169 | 0.43734 | 3.8184e-13 | -150.1294 | 122.3252 | 3.4376e-13 | -161.1438 | 151.2099
Line_1 | 0 | 2.3976 | 2.3976 | 0 | 2.3976 | 2.3976 | 0 | 27.6856 | 27.6856 | 0 | 27.6856 | 27.6856 | -3.5527e-15 | -11.9365 | 11.9365 | 5.9212e-15 | 17.676 | -6.197 | 9.4739e-15 | 7.0103 | -7.0103 | -4.737e-15 | -3.6185 | 10.402 | 0 | 30.4256 | -149.5744 | 0 | -149.5744 | 30.4256 | 1 | 0.5 | 0.5 | 1 | 0.65169 | 0.43734 | 3.3048e-13 | -180 | 180 | 3.4376e-13 | -161.1438 | 151.2099
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1842e-15 | 2.4222e-10 | 6.7019e-10 | -3.5527e-15 | -2.4222e-10 | -6.7019e-10 | 6.8165e-30 | -1.5722e-09 | 8.3092e-10 | -2.1316e-29 | 1.5722e-09 | -8.3092e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.65169 | 0.43734 | 1 | 0.65169 | 0.43734 | 3.2979e-13 | -161.1438 | 151.2099 | 3.4376e-13 | -161.1438 | 151.2099

## LL_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 2.3976 | 2.3976 | 0 | 2.3976 | 2.3976 | 0 | 27.6856 | 27.6856 | 0 | 27.6856 | 27.6856 | 8.2897e-15 | 23.4155 | -0.45749 | -1.0658e-14 | -17.676 | 6.197 | -1.4211e-14 | -0.22679 | 13.7937 | 1.6579e-14 | 3.6185 | -10.402 | 0 | -149.5744 | 30.4256 | 0 | 30.4256 | -149.5744 | 1 | 0.8458 | 0.4985 | 1 | 0.65169 | 0.43734 | 3.8184e-13 | -150.1294 | 122.3252 | 3.4376e-13 | -161.1438 | 151.2099
Line_1 | 0 | 2.3976 | 2.3976 | 0 | 2.3976 | 2.3976 | 0 | 27.6856 | 27.6856 | 0 | 27.6856 | 27.6856 | -3.5527e-15 | -11.9365 | 11.9365 | 5.9212e-15 | 17.676 | -6.197 | 9.4739e-15 | 7.0103 | -7.0103 | -4.737e-15 | -3.6185 | 10.402 | 0 | 30.4256 | -149.5744 | 0 | -149.5744 | 30.4256 | 1 | 0.5 | 0.5 | 1 | 0.65169 | 0.43734 | 3.3048e-13 | -180 | 180 | 3.4376e-13 | -161.1438 | 151.2099
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1842e-15 | 2.4222e-10 | 6.7019e-10 | -3.5527e-15 | -2.4222e-10 | -6.7019e-10 | 6.8165e-30 | -1.5722e-09 | 8.3092e-10 | -2.1316e-29 | 1.5722e-09 | -8.3092e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.65169 | 0.43734 | 1 | 0.65169 | 0.43734 | 3.2979e-13 | -161.1438 | 151.2099 | 3.4376e-13 | -161.1438 | 151.2099

## LL_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 1.3081 | 1.3081 | 0 | 1.3081 | 1.3081 | 0 | 15.105 | 15.105 | 0 | 15.105 | 15.105 | 8.8818e-15 | 13.7181 | 1.6719 | -8.2897e-15 | -12.0096 | 0.036546 | -7.1054e-15 | 1.7406 | 10.8539 | 7.1054e-15 | -0.73098 | -9.8443 | 0 | -142.8911 | 37.1089 | 0 | 37.1089 | -142.8911 | 1 | 0.91546 | 0.72704 | 1 | 0.79654 | 0.65173 | 1.9381e-13 | -135.6599 | 118.3519 | 1.7015e-13 | -139.408 | 127.3216
Line_1 | 0 | 1.3081 | 1.3081 | 0 | 1.3081 | 1.3081 | 0 | 15.105 | 15.105 | 0 | 15.105 | 15.105 | -2.3685e-15 | -10.3011 | 1.745 | 2.3685e-15 | 12.0096 | -0.036546 | 4.737e-15 | 0.27863 | -8.8347 | -2.3685e-15 | 0.73098 | 9.8443 | 0 | 37.1089 | -142.8911 | 0 | -142.8911 | 37.1089 | 1 | 0.68221 | 0.59619 | 1 | 0.79654 | 0.65173 | 1.6289e-13 | -144.4405 | 138.2821 | 1.7015e-13 | -139.408 | 127.3216
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.9606e-15 | 4.2826e-10 | 8.1277e-10 | 1.7764e-15 | -4.2826e-10 | -8.1276e-10 | 2.3685e-15 | -9.7051e-10 | 3.0454e-10 | -4.737e-15 | 9.7052e-10 | -3.0453e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.79654 | 0.65173 | 1 | 0.79654 | 0.65173 | 1.6261e-13 | -139.408 | 127.3216 | 1.7015e-13 | -139.408 | 127.3216

## LL_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 1.3081 | 1.3081 | 0 | 1.3081 | 1.3081 | 0 | 15.105 | 15.105 | 0 | 15.105 | 15.105 | 8.8818e-15 | 13.7181 | 1.6719 | -8.2897e-15 | -12.0096 | 0.036546 | -7.1054e-15 | 1.7406 | 10.8539 | 7.1054e-15 | -0.73098 | -9.8443 | 0 | -142.8911 | 37.1089 | 0 | 37.1089 | -142.8911 | 1 | 0.91546 | 0.72704 | 1 | 0.79654 | 0.65173 | 1.9381e-13 | -135.6599 | 118.3519 | 1.7015e-13 | -139.408 | 127.3216
Line_1 | 0 | 1.3081 | 1.3081 | 0 | 1.3081 | 1.3081 | 0 | 15.105 | 15.105 | 0 | 15.105 | 15.105 | -2.3685e-15 | -10.3011 | 1.745 | 2.3685e-15 | 12.0096 | -0.036546 | 4.737e-15 | 0.27863 | -8.8347 | -2.3685e-15 | 0.73098 | 9.8443 | 0 | 37.1089 | -142.8911 | 0 | -142.8911 | 37.1089 | 1 | 0.68221 | 0.59619 | 1 | 0.79654 | 0.65173 | 1.6289e-13 | -144.4405 | 138.2821 | 1.7015e-13 | -139.408 | 127.3216
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.9606e-15 | 4.2826e-10 | 8.1277e-10 | 1.7764e-15 | -4.2826e-10 | -8.1276e-10 | 2.3685e-15 | -9.7051e-10 | 3.0454e-10 | -4.737e-15 | 9.7052e-10 | -3.0453e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.79654 | 0.65173 | 1 | 0.79654 | 0.65173 | 1.6261e-13 | -139.408 | 127.3216 | 1.7015e-13 | -139.408 | 127.3216

## LG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 2.622 | 0.0049769 | 0.0049769 | 2.6214 | 0.0040536 | 0.0040536 | 30.2768 | 0.057469 | 0.057469 | 30.2698 | 0.046807 | 0.046807 | 21.7137 | 0.056227 | -0.049097 | -10.842 | -0.043085 | 0.041828 | 12.1268 | -0.011956 | -0.04188 | -6.0693 | 0.019501 | 0.046753 | -47.9804 | -105.8602 | -105.8602 | 132.0351 | 72.2065 | 72.2065 | 0.82144 | 1.0003 | 1.1229 | 0.41048 | 1.0104 | 1.3403 | -18.7977 | -117.865 | 114.6037 | -18.7251 | -132.1464 | 120.389
Line_1 | 2.6194 | 0 | 0 | 2.6206 | 0.0023956 | 0.0023956 | 30.2463 | 0 | 0 | 30.2596 | 0.027662 | 0.027662 | 1.1062e-10 | -3.4092e-10 | -2.6988e-09 | 10.8416 | 0.025719 | -0.024083 | -1.1711e-10 | -1.8625e-09 | 5.0121e-10 | 6.0614 | -0.010941 | -0.028187 | 132.1118 | 0 | 0 | -47.9341 | -109.1011 | -109.1011 | 0 | 1.0805 | 1.5664 | 0.41048 | 1.0104 | 1.3403 | 0 | -145.3007 | 124.5504 | -18.7251 | -132.1464 | 120.389
Line_2 | 0 | 0 | 0 | 0.0016595 | 0.0016595 | 0.0016595 | 0 | 0 | 0 | 0.019162 | 0.019162 | 0.019162 | 9.504e-10 | 2.4125e-10 | -1.1823e-09 | 0.00038691 | 0.017366 | -0.017745 | -5.3035e-10 | -8.5814e-10 | 3.6212e-11 | 0.0078562 | -0.0085605 | -0.018566 | 0 | 0 | 0 | -105.9056 | -105.9056 | -105.9056 | 0.41036 | 1.0102 | 1.3405 | 0.41048 | 1.0104 | 1.3403 | -18.6888 | -132.1584 | 120.3839 | -18.7251 | -132.1464 | 120.389

## LG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 2.622 | 0.0049769 | 0.0049769 | 2.6214 | 0.0040536 | 0.0040536 | 30.2768 | 0.057469 | 0.057469 | 30.2698 | 0.046807 | 0.046807 | 21.7137 | 0.056227 | -0.049097 | -10.842 | -0.043085 | 0.041828 | 12.1268 | -0.011956 | -0.04188 | -6.0693 | 0.019501 | 0.046753 | -47.9804 | -105.8602 | -105.8602 | 132.0351 | 72.2065 | 72.2065 | 0.82144 | 1.0003 | 1.1229 | 0.41048 | 1.0104 | 1.3403 | -18.7977 | -117.865 | 114.6037 | -18.7251 | -132.1464 | 120.389
Line_1 | 2.6194 | 0 | 0 | 2.6206 | 0.0023956 | 0.0023956 | 30.2463 | 0 | 0 | 30.2596 | 0.027662 | 0.027662 | 1.1062e-10 | -3.4092e-10 | -2.6988e-09 | 10.8416 | 0.025719 | -0.024083 | -1.1711e-10 | -1.8625e-09 | 5.0121e-10 | 6.0614 | -0.010941 | -0.028187 | 132.1118 | 0 | 0 | -47.9341 | -109.1011 | -109.1011 | 0 | 1.0805 | 1.5664 | 0.41048 | 1.0104 | 1.3403 | 0 | -145.3007 | 124.5504 | -18.7251 | -132.1464 | 120.389
Line_2 | 0 | 0 | 0 | 0.0016595 | 0.0016595 | 0.0016595 | 0 | 0 | 0 | 0.019162 | 0.019162 | 0.019162 | 9.504e-10 | 2.4125e-10 | -1.1823e-09 | 0.00038691 | 0.017366 | -0.017745 | -5.3035e-10 | -8.5814e-10 | 3.6212e-11 | 0.0078562 | -0.0085605 | -0.018566 | 0 | 0 | 0 | -105.9056 | -105.9056 | -105.9056 | 0.41036 | 1.0102 | 1.3405 | 0.41048 | 1.0104 | 1.3403 | -18.6888 | -132.1584 | 120.3839 | -18.7251 | -132.1464 | 120.389

## LG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.067 | 0.0020252 | 0.0020252 | 1.0667 | 0.0016495 | 0.0016495 | 12.3203 | 0.023385 | 0.023385 | 12.3174 | 0.019047 | 0.019047 | 9.2727 | 0.023905 | -0.019298 | -7.4727 | -0.019137 | 0.015731 | 7.7035 | -0.0064497 | -0.017339 | -6.6976 | 0.0064667 | 0.016518 | -46.2671 | -104.1469 | -104.1469 | 133.7485 | 73.9199 | 73.9199 | 0.97848 | 1.0588 | 1.1094 | 0.81469 | 1.0606 | 1.1976 | -6.548 | -119.2459 | 117.7924 | -4.3823 | -124.7506 | 120.3169
Line_1 | 1.0659 | 0 | 0 | 1.0664 | 0.00097482 | 0.00097482 | 12.3079 | 0 | 0 | 12.3133 | 0.011256 | 0.011256 | -5.6806 | 4.0635e-11 | -8.8963e-10 | 7.4738 | 0.011394 | -0.0090719 | -5.6806 | -7.636e-10 | 2.2653e-10 | 6.6914 | -0.0035626 | -0.0099715 | 133.8251 | 0 | 0 | -46.2208 | -107.3878 | -107.3878 | 0.65272 | 1.0724 | 1.2874 | 0.81469 | 1.0606 | 1.1976 | -1.1749 | -130.1686 | 122.5002 | -4.3823 | -124.7506 | 120.3169
Line_2 | 0 | 0 | 0 | 0.00067529 | 0.00067529 | 0.00067529 | 0 | 0 | 0 | 0.0077975 | 0.0077975 | 0.0077975 | 8.4275e-10 | 1.3889e-10 | -4.2925e-10 | -0.0010824 | 0.0077433 | -0.0066596 | -2.5062e-10 | -3.5456e-10 | 2.6537e-11 | 0.0062597 | -0.0029041 | -0.0065465 | 0 | 0 | 0 | -104.1923 | -104.1923 | -104.1923 | 0.81467 | 1.0605 | 1.1977 | 0.81469 | 1.0606 | 1.1976 | -4.3743 | -124.7548 | 120.3148 | -4.3823 | -124.7506 | 120.3169

## LG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.067 | 0.0020252 | 0.0020252 | 1.0667 | 0.0016495 | 0.0016495 | 12.3203 | 0.023385 | 0.023385 | 12.3174 | 0.019047 | 0.019047 | 9.2727 | 0.023905 | -0.019298 | -7.4727 | -0.019137 | 0.015731 | 7.7035 | -0.0064497 | -0.017339 | -6.6976 | 0.0064667 | 0.016518 | -46.2671 | -104.1469 | -104.1469 | 133.7485 | 73.9199 | 73.9199 | 0.97848 | 1.0588 | 1.1094 | 0.81469 | 1.0606 | 1.1976 | -6.548 | -119.2459 | 117.7924 | -4.3823 | -124.7506 | 120.3169
Line_1 | 1.0659 | 0 | 0 | 1.0664 | 0.00097482 | 0.00097482 | 12.3079 | 0 | 0 | 12.3133 | 0.011256 | 0.011256 | -5.6806 | 4.0635e-11 | -8.8963e-10 | 7.4738 | 0.011394 | -0.0090719 | -5.6806 | -7.636e-10 | 2.2653e-10 | 6.6914 | -0.0035626 | -0.0099715 | 133.8251 | 0 | 0 | -46.2208 | -107.3878 | -107.3878 | 0.65272 | 1.0724 | 1.2874 | 0.81469 | 1.0606 | 1.1976 | -1.1749 | -130.1686 | 122.5002 | -4.3823 | -124.7506 | 120.3169
Line_2 | 0 | 0 | 0 | 0.00067529 | 0.00067529 | 0.00067529 | 0 | 0 | 0 | 0.0077975 | 0.0077975 | 0.0077975 | 8.4275e-10 | 1.3889e-10 | -4.2925e-10 | -0.0010824 | 0.0077433 | -0.0066596 | -2.5062e-10 | -3.5456e-10 | 2.6537e-11 | 0.0062597 | -0.0029041 | -0.0065465 | 0 | 0 | 0 | -104.1923 | -104.1923 | -104.1923 | 0.81467 | 1.0605 | 1.1977 | 0.81469 | 1.0606 | 1.1976 | -4.3743 | -124.7548 | 120.3148 | -4.3823 | -124.7506 | 120.3169

## LG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.6097 | 0.0052148 | 0.0052148 | 1.6093 | 0.0043058 | 0.0043058 | 18.5872 | 0.060215 | 0.060215 | 18.5828 | 0.049719 | 0.049719 | 15.7124 | 0.053602 | -0.048245 | -7.8453 | -0.042258 | 0.041371 | 4.5508 | -0.016735 | -0.039202 | -2.2883 | 0.026847 | 0.04739 | -30.9232 | -102.44 | -102.44 | 149.1063 | 76.1991 | 76.1991 | 0.88008 | 0.93255 | 1.0324 | 0.43978 | 1.007 | 1.2653 | -14.7707 | -119.7792 | 116.6563 | -14.6327 | -136.2291 | 125.0782
Line_1 | 1.6081 | 0 | 0 | 1.6088 | 0.0025677 | 0.0025677 | 18.5682 | 0 | 0 | 18.5764 | 0.029649 | 0.029649 | -1.9134e-11 | -1.1833e-09 | -2.9618e-09 | 7.845 | 0.025438 | -0.024243 | -6.9354e-13 | -2.0731e-09 | 1.0462e-09 | 2.2795 | -0.015629 | -0.028628 | 149.253 | 0 | 0 | -30.8349 | -104.6633 | -104.6633 | 0 | 1.1514 | 1.5152 | 0.43978 | 1.007 | 1.2653 | 0 | -149.4085 | 130.8538 | -14.6327 | -136.2291 | 125.0782
Line_2 | 0 | 0 | 0 | 0.0017388 | 0.0017388 | 0.0017388 | 0 | 0 | 0 | 0.020078 | 0.020078 | 0.020078 | 8.5151e-10 | -1.7176e-10 | -1.2513e-09 | 0.00032441 | 0.01682 | -0.017128 | -4.0535e-10 | -1.0329e-09 | 4.0962e-10 | 0.0088238 | -0.011218 | -0.018761 | 0 | 0 | 0 | -102.5272 | -102.5272 | -102.5272 | 0.43965 | 1.0066 | 1.2657 | 0.43978 | 1.007 | 1.2653 | -14.5637 | -136.2512 | 125.0637 | -14.6327 | -136.2291 | 125.0782

## LG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.6097 | 0.0052148 | 0.0052148 | 1.6093 | 0.0043058 | 0.0043058 | 18.5872 | 0.060215 | 0.060215 | 18.5828 | 0.049719 | 0.049719 | 15.7124 | 0.053602 | -0.048245 | -7.8453 | -0.042258 | 0.041371 | 4.5508 | -0.016735 | -0.039202 | -2.2883 | 0.026847 | 0.04739 | -30.9232 | -102.44 | -102.44 | 149.1063 | 76.1991 | 76.1991 | 0.88008 | 0.93255 | 1.0324 | 0.43978 | 1.007 | 1.2653 | -14.7707 | -119.7792 | 116.6563 | -14.6327 | -136.2291 | 125.0782
Line_1 | 1.6081 | 0 | 0 | 1.6088 | 0.0025677 | 0.0025677 | 18.5682 | 0 | 0 | 18.5764 | 0.029649 | 0.029649 | -1.9134e-11 | -1.1833e-09 | -2.9618e-09 | 7.845 | 0.025438 | -0.024243 | -6.9354e-13 | -2.0731e-09 | 1.0462e-09 | 2.2795 | -0.015629 | -0.028628 | 149.253 | 0 | 0 | -30.8349 | -104.6633 | -104.6633 | 0 | 1.1514 | 1.5152 | 0.43978 | 1.007 | 1.2653 | 0 | -149.4085 | 130.8538 | -14.6327 | -136.2291 | 125.0782
Line_2 | 0 | 0 | 0 | 0.0017388 | 0.0017388 | 0.0017388 | 0 | 0 | 0 | 0.020078 | 0.020078 | 0.020078 | 8.5151e-10 | -1.7176e-10 | -1.2513e-09 | 0.00032441 | 0.01682 | -0.017128 | -4.0535e-10 | -1.0329e-09 | 4.0962e-10 | 0.0088238 | -0.011218 | -0.018761 | 0 | 0 | 0 | -102.5272 | -102.5272 | -102.5272 | 0.43965 | 1.0066 | 1.2657 | 0.43978 | 1.007 | 1.2653 | -14.5637 | -136.2512 | 125.0637 | -14.6327 | -136.2291 | 125.0782

## LG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.81736 | 0.0026479 | 0.0026479 | 0.81716 | 0.0021863 | 0.0021863 | 9.438 | 0.030575 | 0.030575 | 9.4358 | 0.025246 | 0.025246 | 7.3778 | 0.029083 | -0.020834 | -5.3504 | -0.023511 | 0.017346 | 4.5205 | -0.0051968 | -0.022884 | -3.9347 | 0.0073507 | 0.02293 | -37.9946 | -109.5114 | -109.5114 | 142.035 | 69.1278 | 69.1278 | 0.91678 | 0.96625 | 1.0122 | 0.70385 | 0.97576 | 1.1389 | -6.498 | -119.6426 | 118.1738 | -1.6341 | -128.2337 | 122.021
Line_1 | 0.81652 | 0 | 0 | 0.81688 | 0.0013038 | 0.0013038 | 9.4284 | 0 | 0 | 9.4326 | 0.015055 | 0.015055 | -3.3335 | -1.7823e-10 | -1.2695e-09 | 5.3526 | 0.014085 | -0.010137 | -3.3335 | -1.0453e-09 | 4.153e-10 | 3.9278 | -0.0041719 | -0.013828 | 142.1816 | 0 | 0 | -37.9063 | -111.7347 | -111.7347 | 0.50002 | 1.0074 | 1.2689 | 0.70385 | 0.97576 | 1.1389 | 7.1816 | -136.4395 | 125.1212 | -1.6341 | -128.2337 | 122.021
Line_2 | 0 | 0 | 0 | 0.00088291 | 0.00088291 | 0.00088291 | 0 | 0 | 0 | 0.010195 | 0.010195 | 0.010195 | 7.6323e-10 | 5.0626e-11 | -5.835e-10 | -0.0022132 | 0.0094263 | -0.0072089 | -7.2589e-11 | -5.1276e-10 | 1.4664e-10 | 0.0068259 | -0.0031787 | -0.0091018 | 0 | 0 | 0 | -109.5985 | -109.5985 | -109.5985 | 0.70388 | 0.97552 | 1.1391 | 0.70385 | 0.97576 | 1.1389 | -1.6117 | -128.2419 | 122.0121 | -1.6341 | -128.2337 | 122.021

## LG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.81736 | 0.0026479 | 0.0026479 | 0.81716 | 0.0021863 | 0.0021863 | 9.438 | 0.030575 | 0.030575 | 9.4358 | 0.025246 | 0.025246 | 7.3778 | 0.029083 | -0.020834 | -5.3504 | -0.023511 | 0.017346 | 4.5205 | -0.0051968 | -0.022884 | -3.9347 | 0.0073507 | 0.02293 | -37.9946 | -109.5114 | -109.5114 | 142.035 | 69.1278 | 69.1278 | 0.91678 | 0.96625 | 1.0122 | 0.70385 | 0.97576 | 1.1389 | -6.498 | -119.6426 | 118.1738 | -1.6341 | -128.2337 | 122.021
Line_1 | 0.81652 | 0 | 0 | 0.81688 | 0.0013038 | 0.0013038 | 9.4284 | 0 | 0 | 9.4326 | 0.015055 | 0.015055 | -3.3335 | -1.7823e-10 | -1.2695e-09 | 5.3526 | 0.014085 | -0.010137 | -3.3335 | -1.0453e-09 | 4.153e-10 | 3.9278 | -0.0041719 | -0.013828 | 142.1816 | 0 | 0 | -37.9063 | -111.7347 | -111.7347 | 0.50002 | 1.0074 | 1.2689 | 0.70385 | 0.97576 | 1.1389 | 7.1816 | -136.4395 | 125.1212 | -1.6341 | -128.2337 | 122.021
Line_2 | 0 | 0 | 0 | 0.00088291 | 0.00088291 | 0.00088291 | 0 | 0 | 0 | 0.010195 | 0.010195 | 0.010195 | 7.6323e-10 | 5.0626e-11 | -5.835e-10 | -0.0022132 | 0.0094263 | -0.0072089 | -7.2589e-11 | -5.1276e-10 | 1.4664e-10 | 0.0068259 | -0.0031787 | -0.0091018 | 0 | 0 | 0 | -109.5985 | -109.5985 | -109.5985 | 0.70388 | 0.97552 | 1.1391 | 0.70385 | 0.97576 | 1.1389 | -1.6117 | -128.2419 | 122.0121 | -1.6341 | -128.2337 | 122.021

## LLG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.0037055 | 3.6665 | 2.5319 | 0.003018 | 3.6665 | 2.5315 | 0.042788 | 42.3366 | 29.2356 | 0.034849 | 42.3366 | 29.2315 | -0.00063243 | 28.2024 | 0.52267 | 0.00094629 | -14.098 | -0.25567 | -0.045083 | 9.1474 | 16.5198 | 0.042987 | -4.5886 | -8.2469 | 87.3454 | -174.0895 | 36.1821 | -94.5878 | 5.9214 | -143.8315 | 1.0538 | 0.70031 | 0.56534 | 1.2338 | 0.35019 | 0.28226 | -3.4583 | -156.1191 | 124.3699 | -5.8489 | -156.0497 | 124.3928
Line_1 | 0 | 3.667 | 2.5296 | 0.0017836 | 3.6666 | 2.5307 | 0 | 42.343 | 29.2088 | 0.020595 | 42.3388 | 29.2225 | -1.685e-09 | 9.8954e-11 | 9.533e-11 | 2.0653e-05 | 14.1002 | 0.25246 | -7.546e-10 | -1.0837e-10 | -3.0933e-11 | -0.025411 | 4.5841 | 8.2445 | 0 | 5.9677 | -143.8833 | 84.1045 | -174.0596 | 36.1467 | 1.4151 | 0 | 0 | 1.2338 | 0.35019 | 0.28226 | -7.5976 | 0 | 0 | -5.8489 | -156.0497 | 124.3928
Line_2 | 0 | 0 | 0 | 0.0012356 | 0.0012356 | 0.0012356 | 0 | 0 | 0 | 0.014267 | 0.014267 | 0.014267 | -6.3182e-10 | 6.9282e-10 | 8.4256e-10 | -0.00096695 | -0.002241 | 0.0032122 | -5.0791e-10 | -8.3055e-10 | 8.7363e-11 | -0.017576 | 0.0044654 | 0.0024287 | 0 | 0 | 0 | 87.3 | 87.3 | 87.3 | 1.2339 | 0.35021 | 0.28206 | 1.2338 | 0.35019 | 0.28226 | -5.8579 | -156.015 | 124.4043 | -5.8489 | -156.0497 | 124.3928

## LLG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.0037055 | 3.6665 | 2.5319 | 0.003018 | 3.6665 | 2.5315 | 0.042788 | 42.3366 | 29.2356 | 0.034849 | 42.3366 | 29.2315 | -0.00063243 | 28.2024 | 0.52267 | 0.00094629 | -14.098 | -0.25567 | -0.045083 | 9.1474 | 16.5198 | 0.042987 | -4.5886 | -8.2469 | 87.3454 | -174.0895 | 36.1821 | -94.5878 | 5.9214 | -143.8315 | 1.0538 | 0.70031 | 0.56534 | 1.2338 | 0.35019 | 0.28226 | -3.4583 | -156.1191 | 124.3699 | -5.8489 | -156.0497 | 124.3928
Line_1 | 0 | 3.667 | 2.5296 | 0.0017836 | 3.6666 | 2.5307 | 0 | 42.343 | 29.2088 | 0.020595 | 42.3388 | 29.2225 | -1.685e-09 | 9.8954e-11 | 9.533e-11 | 2.0653e-05 | 14.1002 | 0.25246 | -7.546e-10 | -1.0837e-10 | -3.0933e-11 | -0.025411 | 4.5841 | 8.2445 | 0 | 5.9677 | -143.8833 | 84.1045 | -174.0596 | 36.1467 | 1.4151 | 0 | 0 | 1.2338 | 0.35019 | 0.28226 | -7.5976 | 0 | 0 | -5.8489 | -156.0497 | 124.3928
Line_2 | 0 | 0 | 0 | 0.0012356 | 0.0012356 | 0.0012356 | 0 | 0 | 0 | 0.014267 | 0.014267 | 0.014267 | -6.3182e-10 | 6.9282e-10 | 8.4256e-10 | -0.00096695 | -0.002241 | 0.0032122 | -5.0791e-10 | -8.3055e-10 | 8.7363e-11 | -0.017576 | 0.0044654 | 0.0024287 | 0 | 0 | 0 | 87.3 | 87.3 | 87.3 | 1.2339 | 0.35021 | 0.28206 | 1.2338 | 0.35019 | 0.28226 | -5.8579 | -156.015 | 124.4043 | -5.8489 | -156.0497 | 124.3928

## LLG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.0017838 | 1.2486 | 1.0423 | 0.0014529 | 1.2487 | 1.042 | 0.020598 | 14.418 | 12.0358 | 0.016776 | 14.4189 | 12.0324 | 0.0025117 | 11.4091 | 6.4303 | -0.0022617 | -9.602 | -5.9239 | -0.021988 | 8.0202 | 8.851 | 0.019283 | -7.9161 | -7.1329 | 81.9741 | -165.5405 | 61.9 | -99.9591 | 14.4744 | -118.1088 | 1.0744 | 0.96727 | 0.90898 | 1.1573 | 0.86306 | 0.77059 | -1.5091 | -130.4346 | 115.9014 | -3.2695 | -126.0227 | 112.1815
Line_1 | 0 | 1.2493 | 1.0407 | 0.00085863 | 1.2489 | 1.0415 | 0 | 14.4259 | 12.0164 | 0.0099146 | 14.4216 | 12.0259 | -6.5867e-10 | -7.804 | -5.4148 | 0.0015963 | 9.6072 | 5.9193 | -4.1668e-10 | -7.804 | -5.4148 | -0.011362 | 7.9133 | 7.1303 | 0 | 14.5351 | -118.1337 | 78.7332 | -165.5004 | 61.88 | 1.2409 | 0.76505 | 0.63727 | 1.1573 | 0.86306 | 0.77059 | -4.7756 | -120.4649 | 106.8663 | -3.2695 | -126.0227 | 112.1815
Line_2 | 0 | 0 | 0 | 0.0005948 | 0.0005948 | 0.0005948 | 0 | 0 | 0 | 0.0068682 | 0.0068682 | 0.0068682 | -2.5079e-10 | 7.3047e-10 | 9.0202e-10 | 0.00066534 | -0.0052361 | 0.0045718 | -2.6661e-10 | -3.6496e-10 | -4.227e-10 | -0.0079204 | 0.0027784 | 0.0026665 | 0 | 0 | 0 | 81.9287 | 81.9287 | 81.9287 | 1.1573 | 0.86313 | 0.77049 | 1.1573 | 0.86306 | 0.77059 | -3.2744 | -126.0176 | 112.1827 | -3.2695 | -126.0227 | 112.1815

## LLG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.0017838 | 1.2486 | 1.0423 | 0.0014529 | 1.2487 | 1.042 | 0.020598 | 14.418 | 12.0358 | 0.016776 | 14.4189 | 12.0324 | 0.0025117 | 11.4091 | 6.4303 | -0.0022617 | -9.602 | -5.9239 | -0.021988 | 8.0202 | 8.851 | 0.019283 | -7.9161 | -7.1329 | 81.9741 | -165.5405 | 61.9 | -99.9591 | 14.4744 | -118.1088 | 1.0744 | 0.96727 | 0.90898 | 1.1573 | 0.86306 | 0.77059 | -1.5091 | -130.4346 | 115.9014 | -3.2695 | -126.0227 | 112.1815
Line_1 | 0 | 1.2493 | 1.0407 | 0.00085863 | 1.2489 | 1.0415 | 0 | 14.4259 | 12.0164 | 0.0099146 | 14.4216 | 12.0259 | -6.5867e-10 | -7.804 | -5.4148 | 0.0015963 | 9.6072 | 5.9193 | -4.1668e-10 | -7.804 | -5.4148 | -0.011362 | 7.9133 | 7.1303 | 0 | 14.5351 | -118.1337 | 78.7332 | -165.5004 | 61.88 | 1.2409 | 0.76505 | 0.63727 | 1.1573 | 0.86306 | 0.77059 | -4.7756 | -120.4649 | 106.8663 | -3.2695 | -126.0227 | 112.1815
Line_2 | 0 | 0 | 0 | 0.0005948 | 0.0005948 | 0.0005948 | 0 | 0 | 0 | 0.0068682 | 0.0068682 | 0.0068682 | -2.5079e-10 | 7.3047e-10 | 9.0202e-10 | 0.00066534 | -0.0052361 | 0.0045718 | -2.6661e-10 | -3.6496e-10 | -4.227e-10 | -0.0079204 | 0.0027784 | 0.0026665 | 0 | 0 | 0 | 81.9287 | 81.9287 | 81.9287 | 1.1573 | 0.86313 | 0.77049 | 1.1573 | 0.86306 | 0.77059 | -3.2744 | -126.0176 | 112.1827 | -3.2695 | -126.0227 | 112.1815

## LLG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.003437 | 2.7635 | 2.1034 | 0.0028379 | 2.7637 | 2.103 | 0.039688 | 31.9104 | 24.288 | 0.03277 | 31.9125 | 24.2838 | -0.0004052 | 25.2259 | 3.439 | 0.0005749 | -12.6188 | -1.7085 | -0.039046 | 2.2643 | 12.6315 | 0.038357 | -1.152 | -6.3002 | 88.197 | -158.1489 | 41.722 | -93.1638 | 21.8631 | -138.2911 | 0.98389 | 0.7937 | 0.539 | 1.1706 | 0.39706 | 0.26881 | -2.3976 | -153.0196 | 116.4921 | -4.0225 | -152.9205 | 116.5361
Line_1 | 0 | 2.7649 | 2.101 | 0.0016924 | 2.7642 | 2.1022 | 0 | 31.9264 | 24.2607 | 0.019542 | 31.9178 | 24.2747 | -1.8007e-09 | -1.5327e-10 | -3.2042e-11 | 1.5139e-06 | 12.6213 | 1.7054 | -4.4607e-10 | -1.1766e-10 | -1.4336e-10 | -0.022876 | 1.1475 | 6.2985 | 0 | 21.9164 | -138.3459 | 85.9737 | -158.1152 | 41.6863 | 1.3577 | 0 | 0 | 1.1706 | 0.39706 | 0.26881 | -5.1411 | 0 | 0 | -4.0225 | -152.9205 | 116.5361
Line_2 | 0 | 0 | 0 | 0.001146 | 0.001146 | 0.001146 | 0 | 0 | 0 | 0.013233 | 0.013233 | 0.013233 | -7.4349e-10 | 6.4474e-10 | 7.1833e-10 | -0.00057641 | -0.002545 | 0.0031284 | -3.0239e-10 | -7.904e-10 | -5.9096e-11 | -0.015481 | 0.004597 | 0.0016934 | 0 | 0 | 0 | 88.1099 | 88.1099 | 88.1099 | 1.1707 | 0.39717 | 0.26847 | 1.1706 | 0.39706 | 0.26881 | -4.0396 | -152.871 | 116.5582 | -4.0225 | -152.9205 | 116.5361

## LLG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.003437 | 2.7635 | 2.1034 | 0.0028379 | 2.7637 | 2.103 | 0.039688 | 31.9104 | 24.288 | 0.03277 | 31.9125 | 24.2838 | -0.0004052 | 25.2259 | 3.439 | 0.0005749 | -12.6188 | -1.7085 | -0.039046 | 2.2643 | 12.6315 | 0.038357 | -1.152 | -6.3002 | 88.197 | -158.1489 | 41.722 | -93.1638 | 21.8631 | -138.2911 | 0.98389 | 0.7937 | 0.539 | 1.1706 | 0.39706 | 0.26881 | -2.3976 | -153.0196 | 116.4921 | -4.0225 | -152.9205 | 116.5361
Line_1 | 0 | 2.7649 | 2.101 | 0.0016924 | 2.7642 | 2.1022 | 0 | 31.9264 | 24.2607 | 0.019542 | 31.9178 | 24.2747 | -1.8007e-09 | -1.5327e-10 | -3.2042e-11 | 1.5139e-06 | 12.6213 | 1.7054 | -4.4607e-10 | -1.1766e-10 | -1.4336e-10 | -0.022876 | 1.1475 | 6.2985 | 0 | 21.9164 | -138.3459 | 85.9737 | -158.1152 | 41.6863 | 1.3577 | 0 | 0 | 1.1706 | 0.39706 | 0.26881 | -5.1411 | 0 | 0 | -4.0225 | -152.9205 | 116.5361
Line_2 | 0 | 0 | 0 | 0.001146 | 0.001146 | 0.001146 | 0 | 0 | 0 | 0.013233 | 0.013233 | 0.013233 | -7.4349e-10 | 6.4474e-10 | 7.1833e-10 | -0.00057641 | -0.002545 | 0.0031284 | -3.0239e-10 | -7.904e-10 | -5.9096e-11 | -0.015481 | 0.004597 | 0.0016934 | 0 | 0 | 0 | 88.1099 | 88.1099 | 88.1099 | 1.1707 | 0.39717 | 0.26847 | 1.1706 | 0.39706 | 0.26881 | -4.0396 | -152.871 | 116.5582 | -4.0225 | -152.9205 | 116.5361

## LLG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.0021321 | 1.0562 | 0.84151 | 0.0017604 | 1.0564 | 0.84117 | 0.024619 | 12.1959 | 9.717 | 0.020328 | 12.1979 | 9.713 | 0.0042966 | 9.8368 | 4.677 | -0.0036278 | -7.7108 | -4.0995 | -0.02388 | 4.9063 | 6.6238 | 0.021982 | -5.2533 | -5.0732 | 78.4412 | -157.4195 | 61.1586 | -102.9197 | 22.5985 | -118.8516 | 0.98557 | 0.90133 | 0.83447 | 1.096 | 0.76491 | 0.67153 | -1.3592 | -130.9108 | 115.9333 | -3.5485 | -123.1351 | 112.2077
Line_1 | 0 | 1.0574 | 0.83948 | 0.0010498 | 1.0568 | 0.84049 | 0 | 12.2097 | 9.6935 | 0.012122 | 12.2025 | 9.7052 | -9.386e-10 | -5.5904 | -3.5236 | 0.0023605 | 7.7166 | 4.095 | -4.0846e-10 | -5.5904 | -3.5236 | -0.013075 | 5.251 | 5.0701 | 0 | 22.6762 | -118.8846 | 76.2179 | -157.3696 | 61.1341 | 1.2077 | 0.64752 | 0.51407 | 1.096 | 0.76491 | 0.67153 | -5.2927 | -112.3238 | 106.1154 | -3.5485 | -123.1351 | 112.2077
Line_2 | 0 | 0 | 0 | 0.00071092 | 0.00071092 | 0.00071092 | 0 | 0 | 0 | 0.0082089 | 0.0082089 | 0.0082089 | -3.9371e-10 | 6.5482e-10 | 7.8636e-10 | 0.0012673 | -0.0058426 | 0.004578 | -2.4955e-10 | -1.5298e-10 | -3.3343e-10 | -0.0089075 | 0.0023002 | 0.0030709 | 0 | 0 | 0 | 78.354 | 78.354 | 78.354 | 1.096 | 0.76509 | 0.67132 | 1.096 | 0.76491 | 0.67153 | -3.5601 | -123.1259 | 112.2149 | -3.5485 | -123.1351 | 112.2077

## LLG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.0021321 | 1.0562 | 0.84151 | 0.0017604 | 1.0564 | 0.84117 | 0.024619 | 12.1959 | 9.717 | 0.020328 | 12.1979 | 9.713 | 0.0042966 | 9.8368 | 4.677 | -0.0036278 | -7.7108 | -4.0995 | -0.02388 | 4.9063 | 6.6238 | 0.021982 | -5.2533 | -5.0732 | 78.4412 | -157.4195 | 61.1586 | -102.9197 | 22.5985 | -118.8516 | 0.98557 | 0.90133 | 0.83447 | 1.096 | 0.76491 | 0.67153 | -1.3592 | -130.9108 | 115.9333 | -3.5485 | -123.1351 | 112.2077
Line_1 | 0 | 1.0574 | 0.83948 | 0.0010498 | 1.0568 | 0.84049 | 0 | 12.2097 | 9.6935 | 0.012122 | 12.2025 | 9.7052 | -9.386e-10 | -5.5904 | -3.5236 | 0.0023605 | 7.7166 | 4.095 | -4.0846e-10 | -5.5904 | -3.5236 | -0.013075 | 5.251 | 5.0701 | 0 | 22.6762 | -118.8846 | 76.2179 | -157.3696 | 61.1341 | 1.2077 | 0.64752 | 0.51407 | 1.096 | 0.76491 | 0.67153 | -5.2927 | -112.3238 | 106.1154 | -3.5485 | -123.1351 | 112.2077
Line_2 | 0 | 0 | 0 | 0.00071092 | 0.00071092 | 0.00071092 | 0 | 0 | 0 | 0.0082089 | 0.0082089 | 0.0082089 | -3.9371e-10 | 6.5482e-10 | 7.8636e-10 | 0.0012673 | -0.0058426 | 0.004578 | -2.4955e-10 | -1.5298e-10 | -3.3343e-10 | -0.0089075 | 0.0023002 | 0.0030709 | 0 | 0 | 0 | 78.354 | 78.354 | 78.354 | 1.096 | 0.76509 | 0.67132 | 1.096 | 0.76491 | 0.67153 | -3.5601 | -123.1259 | 112.2149 | -3.5485 | -123.1351 | 112.2077