## LLL_max_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.34641 | 0.34641 | 0 | 0 | 12 | 12 | -0.023022 | 0.21022 | -0.67342 | 0.88582 | 95.7106 | -84.2894 | 0.056151 | 0.075869 | 3.7526 | -7.6398
Line_1 | 0.17321 | 0.17321 | 0 | 0 | 6 | 6 | 0.15191 | -0.10511 | 0.49601 | -0.44291 | -84.2894 | 95.7106 | 0.086459 | 0.075869 | -11.3174 | -7.6398
Line_2 | 0.17321 | 0.17321 | 0 | 0 | 6 | 6 | 0.15191 | -0.10511 | 0.49601 | -0.44291 | -84.2894 | 95.7106 | 0.086459 | 0.075869 | -11.3174 | -7.6398

## LLL_max_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.34641 | 0.34641 | 0 | 0 | 12 | 12 | -0.023022 | 0.21022 | -0.67342 | 0.88582 | 95.7106 | -84.2894 | 0.056151 | 0.075869 | 3.7526 | -7.6398
Line_1 | 0.17321 | 0.17321 | 0 | 0 | 6 | 6 | 0.15191 | -0.10511 | 0.49601 | -0.44291 | -84.2894 | 95.7106 | 0.086459 | 0.075869 | -11.3174 | -7.6398
Line_2 | 0.17321 | 0.17321 | 0 | 0 | 6 | 6 | 0.15191 | -0.10511 | 0.49601 | -0.44291 | -84.2894 | 95.7106 | 0.086459 | 0.075869 | -11.3174 | -7.6398

## LLL_max_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.34641 | 0.34641 | 0 | 0 | 12 | 12 | -2.5857 | 2.7729 | -4.8404 | 5.0528 | 95.7106 | -84.2894 | 0.45731 | 0.4803 | -22.4001 | -23.0467
Line_1 | 0.1732 | 0.1732 | 0 | 0 | 6 | 6 | 1.4332 | -1.3864 | 2.5795 | -2.5264 | -84.2894 | 95.7106 | 0.49182 | 0.4803 | -23.3473 | -23.0467
Line_2 | 0.1732 | 0.1732 | 0 | 0 | 6 | 6 | 1.4332 | -1.3864 | 2.5795 | -2.5264 | -84.2894 | 95.7106 | 0.49182 | 0.4803 | -23.3473 | -23.0467

## LLL_max_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.34641 | 0.34641 | 0 | 0 | 12 | 12 | -2.5857 | 2.7729 | -4.8404 | 5.0528 | 95.7106 | -84.2894 | 0.45731 | 0.4803 | -22.4001 | -23.0467
Line_1 | 0.1732 | 0.1732 | 0 | 0 | 6 | 6 | 1.4332 | -1.3864 | 2.5795 | -2.5264 | -84.2894 | 95.7106 | 0.49182 | 0.4803 | -23.3473 | -23.0467
Line_2 | 0.1732 | 0.1732 | 0 | 0 | 6 | 6 | 1.4332 | -1.3864 | 2.5795 | -2.5264 | -84.2894 | 95.7106 | 0.49182 | 0.4803 | -23.3473 | -23.0467

## LLL_min_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Line_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## LLL_min_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Line_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## LLL_min_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33546 | 0.33546 | -27.0249 | -27.0249
Line_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33546 | 0.33546 | -27.0249 | -27.0249
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33546 | 0.33546 | -27.0249 | -27.0249

## LLL_min_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33546 | 0.33546 | -27.0249 | -27.0249
Line_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33546 | 0.33546 | -27.0249 | -27.0249
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33546 | 0.33546 | -27.0249 | -27.0249

## LL_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.34641 | 0.34641 | 0.34641 | 0.34641 | 0.34641 | 0.34641 | 4 | 4 | 4 | 4 | 4 | 4 | -0.45073 | -2.037 | 1.8001 | 0.51313 | 2.0994 | -1.7377 | -4.6552 | -1.1403 | -1.524 | 4.726 | 1.2111 | 1.5948 | 95.7105 | -24.2892 | -144.2895 | -84.2895 | 155.7108 | 35.7105 | 1.1692 | 0.58361 | 0.58965 | 1.1884 | 0.60592 | 0.58965 | 0.18008 | -175.0496 | 175.4587 | -0.48629 | -174.3097 | 173.166
Line_1 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 2 | 2 | 2 | 2 | 2 | 2 | 0.27217 | 1.0653 | -0.85326 | -0.25657 | -1.0497 | 0.86886 | 2.3807 | 0.62324 | 0.8151 | -2.363 | -0.60554 | -0.7974 | -84.2895 | 155.7108 | 35.7105 | 95.7105 | -24.2892 | -144.2895 | 1.1981 | 0.61711 | 0.59001 | 1.1884 | 0.60592 | 0.58965 | -0.81144 | -173.9598 | 172.0206 | -0.48629 | -174.3097 | 173.166
Line_2 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 2 | 2 | 2 | 2 | 2 | 2 | 0.27217 | 1.0653 | -0.85326 | -0.25657 | -1.0497 | 0.86886 | 2.3807 | 0.62324 | 0.8151 | -2.363 | -0.60554 | -0.7974 | -84.2895 | 155.7108 | 35.7105 | 95.7105 | -24.2892 | -144.2895 | 1.1981 | 0.61711 | 0.59001 | 1.1884 | 0.60592 | 0.58965 | -0.81144 | -173.9598 | 172.0206 | -0.48629 | -174.3097 | 173.166

## LL_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.34641 | 0.34641 | 0.34641 | 0.34641 | 0.34641 | 0.34641 | 4 | 4 | 4 | 4 | 4 | 4 | -0.45073 | -2.037 | 1.8001 | 0.51313 | 2.0994 | -1.7377 | -4.6552 | -1.1403 | -1.524 | 4.726 | 1.2111 | 1.5948 | 95.7105 | -24.2892 | -144.2895 | -84.2895 | 155.7108 | 35.7105 | 1.1692 | 0.58361 | 0.58965 | 1.1884 | 0.60592 | 0.58965 | 0.18008 | -175.0496 | 175.4587 | -0.48629 | -174.3097 | 173.166
Line_1 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 2 | 2 | 2 | 2 | 2 | 2 | 0.27217 | 1.0653 | -0.85326 | -0.25657 | -1.0497 | 0.86886 | 2.3807 | 0.62324 | 0.8151 | -2.363 | -0.60554 | -0.7974 | -84.2895 | 155.7108 | 35.7105 | 95.7105 | -24.2892 | -144.2895 | 1.1981 | 0.61711 | 0.59001 | 1.1884 | 0.60592 | 0.58965 | -0.81144 | -173.9598 | 172.0206 | -0.48629 | -174.3097 | 173.166
Line_2 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 2 | 2 | 2 | 2 | 2 | 2 | 0.27217 | 1.0653 | -0.85326 | -0.25657 | -1.0497 | 0.86886 | 2.3807 | 0.62324 | 0.8151 | -2.363 | -0.60554 | -0.7974 | -84.2895 | 155.7108 | 35.7105 | 95.7105 | -24.2892 | -144.2895 | 1.1981 | 0.61711 | 0.59001 | 1.1884 | 0.60592 | 0.58965 | -0.81144 | -173.9598 | 172.0206 | -0.48629 | -174.3097 | 173.166

## LL_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.34641 | 0.34641 | 0.34641 | 0.34641 | 0.34641 | 0.34641 | 4 | 4 | 4 | 4 | 4 | 4 | -0.45073 | -2.1404 | 1.0252 | 0.51313 | 2.2028 | -0.96278 | -4.6552 | -1.9754 | -1.852 | 4.726 | 2.0462 | 1.9228 | 95.7105 | -24.2893 | -144.2894 | -84.2895 | 155.7107 | 35.7106 | 1.1692 | 0.72816 | 0.52921 | 1.1884 | 0.75163 | 0.5376 | 0.18008 | -161.5845 | 154.6768 | -0.48629 | -161.3995 | 152.3079
Line_1 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 2 | 2 | 2 | 2 | 2 | 2 | 0.27217 | 1.117 | -0.46579 | -0.25657 | -1.1014 | 0.48139 | 2.3807 | 1.0408 | 0.97912 | -2.363 | -1.0231 | -0.96142 | -84.2895 | 155.7107 | 35.7106 | 95.7105 | -24.2893 | -144.2894 | 1.1981 | 0.76337 | 0.54213 | 1.1884 | 0.75163 | 0.5376 | -0.81144 | -161.3113 | 151.152 | -0.48629 | -161.3995 | 152.3079
Line_2 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 2 | 2 | 2 | 2 | 2 | 2 | 0.27217 | 1.117 | -0.46579 | -0.25657 | -1.1014 | 0.48139 | 2.3807 | 1.0408 | 0.97912 | -2.363 | -1.0231 | -0.96142 | -84.2895 | 155.7107 | 35.7106 | 95.7105 | -24.2893 | -144.2894 | 1.1981 | 0.76337 | 0.54213 | 1.1884 | 0.75163 | 0.5376 | -0.81144 | -161.3113 | 151.152 | -0.48629 | -161.3995 | 152.3079

## LL_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.34641 | 0.34641 | 0.34641 | 0.34641 | 0.34641 | 0.34641 | 4 | 4 | 4 | 4 | 4 | 4 | -0.45073 | -2.1404 | 1.0252 | 0.51313 | 2.2028 | -0.96278 | -4.6552 | -1.9754 | -1.852 | 4.726 | 2.0462 | 1.9228 | 95.7105 | -24.2893 | -144.2894 | -84.2895 | 155.7107 | 35.7106 | 1.1692 | 0.72816 | 0.52921 | 1.1884 | 0.75163 | 0.5376 | 0.18008 | -161.5845 | 154.6768 | -0.48629 | -161.3995 | 152.3079
Line_1 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 2 | 2 | 2 | 2 | 2 | 2 | 0.27217 | 1.117 | -0.46579 | -0.25657 | -1.1014 | 0.48139 | 2.3807 | 1.0408 | 0.97912 | -2.363 | -1.0231 | -0.96142 | -84.2895 | 155.7107 | 35.7106 | 95.7105 | -24.2893 | -144.2894 | 1.1981 | 0.76337 | 0.54213 | 1.1884 | 0.75163 | 0.5376 | -0.81144 | -161.3113 | 151.152 | -0.48629 | -161.3995 | 152.3079
Line_2 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 2 | 2 | 2 | 2 | 2 | 2 | 0.27217 | 1.117 | -0.46579 | -0.25657 | -1.1014 | 0.48139 | 2.3807 | 1.0408 | 0.97912 | -2.363 | -1.0231 | -0.96142 | -84.2895 | 155.7107 | 35.7106 | 95.7105 | -24.2893 | -144.2894 | 1.1981 | 0.76337 | 0.54213 | 1.1884 | 0.75163 | 0.5376 | -0.81144 | -161.3113 | 151.152 | -0.48629 | -161.3995 | 152.3079

## LL_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.3685e-14 | -4.7371e-15 | 9.4738e-15 | 2.1316e-14 | 8.2904e-15 | -7.1046e-15 | -4.737e-15 | 4.7631e-09 | -4.7631e-09 | 9.4739e-15 | -4.7631e-09 | 4.7631e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 1.0553e-12 | -180 | 180 | 1.083e-12 | -180 | 180
Line_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.3685e-15 | 3.361e-19 | -4.7366e-15 | 2.6862e-28 | 8.2894e-15 | 7.1052e-15 | 1.8948e-14 | -1.5877e-09 | 1.5877e-09 | -1.4211e-14 | 1.5877e-09 | -1.5877e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 1.0755e-12 | -180 | 180 | 1.083e-12 | -180 | 180
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.6387e-28 | 3.361e-19 | 4.7373e-15 | -2.3685e-15 | 8.2894e-15 | 2.3682e-15 | 1.4211e-14 | -1.5877e-09 | 1.5877e-09 | -9.4739e-15 | 1.5877e-09 | -1.5877e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 1.0639e-12 | -180 | 180 | 1.083e-12 | -180 | 180

## LL_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.3685e-14 | -4.7371e-15 | 9.4738e-15 | 2.1316e-14 | 8.2904e-15 | -7.1046e-15 | -4.737e-15 | 4.7631e-09 | -4.7631e-09 | 9.4739e-15 | -4.7631e-09 | 4.7631e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 1.0553e-12 | -180 | 180 | 1.083e-12 | -180 | 180
Line_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.3685e-15 | 3.361e-19 | -4.7366e-15 | 2.6862e-28 | 8.2894e-15 | 7.1052e-15 | 1.8948e-14 | -1.5877e-09 | 1.5877e-09 | -1.4211e-14 | 1.5877e-09 | -1.5877e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 1.0755e-12 | -180 | 180 | 1.083e-12 | -180 | 180
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.6387e-28 | 3.361e-19 | 4.7373e-15 | -2.3685e-15 | 8.2894e-15 | 2.3682e-15 | 1.4211e-14 | -1.5877e-09 | 1.5877e-09 | -9.4739e-15 | 1.5877e-09 | -1.5877e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 1.0639e-12 | -180 | 180 | 1.083e-12 | -180 | 180

## LL_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.8948e-14 | -5.5595e-10 | -1.5515e-09 | 2.1316e-14 | 5.5595e-10 | 1.5515e-09 | -9.4739e-15 | 4.8331e-09 | -3.1089e-09 | 9.4739e-15 | -4.8331e-09 | 3.1089e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.60781 | 0.43409 | 1 | 0.60781 | 0.43409 | 8.7662e-13 | -166.2936 | 160.6236 | 9.0428e-13 | -166.2936 | 160.6236
Line_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.737e-15 | 1.8531e-10 | 5.1715e-10 | -4.737e-15 | -1.8531e-10 | -5.1715e-10 | 4.737e-15 | -1.6111e-09 | 1.0363e-09 | -4.737e-15 | 1.6111e-09 | -1.0363e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.60781 | 0.43409 | 1 | 0.60781 | 0.43409 | 8.9856e-13 | -166.2936 | 160.6236 | 9.0428e-13 | -166.2936 | 160.6236
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.3685e-15 | 1.8532e-10 | 5.1715e-10 | 2.3685e-15 | -1.8532e-10 | -5.1715e-10 | 2.3685e-15 | -1.6111e-09 | 1.0363e-09 | -2.3685e-15 | 1.6111e-09 | -1.0363e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.60781 | 0.43409 | 1 | 0.60781 | 0.43409 | 8.8808e-13 | -166.2936 | 160.6236 | 9.0428e-13 | -166.2936 | 160.6236

## LL_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.8948e-14 | -5.5595e-10 | -1.5515e-09 | 2.1316e-14 | 5.5595e-10 | 1.5515e-09 | -9.4739e-15 | 4.8331e-09 | -3.1089e-09 | 9.4739e-15 | -4.8331e-09 | 3.1089e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.60781 | 0.43409 | 1 | 0.60781 | 0.43409 | 8.7662e-13 | -166.2936 | 160.6236 | 9.0428e-13 | -166.2936 | 160.6236
Line_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.737e-15 | 1.8531e-10 | 5.1715e-10 | -4.737e-15 | -1.8531e-10 | -5.1715e-10 | 4.737e-15 | -1.6111e-09 | 1.0363e-09 | -4.737e-15 | 1.6111e-09 | -1.0363e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.60781 | 0.43409 | 1 | 0.60781 | 0.43409 | 8.9856e-13 | -166.2936 | 160.6236 | 9.0428e-13 | -166.2936 | 160.6236
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.3685e-15 | 1.8532e-10 | 5.1715e-10 | 2.3685e-15 | -1.8532e-10 | -5.1715e-10 | 2.3685e-15 | -1.6111e-09 | 1.0363e-09 | -2.3685e-15 | 1.6111e-09 | -1.0363e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.60781 | 0.43409 | 1 | 0.60781 | 0.43409 | 8.8808e-13 | -166.2936 | 160.6236 | 9.0428e-13 | -166.2936 | 160.6236

## LG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.34641 | 0.34641 | 0.34641 | 0.34641 | 0.34641 | 0.34641 | 4 | 4 | 4 | 4 | 4 | 4 | -0.15537 | 0.90214 | -1.6559 | 0.21777 | -0.83974 | 1.7183 | -1.7014 | -4.0446 | -3.7888 | 1.7722 | 4.1154 | 3.8596 | 95.7107 | -24.2895 | -144.2894 | -84.2893 | 155.7105 | 35.7106 | 0.42711 | 1.036 | 1.0337 | 0.44638 | 1.0501 | 1.0562 | 0.49301 | -101.7157 | 102.1025 | -1.2948 | -102.7568 | 101.7116
Line_1 | 0.17321 | 0.17321 | 0.1732 | 0.17321 | 0.17321 | 0.1732 | 2 | 2 | 2 | 2 | 2 | 2 | 0.12448 | -0.40427 | 0.87477 | -0.10888 | 0.41987 | -0.85917 | 0.90379 | 2.0754 | 1.9475 | -0.88609 | -2.0577 | -1.9298 | -84.2893 | 155.7105 | 35.7106 | 95.7107 | -24.2895 | -144.2894 | 0.45616 | 1.0572 | 1.0675 | 0.44638 | 1.0501 | 1.0562 | -2.1316 | -103.2669 | 101.5223 | -1.2948 | -102.7568 | 101.7116
Line_2 | 0.17321 | 0.17321 | 0.1732 | 0.17321 | 0.17321 | 0.1732 | 2 | 2 | 2 | 2 | 2 | 2 | 0.12448 | -0.40427 | 0.87477 | -0.10888 | 0.41987 | -0.85917 | 0.90379 | 2.0754 | 1.9475 | -0.88609 | -2.0577 | -1.9298 | -84.2893 | 155.7105 | 35.7106 | 95.7107 | -24.2895 | -144.2894 | 0.45616 | 1.0572 | 1.0675 | 0.44638 | 1.0501 | 1.0562 | -2.1316 | -103.2669 | 101.5223 | -1.2948 | -102.7568 | 101.7116

## LG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.34641 | 0.34641 | 0.34641 | 0.34641 | 0.34641 | 0.34641 | 4 | 4 | 4 | 4 | 4 | 4 | -0.15537 | 0.90214 | -1.6559 | 0.21777 | -0.83974 | 1.7183 | -1.7014 | -4.0446 | -3.7888 | 1.7722 | 4.1154 | 3.8596 | 95.7107 | -24.2895 | -144.2894 | -84.2893 | 155.7105 | 35.7106 | 0.42711 | 1.036 | 1.0337 | 0.44638 | 1.0501 | 1.0562 | 0.49301 | -101.7157 | 102.1025 | -1.2948 | -102.7568 | 101.7116
Line_1 | 0.17321 | 0.17321 | 0.1732 | 0.17321 | 0.17321 | 0.1732 | 2 | 2 | 2 | 2 | 2 | 2 | 0.12448 | -0.40427 | 0.87477 | -0.10888 | 0.41987 | -0.85917 | 0.90379 | 2.0754 | 1.9475 | -0.88609 | -2.0577 | -1.9298 | -84.2893 | 155.7105 | 35.7106 | 95.7107 | -24.2895 | -144.2894 | 0.45616 | 1.0572 | 1.0675 | 0.44638 | 1.0501 | 1.0562 | -2.1316 | -103.2669 | 101.5223 | -1.2948 | -102.7568 | 101.7116
Line_2 | 0.17321 | 0.17321 | 0.1732 | 0.17321 | 0.17321 | 0.1732 | 2 | 2 | 2 | 2 | 2 | 2 | 0.12448 | -0.40427 | 0.87477 | -0.10888 | 0.41987 | -0.85917 | 0.90379 | 2.0754 | 1.9475 | -0.88609 | -2.0577 | -1.9298 | -84.2893 | 155.7105 | 35.7106 | 95.7107 | -24.2895 | -144.2894 | 0.45616 | 1.0572 | 1.0675 | 0.44638 | 1.0501 | 1.0562 | -2.1316 | -103.2669 | 101.5223 | -1.2948 | -102.7568 | 101.7116

## LG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.34641 | 0.34641 | 0.34641 | 0.34641 | 0.34641 | 0.34641 | 4 | 4 | 4 | 4 | 4 | 4 | -0.72485 | 0.3588 | -1.3973 | 0.78725 | -0.2964 | 1.4597 | -2.6274 | -4.0295 | -4.2669 | 2.6982 | 4.1003 | 4.3377 | 95.7107 | -24.2895 | -144.2894 | -84.2893 | 155.7105 | 35.7106 | 0.68138 | 1.0114 | 1.1225 | 0.70267 | 1.0278 | 1.1442 | -9.7127 | -109.2011 | 107.5779 | -10.5551 | -110.1549 | 107.1114
Line_1 | 0.17321 | 0.17321 | 0.1732 | 0.17321 | 0.17321 | 0.1732 | 2 | 2 | 2 | 2 | 2 | 2 | 0.40922 | -0.1326 | 0.74547 | -0.39362 | 0.1482 | -0.72987 | 1.3668 | 2.0679 | 2.1866 | -1.3491 | -2.0502 | -2.1689 | -84.2893 | 155.7105 | 35.7106 | 95.7107 | -24.2895 | -144.2894 | 0.71337 | 1.0361 | 1.1551 | 0.70267 | 1.0278 | 1.1442 | -10.9574 | -110.6204 | 106.8847 | -10.5551 | -110.1549 | 107.1114
Line_2 | 0.17321 | 0.17321 | 0.1732 | 0.17321 | 0.17321 | 0.1732 | 2 | 2 | 2 | 2 | 2 | 2 | 0.40922 | -0.1326 | 0.74547 | -0.39362 | 0.1482 | -0.72987 | 1.3668 | 2.0679 | 2.1866 | -1.3491 | -2.0502 | -2.1689 | -84.2893 | 155.7105 | 35.7106 | 95.7107 | -24.2895 | -144.2894 | 0.71337 | 1.0361 | 1.1551 | 0.70267 | 1.0278 | 1.1442 | -10.9574 | -110.6204 | 106.8847 | -10.5551 | -110.1549 | 107.1114

## LG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.34641 | 0.34641 | 0.34641 | 0.34641 | 0.34641 | 0.34641 | 4 | 4 | 4 | 4 | 4 | 4 | -0.72485 | 0.3588 | -1.3973 | 0.78725 | -0.2964 | 1.4597 | -2.6274 | -4.0295 | -4.2669 | 2.6982 | 4.1003 | 4.3377 | 95.7107 | -24.2895 | -144.2894 | -84.2893 | 155.7105 | 35.7106 | 0.68138 | 1.0114 | 1.1225 | 0.70267 | 1.0278 | 1.1442 | -9.7127 | -109.2011 | 107.5779 | -10.5551 | -110.1549 | 107.1114
Line_1 | 0.17321 | 0.17321 | 0.1732 | 0.17321 | 0.17321 | 0.1732 | 2 | 2 | 2 | 2 | 2 | 2 | 0.40922 | -0.1326 | 0.74547 | -0.39362 | 0.1482 | -0.72987 | 1.3668 | 2.0679 | 2.1866 | -1.3491 | -2.0502 | -2.1689 | -84.2893 | 155.7105 | 35.7106 | 95.7107 | -24.2895 | -144.2894 | 0.71337 | 1.0361 | 1.1551 | 0.70267 | 1.0278 | 1.1442 | -10.9574 | -110.6204 | 106.8847 | -10.5551 | -110.1549 | 107.1114
Line_2 | 0.17321 | 0.17321 | 0.1732 | 0.17321 | 0.17321 | 0.1732 | 2 | 2 | 2 | 2 | 2 | 2 | 0.40922 | -0.1326 | 0.74547 | -0.39362 | 0.1482 | -0.72987 | 1.3668 | 2.0679 | 2.1866 | -1.3491 | -2.0502 | -2.1689 | -84.2893 | 155.7105 | 35.7106 | 95.7107 | -24.2895 | -144.2894 | 0.71337 | 1.0361 | 1.1551 | 0.70267 | 1.0278 | 1.1442 | -10.9574 | -110.6204 | 106.8847 | -10.5551 | -110.1549 | 107.1114

## LG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.4444e-09 | -6.111e-10 | -6.1111e-10 | 2.4444e-09 | 6.111e-10 | 6.1111e-10 | -9.0795e-15 | -3.1754e-09 | 3.1754e-09 | 6.3165e-15 | 3.1755e-09 | -3.1754e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33333 | 0.88192 | 0.88192 | 0.33333 | 0.88192 | 0.88192 | 8.3009e-09 | -100.8934 | 100.8934 | 1.3879e-08 | -100.8934 | 100.8934
Line_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.1481e-10 | 2.0371e-10 | 2.037e-10 | -8.1481e-10 | -2.037e-10 | -2.037e-10 | -1.184e-15 | 1.0585e-09 | -1.0585e-09 | -3.1582e-15 | -1.0585e-09 | 1.0585e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33333 | 0.88192 | 0.88192 | 0.33333 | 0.88192 | 0.88192 | 1.5738e-08 | -100.8934 | 100.8934 | 1.3879e-08 | -100.8934 | 100.8934
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.1481e-10 | 2.0371e-10 | 2.037e-10 | -8.1481e-10 | -2.037e-10 | -2.0371e-10 | -1.184e-15 | 1.0585e-09 | -1.0585e-09 | -3.1582e-15 | -1.0585e-09 | 1.0585e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33333 | 0.88192 | 0.88192 | 0.33333 | 0.88192 | 0.88192 | 1.5738e-08 | -100.8934 | 100.8934 | 1.3879e-08 | -100.8934 | 100.8934

## LG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.4444e-09 | -6.111e-10 | -6.1111e-10 | 2.4444e-09 | 6.111e-10 | 6.1111e-10 | -9.0795e-15 | -3.1754e-09 | 3.1754e-09 | 6.3165e-15 | 3.1755e-09 | -3.1754e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33333 | 0.88192 | 0.88192 | 0.33333 | 0.88192 | 0.88192 | 8.3009e-09 | -100.8934 | 100.8934 | 1.3879e-08 | -100.8934 | 100.8934
Line_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.1481e-10 | 2.0371e-10 | 2.037e-10 | -8.1481e-10 | -2.037e-10 | -2.037e-10 | -1.184e-15 | 1.0585e-09 | -1.0585e-09 | -3.1582e-15 | -1.0585e-09 | 1.0585e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33333 | 0.88192 | 0.88192 | 0.33333 | 0.88192 | 0.88192 | 1.5738e-08 | -100.8934 | 100.8934 | 1.3879e-08 | -100.8934 | 100.8934
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.1481e-10 | 2.0371e-10 | 2.037e-10 | -8.1481e-10 | -2.037e-10 | -2.0371e-10 | -1.184e-15 | 1.0585e-09 | -1.0585e-09 | -3.1582e-15 | -1.0585e-09 | 1.0585e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33333 | 0.88192 | 0.88192 | 0.33333 | 0.88192 | 0.88192 | 1.5738e-08 | -100.8934 | 100.8934 | 1.3879e-08 | -100.8934 | 100.8934

## LG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.6247e-09 | -1.1402e-09 | -1.7218e-10 | 2.6247e-09 | 1.1402e-09 | 1.7218e-10 | 1.1178e-09 | -1.9471e-09 | 2.506e-09 | -1.1178e-09 | 1.9471e-09 | -2.506e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.54216 | 0.8576 | 0.95472 | 0.54216 | 0.8576 | 0.95472 | -10.8028 | -108.0887 | 106.1949 | -10.8028 | -108.0887 | 106.1949
Line_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.7491e-10 | 3.8007e-10 | 5.739e-11 | -8.7492e-10 | -3.8007e-10 | -5.7391e-11 | -3.726e-10 | 6.4902e-10 | -8.3531e-10 | 3.7259e-10 | -6.4902e-10 | 8.3531e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.54216 | 0.8576 | 0.95472 | 0.54216 | 0.8576 | 0.95472 | -10.8028 | -108.0887 | 106.1949 | -10.8028 | -108.0887 | 106.1949
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.7491e-10 | 3.8007e-10 | 5.7392e-11 | -8.7492e-10 | -3.8007e-10 | -5.7393e-11 | -3.7259e-10 | 6.4903e-10 | -8.3532e-10 | 3.7259e-10 | -6.4903e-10 | 8.3531e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.54216 | 0.8576 | 0.95472 | 0.54216 | 0.8576 | 0.95472 | -10.8028 | -108.0887 | 106.1949 | -10.8028 | -108.0887 | 106.1949

## LG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.6247e-09 | -1.1402e-09 | -1.7218e-10 | 2.6247e-09 | 1.1402e-09 | 1.7218e-10 | 1.1178e-09 | -1.9471e-09 | 2.506e-09 | -1.1178e-09 | 1.9471e-09 | -2.506e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.54216 | 0.8576 | 0.95472 | 0.54216 | 0.8576 | 0.95472 | -10.8028 | -108.0887 | 106.1949 | -10.8028 | -108.0887 | 106.1949
Line_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.7491e-10 | 3.8007e-10 | 5.739e-11 | -8.7492e-10 | -3.8007e-10 | -5.7391e-11 | -3.726e-10 | 6.4902e-10 | -8.3531e-10 | 3.7259e-10 | -6.4902e-10 | 8.3531e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.54216 | 0.8576 | 0.95472 | 0.54216 | 0.8576 | 0.95472 | -10.8028 | -108.0887 | 106.1949 | -10.8028 | -108.0887 | 106.1949
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.7491e-10 | 3.8007e-10 | 5.7392e-11 | -8.7492e-10 | -3.8007e-10 | -5.7393e-11 | -3.7259e-10 | 6.4903e-10 | -8.3532e-10 | 3.7259e-10 | -6.4903e-10 | 8.3531e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.54216 | 0.8576 | 0.95472 | 0.54216 | 0.8576 | 0.95472 | -10.8028 | -108.0887 | 106.1949 | -10.8028 | -108.0887 | 106.1949

## LLG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.34641 | 0.34641 | 0.34641 | 0.34641 | 0.34641 | 0.34641 | 4 | 4 | 4 | 4 | 4 | 4 | -0.30305 | -1.3606 | 1.1975 | 0.36545 | 1.423 | -1.1351 | -3.1783 | -0.83502 | -1.0908 | 3.2491 | 0.90582 | 1.1616 | 95.7105 | -24.2893 | -144.2895 | -84.2895 | 155.7107 | 35.7105 | 0.79817 | 0.39909 | 0.40497 | 0.81739 | 0.4217 | 0.40604 | 0.2638 | -172.7504 | 173.3799 | -0.70704 | -171.8094 | 170.0492
Line_1 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 2 | 2 | 2 | 2 | 2 | 2 | 0.19832 | 0.72708 | -0.55196 | -0.18272 | -0.71148 | 0.56756 | 1.6422 | 0.47061 | 0.59851 | -1.6245 | -0.45291 | -0.58081 | -84.2895 | 155.7107 | 35.7105 | 95.7105 | -24.2893 | -144.2895 | 0.82708 | 0.43305 | 0.40709 | 0.81739 | 0.4217 | 0.40604 | -1.1755 | -171.3758 | 168.3932 | -0.70704 | -171.8094 | 170.0492
Line_2 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 2 | 2 | 2 | 2 | 2 | 2 | 0.19832 | 0.72708 | -0.55196 | -0.18272 | -0.71148 | 0.56756 | 1.6422 | 0.47061 | 0.59851 | -1.6245 | -0.45291 | -0.58081 | -84.2895 | 155.7107 | 35.7105 | 95.7105 | -24.2893 | -144.2895 | 0.82708 | 0.43305 | 0.40709 | 0.81739 | 0.4217 | 0.40604 | -1.1755 | -171.3758 | 168.3932 | -0.70704 | -171.8094 | 170.0492

## LLG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.34641 | 0.34641 | 0.34641 | 0.34641 | 0.34641 | 0.34641 | 4 | 4 | 4 | 4 | 4 | 4 | -0.30305 | -1.3606 | 1.1975 | 0.36545 | 1.423 | -1.1351 | -3.1783 | -0.83502 | -1.0908 | 3.2491 | 0.90582 | 1.1616 | 95.7105 | -24.2893 | -144.2895 | -84.2895 | 155.7107 | 35.7105 | 0.79817 | 0.39909 | 0.40497 | 0.81739 | 0.4217 | 0.40604 | 0.2638 | -172.7504 | 173.3799 | -0.70704 | -171.8094 | 170.0492
Line_1 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 2 | 2 | 2 | 2 | 2 | 2 | 0.19832 | 0.72708 | -0.55196 | -0.18272 | -0.71148 | 0.56756 | 1.6422 | 0.47061 | 0.59851 | -1.6245 | -0.45291 | -0.58081 | -84.2895 | 155.7107 | 35.7105 | 95.7105 | -24.2893 | -144.2895 | 0.82708 | 0.43305 | 0.40709 | 0.81739 | 0.4217 | 0.40604 | -1.1755 | -171.3758 | 168.3932 | -0.70704 | -171.8094 | 170.0492
Line_2 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 2 | 2 | 2 | 2 | 2 | 2 | 0.19832 | 0.72708 | -0.55196 | -0.18272 | -0.71148 | 0.56756 | 1.6422 | 0.47061 | 0.59851 | -1.6245 | -0.45291 | -0.58081 | -84.2895 | 155.7107 | 35.7105 | 95.7105 | -24.2893 | -144.2895 | 0.82708 | 0.43305 | 0.40709 | 0.81739 | 0.4217 | 0.40604 | -1.1755 | -171.3758 | 168.3932 | -0.70704 | -171.8094 | 170.0492

## LLG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.34641 | 0.34641 | 0.34641 | 0.34641 | 0.34641 | 0.34641 | 4 | 4 | 4 | 4 | 4 | 4 | -0.58779 | -1.6714 | 0.084698 | 0.65019 | 1.7338 | -0.022298 | -3.6413 | -2.2391 | -2.0017 | 3.7121 | 2.3099 | 2.0725 | 95.7105 | -24.2893 | -144.2894 | -84.2895 | 155.7107 | 35.7106 | 0.9221 | 0.69854 | 0.50088 | 0.94215 | 0.72206 | 0.51816 | -3.4593 | -151.0299 | 128.1335 | -4.2244 | -151.1817 | 126.327
Line_1 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 2 | 2 | 2 | 2 | 2 | 2 | 0.34069 | 0.88252 | 0.0044511 | -0.32509 | -0.86692 | 0.011149 | 1.8737 | 1.1726 | 1.054 | -1.856 | -1.1549 | -1.0363 | -84.2895 | 155.7107 | 35.7106 | 95.7105 | -24.2893 | -144.2894 | 0.95223 | 0.73382 | 0.52699 | 0.94215 | 0.72206 | 0.51816 | -4.5948 | -151.2539 | 125.4686 | -4.2244 | -151.1817 | 126.327
Line_2 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 2 | 2 | 2 | 2 | 2 | 2 | 0.34069 | 0.88252 | 0.0044511 | -0.32509 | -0.86692 | 0.011149 | 1.8737 | 1.1726 | 1.054 | -1.856 | -1.1549 | -1.0363 | -84.2895 | 155.7107 | 35.7106 | 95.7105 | -24.2893 | -144.2894 | 0.95223 | 0.73382 | 0.52699 | 0.94215 | 0.72206 | 0.51816 | -4.5948 | -151.2539 | 125.4686 | -4.2244 | -151.1817 | 126.327

## LLG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.34641 | 0.34641 | 0.34641 | 0.34641 | 0.34641 | 0.34641 | 4 | 4 | 4 | 4 | 4 | 4 | -0.58779 | -1.6714 | 0.084698 | 0.65019 | 1.7338 | -0.022298 | -3.6413 | -2.2391 | -2.0017 | 3.7121 | 2.3099 | 2.0725 | 95.7105 | -24.2893 | -144.2894 | -84.2895 | 155.7107 | 35.7106 | 0.9221 | 0.69854 | 0.50088 | 0.94215 | 0.72206 | 0.51816 | -3.4593 | -151.0299 | 128.1335 | -4.2244 | -151.1817 | 126.327
Line_1 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 2 | 2 | 2 | 2 | 2 | 2 | 0.34069 | 0.88252 | 0.0044511 | -0.32509 | -0.86692 | 0.011149 | 1.8737 | 1.1726 | 1.054 | -1.856 | -1.1549 | -1.0363 | -84.2895 | 155.7107 | 35.7106 | 95.7105 | -24.2893 | -144.2894 | 0.95223 | 0.73382 | 0.52699 | 0.94215 | 0.72206 | 0.51816 | -4.5948 | -151.2539 | 125.4686 | -4.2244 | -151.1817 | 126.327
Line_2 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 2 | 2 | 2 | 2 | 2 | 2 | 0.34069 | 0.88252 | 0.0044511 | -0.32509 | -0.86692 | 0.011149 | 1.8737 | 1.1726 | 1.054 | -1.856 | -1.1549 | -1.0363 | -84.2895 | 155.7107 | 35.7106 | 95.7105 | -24.2893 | -144.2894 | 0.95223 | 0.73382 | 0.52699 | 0.94215 | 0.72206 | 0.51816 | -4.5948 | -151.2539 | 125.4686 | -4.2244 | -151.1817 | 126.327

## LLG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.4445e-09 | -6.1111e-10 | -6.111e-10 | 2.4444e-09 | 6.1111e-10 | 6.111e-10 | -6.3159e-15 | 3.1754e-09 | -3.1754e-09 | 9.474e-15 | -3.1754e-09 | 3.1754e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.66667 | 0.33333 | 0.33333 | 0.66667 | 0.33333 | 0.33333 | -3.6264e-11 | -180 | 180 | 1.3582e-09 | -180 | 180
Line_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.1481e-10 | 2.037e-10 | 2.037e-10 | -8.1482e-10 | -2.0371e-10 | -2.037e-10 | -3.1579e-15 | -1.0585e-09 | 1.0585e-09 | 6.3159e-15 | 1.0585e-09 | -1.0585e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.66667 | 0.33333 | 0.33333 | 0.66667 | 0.33333 | 0.33333 | 1.823e-09 | -180 | 180 | 1.3582e-09 | -180 | 180
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.1481e-10 | 2.0371e-10 | 2.037e-10 | -8.1482e-10 | -2.0371e-10 | -2.0371e-10 | 2.5925e-20 | -1.0585e-09 | 1.0585e-09 | -1.9315e-20 | 1.0585e-09 | -1.0585e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.66667 | 0.33333 | 0.33333 | 0.66667 | 0.33333 | 0.33333 | 1.823e-09 | -180 | 180 | 1.3582e-09 | -180 | 180

## LLG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.4445e-09 | -6.1111e-10 | -6.111e-10 | 2.4444e-09 | 6.1111e-10 | 6.111e-10 | -6.3159e-15 | 3.1754e-09 | -3.1754e-09 | 9.474e-15 | -3.1754e-09 | 3.1754e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.66667 | 0.33333 | 0.33333 | 0.66667 | 0.33333 | 0.33333 | -3.6264e-11 | -180 | 180 | 1.3582e-09 | -180 | 180
Line_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.1481e-10 | 2.037e-10 | 2.037e-10 | -8.1482e-10 | -2.0371e-10 | -2.037e-10 | -3.1579e-15 | -1.0585e-09 | 1.0585e-09 | 6.3159e-15 | 1.0585e-09 | -1.0585e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.66667 | 0.33333 | 0.33333 | 0.66667 | 0.33333 | 0.33333 | 1.823e-09 | -180 | 180 | 1.3582e-09 | -180 | 180
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.1481e-10 | 2.0371e-10 | 2.037e-10 | -8.1482e-10 | -2.0371e-10 | -2.0371e-10 | 2.5925e-20 | -1.0585e-09 | 1.0585e-09 | -1.9315e-20 | 1.0585e-09 | -1.0585e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.66667 | 0.33333 | 0.33333 | 0.66667 | 0.33333 | 0.33333 | 1.823e-09 | -180 | 180 | 1.3582e-09 | -180 | 180

## LLG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.9417e-09 | -1.5383e-09 | -2.5064e-09 | 1.9417e-09 | 1.5383e-09 | 2.5064e-09 | 5.5888e-10 | 3.6237e-09 | -8.2928e-10 | -5.5888e-10 | -3.6237e-09 | 8.2928e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76796 | 0.56555 | 0.37926 | 0.76796 | 0.56555 | 0.37926 | -3.7935 | -155.6266 | 131.4657 | -3.7935 | -155.6266 | 131.4657
Line_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.4722e-10 | 5.1278e-10 | 8.3546e-10 | -6.4722e-10 | -5.1278e-10 | -8.3546e-10 | -1.8629e-10 | -1.2079e-09 | 2.7643e-10 | 1.8629e-10 | 1.2079e-09 | -2.7643e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76796 | 0.56555 | 0.37926 | 0.76796 | 0.56555 | 0.37926 | -3.7935 | -155.6266 | 131.4657 | -3.7935 | -155.6266 | 131.4657
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.4722e-10 | 5.1278e-10 | 8.3546e-10 | -6.4722e-10 | -5.1278e-10 | -8.3546e-10 | -1.8629e-10 | -1.2079e-09 | 2.7643e-10 | 1.8629e-10 | 1.2079e-09 | -2.7643e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76796 | 0.56555 | 0.37926 | 0.76796 | 0.56555 | 0.37926 | -3.7935 | -155.6266 | 131.4657 | -3.7935 | -155.6266 | 131.4657

## LLG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.9417e-09 | -1.5383e-09 | -2.5064e-09 | 1.9417e-09 | 1.5383e-09 | 2.5064e-09 | 5.5888e-10 | 3.6237e-09 | -8.2928e-10 | -5.5888e-10 | -3.6237e-09 | 8.2928e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76796 | 0.56555 | 0.37926 | 0.76796 | 0.56555 | 0.37926 | -3.7935 | -155.6266 | 131.4657 | -3.7935 | -155.6266 | 131.4657
Line_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.4722e-10 | 5.1278e-10 | 8.3546e-10 | -6.4722e-10 | -5.1278e-10 | -8.3546e-10 | -1.8629e-10 | -1.2079e-09 | 2.7643e-10 | 1.8629e-10 | 1.2079e-09 | -2.7643e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76796 | 0.56555 | 0.37926 | 0.76796 | 0.56555 | 0.37926 | -3.7935 | -155.6266 | 131.4657 | -3.7935 | -155.6266 | 131.4657
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.4722e-10 | 5.1278e-10 | 8.3546e-10 | -6.4722e-10 | -5.1278e-10 | -8.3546e-10 | -1.8629e-10 | -1.2079e-09 | 2.7643e-10 | 1.8629e-10 | 1.2079e-09 | -2.7643e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76796 | 0.56555 | 0.37926 | 0.76796 | 0.56555 | 0.37926 | -3.7935 | -155.6266 | 131.4657 | -3.7935 | -155.6266 | 131.4657