## LLL_max_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.34641 | 0.34641 | 0 | 0 | 12 | 12 | -0.023022 | 0.21022 | -0.67342 | 0.88582 | 95.7106 | -84.2894 | 0.056151 | 0.075869 | 3.7526 | -7.6398
Line_1 | 0.17321 | 0.17321 | 0 | 0 | 6 | 6 | 0.15191 | -0.10511 | 0.49601 | -0.44291 | -84.2894 | 95.7106 | 0.086459 | 0.075869 | -11.3174 | -7.6398
Line_2 | 0.17321 | 0.17321 | 0 | 0 | 6 | 6 | 0.15191 | -0.10511 | 0.49601 | -0.44291 | -84.2894 | 95.7106 | 0.086459 | 0.075869 | -11.3174 | -7.6398
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.086459 | 0.086459 | -11.3174 | -11.3174

## LLL_max_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.34641 | 0.34641 | 0 | 0 | 12 | 12 | -0.023022 | 0.21022 | -0.67342 | 0.88582 | 95.7106 | -84.2894 | 0.056151 | 0.075869 | 3.7526 | -7.6398
Line_1 | 0.17321 | 0.17321 | 0 | 0 | 6 | 6 | 0.15191 | -0.10511 | 0.49601 | -0.44291 | -84.2894 | 95.7106 | 0.086459 | 0.075869 | -11.3174 | -7.6398
Line_2 | 0.17321 | 0.17321 | 0 | 0 | 6 | 6 | 0.15191 | -0.10511 | 0.49601 | -0.44291 | -84.2894 | 95.7106 | 0.086459 | 0.075869 | -11.3174 | -7.6398
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.086459 | 0.086459 | -11.3174 | -11.3174

## LLL_max_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.34641 | 0.34641 | 0 | 0 | 12 | 12 | -2.5857 | 2.7729 | -4.8404 | 5.0528 | 95.7106 | -84.2894 | 0.45731 | 0.4803 | -22.4001 | -23.0467
Line_1 | 0.1732 | 0.1732 | 0 | 0 | 6 | 6 | 1.4332 | -1.3864 | 2.5795 | -2.5264 | -84.2894 | 95.7106 | 0.49182 | 0.4803 | -23.3473 | -23.0467
Line_2 | 0.1732 | 0.1732 | 0 | 0 | 6 | 6 | 1.4332 | -1.3864 | 2.5795 | -2.5264 | -84.2894 | 95.7106 | 0.49182 | 0.4803 | -23.3473 | -23.0467
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.49182 | 0.49182 | -23.3473 | -23.3473

## LLL_max_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.34641 | 0.34641 | 0 | 0 | 12 | 12 | -2.5857 | 2.7729 | -4.8404 | 5.0528 | 95.7106 | -84.2894 | 0.45731 | 0.4803 | -22.4001 | -23.0467
Line_1 | 0.1732 | 0.1732 | 0 | 0 | 6 | 6 | 1.4332 | -1.3864 | 2.5795 | -2.5264 | -84.2894 | 95.7106 | 0.49182 | 0.4803 | -23.3473 | -23.0467
Line_2 | 0.1732 | 0.1732 | 0 | 0 | 6 | 6 | 1.4332 | -1.3864 | 2.5795 | -2.5264 | -84.2894 | 95.7106 | 0.49182 | 0.4803 | -23.3473 | -23.0467
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.49182 | 0.49182 | -23.3473 | -23.3473

## LLL_min_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Line_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## LLL_min_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Line_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## LLL_min_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33546 | 0.33546 | -27.0249 | -27.0249
Line_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33546 | 0.33546 | -27.0249 | -27.0249
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33546 | 0.33546 | -27.0249 | -27.0249
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33546 | 0.33546 | -27.0249 | -27.0249

## LLL_min_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33546 | 0.33546 | -27.0249 | -27.0249
Line_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33546 | 0.33546 | -27.0249 | -27.0249
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33546 | 0.33546 | -27.0249 | -27.0249
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33546 | 0.33546 | -27.0249 | -27.0249

## LL_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.34641 | 0.34641 | 0.34641 | 0.34641 | 0.34641 | 0.34641 | 4 | 4 | 4 | 4 | 4 | 4 | -0.45073 | -2.037 | 1.8001 | 0.51313 | 2.0994 | -1.7377 | -4.6552 | -1.1403 | -1.524 | 4.726 | 1.2111 | 1.5948 | 95.7105 | -24.2892 | -144.2895 | -84.2895 | 155.7108 | 35.7105 | 1.1692 | 0.58361 | 0.58965 | 1.1884 | 0.60592 | 0.58965 | 0.18008 | -175.0496 | 175.4587 | -0.48629 | -174.3097 | 173.166
Line_1 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 2 | 2 | 2 | 2 | 2 | 2 | 0.27217 | 1.0653 | -0.85326 | -0.25657 | -1.0497 | 0.86886 | 2.3807 | 0.62324 | 0.8151 | -2.363 | -0.60554 | -0.7974 | -84.2895 | 155.7108 | 35.7105 | 95.7105 | -24.2892 | -144.2895 | 1.1981 | 0.61711 | 0.59001 | 1.1884 | 0.60592 | 0.58965 | -0.81144 | -173.9598 | 172.0206 | -0.48629 | -174.3097 | 173.166
Line_2 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 2 | 2 | 2 | 2 | 2 | 2 | 0.27217 | 1.0653 | -0.85326 | -0.25657 | -1.0497 | 0.86886 | 2.3807 | 0.62324 | 0.8151 | -2.363 | -0.60554 | -0.7974 | -84.2895 | 155.7108 | 35.7105 | 95.7105 | -24.2892 | -144.2895 | 1.1981 | 0.61711 | 0.59001 | 1.1884 | 0.60592 | 0.58965 | -0.81144 | -173.9598 | 172.0206 | -0.48629 | -174.3097 | 173.166
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5944e-15 | -1.8456e-15 | 1.0295e-14 | -2.2779e-14 | 2.4486e-14 | -3.9837e-15 | -5.7551e-15 | 1.7442e-14 | -7.0874e-15 | -5.3533e-15 | -9.1671e-15 | 1.1847e-14 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1981 | 0.61711 | 0.59001 | 1.1981 | 0.61711 | 0.59001 | -0.81144 | -173.9598 | 172.0206 | -0.81144 | -173.9598 | 172.0206

## LL_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.34641 | 0.34641 | 0.34641 | 0.34641 | 0.34641 | 0.34641 | 4 | 4 | 4 | 4 | 4 | 4 | -0.45073 | -2.037 | 1.8001 | 0.51313 | 2.0994 | -1.7377 | -4.6552 | -1.1403 | -1.524 | 4.726 | 1.2111 | 1.5948 | 95.7105 | -24.2892 | -144.2895 | -84.2895 | 155.7108 | 35.7105 | 1.1692 | 0.58361 | 0.58965 | 1.1884 | 0.60592 | 0.58965 | 0.18008 | -175.0496 | 175.4587 | -0.48629 | -174.3097 | 173.166
Line_1 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 2 | 2 | 2 | 2 | 2 | 2 | 0.27217 | 1.0653 | -0.85326 | -0.25657 | -1.0497 | 0.86886 | 2.3807 | 0.62324 | 0.8151 | -2.363 | -0.60554 | -0.7974 | -84.2895 | 155.7108 | 35.7105 | 95.7105 | -24.2892 | -144.2895 | 1.1981 | 0.61711 | 0.59001 | 1.1884 | 0.60592 | 0.58965 | -0.81144 | -173.9598 | 172.0206 | -0.48629 | -174.3097 | 173.166
Line_2 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 2 | 2 | 2 | 2 | 2 | 2 | 0.27217 | 1.0653 | -0.85326 | -0.25657 | -1.0497 | 0.86886 | 2.3807 | 0.62324 | 0.8151 | -2.363 | -0.60554 | -0.7974 | -84.2895 | 155.7108 | 35.7105 | 95.7105 | -24.2892 | -144.2895 | 1.1981 | 0.61711 | 0.59001 | 1.1884 | 0.60592 | 0.58965 | -0.81144 | -173.9598 | 172.0206 | -0.48629 | -174.3097 | 173.166
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5944e-15 | -1.8456e-15 | 1.0295e-14 | -2.2779e-14 | 2.4486e-14 | -3.9837e-15 | -5.7551e-15 | 1.7442e-14 | -7.0874e-15 | -5.3533e-15 | -9.1671e-15 | 1.1847e-14 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1981 | 0.61711 | 0.59001 | 1.1981 | 0.61711 | 0.59001 | -0.81144 | -173.9598 | 172.0206 | -0.81144 | -173.9598 | 172.0206

## LL_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.34641 | 0.34641 | 0.34641 | 0.34641 | 0.34641 | 0.34641 | 4 | 4 | 4 | 4 | 4 | 4 | -0.45073 | -2.1404 | 1.0252 | 0.51313 | 2.2028 | -0.96278 | -4.6552 | -1.9754 | -1.852 | 4.726 | 2.0462 | 1.9228 | 95.7105 | -24.2893 | -144.2894 | -84.2895 | 155.7107 | 35.7106 | 1.1692 | 0.72816 | 0.52921 | 1.1884 | 0.75163 | 0.5376 | 0.18008 | -161.5845 | 154.6768 | -0.48629 | -161.3995 | 152.3079
Line_1 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 2 | 2 | 2 | 2 | 2 | 2 | 0.27217 | 1.117 | -0.46579 | -0.25657 | -1.1014 | 0.48139 | 2.3807 | 1.0408 | 0.97912 | -2.363 | -1.0231 | -0.96142 | -84.2895 | 155.7107 | 35.7106 | 95.7105 | -24.2893 | -144.2894 | 1.1981 | 0.76337 | 0.54213 | 1.1884 | 0.75163 | 0.5376 | -0.81144 | -161.3113 | 151.152 | -0.48629 | -161.3995 | 152.3079
Line_2 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 2 | 2 | 2 | 2 | 2 | 2 | 0.27217 | 1.117 | -0.46579 | -0.25657 | -1.1014 | 0.48139 | 2.3807 | 1.0408 | 0.97912 | -2.363 | -1.0231 | -0.96142 | -84.2895 | 155.7107 | 35.7106 | 95.7105 | -24.2893 | -144.2894 | 1.1981 | 0.76337 | 0.54213 | 1.1884 | 0.75163 | 0.5376 | -0.81144 | -161.3113 | 151.152 | -0.48629 | -161.3995 | 152.3079
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1189e-14 | -2.3174e-15 | -4.4987e-15 | -1.6944e-14 | 6.8002e-15 | -2.4781e-15 | -1.151e-14 | 6.8508e-15 | 2.4781e-15 | 5.9159e-15 | 1.3752e-14 | -4.4987e-15 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1981 | 0.76337 | 0.54213 | 1.1981 | 0.76337 | 0.54213 | -0.81144 | -161.3113 | 151.152 | -0.81144 | -161.3113 | 151.152

## LL_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.34641 | 0.34641 | 0.34641 | 0.34641 | 0.34641 | 0.34641 | 4 | 4 | 4 | 4 | 4 | 4 | -0.45073 | -2.1404 | 1.0252 | 0.51313 | 2.2028 | -0.96278 | -4.6552 | -1.9754 | -1.852 | 4.726 | 2.0462 | 1.9228 | 95.7105 | -24.2893 | -144.2894 | -84.2895 | 155.7107 | 35.7106 | 1.1692 | 0.72816 | 0.52921 | 1.1884 | 0.75163 | 0.5376 | 0.18008 | -161.5845 | 154.6768 | -0.48629 | -161.3995 | 152.3079
Line_1 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 2 | 2 | 2 | 2 | 2 | 2 | 0.27217 | 1.117 | -0.46579 | -0.25657 | -1.1014 | 0.48139 | 2.3807 | 1.0408 | 0.97912 | -2.363 | -1.0231 | -0.96142 | -84.2895 | 155.7107 | 35.7106 | 95.7105 | -24.2893 | -144.2894 | 1.1981 | 0.76337 | 0.54213 | 1.1884 | 0.75163 | 0.5376 | -0.81144 | -161.3113 | 151.152 | -0.48629 | -161.3995 | 152.3079
Line_2 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 2 | 2 | 2 | 2 | 2 | 2 | 0.27217 | 1.117 | -0.46579 | -0.25657 | -1.1014 | 0.48139 | 2.3807 | 1.0408 | 0.97912 | -2.363 | -1.0231 | -0.96142 | -84.2895 | 155.7107 | 35.7106 | 95.7105 | -24.2893 | -144.2894 | 1.1981 | 0.76337 | 0.54213 | 1.1884 | 0.75163 | 0.5376 | -0.81144 | -161.3113 | 151.152 | -0.48629 | -161.3995 | 152.3079
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1189e-14 | -2.3174e-15 | -4.4987e-15 | -1.6944e-14 | 6.8002e-15 | -2.4781e-15 | -1.151e-14 | 6.8508e-15 | 2.4781e-15 | 5.9159e-15 | 1.3752e-14 | -4.4987e-15 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1981 | 0.76337 | 0.54213 | 1.1981 | 0.76337 | 0.54213 | -0.81144 | -161.3113 | 151.152 | -0.81144 | -161.3113 | 151.152

## LL_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6579e-14 | 1.3027e-14 | 9.4738e-15 | -1.8948e-14 | -1.1842e-14 | -4.7362e-15 | -9.4739e-15 | 4.7631e-09 | -4.7631e-09 | 1.4211e-14 | -4.7631e-09 | 4.7631e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 6.4455e-13 | -180 | 180 | 6.3604e-13 | -180 | 180
Line_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.8948e-14 | -1.0658e-14 | 3.3631e-19 | 1.4211e-14 | 1.1842e-14 | 4.7367e-15 | 4.737e-15 | -1.5877e-09 | 1.5877e-09 | -4.737e-15 | 1.5877e-09 | -1.5877e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 6.0887e-13 | -180 | 180 | 6.3604e-13 | -180 | 180
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.1316e-14 | -5.9209e-15 | -4.7366e-15 | 1.8948e-14 | 7.1052e-15 | 4.7367e-15 | 4.737e-15 | -1.5877e-09 | 1.5877e-09 | -4.737e-15 | 1.5877e-09 | -1.5877e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 6.0674e-13 | -180 | 180 | 6.3604e-13 | -180 | 180
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.1842e-15 | 4.737e-15 | -4.737e-15 | 1.1842e-15 | 2.3685e-15 | 0 | 7.1054e-15 | -1.0034e-24 | -5.0162e-29 | -7.1054e-15 | -5.017e-25 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 6.0887e-13 | -180 | 180 | 6.0674e-13 | -180 | 180

## LL_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6579e-14 | 1.3027e-14 | 9.4738e-15 | -1.8948e-14 | -1.1842e-14 | -4.7362e-15 | -9.4739e-15 | 4.7631e-09 | -4.7631e-09 | 1.4211e-14 | -4.7631e-09 | 4.7631e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 6.4455e-13 | -180 | 180 | 6.3604e-13 | -180 | 180
Line_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.8948e-14 | -1.0658e-14 | 3.3631e-19 | 1.4211e-14 | 1.1842e-14 | 4.7367e-15 | 4.737e-15 | -1.5877e-09 | 1.5877e-09 | -4.737e-15 | 1.5877e-09 | -1.5877e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 6.0887e-13 | -180 | 180 | 6.3604e-13 | -180 | 180
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.1316e-14 | -5.9209e-15 | -4.7366e-15 | 1.8948e-14 | 7.1052e-15 | 4.7367e-15 | 4.737e-15 | -1.5877e-09 | 1.5877e-09 | -4.737e-15 | 1.5877e-09 | -1.5877e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 6.0674e-13 | -180 | 180 | 6.3604e-13 | -180 | 180
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.1842e-15 | 4.737e-15 | -4.737e-15 | 1.1842e-15 | 2.3685e-15 | 0 | 7.1054e-15 | -1.0034e-24 | -5.0162e-29 | -7.1054e-15 | -5.017e-25 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 6.0887e-13 | -180 | 180 | 6.0674e-13 | -180 | 180

## LL_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6579e-14 | -5.5594e-10 | -1.5515e-09 | -1.8948e-14 | 5.5595e-10 | 1.5515e-09 | -1.6579e-14 | 4.8332e-09 | -3.1089e-09 | 1.4211e-14 | -4.8332e-09 | 3.1089e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.60781 | 0.43409 | 1 | 0.60781 | 0.43409 | 5.4641e-13 | -166.2936 | 160.6236 | 5.2204e-13 | -166.2936 | 160.6236
Line_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.1842e-14 | 1.8532e-10 | 5.1716e-10 | 1.1842e-14 | -1.8532e-10 | -5.1716e-10 | 4.737e-15 | -1.6111e-09 | 1.0363e-09 | -9.4739e-15 | 1.6111e-09 | -1.0363e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.60781 | 0.43409 | 1 | 0.60781 | 0.43409 | 4.9636e-13 | -166.2936 | 160.6236 | 5.2204e-13 | -166.2936 | 160.6236
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.6579e-14 | 1.8532e-10 | 5.1716e-10 | 1.6579e-14 | -1.8531e-10 | -5.1716e-10 | 1.1842e-14 | -1.6111e-09 | 1.0363e-09 | -1.4211e-14 | 1.6111e-09 | -1.0363e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.60781 | 0.43409 | 1 | 0.60781 | 0.43409 | 4.938e-13 | -166.2936 | 160.6236 | 5.2204e-13 | -166.2936 | 160.6236
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3685e-15 | 8.6301e-15 | 1.3644e-15 | -4.737e-15 | -3.8205e-15 | -1.3644e-15 | -7.1054e-15 | -1.7158e-14 | 3.8796e-15 | 2.3685e-15 | 3.5135e-15 | -3.8796e-15 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.60781 | 0.43409 | 1 | 0.60781 | 0.43409 | 4.9636e-13 | -166.2936 | 160.6236 | 4.938e-13 | -166.2936 | 160.6236

## LL_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6579e-14 | -5.5594e-10 | -1.5515e-09 | -1.8948e-14 | 5.5595e-10 | 1.5515e-09 | -1.6579e-14 | 4.8332e-09 | -3.1089e-09 | 1.4211e-14 | -4.8332e-09 | 3.1089e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.60781 | 0.43409 | 1 | 0.60781 | 0.43409 | 5.4641e-13 | -166.2936 | 160.6236 | 5.2204e-13 | -166.2936 | 160.6236
Line_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.1842e-14 | 1.8532e-10 | 5.1716e-10 | 1.1842e-14 | -1.8532e-10 | -5.1716e-10 | 4.737e-15 | -1.6111e-09 | 1.0363e-09 | -9.4739e-15 | 1.6111e-09 | -1.0363e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.60781 | 0.43409 | 1 | 0.60781 | 0.43409 | 4.9636e-13 | -166.2936 | 160.6236 | 5.2204e-13 | -166.2936 | 160.6236
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.6579e-14 | 1.8532e-10 | 5.1716e-10 | 1.6579e-14 | -1.8531e-10 | -5.1716e-10 | 1.1842e-14 | -1.6111e-09 | 1.0363e-09 | -1.4211e-14 | 1.6111e-09 | -1.0363e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.60781 | 0.43409 | 1 | 0.60781 | 0.43409 | 4.938e-13 | -166.2936 | 160.6236 | 5.2204e-13 | -166.2936 | 160.6236
Line_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3685e-15 | 8.6301e-15 | 1.3644e-15 | -4.737e-15 | -3.8205e-15 | -1.3644e-15 | -7.1054e-15 | -1.7158e-14 | 3.8796e-15 | 2.3685e-15 | 3.5135e-15 | -3.8796e-15 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.60781 | 0.43409 | 1 | 0.60781 | 0.43409 | 4.9636e-13 | -166.2936 | 160.6236 | 4.938e-13 | -166.2936 | 160.6236

## LG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.33919 | 0.34943 | 0.35073 | 0.34099 | 0.34866 | 0.34965 | 3.9166 | 4.0348 | 4.0499 | 3.9374 | 4.026 | 4.0374 | -0.0091562 | -0.34307 | -0.55399 | 0.062311 | 0.43252 | 0.59902 | -0.23114 | -4.6943 | -4.6895 | 0.29966 | 4.7483 | 4.7564 | 95.839 | -25.3779 | -143.3292 | -84.1927 | 154.8918 | 36.4327 | 0.059063 | 1.1665 | 1.166 | 0.077733 | 1.1843 | 1.1874 | 3.5706 | -119.5577 | 119.9334 | -5.9393 | -120.3129 | 119.2547
Line_1 | 0.1723 | 0.17358 | 0.17374 | 0.1705 | 0.17433 | 0.17482 | 1.9896 | 2.0043 | 2.0062 | 1.9687 | 2.013 | 2.0187 | 0.045644 | 0.25423 | 0.29389 | -0.031155 | -0.21626 | -0.29951 | 0.16872 | 2.3787 | 2.3848 | -0.14983 | -2.3742 | -2.3782 | -84.2573 | 155.4363 | 35.9528 | 95.8073 | -25.1082 | -143.5673 | 0.087849 | 1.1936 | 1.1977 | 0.077733 | 1.1843 | 1.1874 | -9.3954 | -120.6642 | 118.9274 | -5.9393 | -120.3129 | 119.2547
Line_2 | 0.1723 | 0.17358 | 0.17374 | 0.1705 | 0.17433 | 0.17482 | 1.9896 | 2.0043 | 2.0062 | 1.9687 | 2.013 | 2.0187 | 0.045644 | 0.25423 | 0.29389 | -0.031155 | -0.21626 | -0.29951 | 0.16872 | 2.3787 | 2.3848 | -0.14983 | -2.3742 | -2.3782 | -84.2573 | 155.4363 | 35.9528 | 95.8073 | -25.1082 | -143.5673 | 0.087849 | 1.1936 | 1.1977 | 0.077733 | 1.1843 | 1.1874 | -9.3954 | -120.6642 | 118.9274 | -5.9393 | -120.3129 | 119.2547
Line_3 | 0.00090864 | 0.00090864 | 0.00090864 | 0.00090864 | 0.00090864 | 0.00090864 | 0.010492 | 0.010492 | 0.010492 | 0.010492 | 0.010492 | 0.010492 | 0.00014446 | 0.010814 | -0.010958 | 0.00014446 | 0.010814 | -0.010958 | 0.00091033 | -0.0063156 | -0.006151 | 0.00091033 | -0.0063156 | -0.006151 | -90.3783 | -90.3783 | -90.3783 | -90.3783 | -90.3783 | -90.3783 | 0.087849 | 1.1936 | 1.1977 | 0.087849 | 1.1936 | 1.1977 | -9.3954 | -120.6642 | 118.9274 | -9.3954 | -120.6642 | 118.9274

## LG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.33919 | 0.34943 | 0.35073 | 0.34099 | 0.34866 | 0.34965 | 3.9166 | 4.0348 | 4.0499 | 3.9374 | 4.026 | 4.0374 | -0.0091562 | -0.34307 | -0.55399 | 0.062311 | 0.43252 | 0.59902 | -0.23114 | -4.6943 | -4.6895 | 0.29966 | 4.7483 | 4.7564 | 95.839 | -25.3779 | -143.3292 | -84.1927 | 154.8918 | 36.4327 | 0.059063 | 1.1665 | 1.166 | 0.077733 | 1.1843 | 1.1874 | 3.5706 | -119.5577 | 119.9334 | -5.9393 | -120.3129 | 119.2547
Line_1 | 0.1723 | 0.17358 | 0.17374 | 0.1705 | 0.17433 | 0.17482 | 1.9896 | 2.0043 | 2.0062 | 1.9687 | 2.013 | 2.0187 | 0.045644 | 0.25423 | 0.29389 | -0.031155 | -0.21626 | -0.29951 | 0.16872 | 2.3787 | 2.3848 | -0.14983 | -2.3742 | -2.3782 | -84.2573 | 155.4363 | 35.9528 | 95.8073 | -25.1082 | -143.5673 | 0.087849 | 1.1936 | 1.1977 | 0.077733 | 1.1843 | 1.1874 | -9.3954 | -120.6642 | 118.9274 | -5.9393 | -120.3129 | 119.2547
Line_2 | 0.1723 | 0.17358 | 0.17374 | 0.1705 | 0.17433 | 0.17482 | 1.9896 | 2.0043 | 2.0062 | 1.9687 | 2.013 | 2.0187 | 0.045644 | 0.25423 | 0.29389 | -0.031155 | -0.21626 | -0.29951 | 0.16872 | 2.3787 | 2.3848 | -0.14983 | -2.3742 | -2.3782 | -84.2573 | 155.4363 | 35.9528 | 95.8073 | -25.1082 | -143.5673 | 0.087849 | 1.1936 | 1.1977 | 0.077733 | 1.1843 | 1.1874 | -9.3954 | -120.6642 | 118.9274 | -5.9393 | -120.3129 | 119.2547
Line_3 | 0.00090864 | 0.00090864 | 0.00090864 | 0.00090864 | 0.00090864 | 0.00090864 | 0.010492 | 0.010492 | 0.010492 | 0.010492 | 0.010492 | 0.010492 | 0.00014446 | 0.010814 | -0.010958 | 0.00014446 | 0.010814 | -0.010958 | 0.00091033 | -0.0063156 | -0.006151 | 0.00091033 | -0.0063156 | -0.006151 | -90.3783 | -90.3783 | -90.3783 | -90.3783 | -90.3783 | -90.3783 | 0.087849 | 1.1936 | 1.1977 | 0.087849 | 1.1936 | 1.1977 | -9.3954 | -120.6642 | 118.9274 | -9.3954 | -120.6642 | 118.9274

## LG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.34145 | 0.34947 | 0.34836 | 0.34269 | 0.3487 | 0.34787 | 3.9427 | 4.0354 | 4.0225 | 3.957 | 4.0265 | 4.0169 | -0.84668 | -0.38776 | -0.53026 | 0.90695 | 0.46751 | 0.57764 | -1.6026 | -4.6916 | -4.6677 | 1.6752 | 4.7488 | 4.7394 | 95.602 | -24.9409 | -143.5294 | -84.37 | 155.2204 | 36.2814 | 0.45971 | 1.1666 | 1.1679 | 0.48142 | 1.1851 | 1.1886 | -22.246 | -119.6656 | 119.9895 | -22.8007 | -120.4021 | 119.3324
Line_1 | 0.17258 | 0.17359 | 0.17345 | 0.17134 | 0.17435 | 0.17394 | 1.9928 | 2.0044 | 2.0028 | 1.9785 | 2.0132 | 2.0084 | 0.47234 | 0.2625 | 0.28803 | -0.45348 | -0.23375 | -0.28882 | 0.86047 | 2.38 | 2.3834 | -0.83761 | -2.3744 | -2.3697 | -84.3159 | 155.5463 | 35.9014 | 95.63 | -24.7796 | -143.7186 | 0.49256 | 1.1946 | 1.1987 | 0.48142 | 1.1851 | 1.1886 | -23.0797 | -120.7477 | 119.0108 | -22.8007 | -120.4021 | 119.3324
Line_2 | 0.17258 | 0.17359 | 0.17345 | 0.17134 | 0.17435 | 0.17394 | 1.9928 | 2.0044 | 2.0028 | 1.9785 | 2.0132 | 2.0084 | 0.47234 | 0.2625 | 0.28803 | -0.45348 | -0.23375 | -0.28882 | 0.86047 | 2.38 | 2.3834 | -0.83761 | -2.3744 | -2.3697 | -84.3159 | 155.5463 | 35.9014 | 95.63 | -24.7796 | -143.7186 | 0.49256 | 1.1946 | 1.1987 | 0.48142 | 1.1851 | 1.1886 | -23.0797 | -120.7477 | 119.0108 | -22.8007 | -120.4021 | 119.3324
Line_3 | 0.0006258 | 0.0006258 | 0.0006258 | 0.0006258 | 0.0006258 | 0.0006258 | 0.0072261 | 0.0072261 | 0.0072261 | 0.0072261 | 0.0072261 | 0.0072261 | 0.0020992 | 0.0062294 | -0.0083286 | 0.0020992 | 0.0062294 | -0.0083286 | 0.0028744 | -0.0059756 | -0.0023803 | 0.0028744 | -0.0059756 | -0.0023803 | -76.9393 | -76.9393 | -76.9393 | -76.9393 | -76.9393 | -76.9393 | 0.49256 | 1.1946 | 1.1987 | 0.49256 | 1.1946 | 1.1987 | -23.0797 | -120.7477 | 119.0108 | -23.0797 | -120.7477 | 119.0108

## LG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.34145 | 0.34947 | 0.34836 | 0.34269 | 0.3487 | 0.34787 | 3.9427 | 4.0354 | 4.0225 | 3.957 | 4.0265 | 4.0169 | -0.84668 | -0.38776 | -0.53026 | 0.90695 | 0.46751 | 0.57764 | -1.6026 | -4.6916 | -4.6677 | 1.6752 | 4.7488 | 4.7394 | 95.602 | -24.9409 | -143.5294 | -84.37 | 155.2204 | 36.2814 | 0.45971 | 1.1666 | 1.1679 | 0.48142 | 1.1851 | 1.1886 | -22.246 | -119.6656 | 119.9895 | -22.8007 | -120.4021 | 119.3324
Line_1 | 0.17258 | 0.17359 | 0.17345 | 0.17134 | 0.17435 | 0.17394 | 1.9928 | 2.0044 | 2.0028 | 1.9785 | 2.0132 | 2.0084 | 0.47234 | 0.2625 | 0.28803 | -0.45348 | -0.23375 | -0.28882 | 0.86047 | 2.38 | 2.3834 | -0.83761 | -2.3744 | -2.3697 | -84.3159 | 155.5463 | 35.9014 | 95.63 | -24.7796 | -143.7186 | 0.49256 | 1.1946 | 1.1987 | 0.48142 | 1.1851 | 1.1886 | -23.0797 | -120.7477 | 119.0108 | -22.8007 | -120.4021 | 119.3324
Line_2 | 0.17258 | 0.17359 | 0.17345 | 0.17134 | 0.17435 | 0.17394 | 1.9928 | 2.0044 | 2.0028 | 1.9785 | 2.0132 | 2.0084 | 0.47234 | 0.2625 | 0.28803 | -0.45348 | -0.23375 | -0.28882 | 0.86047 | 2.38 | 2.3834 | -0.83761 | -2.3744 | -2.3697 | -84.3159 | 155.5463 | 35.9014 | 95.63 | -24.7796 | -143.7186 | 0.49256 | 1.1946 | 1.1987 | 0.48142 | 1.1851 | 1.1886 | -23.0797 | -120.7477 | 119.0108 | -22.8007 | -120.4021 | 119.3324
Line_3 | 0.0006258 | 0.0006258 | 0.0006258 | 0.0006258 | 0.0006258 | 0.0006258 | 0.0072261 | 0.0072261 | 0.0072261 | 0.0072261 | 0.0072261 | 0.0072261 | 0.0020992 | 0.0062294 | -0.0083286 | 0.0020992 | 0.0062294 | -0.0083286 | 0.0028744 | -0.0059756 | -0.0023803 | 0.0028744 | -0.0059756 | -0.0023803 | -76.9393 | -76.9393 | -76.9393 | -76.9393 | -76.9393 | -76.9393 | 0.49256 | 1.1946 | 1.1987 | 0.49256 | 1.1946 | 1.1987 | -23.0797 | -120.7477 | 119.0108 | -23.0797 | -120.7477 | 119.0108

## LG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.0065195 | 0.0065195 | 0.0065195 | 0.0048915 | 0.0048915 | 0.0048915 | 0.075281 | 0.075281 | 0.075281 | 0.056482 | 0.056482 | 0.056482 | -2.4188e-06 | 0.065596 | -0.064787 | 0.00020011 | -0.049068 | 0.048755 | 0.00020218 | -0.036532 | -0.037869 | -0.0001106 | 0.02736 | 0.028543 | -90.5876 | -90.5876 | -90.5876 | 89.3071 | 89.3071 | 89.3071 | 0.0026858 | 0.99737 | 0.99684 | 0.0040479 | 0.99466 | 1.0002 | 0.097822 | -119.7022 | 119.7195 | 60.3778 | -119.8368 | 119.6537
Line_1 | 0.00081542 | 0.00081542 | 0.00081542 | 0.0024457 | 0.0024457 | 0.0024457 | 0.0094157 | 0.0094157 | 0.0094157 | 0.028241 | 0.028241 | 0.028241 | 4.2811e-05 | -0.0081749 | 0.0081321 | -0.00010005 | 0.024534 | -0.024377 | -1.6448e-05 | 0.0045546 | 0.0047684 | 5.5299e-05 | -0.01368 | -0.014272 | 89.249 | 89.249 | 89.249 | -90.6929 | -90.6929 | -90.6929 | 0.0048708 | 0.99389 | 1.0012 | 0.0040479 | 0.99466 | 1.0002 | 68.2319 | -119.8753 | 119.635 | 60.3778 | -119.8368 | 119.6537
Line_2 | 0.00081542 | 0.00081542 | 0.00081542 | 0.0024457 | 0.0024457 | 0.0024457 | 0.0094157 | 0.0094157 | 0.0094157 | 0.028241 | 0.028241 | 0.028241 | 4.2811e-05 | -0.0081749 | 0.0081321 | -0.00010005 | 0.024534 | -0.024377 | -1.6448e-05 | 0.0045546 | 0.0047684 | 5.5299e-05 | -0.01368 | -0.014272 | 89.249 | 89.249 | 89.249 | -90.6929 | -90.6929 | -90.6929 | 0.0048708 | 0.99389 | 1.0012 | 0.0040479 | 0.99466 | 1.0002 | 68.2319 | -119.8753 | 119.635 | 60.3778 | -119.8368 | 119.6537
Line_3 | 0.00081542 | 0.00081542 | 0.00081542 | 0.00081542 | 0.00081542 | 0.00081542 | 0.0094157 | 0.0094157 | 0.0094157 | 0.0094157 | 0.0094157 | 0.0094157 | -4.2811e-05 | 0.0081749 | -0.0081321 | -4.2811e-05 | 0.0081749 | -0.0081321 | 1.6448e-05 | -0.0045546 | -0.0047684 | 1.6448e-05 | -0.0045546 | -0.0047684 | -90.751 | -90.751 | -90.751 | -90.751 | -90.751 | -90.751 | 0.0048708 | 0.99389 | 1.0012 | 0.0048708 | 0.99389 | 1.0012 | 68.2319 | -119.8753 | 119.635 | 68.2319 | -119.8753 | 119.635

## LG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.0065195 | 0.0065195 | 0.0065195 | 0.0048915 | 0.0048915 | 0.0048915 | 0.075281 | 0.075281 | 0.075281 | 0.056482 | 0.056482 | 0.056482 | -2.4188e-06 | 0.065596 | -0.064787 | 0.00020011 | -0.049068 | 0.048755 | 0.00020218 | -0.036532 | -0.037869 | -0.0001106 | 0.02736 | 0.028543 | -90.5876 | -90.5876 | -90.5876 | 89.3071 | 89.3071 | 89.3071 | 0.0026858 | 0.99737 | 0.99684 | 0.0040479 | 0.99466 | 1.0002 | 0.097822 | -119.7022 | 119.7195 | 60.3778 | -119.8368 | 119.6537
Line_1 | 0.00081542 | 0.00081542 | 0.00081542 | 0.0024457 | 0.0024457 | 0.0024457 | 0.0094157 | 0.0094157 | 0.0094157 | 0.028241 | 0.028241 | 0.028241 | 4.2811e-05 | -0.0081749 | 0.0081321 | -0.00010005 | 0.024534 | -0.024377 | -1.6448e-05 | 0.0045546 | 0.0047684 | 5.5299e-05 | -0.01368 | -0.014272 | 89.249 | 89.249 | 89.249 | -90.6929 | -90.6929 | -90.6929 | 0.0048708 | 0.99389 | 1.0012 | 0.0040479 | 0.99466 | 1.0002 | 68.2319 | -119.8753 | 119.635 | 60.3778 | -119.8368 | 119.6537
Line_2 | 0.00081542 | 0.00081542 | 0.00081542 | 0.0024457 | 0.0024457 | 0.0024457 | 0.0094157 | 0.0094157 | 0.0094157 | 0.028241 | 0.028241 | 0.028241 | 4.2811e-05 | -0.0081749 | 0.0081321 | -0.00010005 | 0.024534 | -0.024377 | -1.6448e-05 | 0.0045546 | 0.0047684 | 5.5299e-05 | -0.01368 | -0.014272 | 89.249 | 89.249 | 89.249 | -90.6929 | -90.6929 | -90.6929 | 0.0048708 | 0.99389 | 1.0012 | 0.0040479 | 0.99466 | 1.0002 | 68.2319 | -119.8753 | 119.635 | 60.3778 | -119.8368 | 119.6537
Line_3 | 0.00081542 | 0.00081542 | 0.00081542 | 0.00081542 | 0.00081542 | 0.00081542 | 0.0094157 | 0.0094157 | 0.0094157 | 0.0094157 | 0.0094157 | 0.0094157 | -4.2811e-05 | 0.0081749 | -0.0081321 | -4.2811e-05 | 0.0081749 | -0.0081321 | 1.6448e-05 | -0.0045546 | -0.0047684 | 1.6448e-05 | -0.0045546 | -0.0047684 | -90.751 | -90.751 | -90.751 | -90.751 | -90.751 | -90.751 | 0.0048708 | 0.99389 | 1.0012 | 0.0048708 | 0.99389 | 1.0012 | 68.2319 | -119.8753 | 119.635 | 68.2319 | -119.8753 | 119.635

## LG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.0046739 | 0.0046739 | 0.0046739 | 0.0035068 | 0.0035068 | 0.0035068 | 0.05397 | 0.05397 | 0.05397 | 0.040493 | 0.040493 | 0.040493 | 0.011349 | 0.040299 | -0.051234 | -0.0083932 | -0.030183 | 0.038518 | 0.014261 | -0.035684 | -0.016713 | -0.010694 | 0.026739 | 0.012631 | -78.2906 | -78.2906 | -78.2906 | 101.6041 | 101.6041 | 101.6041 | 0.3377 | 0.99736 | 0.99853 | 0.33573 | 0.99582 | 1.0011 | -26.8025 | -119.8146 | 119.7761 | -26.5217 | -119.9328 | 119.7596
Line_1 | 0.00058458 | 0.00058458 | 0.00058458 | 0.0017534 | 0.0017534 | 0.0017534 | 0.0067502 | 0.0067502 | 0.0067502 | 0.020246 | 0.020246 | 0.020246 | -0.0013925 | -0.0050313 | 0.0064238 | 0.0041966 | 0.015092 | -0.019259 | -0.0017832 | 0.0044533 | 0.0021131 | 0.0053472 | -0.013369 | -0.0063155 | 101.546 | 101.546 | 101.546 | -78.3959 | -78.3959 | -78.3959 | 0.33517 | 0.99539 | 1.0018 | 0.33573 | 0.99582 | 1.0011 | -26.4407 | -119.9666 | 119.7548 | -26.5217 | -119.9328 | 119.7596
Line_2 | 0.00058458 | 0.00058458 | 0.00058458 | 0.0017534 | 0.0017534 | 0.0017534 | 0.0067502 | 0.0067502 | 0.0067502 | 0.020246 | 0.020246 | 0.020246 | -0.0013925 | -0.0050313 | 0.0064238 | 0.0041966 | 0.015092 | -0.019259 | -0.0017832 | 0.0044533 | 0.0021131 | 0.0053472 | -0.013369 | -0.0063155 | 101.546 | 101.546 | 101.546 | -78.3959 | -78.3959 | -78.3959 | 0.33517 | 0.99539 | 1.0018 | 0.33573 | 0.99582 | 1.0011 | -26.4407 | -119.9666 | 119.7548 | -26.5217 | -119.9328 | 119.7596
Line_3 | 0.00058458 | 0.00058458 | 0.00058458 | 0.00058458 | 0.00058458 | 0.00058458 | 0.0067502 | 0.0067502 | 0.0067502 | 0.0067502 | 0.0067502 | 0.0067502 | 0.0013925 | 0.0050313 | -0.0064238 | 0.0013925 | 0.0050313 | -0.0064238 | 0.0017832 | -0.0044533 | -0.0021131 | 0.0017832 | -0.0044533 | -0.0021131 | -78.454 | -78.454 | -78.454 | -78.454 | -78.454 | -78.454 | 0.33517 | 0.99539 | 1.0018 | 0.33517 | 0.99539 | 1.0018 | -26.4407 | -119.9666 | 119.7548 | -26.4407 | -119.9666 | 119.7548

## LG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.0046739 | 0.0046739 | 0.0046739 | 0.0035068 | 0.0035068 | 0.0035068 | 0.05397 | 0.05397 | 0.05397 | 0.040493 | 0.040493 | 0.040493 | 0.011349 | 0.040299 | -0.051234 | -0.0083932 | -0.030183 | 0.038518 | 0.014261 | -0.035684 | -0.016713 | -0.010694 | 0.026739 | 0.012631 | -78.2906 | -78.2906 | -78.2906 | 101.6041 | 101.6041 | 101.6041 | 0.3377 | 0.99736 | 0.99853 | 0.33573 | 0.99582 | 1.0011 | -26.8025 | -119.8146 | 119.7761 | -26.5217 | -119.9328 | 119.7596
Line_1 | 0.00058458 | 0.00058458 | 0.00058458 | 0.0017534 | 0.0017534 | 0.0017534 | 0.0067502 | 0.0067502 | 0.0067502 | 0.020246 | 0.020246 | 0.020246 | -0.0013925 | -0.0050313 | 0.0064238 | 0.0041966 | 0.015092 | -0.019259 | -0.0017832 | 0.0044533 | 0.0021131 | 0.0053472 | -0.013369 | -0.0063155 | 101.546 | 101.546 | 101.546 | -78.3959 | -78.3959 | -78.3959 | 0.33517 | 0.99539 | 1.0018 | 0.33573 | 0.99582 | 1.0011 | -26.4407 | -119.9666 | 119.7548 | -26.5217 | -119.9328 | 119.7596
Line_2 | 0.00058458 | 0.00058458 | 0.00058458 | 0.0017534 | 0.0017534 | 0.0017534 | 0.0067502 | 0.0067502 | 0.0067502 | 0.020246 | 0.020246 | 0.020246 | -0.0013925 | -0.0050313 | 0.0064238 | 0.0041966 | 0.015092 | -0.019259 | -0.0017832 | 0.0044533 | 0.0021131 | 0.0053472 | -0.013369 | -0.0063155 | 101.546 | 101.546 | 101.546 | -78.3959 | -78.3959 | -78.3959 | 0.33517 | 0.99539 | 1.0018 | 0.33573 | 0.99582 | 1.0011 | -26.4407 | -119.9666 | 119.7548 | -26.5217 | -119.9328 | 119.7596
Line_3 | 0.00058458 | 0.00058458 | 0.00058458 | 0.00058458 | 0.00058458 | 0.00058458 | 0.0067502 | 0.0067502 | 0.0067502 | 0.0067502 | 0.0067502 | 0.0067502 | 0.0013925 | 0.0050313 | -0.0064238 | 0.0013925 | 0.0050313 | -0.0064238 | 0.0017832 | -0.0044533 | -0.0021131 | 0.0017832 | -0.0044533 | -0.0021131 | -78.454 | -78.454 | -78.454 | -78.454 | -78.454 | -78.454 | 0.33517 | 0.99539 | 1.0018 | 0.33517 | 0.99539 | 1.0018 | -26.4407 | -119.9666 | 119.7548 | -26.4407 | -119.9666 | 119.7548

## LLG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.35365 | 0.34351 | 0.34218 | 0.35184 | 0.34423 | 0.34322 | 4.0837 | 3.9666 | 3.9511 | 4.0628 | 3.9748 | 3.9632 | -0.44628 | -0.022585 | 0.005745 | 0.51828 | 0.078397 | 0.0541 | -4.7293 | -0.22698 | -0.22841 | 4.7793 | 0.30321 | 0.29161 | 95.5868 | -23.179 | -145.2761 | -84.3837 | 156.5423 | 34.9731 | 1.1632 | 0.057507 | 0.057826 | 1.1833 | 0.07879 | 0.074834 | 0.1959 | -118.8613 | 126.1647 | -0.57282 | -127.9547 | 114.4628
Line_1 | 0.17411 | 0.17284 | 0.17267 | 0.17592 | 0.17211 | 0.17161 | 2.0105 | 1.9958 | 1.9938 | 2.0314 | 1.9874 | 1.9816 | 0.27593 | 0.052647 | 0.043649 | -0.25914 | -0.039199 | -0.02705 | 2.3829 | 0.17108 | 0.16296 | -2.3896 | -0.1516 | -0.1458 | -84.3214 | 155.9869 | 35.4663 | 95.6163 | -23.4577 | -145.0269 | 1.1932 | 0.08969 | 0.084615 | 1.1833 | 0.07879 | 0.074834 | -0.92658 | -131.1178 | 110.4716 | -0.57282 | -127.9547 | 114.4628
Line_2 | 0.17411 | 0.17284 | 0.17267 | 0.17592 | 0.17211 | 0.17161 | 2.0105 | 1.9958 | 1.9938 | 2.0314 | 1.9874 | 1.9816 | 0.27593 | 0.052647 | 0.043649 | -0.25914 | -0.039199 | -0.02705 | 2.3829 | 0.17108 | 0.16296 | -2.3896 | -0.1516 | -0.1458 | -84.3214 | 155.9869 | 35.4663 | 95.6163 | -23.4577 | -145.0269 | 1.1932 | 0.08969 | 0.084615 | 1.1833 | 0.07879 | 0.074834 | -0.92658 | -131.1178 | 110.4716 | -0.57282 | -127.9547 | 114.4628
Line_3 | 0.00091115 | 0.00091115 | 0.00091115 | 0.00091115 | 0.00091115 | 0.00091115 | 0.010521 | 0.010521 | 0.010521 | 0.010521 | 0.010521 | 0.010521 | -0.00011671 | -0.00071515 | 0.00083185 | -0.00011671 | -0.00071515 | 0.00083185 | -0.012553 | 0.00061564 | 0.00031708 | -0.012553 | 0.00061564 | 0.00031708 | 89.6061 | 89.6061 | 89.6061 | 89.6061 | 89.6061 | 89.6061 | 1.1932 | 0.08969 | 0.084615 | 1.1932 | 0.08969 | 0.084615 | -0.92658 | -131.1178 | 110.4716 | -0.92658 | -131.1178 | 110.4716

## LLG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.35365 | 0.34351 | 0.34218 | 0.35184 | 0.34423 | 0.34322 | 4.0837 | 3.9666 | 3.9511 | 4.0628 | 3.9748 | 3.9632 | -0.44628 | -0.022585 | 0.005745 | 0.51828 | 0.078397 | 0.0541 | -4.7293 | -0.22698 | -0.22841 | 4.7793 | 0.30321 | 0.29161 | 95.5868 | -23.179 | -145.2761 | -84.3837 | 156.5423 | 34.9731 | 1.1632 | 0.057507 | 0.057826 | 1.1833 | 0.07879 | 0.074834 | 0.1959 | -118.8613 | 126.1647 | -0.57282 | -127.9547 | 114.4628
Line_1 | 0.17411 | 0.17284 | 0.17267 | 0.17592 | 0.17211 | 0.17161 | 2.0105 | 1.9958 | 1.9938 | 2.0314 | 1.9874 | 1.9816 | 0.27593 | 0.052647 | 0.043649 | -0.25914 | -0.039199 | -0.02705 | 2.3829 | 0.17108 | 0.16296 | -2.3896 | -0.1516 | -0.1458 | -84.3214 | 155.9869 | 35.4663 | 95.6163 | -23.4577 | -145.0269 | 1.1932 | 0.08969 | 0.084615 | 1.1833 | 0.07879 | 0.074834 | -0.92658 | -131.1178 | 110.4716 | -0.57282 | -127.9547 | 114.4628
Line_2 | 0.17411 | 0.17284 | 0.17267 | 0.17592 | 0.17211 | 0.17161 | 2.0105 | 1.9958 | 1.9938 | 2.0314 | 1.9874 | 1.9816 | 0.27593 | 0.052647 | 0.043649 | -0.25914 | -0.039199 | -0.02705 | 2.3829 | 0.17108 | 0.16296 | -2.3896 | -0.1516 | -0.1458 | -84.3214 | 155.9869 | 35.4663 | 95.6163 | -23.4577 | -145.0269 | 1.1932 | 0.08969 | 0.084615 | 1.1833 | 0.07879 | 0.074834 | -0.92658 | -131.1178 | 110.4716 | -0.57282 | -127.9547 | 114.4628
Line_3 | 0.00091115 | 0.00091115 | 0.00091115 | 0.00091115 | 0.00091115 | 0.00091115 | 0.010521 | 0.010521 | 0.010521 | 0.010521 | 0.010521 | 0.010521 | -0.00011671 | -0.00071515 | 0.00083185 | -0.00011671 | -0.00071515 | 0.00083185 | -0.012553 | 0.00061564 | 0.00031708 | -0.012553 | 0.00061564 | 0.00031708 | 89.6061 | 89.6061 | 89.6061 | 89.6061 | 89.6061 | 89.6061 | 1.1932 | 0.08969 | 0.084615 | 1.1932 | 0.08969 | 0.084615 | -0.92658 | -131.1178 | 110.4716 | -0.92658 | -131.1178 | 110.4716

## LLG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.35138 | 0.34338 | 0.34452 | 0.35014 | 0.34414 | 0.34498 | 4.0574 | 3.9651 | 3.9782 | 4.0431 | 3.9738 | 3.9835 | -0.46733 | -0.88228 | -0.82623 | 0.53201 | 0.93704 | 0.89421 | -4.7044 | -1.5945 | -1.6214 | 4.7625 | 1.6735 | 1.6859 | 95.8165 | -23.6253 | -145.0594 | -84.2103 | 156.2082 | 35.1339 | 1.1652 | 0.45959 | 0.45745 | 1.1853 | 0.48265 | 0.47907 | 0.14339 | -142.5826 | 97.9385 | -0.58426 | -143.0381 | 97.1924
Line_1 | 0.17383 | 0.17283 | 0.17296 | 0.17507 | 0.17207 | 0.17249 | 2.0072 | 1.9956 | 1.9972 | 2.0215 | 1.9869 | 1.9918 | 0.27836 | 0.48058 | 0.46951 | -0.266 | -0.46852 | -0.44711 | 2.3827 | 0.86118 | 0.85911 | -2.3812 | -0.83673 | -0.84296 | -84.263 | 155.8759 | 35.5189 | 95.7897 | -23.7918 | -144.8661 | 1.1952 | 0.49418 | 0.4902 | 1.1853 | 0.48265 | 0.47907 | -0.9263 | -143.2875 | 96.8618 | -0.58426 | -143.0381 | 97.1924
Line_2 | 0.17383 | 0.17283 | 0.17296 | 0.17507 | 0.17207 | 0.17249 | 2.0072 | 1.9956 | 1.9972 | 2.0215 | 1.9869 | 1.9918 | 0.27836 | 0.48058 | 0.46951 | -0.266 | -0.46852 | -0.44711 | 2.3827 | 0.86118 | 0.85911 | -2.3812 | -0.83673 | -0.84296 | -84.263 | 155.8759 | 35.5189 | 95.7897 | -23.7918 | -144.8661 | 1.1952 | 0.49418 | 0.4902 | 1.1853 | 0.48265 | 0.47907 | -0.9263 | -143.2875 | 96.8618 | -0.58426 | -143.0381 | 97.1924
Line_3 | 0.00062698 | 0.00062698 | 0.00062698 | 0.00062698 | 0.00062698 | 0.00062698 | 0.0072398 | 0.0072398 | 0.0072398 | 0.0072398 | 0.0072398 | 0.0072398 | -0.0020936 | -0.0014345 | 0.0035281 | -0.0020936 | -0.0014345 | 0.0035281 | -0.0083958 | 0.0032776 | -0.00038413 | -0.0083958 | 0.0032776 | -0.00038413 | 103.0755 | 103.0755 | 103.0755 | 103.0755 | 103.0755 | 103.0755 | 1.1952 | 0.49418 | 0.4902 | 1.1952 | 0.49418 | 0.4902 | -0.9263 | -143.2875 | 96.8618 | -0.9263 | -143.2875 | 96.8618

## LLG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.35138 | 0.34338 | 0.34452 | 0.35014 | 0.34414 | 0.34498 | 4.0574 | 3.9651 | 3.9782 | 4.0431 | 3.9738 | 3.9835 | -0.46733 | -0.88228 | -0.82623 | 0.53201 | 0.93704 | 0.89421 | -4.7044 | -1.5945 | -1.6214 | 4.7625 | 1.6735 | 1.6859 | 95.8165 | -23.6253 | -145.0594 | -84.2103 | 156.2082 | 35.1339 | 1.1652 | 0.45959 | 0.45745 | 1.1853 | 0.48265 | 0.47907 | 0.14339 | -142.5826 | 97.9385 | -0.58426 | -143.0381 | 97.1924
Line_1 | 0.17383 | 0.17283 | 0.17296 | 0.17507 | 0.17207 | 0.17249 | 2.0072 | 1.9956 | 1.9972 | 2.0215 | 1.9869 | 1.9918 | 0.27836 | 0.48058 | 0.46951 | -0.266 | -0.46852 | -0.44711 | 2.3827 | 0.86118 | 0.85911 | -2.3812 | -0.83673 | -0.84296 | -84.263 | 155.8759 | 35.5189 | 95.7897 | -23.7918 | -144.8661 | 1.1952 | 0.49418 | 0.4902 | 1.1853 | 0.48265 | 0.47907 | -0.9263 | -143.2875 | 96.8618 | -0.58426 | -143.0381 | 97.1924
Line_2 | 0.17383 | 0.17283 | 0.17296 | 0.17507 | 0.17207 | 0.17249 | 2.0072 | 1.9956 | 1.9972 | 2.0215 | 1.9869 | 1.9918 | 0.27836 | 0.48058 | 0.46951 | -0.266 | -0.46852 | -0.44711 | 2.3827 | 0.86118 | 0.85911 | -2.3812 | -0.83673 | -0.84296 | -84.263 | 155.8759 | 35.5189 | 95.7897 | -23.7918 | -144.8661 | 1.1952 | 0.49418 | 0.4902 | 1.1853 | 0.48265 | 0.47907 | -0.9263 | -143.2875 | 96.8618 | -0.58426 | -143.0381 | 97.1924
Line_3 | 0.00062698 | 0.00062698 | 0.00062698 | 0.00062698 | 0.00062698 | 0.00062698 | 0.0072398 | 0.0072398 | 0.0072398 | 0.0072398 | 0.0072398 | 0.0072398 | -0.0020936 | -0.0014345 | 0.0035281 | -0.0020936 | -0.0014345 | 0.0035281 | -0.0083958 | 0.0032776 | -0.00038413 | -0.0083958 | 0.0032776 | -0.00038413 | 103.0755 | 103.0755 | 103.0755 | 103.0755 | 103.0755 | 103.0755 | 1.1952 | 0.49418 | 0.4902 | 1.1952 | 0.49418 | 0.4902 | -0.9263 | -143.2875 | 96.8618 | -0.9263 | -143.2875 | 96.8618

## LLG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.00654 | 0.00654 | 0.00654 | 0.0049068 | 0.0049068 | 0.0049068 | 0.075517 | 0.075517 | 0.075517 | 0.056659 | 0.056659 | 0.056659 | 0.00081619 | -2.434e-06 | -2.434e-06 | -0.00051665 | 0.00020136 | 0.00020136 | -0.075072 | 0.00020345 | 0.00020345 | 0.056366 | -0.00011129 | -0.00011129 | 89.3947 | 89.3947 | 89.3947 | -90.7106 | -90.7106 | -90.7106 | 0.99417 | 0.0026943 | 0.0026943 | 0.99486 | 0.0040606 | 0.0040606 | 0.017615 | -179.9199 | -179.9199 | -0.18544 | -119.6399 | -119.6399
Line_1 | 0.00081798 | 0.00081798 | 0.00081798 | 0.0024534 | 0.0024534 | 0.0024534 | 0.0094452 | 0.0094452 | 0.0094452 | 0.02833 | 0.02833 | 0.02833 | -8.616e-05 | 4.308e-05 | 4.308e-05 | 0.00025832 | -0.00010068 | -0.00010068 | 0.0093981 | -1.6552e-05 | -1.6552e-05 | -0.028183 | 5.5646e-05 | 5.5646e-05 | -90.7687 | -90.7687 | -90.7687 | 89.2894 | 89.2894 | 89.2894 | 0.99506 | 0.0048861 | 0.0048861 | 0.99486 | 0.0040606 | 0.0040606 | -0.24343 | -111.7858 | -111.7858 | -0.18544 | -119.6399 | -119.6399
Line_2 | 0.00081798 | 0.00081798 | 0.00081798 | 0.0024534 | 0.0024534 | 0.0024534 | 0.0094452 | 0.0094452 | 0.0094452 | 0.02833 | 0.02833 | 0.02833 | -8.616e-05 | 4.308e-05 | 4.308e-05 | 0.00025832 | -0.00010068 | -0.00010068 | 0.0093981 | -1.6552e-05 | -1.6552e-05 | -0.028183 | 5.5646e-05 | 5.5646e-05 | -90.7687 | -90.7687 | -90.7687 | 89.2894 | 89.2894 | 89.2894 | 0.99506 | 0.0048861 | 0.0048861 | 0.99486 | 0.0040606 | 0.0040606 | -0.24343 | -111.7858 | -111.7858 | -0.18544 | -119.6399 | -119.6399
Line_3 | 0.00081798 | 0.00081798 | 0.00081798 | 0.00081798 | 0.00081798 | 0.00081798 | 0.0094452 | 0.0094452 | 0.0094452 | 0.0094452 | 0.0094452 | 0.0094452 | 8.616e-05 | -4.308e-05 | -4.308e-05 | 8.616e-05 | -4.308e-05 | -4.308e-05 | -0.0093981 | 1.6552e-05 | 1.6552e-05 | -0.0093981 | 1.6552e-05 | 1.6552e-05 | 89.2313 | 89.2313 | 89.2313 | 89.2313 | 89.2313 | 89.2313 | 0.99506 | 0.0048861 | 0.0048861 | 0.99506 | 0.0048861 | 0.0048861 | -0.24343 | -111.7858 | -111.7858 | -0.24343 | -111.7858 | -111.7858

## LLG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.00654 | 0.00654 | 0.00654 | 0.0049068 | 0.0049068 | 0.0049068 | 0.075517 | 0.075517 | 0.075517 | 0.056659 | 0.056659 | 0.056659 | 0.00081619 | -2.434e-06 | -2.434e-06 | -0.00051665 | 0.00020136 | 0.00020136 | -0.075072 | 0.00020345 | 0.00020345 | 0.056366 | -0.00011129 | -0.00011129 | 89.3947 | 89.3947 | 89.3947 | -90.7106 | -90.7106 | -90.7106 | 0.99417 | 0.0026943 | 0.0026943 | 0.99486 | 0.0040606 | 0.0040606 | 0.017615 | -179.9199 | -179.9199 | -0.18544 | -119.6399 | -119.6399
Line_1 | 0.00081798 | 0.00081798 | 0.00081798 | 0.0024534 | 0.0024534 | 0.0024534 | 0.0094452 | 0.0094452 | 0.0094452 | 0.02833 | 0.02833 | 0.02833 | -8.616e-05 | 4.308e-05 | 4.308e-05 | 0.00025832 | -0.00010068 | -0.00010068 | 0.0093981 | -1.6552e-05 | -1.6552e-05 | -0.028183 | 5.5646e-05 | 5.5646e-05 | -90.7687 | -90.7687 | -90.7687 | 89.2894 | 89.2894 | 89.2894 | 0.99506 | 0.0048861 | 0.0048861 | 0.99486 | 0.0040606 | 0.0040606 | -0.24343 | -111.7858 | -111.7858 | -0.18544 | -119.6399 | -119.6399
Line_2 | 0.00081798 | 0.00081798 | 0.00081798 | 0.0024534 | 0.0024534 | 0.0024534 | 0.0094452 | 0.0094452 | 0.0094452 | 0.02833 | 0.02833 | 0.02833 | -8.616e-05 | 4.308e-05 | 4.308e-05 | 0.00025832 | -0.00010068 | -0.00010068 | 0.0093981 | -1.6552e-05 | -1.6552e-05 | -0.028183 | 5.5646e-05 | 5.5646e-05 | -90.7687 | -90.7687 | -90.7687 | 89.2894 | 89.2894 | 89.2894 | 0.99506 | 0.0048861 | 0.0048861 | 0.99486 | 0.0040606 | 0.0040606 | -0.24343 | -111.7858 | -111.7858 | -0.18544 | -119.6399 | -119.6399
Line_3 | 0.00081798 | 0.00081798 | 0.00081798 | 0.00081798 | 0.00081798 | 0.00081798 | 0.0094452 | 0.0094452 | 0.0094452 | 0.0094452 | 0.0094452 | 0.0094452 | 8.616e-05 | -4.308e-05 | -4.308e-05 | 8.616e-05 | -4.308e-05 | -4.308e-05 | -0.0093981 | 1.6552e-05 | 1.6552e-05 | -0.0093981 | 1.6552e-05 | 1.6552e-05 | 89.2313 | 89.2313 | 89.2313 | 89.2313 | 89.2313 | 89.2313 | 0.99506 | 0.0048861 | 0.0048861 | 0.99506 | 0.0048861 | 0.0048861 | -0.24343 | -111.7858 | -111.7858 | -0.24343 | -111.7858 | -111.7858

## LLG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.0046844 | 0.0046844 | 0.0046844 | 0.0035146 | 0.0035146 | 0.0035146 | 0.054091 | 0.054091 | 0.054091 | 0.040583 | 0.040583 | 0.040583 | -0.010982 | -0.0065562 | 0.017955 | 0.0082691 | 0.0050448 | -0.013372 | -0.052736 | 0.01705 | -0.002621 | 0.039603 | -0.012762 | 0.001963 | 101.7245 | 101.7245 | 101.7245 | -78.3808 | -78.3809 | -78.3809 | 0.99587 | 0.33772 | 0.33545 | 0.9969 | 0.33815 | 0.33303 | -0.038988 | -147.2429 | 93.419 | -0.1747 | -146.8128 | 93.2682
Line_1 | 0.00058589 | 0.00058589 | 0.00058589 | 0.0017573 | 0.0017573 | 0.0017573 | 0.0067653 | 0.0067653 | 0.0067653 | 0.020292 | 0.020292 | 0.020292 | 0.0013767 | 0.000848 | -0.0022247 | -0.0041346 | -0.0025224 | 0.0066862 | 0.0066044 | -0.0021257 | 0.00032598 | -0.019802 | 0.0063812 | -0.00098148 | -78.4389 | -78.4389 | -78.439 | 101.6192 | 101.6192 | 101.6192 | 0.99719 | 0.33828 | 0.33234 | 0.9969 | 0.33815 | 0.33303 | -0.21346 | -146.6902 | 93.2248 | -0.1747 | -146.8128 | 93.2682
Line_2 | 0.00058589 | 0.00058589 | 0.00058589 | 0.0017573 | 0.0017573 | 0.0017573 | 0.0067653 | 0.0067653 | 0.0067653 | 0.020292 | 0.020292 | 0.020292 | 0.0013767 | 0.000848 | -0.0022247 | -0.0041346 | -0.0025224 | 0.0066862 | 0.0066044 | -0.0021257 | 0.00032598 | -0.019802 | 0.0063812 | -0.00098148 | -78.4389 | -78.4389 | -78.439 | 101.6192 | 101.6192 | 101.6192 | 0.99719 | 0.33828 | 0.33234 | 0.9969 | 0.33815 | 0.33303 | -0.21346 | -146.6902 | 93.2248 | -0.1747 | -146.8128 | 93.2682
Line_3 | 0.00058589 | 0.00058589 | 0.00058589 | 0.00058589 | 0.00058589 | 0.00058589 | 0.0067653 | 0.0067653 | 0.0067653 | 0.0067653 | 0.0067653 | 0.0067653 | -0.0013767 | -0.000848 | 0.0022247 | -0.0013767 | -0.000848 | 0.0022247 | -0.0066044 | 0.0021257 | -0.00032598 | -0.0066044 | 0.0021257 | -0.00032598 | 101.5611 | 101.5611 | 101.5611 | 101.5611 | 101.5611 | 101.5611 | 0.99719 | 0.33828 | 0.33234 | 0.99719 | 0.33828 | 0.33234 | -0.21346 | -146.6902 | 93.2248 | -0.21346 | -146.6902 | 93.2248

## LLG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.0046844 | 0.0046844 | 0.0046844 | 0.0035146 | 0.0035146 | 0.0035146 | 0.054091 | 0.054091 | 0.054091 | 0.040583 | 0.040583 | 0.040583 | -0.010982 | -0.0065562 | 0.017955 | 0.0082691 | 0.0050448 | -0.013372 | -0.052736 | 0.01705 | -0.002621 | 0.039603 | -0.012762 | 0.001963 | 101.7245 | 101.7245 | 101.7245 | -78.3808 | -78.3809 | -78.3809 | 0.99587 | 0.33772 | 0.33545 | 0.9969 | 0.33815 | 0.33303 | -0.038988 | -147.2429 | 93.419 | -0.1747 | -146.8128 | 93.2682
Line_1 | 0.00058589 | 0.00058589 | 0.00058589 | 0.0017573 | 0.0017573 | 0.0017573 | 0.0067653 | 0.0067653 | 0.0067653 | 0.020292 | 0.020292 | 0.020292 | 0.0013767 | 0.000848 | -0.0022247 | -0.0041346 | -0.0025224 | 0.0066862 | 0.0066044 | -0.0021257 | 0.00032598 | -0.019802 | 0.0063812 | -0.00098148 | -78.4389 | -78.4389 | -78.439 | 101.6192 | 101.6192 | 101.6192 | 0.99719 | 0.33828 | 0.33234 | 0.9969 | 0.33815 | 0.33303 | -0.21346 | -146.6902 | 93.2248 | -0.1747 | -146.8128 | 93.2682
Line_2 | 0.00058589 | 0.00058589 | 0.00058589 | 0.0017573 | 0.0017573 | 0.0017573 | 0.0067653 | 0.0067653 | 0.0067653 | 0.020292 | 0.020292 | 0.020292 | 0.0013767 | 0.000848 | -0.0022247 | -0.0041346 | -0.0025224 | 0.0066862 | 0.0066044 | -0.0021257 | 0.00032598 | -0.019802 | 0.0063812 | -0.00098148 | -78.4389 | -78.4389 | -78.439 | 101.6192 | 101.6192 | 101.6192 | 0.99719 | 0.33828 | 0.33234 | 0.9969 | 0.33815 | 0.33303 | -0.21346 | -146.6902 | 93.2248 | -0.1747 | -146.8128 | 93.2682
Line_3 | 0.00058589 | 0.00058589 | 0.00058589 | 0.00058589 | 0.00058589 | 0.00058589 | 0.0067653 | 0.0067653 | 0.0067653 | 0.0067653 | 0.0067653 | 0.0067653 | -0.0013767 | -0.000848 | 0.0022247 | -0.0013767 | -0.000848 | 0.0022247 | -0.0066044 | 0.0021257 | -0.00032598 | -0.0066044 | 0.0021257 | -0.00032598 | 101.5611 | 101.5611 | 101.5611 | 101.5611 | 101.5611 | 101.5611 | 0.99719 | 0.33828 | 0.33234 | 0.99719 | 0.33828 | 0.33234 | -0.21346 | -146.6902 | 93.2248 | -0.21346 | -146.6902 | 93.2248