## LLL_max
name | pf_ikss_ka | pf_skss_mw | pf_rk_ohm | pf_xk_ohm | pf_vm_pu | pf_va_degree
Bus_0 | 5.2486 | 1000.0001 | 1.3244 | 13.2439 | 0 | 84.2894
Bus_1 | 5.4963 | 190.3978 | 0.10773 | 2.3084 | 0 | 87.328
Bus_2 | 4.283 | 148.3662 | 0.62773 | 2.8984 | 0 | 77.7798
Bus_3(1) | 3.4587 | 119.8128 | 1.1477 | 3.4884 | 0 | 71.7883
Bus_4 | 3.4587 | 119.8128 | 1.1477 | 3.4884 | 0 | 71.7883

## LLL_max_branch
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_vm_pu
Line_0 | 0 | 4.283 | 0 | 9.2778 | 0 | 148.3662 | 6.297e-19 | -1e-07 | -4.9284e-19 | -1e-07
Line_1 | 3.4587 | 0 | 6.7756 | 0 | 119.8128 | 0 | -1e-07 | 1.6014e-19 | -1e-07 | -1.2512e-19
Line_2 | 3.4587 | 0 | 6.7756 | 0 | 119.8128 | 0 | -1e-07 | 1.6014e-19 | -1e-07 | -1.2512e-19

## LLL_max_fault
name | pf_ikss_ka | pf_skss_mw | pf_rk_ohm | pf_xk_ohm | pf_vm_pu | pf_va_degree
Bus_0 | 3.618 | 689.314 | 1.3244 | 13.2439 | 0.40283 | 45
Bus_1 | 1.4245 | 49.3473 | 0.10773 | 2.3084 | 0.87234 | 45
Bus_2 | 1.3097 | 45.3689 | 0.62773 | 2.8984 | 0.80202 | 45
Bus_3(1) | 1.2119 | 41.9813 | 1.1477 | 3.4884 | 0.74213 | 45
Bus_4 | 1.2119 | 41.9813 | 1.1477 | 3.4884 | 0.74213 | 45

## LLL_max_fault_branch
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_vm_pu
Line_0 | 0 | 1.3097 | 0 | 2.8371 | 0 | 45.3689 | -6.0676e-09 | -25.7292 | 5.5265e-09 | -25.7292
Line_1 | 1.2119 | 0 | 2.3741 | 0 | 41.9813 | 0 | -22.0304 | -2.495e-09 | -22.0304 | 1.6066e-09
Line_2 | 1.2119 | 0 | 2.3741 | 0 | 41.9813 | 0 | -22.0304 | -2.495e-09 | -22.0304 | 1.6066e-09

## LLL_min
name | pf_ikss_ka | pf_skss_mw | pf_rk_ohm | pf_xk_ohm | pf_vm_pu | pf_va_degree
Bus_0 | 4.1989 | 800 | 1.505 | 15.0499 | 0 | 84.2894
Bus_1 | 4.7732 | 165.3474 | 0.11535 | 2.4164 | 0 | 87.2669
Bus_2 | 3.6016 | 124.7634 | 1.1138 | 3.0064 | 0 | 69.6723
Bus_3(1) | 2.7686 | 95.9057 | 2.1122 | 3.5964 | 0 | 59.5744
Bus_4 | 2.7686 | 95.9057 | 2.1122 | 3.5964 | 0 | 59.5744

## LLL_min_branch
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_vm_pu
Line_0 | 0 | 3.6016 | 0 | 6.8381 | 0 | 124.7634 | 7.2789e-20 | -1e-07 | 2.6702e-19 | -1e-07
Line_1 | 2.7686 | 0 | 4.6525 | 0 | 95.9057 | 0 | -1e-07 | 1.7283e-20 | -1e-07 | 6.3218e-20
Line_2 | 2.7686 | 0 | 4.6525 | 0 | 95.9057 | 0 | -1e-07 | 1.7283e-20 | -1e-07 | 6.3218e-20

## LLL_min_fault
name | pf_ikss_ka | pf_skss_mw | pf_rk_ohm | pf_xk_ohm | pf_vm_pu | pf_va_degree
Bus_0 | 3.0129 | 574.037 | 1.505 | 15.0499 | 0.33546 | 45
Bus_1 | 1.2817 | 44.3979 | 0.11535 | 2.4164 | 0.78485 | 45
Bus_2 | 1.1462 | 39.7072 | 1.1138 | 3.0064 | 0.70193 | 45
Bus_3(1) | 1.0349 | 35.8516 | 2.1122 | 3.5964 | 0.63377 | 45
Bus_4 | 1.0349 | 35.8516 | 2.1122 | 3.5964 | 0.63377 | 45

## LLL_min_fault_branch
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_vm_pu
Line_0 | 0 | 1.1462 | 0 | 2.1763 | 0 | 39.7072 | -5.1465e-09 | -19.7082 | 4.6774e-09 | -19.7082
Line_1 | 1.0349 | 0 | 1.7392 | 0 | 35.8516 | 0 | -16.0667 | -2.233e-09 | -16.0667 | 1.0258e-09
Line_2 | 1.0349 | 0 | 1.7392 | 0 | 35.8516 | 0 | -16.0667 | -2.233e-09 | -16.0667 | 1.0258e-09

## LL_max
name | pf_ikss_a_ka | pf_ikss_b_ka | pf_ikss_c_ka | pf_skss_a_mw | pf_skss_b_mw | pf_skss_c_mw | pf_rk0_ohm | pf_xk0_ohm | pf_rk1_ohm | pf_xk1_ohm | pf_rk2_ohm | pf_xk2_ohm | pf_vm_a_pu | pf_vm_b_pu | pf_vm_c_pu | pf_va_a_degree | pf_va_b_degree | pf_va_c_degree
Bus_0 | 0 | 4.5455 | 4.5455 | 0 | 288.6752 | 288.6752 | 1.3022 | 13.1336 | 1.3244 | 13.2439 | 1.3244 | 13.2439 | 0.95263 | 0 | 0.95263 | -8.6923e-11 | 0 | -180
Bus_1 | 0 | 4.7599 | 4.7599 | 0 | 54.9631 | 54.9631 | 0.042357 | 0.8917 | 0.10773 | 2.3084 | 0.10773 | 2.3084 | 0.95263 | 0 | 0.95263 | -4.0049e-12 | 0 | -180
Bus_2 | 0 | 3.7092 | 3.7092 | 0 | 42.8296 | 42.8296 | 3.7562 | 2.3518 | 0.62773 | 2.8984 | 0.62773 | 2.8984 | 0.95263 | 0 | 0.95263 | -1.2466e-11 | 0 | -180
Bus_3(1) | 0 | 2.9953 | 2.9953 | 0 | 34.587 | 34.587 | 7.4596 | 3.8148 | 1.1477 | 3.4884 | 1.1477 | 3.4884 | 0.95263 | 0 | 0.95263 | -1.466e-11 | 0 | -180
Bus_4 | 0 | 2.9953 | 2.9953 | 0 | 34.587 | 34.587 | 7.4596 | 3.8148 | 1.1477 | 3.4884 | 1.1477 | 3.4884 | 0.95263 | 0 | 0.95263 | -1.4655e-11 | 0 | -180

## LL_max_branch
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mw | pf_q_b_from_mw | pf_q_c_from_mw | pf_q_a_to_mw | pf_q_b_to_mw | pf_q_c_to_mw
Line_0 | 0 | 0 | 0 | 0 | 3.7092 | 3.7092 | 0 | 0 | 0 | 0 | 42.8296 | 42.8296 | -4.1685e-14 | -7.816e-15 | 1.0421e-14 | 5.2106e-15 | -23.0225 | 23.0225 | -1.5632e-14 | 5.7634e-09 | -5.7634e-09 | 1.5632e-14 | 4.9861 | -4.9861
Line_1 | 0 | 2.9953 | 2.9953 | 0 | 0 | 0 | 0 | 34.587 | 34.587 | 0 | 0 | 0 | -1.0421e-14 | -18.0699 | 18.0699 | -1.0421e-14 | 7.816e-15 | -1.5632e-14 | 1.0421e-14 | 5.9452 | -5.9452 | 5.2106e-15 | 1.9212e-09 | -1.9211e-09
Line_2 | 0 | 2.9953 | 2.9953 | 0 | 0 | 0 | 0 | 34.587 | 34.587 | 0 | 0 | 0 | 1.0421e-14 | -18.0699 | 18.0699 | -1.0421e-14 | 1.8237e-14 | -5.2106e-15 | -5.2106e-15 | 5.9452 | -5.9452 | -5.2106e-15 | 1.9211e-09 | -1.9211e-09

## LL_max_fault
name | pf_ikss_a_ka | pf_ikss_b_ka | pf_ikss_c_ka | pf_skss_a_mw | pf_skss_b_mw | pf_skss_c_mw | pf_rk0_ohm | pf_xk0_ohm | pf_rk1_ohm | pf_xk1_ohm | pf_rk2_ohm | pf_xk2_ohm | pf_vm_a_pu | pf_vm_b_pu | pf_vm_c_pu | pf_va_a_degree | pf_va_b_degree | pf_va_c_degree
Bus_0 | 0 | 3.7342 | 3.7342 | 0 | 237.1508 | 237.1508 | 1.3022 | 13.1336 | 1.3244 | 13.2439 | 1.3244 | 13.2439 | 1.0202 | 0.24004 | 0.89607 | 5.7662 | -121.3466 | 173.4316
Bus_1 | 0 | 2.011 | 2.011 | 0 | 23.2205 | 23.2205 | 0.042357 | 0.8917 | 0.10773 | 2.3084 | 0.10773 | 2.3084 | 1.1075 | 0.71098 | 0.91717 | 17.922 | -106.528 | 158.1868
Bus_2 | 0 | 1.7631 | 1.7631 | 0 | 20.3584 | 20.3584 | 3.7562 | 2.3518 | 0.62773 | 2.8984 | 0.62773 | 2.8984 | 1.0759 | 0.62335 | 0.92294 | 16.2567 | -104.913 | 160.9544
Bus_3(1) | 0 | 1.5688 | 1.5688 | 0 | 18.1144 | 18.1144 | 7.4596 | 3.8148 | 1.1477 | 3.4884 | 1.1477 | 3.4884 | 1.0531 | 0.55464 | 0.92719 | 14.8259 | -103.6532 | 163.1035
Bus_4 | 0 | 1.5688 | 1.5688 | 0 | 18.1144 | 18.1144 | 7.4596 | 3.8148 | 1.1477 | 3.4884 | 1.1477 | 3.4884 | 1.0531 | 0.55464 | 0.92719 | 14.8259 | -103.6532 | 163.1035

## LL_max_fault_branch
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mw | pf_q_b_from_mw | pf_q_c_from_mw | pf_q_a_to_mw | pf_q_b_to_mw | pf_q_c_to_mw
Line_0 | 0 | 0 | 0 | 0 | 1.7631 | 1.7631 | 0 | 0 | 0 | 0 | 20.3584 | 20.3584 | -2.6053e-15 | -9.5548e-10 | -3.0749e-09 | 2.6053e-15 | -17.4596 | 1.9173 | -1.3027e-14 | 4.0277e-09 | -3.5664e-10 | 5.2106e-15 | -2.1579 | -13.3845
Line_1 | 0 | 1.5688 | 1.5688 | 0 | 0 | 0 | 0 | 18.1144 | 18.1144 | 0 | 0 | 0 | -5.2106e-15 | -14.6611 | 2.3562 | 9.9672e-30 | -4.734e-10 | -1.0337e-09 | 2.6053e-15 | -0.96958 | -11.3353 | -2.6053e-15 | 1.3544e-09 | -3.8386e-10
Line_2 | 0 | 1.5688 | 1.5688 | 0 | 0 | 0 | 0 | 18.1144 | 18.1144 | 0 | 0 | 0 | 0 | -14.6611 | 2.3562 | 7.816e-15 | -4.7337e-10 | -1.0337e-09 | 0 | -0.96958 | -11.3353 | -1.0421e-14 | 1.3544e-09 | -3.8387e-10

## LL_min
name | pf_ikss_a_ka | pf_ikss_b_ka | pf_ikss_c_ka | pf_skss_a_mw | pf_skss_b_mw | pf_skss_c_mw | pf_rk0_ohm | pf_xk0_ohm | pf_rk1_ohm | pf_xk1_ohm | pf_rk2_ohm | pf_xk2_ohm | pf_vm_a_pu | pf_vm_b_pu | pf_vm_c_pu | pf_va_a_degree | pf_va_b_degree | pf_va_c_degree
Bus_0 | 0 | 3.6364 | 3.6364 | 0 | 230.9401 | 230.9401 | 1.4764 | 14.9076 | 1.505 | 15.0499 | 1.505 | 15.0499 | 0.86603 | 0 | 0.86603 | 1.72e-10 | 0 | 180
Bus_1 | 0 | 4.1337 | 4.1337 | 0 | 47.7317 | 47.7317 | 0.048006 | 0.96109 | 0.11535 | 2.4164 | 0.11535 | 2.4164 | 0.86603 | 0 | 0.86603 | 3.0755e-11 | 0 | 180
Bus_2 | 0 | 3.1191 | 3.1191 | 0 | 36.0161 | 36.0161 | 7.1792 | 2.3813 | 1.1138 | 3.0064 | 1.1138 | 3.0064 | 0.86603 | 0 | 0.86603 | 1.7229e-10 | 0 | 180
Bus_3(1) | 0 | 2.3976 | 2.3976 | 0 | 27.6856 | 27.6856 | 14.2898 | 3.8206 | 2.1122 | 3.5964 | 2.1122 | 3.5964 | 0.86603 | 0 | 0.86603 | 1.9331e-10 | 0 | 180
Bus_4 | 0 | 2.3976 | 2.3976 | 0 | 27.6856 | 27.6856 | 14.2898 | 3.8206 | 2.1122 | 3.5964 | 2.1122 | 3.5964 | 0.86603 | 0 | 0.86603 | 1.9332e-10 | 0 | 180

## LL_min_branch
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mw | pf_q_b_from_mw | pf_q_c_from_mw | pf_q_a_to_mw | pf_q_b_to_mw | pf_q_c_to_mw
Line_0 | 0 | 0 | 0 | 0 | 3.1191 | 3.1191 | 0 | 0 | 0 | 0 | 36.0161 | 36.0161 | 9.4739e-15 | -2.3685e-15 | 2.3685e-15 | -7.1054e-15 | -16.8865 | 16.8865 | -9.4739e-15 | 4.7631e-09 | -4.7631e-09 | 9.4739e-15 | 6.2558 | -6.2558
Line_1 | 0 | 2.3976 | 2.3976 | 0 | 0 | 0 | 0 | 27.6856 | 27.6856 | 0 | 0 | 0 | -3.5527e-15 | -11.9365 | 11.9365 | 4.737e-15 | 8.2897e-15 | 2.3685e-15 | 9.4739e-15 | 7.0103 | -7.0103 | -4.737e-15 | 1.5877e-09 | -1.5877e-09
Line_2 | 0 | 2.3976 | 2.3976 | 0 | 0 | 0 | 0 | 27.6856 | 27.6856 | 0 | 0 | 0 | -1.1842e-15 | -11.9365 | 11.9365 | 2.3685e-15 | 8.2897e-15 | 2.3685e-15 | 7.1054e-15 | 7.0103 | -7.0103 | 9.4739e-15 | 1.5877e-09 | -1.5877e-09

## LL_min_fault
name | pf_ikss_a_ka | pf_ikss_b_ka | pf_ikss_c_ka | pf_skss_a_mw | pf_skss_b_mw | pf_skss_c_mw | pf_rk0_ohm | pf_xk0_ohm | pf_rk1_ohm | pf_xk1_ohm | pf_rk2_ohm | pf_xk2_ohm | pf_vm_a_pu | pf_vm_b_pu | pf_vm_c_pu | pf_va_a_degree | pf_va_b_degree | pf_va_c_degree
Bus_0 | 0 | 3.0554 | 3.0554 | 0 | 194.0418 | 194.0418 | 1.4764 | 14.9076 | 1.505 | 15.0499 | 1.505 | 15.0499 | 0.92203 | 0.19641 | 0.81801 | 5.174 | -122.1449 | 174.1659
Bus_1 | 0 | 1.7957 | 1.7957 | 0 | 20.7353 | 20.7353 | 0.048006 | 0.96109 | 0.11535 | 2.4164 | 0.11535 | 2.4164 | 1.0057 | 0.63489 | 0.83074 | 17.5701 | -106.9886 | 158.5648
Bus_2 | 0 | 1.5183 | 1.5183 | 0 | 17.5318 | 17.5318 | 7.1792 | 2.3813 | 1.1138 | 3.0064 | 1.1138 | 3.0064 | 0.95734 | 0.5368 | 0.85298 | 15.9329 | -101.7238 | 162.0554
Bus_3(1) | 0 | 1.3081 | 1.3081 | 0 | 15.105 | 15.105 | 14.2898 | 3.8206 | 2.1122 | 3.5964 | 2.1122 | 3.5964 | 0.92653 | 0.4625 | 0.86515 | 14.3131 | -97.8911 | 164.6473
Bus_4 | 0 | 1.3081 | 1.3081 | 0 | 15.105 | 15.105 | 14.2898 | 3.8206 | 2.1122 | 3.5964 | 2.1122 | 3.5964 | 0.92653 | 0.4625 | 0.86515 | 14.3131 | -97.8911 | 164.6473

## LL_min_fault_branch
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mw | pf_q_b_from_mw | pf_q_c_from_mw | pf_q_a_to_mw | pf_q_b_to_mw | pf_q_c_to_mw
Line_0 | 0 | 0 | 0 | 0 | 1.5183 | 1.5183 | 0 | 0 | 0 | 0 | 17.5318 | 17.5318 | 9.1778e-15 | -8.0025e-10 | -2.5674e-09 | -5.3291e-15 | -13.0917 | 1.5655 | -1.1842e-14 | 3.4014e-09 | -3.4065e-10 | 1.1842e-14 | -0.95344 | -10.5727
Line_1 | 0 | 1.3081 | 1.3081 | 0 | 0 | 0 | 0 | 15.105 | 15.105 | 0 | 0 | 0 | -2.3685e-15 | -10.3011 | 1.745 | 3.5527e-15 | -4.7979e-10 | -8.2616e-10 | 4.737e-15 | 0.27863 | -8.8347 | -2.3685e-15 | 1.0532e-09 | -4.5326e-10
Line_2 | 0 | 1.3081 | 1.3081 | 0 | 0 | 0 | 0 | 15.105 | 15.105 | 0 | 0 | 0 | 5.9212e-16 | -10.3011 | 1.745 | 2.3685e-15 | -4.7979e-10 | -8.2616e-10 | -7.1054e-15 | 0.27863 | -8.8347 | 8.9036e-30 | 1.0532e-09 | -4.5326e-10

## LLG_max
name | pf_ikss_a_ka | pf_ikss_b_ka | pf_ikss_c_ka | pf_skss_a_mw | pf_skss_b_mw | pf_skss_c_mw | pf_rk0_ohm | pf_xk0_ohm | pf_rk1_ohm | pf_xk1_ohm | pf_rk2_ohm | pf_xk2_ohm | pf_vm_a_pu | pf_vm_b_pu | pf_vm_c_pu | pf_va_a_degree | pf_va_b_degree | pf_va_c_degree
Bus_0 | 0 | 5.2548 | 5.2573 | 0 | 333.7237 | 333.8855 | 1.3022 | 13.1336 | 1.3244 | 13.2439 | 1.3244 | 13.2439 | 0.63329 | 0 | 0.63329 | 0.016126 | 0 | -179.9839
Bus_1 | 0 | 6.6563 | 6.6538 | 0 | 76.8598 | 76.832 | 0.042357 | 0.8917 | 0.10773 | 2.3084 | 0.10773 | 2.3084 | 0.41521 | 0 | 0.41521 | -0.026833 | 0 | 179.9732
Bus_2 | 0 | 4.8903 | 3.0746 | 0 | 56.4683 | 35.5022 | 3.7562 | 2.3518 | 0.62773 | 2.8984 | 0.62773 | 2.8984 | 0.75809 | 0 | 0.75809 | -10.9913 | 0 | 169.0087
Bus_3(1) | 0 | 3.667 | 2.5296 | 0 | 42.343 | 29.2088 | 7.4596 | 3.8148 | 1.1477 | 3.4884 | 1.1477 | 3.4884 | 0.817 | 0 | 0.817 | -7.5976 | 0 | 172.4024
Bus_4 | 0 | 3.667 | 2.5296 | 0 | 42.343 | 29.2088 | 7.4596 | 3.8148 | 1.1477 | 3.4884 | 1.1477 | 3.4884 | 0.817 | 0 | 0.817 | -7.5976 | 0 | 172.4024

## LLG_max_branch
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mw | pf_q_b_from_mw | pf_q_c_from_mw | pf_q_a_to_mw | pf_q_b_to_mw | pf_q_c_to_mw
Line_0 | 0.0035648 | 0.0035648 | 0.0035648 | 0.0043336 | 4.8898 | 3.0779 | 0.041162 | 0.041162 | 0.041162 | 0.05004 | 56.4627 | 35.5408 | 0.00010571 | -6.2011e-13 | 7.3801e-14 | -2.6034e-05 | 1.9387e-10 | 1.5447e-10 | -0.029602 | -2.7555e-13 | 6.7413e-13 | 0.065706 | -2.223e-10 | -1.0116e-10
Line_1 | 0 | 3.667 | 2.5296 | 0.0021668 | 0.0021668 | 0.0021668 | 0 | 42.343 | 29.2088 | 0.02502 | 0.02502 | 0.02502 | -1.685e-09 | 9.8954e-11 | 9.533e-11 | 1.3016e-05 | -8.8186e-14 | -3.8598e-14 | -7.546e-10 | -1.0837e-10 | -3.0933e-11 | -0.032853 | -9.6473e-14 | 1.2413e-13
Line_2 | 0 | 3.667 | 2.5296 | 0.0021668 | 0.0021668 | 0.0021668 | 0 | 42.343 | 29.2088 | 0.02502 | 0.02502 | 0.02502 | -1.685e-09 | 9.896e-11 | 9.5312e-11 | 1.3016e-05 | -8.8186e-14 | -3.8598e-14 | -7.5462e-10 | -1.0839e-10 | -3.0952e-11 | -0.032853 | -9.6473e-14 | 1.2413e-13

## LLG_max_fault
name | pf_ikss_a_ka | pf_ikss_b_ka | pf_ikss_c_ka | pf_skss_a_mw | pf_skss_b_mw | pf_skss_c_mw | pf_rk0_ohm | pf_xk0_ohm | pf_rk1_ohm | pf_xk1_ohm | pf_rk2_ohm | pf_xk2_ohm | pf_vm_a_pu | pf_vm_b_pu | pf_vm_c_pu | pf_va_a_degree | pf_va_b_degree | pf_va_c_degree
Bus_0 | 0 | 3.6223 | 3.6206 | 0 | 230.0463 | 229.9412 | 1.3022 | 13.1336 | 1.3244 | 13.2439 | 1.3244 | 13.2439 | 0.83701 | 0.40283 | 0.69119 | 8.9451 | -115.8808 | 160.3633
Bus_1 | 0 | 1.5005 | 1.4185 | 0 | 17.3261 | 16.379 | 0.042357 | 0.8917 | 0.10773 | 2.3084 | 0.10773 | 2.3084 | 1.0272 | 0.87234 | 0.93702 | 21.5117 | -100.051 | 149.0209
Bus_2 | 0 | 1.3675 | 1.1818 | 0 | 15.7907 | 13.6465 | 3.7562 | 2.3518 | 0.62773 | 2.8984 | 0.62773 | 2.8984 | 1.0079 | 0.80202 | 0.92648 | 20.1579 | -99.5297 | 151.3914
Bus_3(1) | 0 | 1.2493 | 1.0407 | 0 | 14.4259 | 12.0164 | 7.4596 | 3.8148 | 1.1477 | 3.4884 | 1.1477 | 3.4884 | 0.99135 | 0.74213 | 0.91821 | 18.8974 | -99.0862 | 153.3575
Bus_4 | 0 | 1.2493 | 1.0407 | 0 | 14.4259 | 12.0164 | 7.4596 | 3.8148 | 1.1477 | 3.4884 | 1.1477 | 3.4884 | 0.99135 | 0.74213 | 0.91821 | 18.8974 | -99.0862 | 153.3575

## LLG_max_fault_branch
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mw | pf_q_b_from_mw | pf_q_c_from_mw | pf_q_a_to_mw | pf_q_b_to_mw | pf_q_c_to_mw
Line_0 | 0.00059849 | 0.00059849 | 0.00059849 | 0.0014922 | 1.3669 | 1.1833 | 0.0069108 | 0.0069108 | 0.0069108 | 0.01723 | 15.784 | 13.6633 | -0.004426 | -0.0014359 | 0.0058649 | -0.0027932 | -9.3371 | -6.994 | -0.0057402 | 0.0061855 | -0.0012797 | 0.019902 | -9.3559 | -6.9901
Line_1 | 0 | 1.2493 | 1.0407 | 0.00074609 | 0.00074609 | 0.00074609 | 0 | 14.4259 | 12.0164 | 0.0086151 | 0.0086151 | 0.0086151 | -6.5867e-10 | -7.804 | -5.4148 | 0.0013966 | -0.0066743 | 0.0052792 | -4.1668e-10 | -7.804 | -5.4148 | -0.0099512 | 0.0027391 | 0.0033171
Line_2 | 0 | 1.2493 | 1.0407 | 0.00074609 | 0.00074609 | 0.00074609 | 0 | 14.4259 | 12.0164 | 0.0086151 | 0.0086151 | 0.0086151 | -6.5867e-10 | -7.804 | -5.4148 | 0.0013966 | -0.0066743 | 0.0052792 | -4.1668e-10 | -7.804 | -5.4148 | -0.0099512 | 0.0027391 | 0.0033171

## LLG_min
name | pf_ikss_a_ka | pf_ikss_b_ka | pf_ikss_c_ka | pf_skss_a_mw | pf_skss_b_mw | pf_skss_c_mw | pf_rk0_ohm | pf_xk0_ohm | pf_rk1_ohm | pf_xk1_ohm | pf_rk2_ohm | pf_xk2_ohm | pf_vm_a_pu | pf_vm_b_pu | pf_vm_c_pu | pf_va_a_degree | pf_va_b_degree | pf_va_c_degree
Bus_0 | 0 | 4.2045 | 4.2068 | 0 | 267.0216 | 267.1682 | 1.4764 | 14.9076 | 1.505 | 15.0499 | 1.505 | 15.0499 | 0.5755 | 0 | 0.5755 | 0.018275 | 0 | -179.9817
Bus_1 | 0 | 5.7463 | 5.7406 | 0 | 66.3521 | 66.2873 | 0.048006 | 0.96109 | 0.11535 | 2.4164 | 0.11535 | 2.4164 | 0.38371 | 0 | 0.38371 | -0.070431 | 0 | 179.9296
Bus_2 | 0 | 3.8712 | 2.5441 | 0 | 44.7013 | 29.377 | 7.1792 | 2.3813 | 1.1138 | 3.0064 | 1.1138 | 3.0064 | 0.7567 | 0 | 0.7567 | -8.3121 | 0 | 171.6879
Bus_3(1) | 0 | 2.7649 | 2.101 | 0 | 31.9264 | 24.2607 | 14.2898 | 3.8206 | 2.1122 | 3.5964 | 2.1122 | 3.5964 | 0.78386 | 0 | 0.78386 | -5.1411 | 0 | 174.8589
Bus_4 | 0 | 2.7649 | 2.101 | 0 | 31.9264 | 24.2607 | 14.2898 | 3.8206 | 2.1122 | 3.5964 | 2.1122 | 3.5964 | 0.78386 | 0 | 0.78386 | -5.1411 | 0 | 174.8589

## LLG_min_branch
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mw | pf_q_b_from_mw | pf_q_c_from_mw | pf_q_a_to_mw | pf_q_b_to_mw | pf_q_c_to_mw
Line_0 | 0.0032943 | 0.0032943 | 0.0032943 | 0.0043257 | 3.8699 | 2.5472 | 0.038039 | 0.038039 | 0.038039 | 0.049949 | 44.6861 | 29.4126 | 0.00017333 | 2.4773e-15 | 3.6591e-13 | -4.9801e-05 | -1.8829e-10 | -4.3916e-11 | -0.02528 | 4.2173e-13 | -2.1354e-13 | 0.065466 | -1.7634e-10 | -1.6429e-10
Line_1 | 0 | 2.7649 | 2.101 | 0.0021629 | 0.0021629 | 0.0021629 | 0 | 31.9264 | 24.2607 | 0.024974 | 0.024974 | 0.024974 | -1.8007e-09 | -1.5327e-10 | -3.2042e-11 | 2.49e-05 | -1.2592e-13 | 1.2442e-13 | -4.4607e-10 | -1.1766e-10 | -1.4336e-10 | -0.032733 | 7.0221e-14 | 7.328e-14
Line_2 | 0 | 2.7649 | 2.101 | 0.0021629 | 0.0021629 | 0.0021629 | 0 | 31.9264 | 24.2607 | 0.024974 | 0.024974 | 0.024974 | -1.8007e-09 | -1.5327e-10 | -3.2053e-11 | 2.49e-05 | -1.2592e-13 | 1.2442e-13 | -4.4609e-10 | -1.1766e-10 | -1.4337e-10 | -0.032733 | 7.0221e-14 | 7.328e-14

## LLG_min_fault
name | pf_ikss_a_ka | pf_ikss_b_ka | pf_ikss_c_ka | pf_skss_a_mw | pf_skss_b_mw | pf_skss_c_mw | pf_rk0_ohm | pf_xk0_ohm | pf_rk1_ohm | pf_xk1_ohm | pf_rk2_ohm | pf_xk2_ohm | pf_vm_a_pu | pf_vm_b_pu | pf_vm_c_pu | pf_va_a_degree | pf_va_b_degree | pf_va_c_degree
Bus_0 | 0 | 3.0171 | 3.0157 | 0 | 191.6095 | 191.5209 | 1.4764 | 14.9076 | 1.505 | 15.0499 | 1.505 | 15.0499 | 0.74636 | 0.33546 | 0.61767 | 8.0954 | -117.0249 | 161.7211
Bus_1 | 0 | 1.3511 | 1.2766 | 0 | 15.6012 | 14.7406 | 0.048006 | 0.96109 | 0.11535 | 2.4164 | 0.11535 | 2.4164 | 0.93054 | 0.78485 | 0.84636 | 21.2049 | -100.4046 | 149.0427
Bus_2 | 0 | 1.2 | 0.97241 | 0 | 13.8559 | 11.2284 | 7.1792 | 2.3813 | 1.1138 | 3.0064 | 1.1138 | 3.0064 | 0.90544 | 0.70193 | 0.85141 | 19.9006 | -97.6343 | 152.9265
Bus_3(1) | 0 | 1.0574 | 0.83948 | 0 | 12.2097 | 9.6935 | 14.2898 | 3.8206 | 2.1122 | 3.5964 | 2.1122 | 3.5964 | 0.8824 | 0.63377 | 0.85167 | 18.6039 | -95.3977 | 155.7752
Bus_4 | 0 | 1.0574 | 0.83948 | 0 | 12.2097 | 9.6935 | 14.2898 | 3.8206 | 2.1122 | 3.5964 | 2.1122 | 3.5964 | 0.8824 | 0.63377 | 0.85167 | 18.6039 | -95.3977 | 155.7752

## LLG_min_fault_branch
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mw | pf_q_b_from_mw | pf_q_c_from_mw | pf_q_a_to_mw | pf_q_b_to_mw | pf_q_c_to_mw
Line_0 | 0.00058159 | 0.00058159 | 0.00058159 | 0.0019688 | 1.1988 | 0.97436 | 0.0067156 | 0.0067156 | 0.0067156 | 0.022734 | 13.8431 | 11.251 | -0.0038499 | -0.0012808 | 0.0051361 | -0.0057053 | -7.1831 | -4.7386 | -0.0051078 | 0.0054067 | -0.0010868 | 0.024888 | -7.2026 | -4.7362
Line_1 | 0 | 1.0574 | 0.83948 | 0.0009844 | 0.0009844 | 0.0009844 | 0 | 12.2097 | 9.6935 | 0.011367 | 0.011367 | 0.011367 | -9.386e-10 | -5.5904 | -3.5236 | 0.0028527 | -0.0082106 | 0.0053631 | -4.0846e-10 | -5.5904 | -3.5236 | -0.012444 | 0.0015338 | 0.0041295
Line_2 | 0 | 1.0574 | 0.83948 | 0.0009844 | 0.0009844 | 0.0009844 | 0 | 12.2097 | 9.6935 | 0.011367 | 0.011367 | 0.011367 | -9.3859e-10 | -5.5904 | -3.5236 | 0.0028527 | -0.0082106 | 0.0053631 | -4.0847e-10 | -5.5904 | -3.5236 | -0.012444 | 0.0015338 | 0.0041295

## LG_max
name | pf_ikss_a_ka | pf_ikss_b_ka | pf_ikss_c_ka | pf_skss_a_mw | pf_skss_b_mw | pf_skss_c_mw | pf_rk0_ohm | pf_xk0_ohm | pf_rk1_ohm | pf_xk1_ohm | pf_rk2_ohm | pf_xk2_ohm | pf_vm_a_pu | pf_vm_b_pu | pf_vm_c_pu | pf_va_a_degree | pf_va_b_degree | pf_va_c_degree
Bus_0 | 5.2634 | 0 | 0 | 334.2712 | 0 | 0 | 1.3022 | 13.1336 | 1.3244 | 13.2439 | 1.3244 | 13.2439 | 0.63435 | 1.1 | 0.63404 | 60.1478 | -90 | 119.8682
Bus_1 | 6.9098 | 0 | 0 | 79.7881 | 0 | 0 | 0.042357 | 0.8917 | 0.10773 | 2.3084 | 0.10773 | 2.3084 | 0.57111 | 1.1 | 0.57131 | 74.3344 | -90 | 105.6598
Bus_2 | 3.9832 | 0 | 0 | 45.9941 | 0 | 0 | 3.7562 | 2.3518 | 0.62773 | 2.8984 | 0.62773 | 2.8984 | 0.53079 | 1.1 | 0.84425 | 41.842 | -90 | 117.9292
Bus_3(1) | 2.6194 | 0 | 0 | 30.2463 | 0 | 0 | 7.4596 | 3.8148 | 1.1477 | 3.4884 | 1.1477 | 3.4884 | 0.62385 | 1.1 | 0.90437 | 34.6993 | -90 | 124.5504
Bus_4 | 2.6194 | 0 | 0 | 30.2463 | 0 | 0 | 7.4596 | 3.8148 | 1.1477 | 3.4884 | 1.1477 | 3.4884 | 0.62385 | 1.1 | 0.90437 | 34.6993 | -90 | 124.5504

## LG_max_branch
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mw | pf_q_b_from_mw | pf_q_c_from_mw | pf_q_a_to_mw | pf_q_b_to_mw | pf_q_c_to_mw
Line_0 | 0.002648 | 0.002648 | 0.002648 | 3.9859 | 0.0050455 | 0.0050455 | 0.030576 | 0.030576 | 0.030576 | 46.025 | 0.05826 | 0.05826 | -5.8074e-13 | 0.029157 | -0.029098 | 3.4677e-10 | -0.049739 | 0.049703 | 4.5102e-14 | -0.0080427 | -0.0082912 | -2.5315e-10 | 0.019873 | 0.069191
Line_1 | 2.6194 | 0 | 0 | 0.0025227 | 0.0025227 | 0.0025227 | 30.2463 | 0 | 0 | 0.02913 | 0.02913 | 0.02913 | 1.1062e-10 | -3.4092e-10 | -2.6988e-09 | -2.5234e-13 | 0.024869 | -0.024852 | -1.1711e-10 | -1.8625e-09 | 5.0121e-10 | -1.0083e-13 | -0.0099363 | -0.034596
Line_2 | 2.6194 | 0 | 0 | 0.0025227 | 0.0025227 | 0.0025227 | 30.2463 | 0 | 0 | 0.02913 | 0.02913 | 0.02913 | 1.1063e-10 | -3.4092e-10 | -2.6988e-09 | -2.5234e-13 | 0.024869 | -0.024852 | -1.1711e-10 | -1.8625e-09 | 5.0124e-10 | -1.0083e-13 | -0.0099363 | -0.034596

## LG_max_fault
name | pf_ikss_a_ka | pf_ikss_b_ka | pf_ikss_c_ka | pf_skss_a_mw | pf_skss_b_mw | pf_skss_c_mw | pf_rk0_ohm | pf_xk0_ohm | pf_rk1_ohm | pf_xk1_ohm | pf_rk2_ohm | pf_xk2_ohm | pf_vm_a_pu | pf_vm_b_pu | pf_vm_c_pu | pf_va_a_degree | pf_va_b_degree | pf_va_c_degree
Bus_0 | 3.6249 | 0 | 0 | 230.2146 | 0 | 0 | 1.3022 | 13.1336 | 1.3244 | 13.2439 | 1.3244 | 13.2439 | 0.69104 | 1.1 | 0.83758 | 40.4328 | -90 | 128.9019
Bus_1 | 1.4907 | 0 | 0 | 17.2132 | 0 | 0 | 0.042357 | 0.8917 | 0.10773 | 2.3084 | 0.10773 | 2.3084 | 0.92824 | 1.1 | 1.0361 | 29.2627 | -90 | 141.408
Bus_2 | 1.2453 | 0 | 0 | 14.3794 | 0 | 0 | 3.7562 | 2.3518 | 0.62773 | 2.8984 | 0.62773 | 2.8984 | 0.91541 | 1.1 | 1.0162 | 30.2778 | -90 | 141.0749
Bus_3(1) | 1.0659 | 0 | 0 | 12.3079 | 0 | 0 | 7.4596 | 3.8148 | 1.1477 | 3.4884 | 1.1477 | 3.4884 | 0.90498 | 1.1 | 1.0026 | 30.9478 | -90 | 140.729
Bus_4 | 1.0659 | 0 | 0 | 12.3079 | 0 | 0 | 7.4596 | 3.8148 | 1.1477 | 3.4884 | 1.1477 | 3.4884 | 0.90498 | 1.1 | 1.0026 | 30.9478 | -90 | 140.729

## LG_max_fault_branch
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mw | pf_q_b_from_mw | pf_q_c_from_mw | pf_q_a_to_mw | pf_q_b_to_mw | pf_q_c_to_mw
Line_0 | 0.00057127 | 0.00057127 | 0.00057127 | 1.2461 | 0.0015774 | 0.0015774 | 0.0065964 | 0.0065964 | 0.0065964 | 14.389 | 0.018214 | 0.018214 | 0.0040352 | 0.0032102 | -0.0072427 | -7.7506 | -0.018142 | 0.015021 | 0.0044696 | -0.0061037 | 0.00087388 | -7.7672 | 0.0060098 | 0.016231
Line_1 | 1.0659 | 0 | 0 | 0.00078869 | 0.00078869 | 0.00078869 | 12.3079 | 0 | 0 | 0.009107 | 0.009107 | 0.009107 | -5.6806 | 4.0635e-11 | -8.8963e-10 | -0.001559 | 0.0090711 | -0.0075105 | -5.6806 | -7.636e-10 | 2.2653e-10 | 0.0067676 | -0.0030049 | -0.0081153
Line_2 | 1.0659 | 0 | 0 | 0.00078869 | 0.00078869 | 0.00078869 | 12.3079 | 0 | 0 | 0.009107 | 0.009107 | 0.009107 | -5.6806 | 4.0633e-11 | -8.8964e-10 | -0.001559 | 0.0090711 | -0.0075105 | -5.6806 | -7.636e-10 | 2.2651e-10 | 0.0067676 | -0.0030049 | -0.0081153

## LG_min
name | pf_ikss_a_ka | pf_ikss_b_ka | pf_ikss_c_ka | pf_skss_a_mw | pf_skss_b_mw | pf_skss_c_mw | pf_rk0_ohm | pf_xk0_ohm | pf_rk1_ohm | pf_xk1_ohm | pf_rk2_ohm | pf_xk2_ohm | pf_vm_a_pu | pf_vm_b_pu | pf_vm_c_pu | pf_va_a_degree | pf_va_b_degree | pf_va_c_degree
Bus_0 | 4.2123 | 0 | 0 | 267.5184 | 0 | 0 | 1.4764 | 14.9076 | 1.505 | 15.0499 | 1.505 | 15.0499 | 0.57659 | 1 | 0.57627 | 60.1678 | -90 | 119.8503
Bus_1 | 5.972 | 0 | 0 | 68.9585 | 0 | 0 | 0.048006 | 0.96109 | 0.11535 | 2.4164 | 0.11535 | 2.4164 | 0.51998 | 1 | 0.52049 | 73.9605 | -90 | 106.0234
Bus_2 | 2.7477 | 0 | 0 | 31.7273 | 0 | 0 | 7.1792 | 2.3813 | 1.1138 | 3.0064 | 1.1138 | 3.0064 | 0.56005 | 1 | 0.8522 | 31.6294 | -90 | 124.0257
Bus_3(1) | 1.6081 | 0 | 0 | 18.5682 | 0 | 0 | 14.2898 | 3.8206 | 2.1122 | 3.5964 | 2.1122 | 3.5964 | 0.66477 | 1 | 0.87481 | 30.5915 | -90 | 130.8538
Bus_4 | 1.6081 | 0 | 0 | 18.5682 | 0 | 0 | 14.2898 | 3.8206 | 2.1122 | 3.5964 | 2.1122 | 3.5964 | 0.66477 | 1 | 0.87481 | 30.5915 | -90 | 130.8538

## LG_min_branch
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mw | pf_q_b_from_mw | pf_q_c_from_mw | pf_q_a_to_mw | pf_q_b_to_mw | pf_q_c_to_mw
Line_0 | 0.0024669 | 0.0024669 | 0.0024669 | 2.7495 | 0.0059403 | 0.0059403 | 0.028485 | 0.028485 | 0.028485 | 31.7489 | 0.068592 | 0.068592 | 9.6135e-14 | 0.024717 | -0.024619 | -7.0607e-11 | -0.054549 | 0.054455 | 1.9016e-13 | -0.0068736 | -0.0073027 | -1.7428e-11 | 0.038101 | 0.085355
Line_1 | 1.6081 | 0 | 0 | 0.0029701 | 0.0029701 | 0.0029701 | 18.5682 | 0 | 0 | 0.034296 | 0.034296 | 0.034296 | -1.9134e-11 | -1.1833e-09 | -2.9618e-09 | 6.2452e-15 | 0.027274 | -0.027227 | -6.9354e-13 | -2.0731e-09 | 1.0462e-09 | 7.8313e-14 | -0.01905 | -0.042678
Line_2 | 1.6081 | 0 | 0 | 0.0029701 | 0.0029701 | 0.0029701 | 18.5682 | 0 | 0 | 0.034296 | 0.034296 | 0.034296 | -1.9134e-11 | -1.1832e-09 | -2.9618e-09 | 6.2452e-15 | 0.027274 | -0.027227 | -6.9448e-13 | -2.0731e-09 | 1.0462e-09 | 7.8313e-14 | -0.01905 | -0.042678

## LG_min_fault
name | pf_ikss_a_ka | pf_ikss_b_ka | pf_ikss_c_ka | pf_skss_a_mw | pf_skss_b_mw | pf_skss_c_mw | pf_rk0_ohm | pf_xk0_ohm | pf_rk1_ohm | pf_xk1_ohm | pf_rk2_ohm | pf_xk2_ohm | pf_vm_a_pu | pf_vm_b_pu | pf_vm_c_pu | pf_va_a_degree | pf_va_b_degree | pf_va_c_degree
Bus_0 | 3.0198 | 0 | 0 | 191.783 | 0 | 0 | 1.4764 | 14.9076 | 1.505 | 15.0499 | 1.505 | 15.0499 | 0.61755 | 1 | 0.74699 | 41.809 | -90 | 128.0401
Bus_1 | 1.3425 | 0 | 0 | 15.5017 | 0 | 0 | 0.048006 | 0.96109 | 0.11535 | 2.4164 | 0.11535 | 2.4164 | 0.83799 | 1 | 0.93906 | 29.3078 | -90 | 141.0917
Bus_2 | 1.0246 | 0 | 0 | 11.8316 | 0 | 0 | 7.1792 | 2.3813 | 1.1138 | 3.0064 | 1.1138 | 3.0064 | 0.83625 | 1 | 0.91801 | 30.8074 | -90 | 141.4811
Bus_3(1) | 0.81652 | 0 | 0 | 9.4284 | 0 | 0 | 14.2898 | 3.8206 | 2.1122 | 3.5964 | 2.1122 | 3.5964 | 0.83184 | 1 | 0.90454 | 31.6819 | -90 | 141.4979
Bus_4 | 0.81652 | 0 | 0 | 9.4284 | 0 | 0 | 14.2898 | 3.8206 | 2.1122 | 3.5964 | 2.1122 | 3.5964 | 0.83184 | 1 | 0.90454 | 31.6819 | -90 | 141.4979

## LG_min_fault_branch
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mw | pf_q_b_from_mw | pf_q_c_from_mw | pf_q_a_to_mw | pf_q_b_to_mw | pf_q_c_to_mw
Line_0 | 0.00055455 | 0.00055455 | 0.00055455 | 1.0253 | 0.0022152 | 0.0022152 | 0.0064034 | 0.0064034 | 0.0064034 | 11.8396 | 0.025579 | 0.025579 | 0.0035052 | 0.0028978 | -0.0063981 | -5.2423 | -0.023609 | 0.016386 | 0.0039276 | -0.0053468 | 0.00070278 | -5.2638 | 0.0062244 | 0.025283
Line_1 | 0.81652 | 0 | 0 | 0.0011076 | 0.0011076 | 0.0011076 | 9.4284 | 0 | 0 | 0.01279 | 0.01279 | 0.01279 | -3.3335 | -1.7823e-10 | -1.2695e-09 | -0.0036049 | 0.011805 | -0.0081931 | -3.3335 | -1.0453e-09 | 4.153e-10 | 0.0071697 | -0.0031122 | -0.012642
Line_2 | 0.81652 | 0 | 0 | 0.0011076 | 0.0011076 | 0.0011076 | 9.4284 | 0 | 0 | 0.01279 | 0.01279 | 0.01279 | -3.3335 | -1.7823e-10 | -1.2695e-09 | -0.0036049 | 0.011805 | -0.0081931 | -3.3335 | -1.0453e-09 | 4.1529e-10 | 0.0071697 | -0.0031122 | -0.012642