## LLL_max_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 4.283 | 4.283 | 0 | 9.2778 | 148.3662 | 148.3662 | 28.6163 | -1e-07 | 32.4685 | -1e-07 | -77.7798 | 102.2202 | 0.29171 | 0 | -29.1714 | 0
Line_1 | 0.14434 | 0.14434 | 0 | 0.20412 | 5 | 5 | 0.0325 | -1e-07 | 0.036875 | -1e-07 | -77.7798 | 102.2202 | 0.0098306 | 0 | -29.1714 | 0
Line_2 | 0.14434 | 0.14434 | 0 | 0.20412 | 5 | 5 | 0.0325 | -1e-07 | 0.036875 | -1e-07 | -77.7798 | 102.2202 | 0.0098306 | 0 | -29.1714 | 0

## LLL_max_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 4.283 | 4.283 | 0 | 9.2778 | 148.3662 | 148.3662 | 28.6163 | -1e-07 | 32.4685 | -1e-07 | -77.7798 | 102.2202 | 0.29171 | 0 | -29.1714 | 0
Line_1 | 0.14434 | 0.14434 | 0 | 0.20412 | 5 | 5 | 0.0325 | -1e-07 | 0.036875 | -1e-07 | -77.7798 | 102.2202 | 0.0098306 | 0 | -29.1714 | 0
Line_2 | 0.14434 | 0.14434 | 0 | 0.20412 | 5 | 5 | 0.0325 | -1e-07 | 0.036875 | -1e-07 | -77.7798 | 102.2202 | 0.0098306 | 0 | -29.1714 | 0

## LLL_max_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 1.1384 | 1.1384 | 0 | 2.4661 | 39.4369 | 39.4369 | 28.164 | -26.1422 | 23.6571 | -21.3631 | -48.785 | 131.215 | 0.93266 | 0.85607 | -8.7555 | -9.5297
Line_1 | 0.14434 | 0.14434 | 0 | 0.20412 | 5 | 5 | 1.6186 | -1.5861 | 4.0125 | -3.9756 | -77.7798 | 102.2202 | 0.86534 | 0.85607 | -9.7485 | -9.5297
Line_2 | 0.14434 | 0.14434 | 0 | 0.20412 | 5 | 5 | 1.6186 | -1.5861 | 4.0125 | -3.9756 | -77.7798 | 102.2202 | 0.86534 | 0.85607 | -9.7485 | -9.5297

## LLL_max_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 1.1384 | 1.1384 | 0 | 2.4661 | 39.4369 | 39.4369 | 28.164 | -26.1422 | 23.6571 | -21.3631 | -48.785 | 131.215 | 0.93266 | 0.85607 | -8.7555 | -9.5297
Line_1 | 0.14434 | 0.14434 | 0 | 0.20412 | 5 | 5 | 1.6186 | -1.5861 | 4.0125 | -3.9756 | -77.7798 | 102.2202 | 0.86534 | 0.85607 | -9.7485 | -9.5297
Line_2 | 0.14434 | 0.14434 | 0 | 0.20412 | 5 | 5 | 1.6186 | -1.5861 | 4.0125 | -3.9756 | -77.7798 | 102.2202 | 0.86534 | 0.85607 | -9.7485 | -9.5297

## LLL_min_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 3.6016 | 3.6016 | 0 | 6.8381 | 124.7634 | 124.7634 | 38.8525 | -1e-07 | 22.9597 | -1e-07 | -69.6723 | 110.3277 | 0.36172 | 0 | -39.0915 | 0
Line_1 | 0 | 0 | 0 | 4.4908e-10 | 0 | 0 | 0 | 1.7305e-20 | 0 | 6.32e-20 | 0 | 0 | 0 | 0 | 0 | 0
Line_2 | 0 | 0 | 0 | 4.4908e-10 | 0 | 0 | 0 | 1.7305e-20 | 0 | 6.32e-20 | 0 | 0 | 0 | 0 | 0 | 0

## LLL_min_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 3.6016 | 3.6016 | 0 | 6.8381 | 124.7634 | 124.7634 | 38.8525 | -1e-07 | 22.9597 | -1e-07 | -69.6723 | 110.3277 | 0.36172 | 0 | -39.0915 | 0
Line_1 | 0 | 0 | 0 | 4.4908e-10 | 0 | 0 | 0 | 1.7305e-20 | 0 | 6.32e-20 | 0 | 0 | 0 | 0 | 0 | 0
Line_2 | 0 | 0 | 0 | 4.4908e-10 | 0 | 0 | 0 | 1.7305e-20 | 0 | 6.32e-20 | 0 | 0 | 0 | 0 | 0 | 0

## LLL_min_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 1.1462 | 1.1462 | 0 | 2.1763 | 39.7072 | 39.7072 | 23.6436 | -19.7082 | 22.0338 | -19.7082 | -52.6343 | 127.3657 | 0.81393 | 0.70193 | -9.6527 | -7.6343
Line_1 | 0 | 0 | 0 | 1.4292e-10 | 0 | 0 | 0 | -2.233e-09 | 0 | 1.0258e-09 | 0 | 0 | 0.70193 | 0.70193 | -7.6343 | -7.6343
Line_2 | 0 | 0 | 0 | 1.4292e-10 | 0 | 0 | 0 | -2.233e-09 | 0 | 1.0258e-09 | 0 | 0 | 0.70193 | 0.70193 | -7.6343 | -7.6343

## LLL_min_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 1.1462 | 1.1462 | 0 | 2.1763 | 39.7072 | 39.7072 | 23.6436 | -19.7082 | 22.0338 | -19.7082 | -52.6343 | 127.3657 | 0.81393 | 0.70193 | -9.6527 | -7.6343
Line_1 | 0 | 0 | 0 | 1.4292e-10 | 0 | 0 | 0 | -2.233e-09 | 0 | 1.0258e-09 | 0 | 0 | 0.70193 | 0.70193 | -7.6343 | -7.6343
Line_2 | 0 | 0 | 0 | 1.4292e-10 | 0 | 0 | 0 | -2.233e-09 | 0 | 1.0258e-09 | 0 | 0 | 0.70193 | 0.70193 | -7.6343 | -7.6343

## LL_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.28867 | 3.712 | 3.712 | 0.28867 | 3.712 | 3.712 | 3.3333 | 42.862 | 42.862 | 3.3333 | 42.862 | 42.862 | -0.78508 | 31.5321 | -17.6165 | 0.82842 | -24.3672 | 24.7814 | -3.7759 | 1.8509 | 12.4953 | 3.8251 | 6.2785 | -4.3659 | 102.22 | -165.5514 | 9.9917 | -77.78 | 14.4486 | -170.0083 | 1.157 | 0.73693 | 0.5039 | 1.1741 | 0.58707 | 0.58707 | 0.47457 | -162.192 | 154.6437 | -8.1315e-06 | 180 | 180
Line_1 | 0.14434 | 0.14434 | 0.14434 | 0.14434 | 0.14434 | 0.14434 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 0.42504 | 0.94255 | -0.71378 | -0.41421 | -0.93172 | 0.72461 | 1.9248 | 0.31107 | 0.66979 | -1.9126 | -0.29878 | -0.6575 | -77.78 | 162.2204 | 42.22 | 102.22 | -17.7796 | -137.78 | 1.1827 | 0.59553 | 0.58729 | 1.1741 | 0.58707 | 0.58707 | -0.23213 | -179.5153 | 179.041 | -8.1315e-06 | 180 | 180
Line_2 | 0.14434 | 0.14434 | 0.14434 | 0.14434 | 0.14434 | 0.14434 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 0.42504 | 0.94255 | -0.71378 | -0.41421 | -0.93172 | 0.72461 | 1.9248 | 0.31107 | 0.66979 | -1.9126 | -0.29878 | -0.6575 | -77.78 | 162.2204 | 42.22 | 102.22 | -17.7796 | -137.78 | 1.1827 | 0.59553 | 0.58729 | 1.1741 | 0.58707 | 0.58707 | -0.23213 | -179.5153 | 179.041 | -8.1315e-06 | 180 | 180

## LL_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.28867 | 3.712 | 3.712 | 0.28867 | 3.712 | 3.712 | 3.3333 | 42.862 | 42.862 | 3.3333 | 42.862 | 42.862 | -0.78508 | 31.5321 | -17.6165 | 0.82842 | -24.3672 | 24.7814 | -3.7759 | 1.8509 | 12.4953 | 3.8251 | 6.2785 | -4.3659 | 102.22 | -165.5514 | 9.9917 | -77.78 | 14.4486 | -170.0083 | 1.157 | 0.73693 | 0.5039 | 1.1741 | 0.58707 | 0.58707 | 0.47457 | -162.192 | 154.6437 | -8.1315e-06 | 180 | 180
Line_1 | 0.14434 | 0.14434 | 0.14434 | 0.14434 | 0.14434 | 0.14434 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 0.42504 | 0.94255 | -0.71378 | -0.41421 | -0.93172 | 0.72461 | 1.9248 | 0.31107 | 0.66979 | -1.9126 | -0.29878 | -0.6575 | -77.78 | 162.2204 | 42.22 | 102.22 | -17.7796 | -137.78 | 1.1827 | 0.59553 | 0.58729 | 1.1741 | 0.58707 | 0.58707 | -0.23213 | -179.5153 | 179.041 | -8.1315e-06 | 180 | 180
Line_2 | 0.14434 | 0.14434 | 0.14434 | 0.14434 | 0.14434 | 0.14434 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 0.42504 | 0.94255 | -0.71378 | -0.41421 | -0.93172 | 0.72461 | 1.9248 | 0.31107 | 0.66979 | -1.9126 | -0.29878 | -0.6575 | -77.78 | 162.2204 | 42.22 | 102.22 | -17.7796 | -137.78 | 1.1827 | 0.59553 | 0.58729 | 1.1741 | 0.58707 | 0.58707 | -0.23213 | -179.5153 | 179.041 | -8.1315e-06 | 180 | 180

## LL_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.28867 | 1.7018 | 1.6008 | 0.28867 | 1.7018 | 1.6008 | 3.3333 | 19.6505 | 18.4849 | 3.3333 | 19.6505 | 18.4849 | -0.78509 | 19.6311 | -1.0159 | 0.82842 | -18.1252 | 2.3485 | -3.776 | 1.6514 | 14.4041 | 3.8251 | 0.057272 | -12.8922 | 102.2201 | -142.6862 | 27.9149 | -77.7799 | 37.3138 | -152.0851 | 1.157 | 1.0025 | 0.78117 | 1.1741 | 0.92238 | 0.70892 | 0.47457 | -137.8777 | 121.9492 | -5.5203e-06 | -142.8673 | 128.239
Line_1 | 0.14434 | 0.14434 | 0.14434 | 0.14434 | 0.14434 | 0.14434 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 0.42504 | 0.89452 | 0.092865 | -0.41421 | -0.88369 | -0.082032 | 1.9249 | 1.2702 | 1.191 | -1.9126 | -1.2579 | -1.1787 | -77.7799 | 162.2203 | 42.2201 | 102.2201 | -17.7797 | -137.7799 | 1.1827 | 0.93216 | 0.71675 | 1.1741 | 0.92238 | 0.70892 | -0.23213 | -142.9336 | 127.7616 | -5.5203e-06 | -142.8673 | 128.239
Line_2 | 0.14434 | 0.14434 | 0.14434 | 0.14434 | 0.14434 | 0.14434 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 0.42504 | 0.89452 | 0.092865 | -0.41421 | -0.88369 | -0.082032 | 1.9249 | 1.2702 | 1.191 | -1.9126 | -1.2579 | -1.1787 | -77.7799 | 162.2203 | 42.2201 | 102.2201 | -17.7797 | -137.7799 | 1.1827 | 0.93216 | 0.71675 | 1.1741 | 0.92238 | 0.70892 | -0.23213 | -142.9336 | 127.7616 | -5.5203e-06 | -142.8673 | 128.239

## LL_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.28867 | 1.7018 | 1.6008 | 0.28867 | 1.7018 | 1.6008 | 3.3333 | 19.6505 | 18.4849 | 3.3333 | 19.6505 | 18.4849 | -0.78509 | 19.6311 | -1.0159 | 0.82842 | -18.1252 | 2.3485 | -3.776 | 1.6514 | 14.4041 | 3.8251 | 0.057272 | -12.8922 | 102.2201 | -142.6862 | 27.9149 | -77.7799 | 37.3138 | -152.0851 | 1.157 | 1.0025 | 0.78117 | 1.1741 | 0.92238 | 0.70892 | 0.47457 | -137.8777 | 121.9492 | -5.5203e-06 | -142.8673 | 128.239
Line_1 | 0.14434 | 0.14434 | 0.14434 | 0.14434 | 0.14434 | 0.14434 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 0.42504 | 0.89452 | 0.092865 | -0.41421 | -0.88369 | -0.082032 | 1.9249 | 1.2702 | 1.191 | -1.9126 | -1.2579 | -1.1787 | -77.7799 | 162.2203 | 42.2201 | 102.2201 | -17.7797 | -137.7799 | 1.1827 | 0.93216 | 0.71675 | 1.1741 | 0.92238 | 0.70892 | -0.23213 | -142.9336 | 127.7616 | -5.5203e-06 | -142.8673 | 128.239
Line_2 | 0.14434 | 0.14434 | 0.14434 | 0.14434 | 0.14434 | 0.14434 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 0.42504 | 0.89452 | 0.092865 | -0.41421 | -0.88369 | -0.082032 | 1.9249 | 1.2702 | 1.191 | -1.9126 | -1.2579 | -1.1787 | -77.7799 | 162.2203 | 42.2201 | 102.2201 | -17.7797 | -137.7799 | 1.1827 | 0.93216 | 0.71675 | 1.1741 | 0.92238 | 0.70892 | -0.23213 | -142.9336 | 127.7616 | -5.5203e-06 | -142.8673 | 128.239

## LL_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 3.1191 | 3.1191 | 0 | 3.1191 | 3.1191 | 0 | 36.0161 | 36.0161 | 0 | 36.0161 | 36.0161 | -1.4211e-14 | 26.5997 | -7.1734 | 1.4211e-14 | -16.8865 | 16.8865 | -9.4739e-15 | -0.51586 | 11.9957 | 9.4739e-15 | 6.2558 | -6.2558 | 0 | -159.6723 | 20.3277 | 0 | 20.3277 | -159.6723 | 1 | 0.73869 | 0.38808 | 1 | 0.5 | 0.5 | 5.5618e-13 | -160.7833 | 141.207 | 5.9478e-13 | -180 | 180
Line_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3685e-15 | -2.3684e-15 | 2.3686e-15 | -4.737e-15 | 4.7369e-15 | 4.7369e-15 | 2.5293e-29 | -1.5877e-09 | 1.5877e-09 | -4.9174e-29 | 1.5877e-09 | -1.5877e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 6.1187e-13 | -180 | 180 | 5.9478e-13 | -180 | 180
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.3685e-15 | -2.3684e-15 | 2.3686e-15 | 4.737e-15 | 4.7369e-15 | -1.4433e-20 | 1.4211e-14 | -1.5877e-09 | 1.5877e-09 | -1.4211e-14 | 1.5877e-09 | -1.5877e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 5.7542e-13 | -180 | 180 | 5.9478e-13 | -180 | 180

## LL_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 3.1191 | 3.1191 | 0 | 3.1191 | 3.1191 | 0 | 36.0161 | 36.0161 | 0 | 36.0161 | 36.0161 | -1.4211e-14 | 26.5997 | -7.1734 | 1.4211e-14 | -16.8865 | 16.8865 | -9.4739e-15 | -0.51586 | 11.9957 | 9.4739e-15 | 6.2558 | -6.2558 | 0 | -159.6723 | 20.3277 | 0 | 20.3277 | -159.6723 | 1 | 0.73869 | 0.38808 | 1 | 0.5 | 0.5 | 5.5618e-13 | -160.7833 | 141.207 | 5.9478e-13 | -180 | 180
Line_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3685e-15 | -2.3684e-15 | 2.3686e-15 | -4.737e-15 | 4.7369e-15 | 4.7369e-15 | 2.5293e-29 | -1.5877e-09 | 1.5877e-09 | -4.9174e-29 | 1.5877e-09 | -1.5877e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 6.1187e-13 | -180 | 180 | 5.9478e-13 | -180 | 180
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.3685e-15 | -2.3684e-15 | 2.3686e-15 | 4.737e-15 | 4.7369e-15 | -1.4433e-20 | 1.4211e-14 | -1.5877e-09 | 1.5877e-09 | -1.4211e-14 | 1.5877e-09 | -1.5877e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 5.7542e-13 | -180 | 180 | 5.9478e-13 | -180 | 180

## LL_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 1.5183 | 1.5183 | 0 | 1.5183 | 1.5183 | 0 | 17.5318 | 17.5318 | 0 | 17.5318 | 17.5318 | -7.1054e-15 | 15.3932 | 0.73601 | 6.5133e-15 | -13.0917 | 1.5655 | -2.3685e-15 | 2.3135 | 11.9328 | 2.3685e-15 | -0.95344 | -10.5727 | 0 | -146.7238 | 33.2762 | 0 | 33.2762 | -146.7238 | 1 | 0.88788 | 0.68193 | 1 | 0.74872 | 0.60963 | 2.4839e-13 | -138.1765 | 119.7467 | 2.7696e-13 | -142.5584 | 131.6989
Line_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.9212e-16 | 4.7979e-10 | 8.2616e-10 | -5.9212e-16 | -4.7979e-10 | -8.2615e-10 | -2.3685e-15 | -1.0531e-09 | 4.5326e-10 | 2.3685e-15 | 1.0532e-09 | -4.5325e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.74872 | 0.60963 | 1 | 0.74872 | 0.60963 | 2.8624e-13 | -142.5584 | 131.6989 | 2.7696e-13 | -142.5584 | 131.6989
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.3685e-15 | 4.798e-10 | 8.2616e-10 | 2.3685e-15 | -4.798e-10 | -8.2616e-10 | 4.737e-15 | -1.0532e-09 | 4.5325e-10 | -4.737e-15 | 1.0532e-09 | -4.5326e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.74872 | 0.60963 | 1 | 0.74872 | 0.60963 | 2.6742e-13 | -142.5584 | 131.6989 | 2.7696e-13 | -142.5584 | 131.6989

## LL_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 1.5183 | 1.5183 | 0 | 1.5183 | 1.5183 | 0 | 17.5318 | 17.5318 | 0 | 17.5318 | 17.5318 | -7.1054e-15 | 15.3932 | 0.73601 | 6.5133e-15 | -13.0917 | 1.5655 | -2.3685e-15 | 2.3135 | 11.9328 | 2.3685e-15 | -0.95344 | -10.5727 | 0 | -146.7238 | 33.2762 | 0 | 33.2762 | -146.7238 | 1 | 0.88788 | 0.68193 | 1 | 0.74872 | 0.60963 | 2.4839e-13 | -138.1765 | 119.7467 | 2.7696e-13 | -142.5584 | 131.6989
Line_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.9212e-16 | 4.7979e-10 | 8.2616e-10 | -5.9212e-16 | -4.7979e-10 | -8.2615e-10 | -2.3685e-15 | -1.0531e-09 | 4.5326e-10 | 2.3685e-15 | 1.0532e-09 | -4.5325e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.74872 | 0.60963 | 1 | 0.74872 | 0.60963 | 2.8624e-13 | -142.5584 | 131.6989 | 2.7696e-13 | -142.5584 | 131.6989
Line_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.3685e-15 | 4.798e-10 | 8.2616e-10 | 2.3685e-15 | -4.798e-10 | -8.2616e-10 | 4.737e-15 | -1.0532e-09 | 4.5325e-10 | -4.737e-15 | 1.0532e-09 | -4.5326e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.74872 | 0.60963 | 1 | 0.74872 | 0.60963 | 2.6742e-13 | -142.5584 | 131.6989 | 2.7696e-13 | -142.5584 | 131.6989

## LG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 4.1633 | 0.28748 | 0.295 | 4.1626 | 0.28762 | 0.29371 | 48.0734 | 3.3196 | 3.4064 | 48.065 | 3.3211 | 3.3915 | 28.7081 | -0.17786 | -1.6122 | 2.8003e-10 | 1.5253 | 1.5071 | 15.1193 | -3.1912 | -3.6694 | -3.5427e-10 | 2.6883 | 5.1327 | -55.9517 | -19.0886 | -137.3554 | 124.0647 | 161.1888 | 42.5383 | 0.67493 | 0.96283 | 1.1766 | 0 | 0.93069 | 1.5773 | -28.1779 | -112.2787 | 108.9257 | 0 | -138.3815 | 116.1751
Line_1 | 0.14434 | 0.14434 | 0.14434 | 0.14238 | 0.14381 | 0.14686 | 1.6667 | 1.6667 | 1.6667 | 1.6441 | 1.6606 | 1.6958 | 0.010121 | 0.8006 | 0.738 | 1.3303e-11 | -0.76267 | -0.75353 | 0.012556 | 1.3467 | 2.5392 | -7.8499e-12 | -1.3442 | -2.5664 | -77.7797 | 162.22 | 42.2202 | 102.9337 | -18.8112 | -137.4617 | 0.0096766 | 0.94 | 1.5866 | 0 | 0.93069 | 1.5773 | -26.6509 | -138.5116 | 116.0139 | 0 | -138.3815 | 116.1751
Line_2 | 0.14434 | 0.14434 | 0.14434 | 0.14238 | 0.14381 | 0.14686 | 1.6667 | 1.6667 | 1.6667 | 1.6441 | 1.6606 | 1.6958 | 0.010121 | 0.8006 | 0.738 | 1.3303e-11 | -0.76267 | -0.75353 | 0.012556 | 1.3467 | 2.5392 | -7.8499e-12 | -1.3442 | -2.5664 | -77.7797 | 162.22 | 42.2202 | 102.9337 | -18.8112 | -137.4617 | 0.0096766 | 0.94 | 1.5866 | 0 | 0.93069 | 1.5773 | -26.6509 | -138.5116 | 116.0139 | 0 | -138.3815 | 116.1751

## LG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 4.1633 | 0.28748 | 0.295 | 4.1626 | 0.28762 | 0.29371 | 48.0734 | 3.3196 | 3.4064 | 48.065 | 3.3211 | 3.3915 | 28.7081 | -0.17786 | -1.6122 | 2.8003e-10 | 1.5253 | 1.5071 | 15.1193 | -3.1912 | -3.6694 | -3.5427e-10 | 2.6883 | 5.1327 | -55.9517 | -19.0886 | -137.3554 | 124.0647 | 161.1888 | 42.5383 | 0.67493 | 0.96283 | 1.1766 | 0 | 0.93069 | 1.5773 | -28.1779 | -112.2787 | 108.9257 | 0 | -138.3815 | 116.1751
Line_1 | 0.14434 | 0.14434 | 0.14434 | 0.14238 | 0.14381 | 0.14686 | 1.6667 | 1.6667 | 1.6667 | 1.6441 | 1.6606 | 1.6958 | 0.010121 | 0.8006 | 0.738 | 1.3303e-11 | -0.76267 | -0.75353 | 0.012556 | 1.3467 | 2.5392 | -7.8499e-12 | -1.3442 | -2.5664 | -77.7797 | 162.22 | 42.2202 | 102.9337 | -18.8112 | -137.4617 | 0.0096766 | 0.94 | 1.5866 | 0 | 0.93069 | 1.5773 | -26.6509 | -138.5116 | 116.0139 | 0 | -138.3815 | 116.1751
Line_2 | 0.14434 | 0.14434 | 0.14434 | 0.14238 | 0.14381 | 0.14686 | 1.6667 | 1.6667 | 1.6667 | 1.6441 | 1.6606 | 1.6958 | 0.010121 | 0.8006 | 0.738 | 1.3303e-11 | -0.76267 | -0.75353 | 0.012556 | 1.3467 | 2.5392 | -7.8499e-12 | -1.3442 | -2.5664 | -77.7797 | 162.22 | 42.2202 | 102.9337 | -18.8112 | -137.4617 | 0.0096766 | 0.94 | 1.5866 | 0 | 0.93069 | 1.5773 | -26.6509 | -138.5116 | 116.0139 | 0 | -138.3815 | 116.1751

## LG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.102 | 0.2886 | 0.29047 | 1.1019 | 0.28858 | 0.29011 | 12.7253 | 3.3325 | 3.3541 | 12.7232 | 3.3323 | 3.3499 | 10.5279 | -0.62573 | -1.0415 | -8.2825 | 1.0861 | 0.97572 | 7.3636 | -3.5823 | -3.7785 | -6.415 | 3.5174 | 4.2405 | -41.4753 | -18.1825 | -137.5941 | 138.5446 | 161.9017 | 42.3618 | 1.0096 | 1.0913 | 1.1685 | 0.8234 | 1.1047 | 1.2989 | -6.505 | -118.0904 | 116.996 | -3.697 | -125.2589 | 119.4039
Line_1 | 0.14434 | 0.14434 | 0.14434 | 0.14367 | 0.14429 | 0.14506 | 1.6667 | 1.6667 | 1.6667 | 1.6589 | 1.6661 | 1.675 | 0.38697 | 0.56392 | 0.49121 | -0.37867 | -0.54307 | -0.48786 | 1.3321 | 1.7683 | 2.1234 | -1.3124 | -1.7587 | -2.1203 | -77.7798 | 162.2201 | 42.2202 | 102.397 | -18.0983 | -137.6382 | 0.83228 | 1.1136 | 1.3077 | 0.8234 | 1.1047 | 1.2989 | -3.9785 | -125.468 | 119.195 | -3.697 | -125.2589 | 119.4039
Line_2 | 0.14434 | 0.14434 | 0.14434 | 0.14367 | 0.14429 | 0.14506 | 1.6667 | 1.6667 | 1.6667 | 1.6589 | 1.6661 | 1.675 | 0.38697 | 0.56392 | 0.49121 | -0.37867 | -0.54307 | -0.48786 | 1.3321 | 1.7683 | 2.1234 | -1.3124 | -1.7587 | -2.1203 | -77.7798 | 162.2201 | 42.2202 | 102.397 | -18.0983 | -137.6382 | 0.83228 | 1.1136 | 1.3077 | 0.8234 | 1.1047 | 1.2989 | -3.9785 | -125.468 | 119.195 | -3.697 | -125.2589 | 119.4039

## LG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.102 | 0.2886 | 0.29047 | 1.1019 | 0.28858 | 0.29011 | 12.7253 | 3.3325 | 3.3541 | 12.7232 | 3.3323 | 3.3499 | 10.5279 | -0.62573 | -1.0415 | -8.2825 | 1.0861 | 0.97572 | 7.3636 | -3.5823 | -3.7785 | -6.415 | 3.5174 | 4.2405 | -41.4753 | -18.1825 | -137.5941 | 138.5446 | 161.9017 | 42.3618 | 1.0096 | 1.0913 | 1.1685 | 0.8234 | 1.1047 | 1.2989 | -6.505 | -118.0904 | 116.996 | -3.697 | -125.2589 | 119.4039
Line_1 | 0.14434 | 0.14434 | 0.14434 | 0.14367 | 0.14429 | 0.14506 | 1.6667 | 1.6667 | 1.6667 | 1.6589 | 1.6661 | 1.675 | 0.38697 | 0.56392 | 0.49121 | -0.37867 | -0.54307 | -0.48786 | 1.3321 | 1.7683 | 2.1234 | -1.3124 | -1.7587 | -2.1203 | -77.7798 | 162.2201 | 42.2202 | 102.397 | -18.0983 | -137.6382 | 0.83228 | 1.1136 | 1.3077 | 0.8234 | 1.1047 | 1.2989 | -3.9785 | -125.468 | 119.195 | -3.697 | -125.2589 | 119.4039
Line_2 | 0.14434 | 0.14434 | 0.14434 | 0.14367 | 0.14429 | 0.14506 | 1.6667 | 1.6667 | 1.6667 | 1.6589 | 1.6661 | 1.675 | 0.38697 | 0.56392 | 0.49121 | -0.37867 | -0.54307 | -0.48786 | 1.3321 | 1.7683 | 2.1234 | -1.3124 | -1.7587 | -2.1203 | -77.7798 | 162.2201 | 42.2202 | 102.397 | -18.0983 | -137.6382 | 0.83228 | 1.1136 | 1.3077 | 0.8234 | 1.1047 | 1.2989 | -3.9785 | -125.468 | 119.195 | -3.697 | -125.2589 | 119.4039

## LG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 2.8299 | 0.0074751 | 0.0074751 | 2.8294 | 0.0059593 | 0.0059593 | 32.6772 | 0.086315 | 0.086315 | 32.6716 | 0.068812 | 0.068812 | 24.3023 | 0.073013 | -0.062898 | -9.7634e-11 | -0.053903 | 0.053808 | 6.9944 | -0.0036636 | -0.065947 | 1.2544e-11 | 0.036611 | 0.087635 | -40.3824 | -114.6203 | -114.6203 | 139.6468 | 64.6526 | 64.6526 | 0.7739 | 0.84695 | 1.0558 | 0 | 0.94694 | 1.4945 | -24.3261 | -117.4928 | 111.7352 | 0 | -149.5321 | 123.1025
Line_1 | 0 | 0 | 0 | 0.0029796 | 0.0029796 | 0.0029796 | 0 | 0 | 0 | 0.034406 | 0.034406 | 0.034406 | 8.0779e-13 | -2.6566e-10 | -2.722e-09 | 3.938e-14 | 0.026951 | -0.026904 | 3.3307e-12 | -1.7124e-09 | 2.9423e-10 | 9.589e-14 | -0.018306 | -0.043818 | 0 | 0 | 0 | -115.3474 | -115.3474 | -115.3474 | 0.00093492 | 0.94629 | 1.4951 | 0 | 0.94694 | 1.4945 | 76.3154 | -149.5727 | 123.0764 | 0 | -149.5321 | 123.1025
Line_2 | 0 | 0 | 0 | 0.0029796 | 0.0029796 | 0.0029796 | 0 | 0 | 0 | 0.034406 | 0.034406 | 0.034406 | 8.0778e-13 | -2.6564e-10 | -2.722e-09 | 3.938e-14 | 0.026951 | -0.026904 | 3.3307e-12 | -1.7124e-09 | 2.942e-10 | 9.589e-14 | -0.018306 | -0.043818 | 0 | 0 | 0 | -115.3474 | -115.3474 | -115.3474 | 0.00093492 | 0.94629 | 1.4951 | 0 | 0.94694 | 1.4945 | 76.3154 | -149.5727 | 123.0764 | 0 | -149.5321 | 123.1025

## LG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 2.8299 | 0.0074751 | 0.0074751 | 2.8294 | 0.0059593 | 0.0059593 | 32.6772 | 0.086315 | 0.086315 | 32.6716 | 0.068812 | 0.068812 | 24.3023 | 0.073013 | -0.062898 | -9.7634e-11 | -0.053903 | 0.053808 | 6.9944 | -0.0036636 | -0.065947 | 1.2544e-11 | 0.036611 | 0.087635 | -40.3824 | -114.6203 | -114.6203 | 139.6468 | 64.6526 | 64.6526 | 0.7739 | 0.84695 | 1.0558 | 0 | 0.94694 | 1.4945 | -24.3261 | -117.4928 | 111.7352 | 0 | -149.5321 | 123.1025
Line_1 | 0 | 0 | 0 | 0.0029796 | 0.0029796 | 0.0029796 | 0 | 0 | 0 | 0.034406 | 0.034406 | 0.034406 | 8.0779e-13 | -2.6566e-10 | -2.722e-09 | 3.938e-14 | 0.026951 | -0.026904 | 3.3307e-12 | -1.7124e-09 | 2.9423e-10 | 9.589e-14 | -0.018306 | -0.043818 | 0 | 0 | 0 | -115.3474 | -115.3474 | -115.3474 | 0.00093492 | 0.94629 | 1.4951 | 0 | 0.94694 | 1.4945 | 76.3154 | -149.5727 | 123.0764 | 0 | -149.5321 | 123.1025
Line_2 | 0 | 0 | 0 | 0.0029796 | 0.0029796 | 0.0029796 | 0 | 0 | 0 | 0.034406 | 0.034406 | 0.034406 | 8.0778e-13 | -2.6564e-10 | -2.722e-09 | 3.938e-14 | 0.026951 | -0.026904 | 3.3307e-12 | -1.7124e-09 | 2.942e-10 | 9.589e-14 | -0.018306 | -0.043818 | 0 | 0 | 0 | -115.3474 | -115.3474 | -115.3474 | 0.00093492 | 0.94629 | 1.4951 | 0 | 0.94694 | 1.4945 | 76.3154 | -149.5727 | 123.0764 | 0 | -149.5321 | 123.1025

## LG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.0368 | 0.0027386 | 0.0027386 | 1.0366 | 0.0021832 | 0.0021832 | 11.9717 | 0.031623 | 0.031623 | 11.9696 | 0.02521 | 0.02521 | 8.6189 | 0.029861 | -0.01866 | -5.3588 | -0.023229 | 0.015192 | 6.3231 | -0.00070754 | -0.026117 | -5.3807 | 0.004883 | 0.025629 | -43.4024 | -117.6403 | -117.6403 | 136.6268 | 61.6326 | 61.6326 | 0.89291 | 0.94457 | 1.015 | 0.63444 | 0.94156 | 1.1818 | -7.1372 | -118.9976 | 116.8153 | 1.7434 | -130.2389 | 120.974
Line_1 | 0 | 0 | 0 | 0.0010916 | 0.0010916 | 0.0010916 | 0 | 0 | 0 | 0.012605 | 0.012605 | 0.012605 | 8.4917e-10 | 1.4771e-10 | -7.897e-10 | -0.0040119 | 0.011615 | -0.0075962 | 7.1978e-11 | -6.1396e-10 | 7.2749e-11 | 0.0069179 | -0.0024415 | -0.012815 | 0 | 0 | 0 | -118.3674 | -118.3674 | -118.3674 | 0.63455 | 0.94125 | 1.1821 | 0.63444 | 0.94156 | 1.1818 | 1.7727 | -130.2472 | 120.9617 | 1.7434 | -130.2389 | 120.974
Line_2 | 0 | 0 | 0 | 0.0010916 | 0.0010916 | 0.0010916 | 0 | 0 | 0 | 0.012605 | 0.012605 | 0.012605 | 8.4917e-10 | 1.4771e-10 | -7.897e-10 | -0.0040119 | 0.011615 | -0.0075962 | 7.1981e-11 | -6.1396e-10 | 7.2755e-11 | 0.0069179 | -0.0024415 | -0.012815 | 0 | 0 | 0 | -118.3674 | -118.3674 | -118.3674 | 0.63455 | 0.94125 | 1.1821 | 0.63444 | 0.94156 | 1.1818 | 1.7727 | -130.2472 | 120.9617 | 1.7434 | -130.2389 | 120.974

## LG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.0368 | 0.0027386 | 0.0027386 | 1.0366 | 0.0021832 | 0.0021832 | 11.9717 | 0.031623 | 0.031623 | 11.9696 | 0.02521 | 0.02521 | 8.6189 | 0.029861 | -0.01866 | -5.3588 | -0.023229 | 0.015192 | 6.3231 | -0.00070754 | -0.026117 | -5.3807 | 0.004883 | 0.025629 | -43.4024 | -117.6403 | -117.6403 | 136.6268 | 61.6326 | 61.6326 | 0.89291 | 0.94457 | 1.015 | 0.63444 | 0.94156 | 1.1818 | -7.1372 | -118.9976 | 116.8153 | 1.7434 | -130.2389 | 120.974
Line_1 | 0 | 0 | 0 | 0.0010916 | 0.0010916 | 0.0010916 | 0 | 0 | 0 | 0.012605 | 0.012605 | 0.012605 | 8.4917e-10 | 1.4771e-10 | -7.897e-10 | -0.0040119 | 0.011615 | -0.0075962 | 7.1978e-11 | -6.1396e-10 | 7.2749e-11 | 0.0069179 | -0.0024415 | -0.012815 | 0 | 0 | 0 | -118.3674 | -118.3674 | -118.3674 | 0.63455 | 0.94125 | 1.1821 | 0.63444 | 0.94156 | 1.1818 | 1.7727 | -130.2472 | 120.9617 | 1.7434 | -130.2389 | 120.974
Line_2 | 0 | 0 | 0 | 0.0010916 | 0.0010916 | 0.0010916 | 0 | 0 | 0 | 0.012605 | 0.012605 | 0.012605 | 8.4917e-10 | 1.4771e-10 | -7.897e-10 | -0.0040119 | 0.011615 | -0.0075962 | 7.1981e-11 | -6.1396e-10 | 7.2755e-11 | 0.0069179 | -0.0024415 | -0.012815 | 0 | 0 | 0 | -118.3674 | -118.3674 | -118.3674 | 0.63455 | 0.94125 | 1.1821 | 0.63444 | 0.94156 | 1.1818 | 1.7727 | -130.2472 | 120.9617 | 1.7434 | -130.2389 | 120.974

## LLG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.29404 | 5.0866 | 2.8833 | 0.29288 | 5.0867 | 2.8824 | 3.3952 | 58.7347 | 33.2931 | 3.3819 | 58.7356 | 33.2825 | -1.1694 | 33.6739 | -0.71306 | 1.9576 | 1.9346e-10 | 1.2193e-10 | -3.2793 | 7.4688 | 16.1089 | 4.3176 | -1.1592e-10 | -3.4492e-11 | 101.7631 | 176.3509 | 41.0626 | -78.1594 | -3.6354 | -138.9536 | 1.0254 | 0.58726 | 0.48433 | 1.4018 | 0 | 0 | -7.8638 | -171.1435 | 133.5971 | -12.5493 | 0 | 0
Line_1 | 0.14434 | 0.14434 | 0.14434 | 0.14644 | 0.14415 | 0.14245 | 1.6667 | 1.6667 | 1.6667 | 1.6909 | 1.6645 | 1.6449 | 0.99033 | 0.010533 | 0.010471 | -0.97881 | 6.0886e-12 | 6.0066e-12 | 2.1336 | 0.012884 | 0.011736 | -2.1588 | -1.9432e-12 | -1.7716e-12 | -77.7799 | 162.2203 | 42.22 | 101.8406 | -16.8639 | -138.3164 | 1.4114 | 0.009985 | 0.0094365 | 1.4018 | 0 | 0 | -12.6785 | -147.0471 | 90.4805 | -12.5493 | 0 | 0
Line_2 | 0.14434 | 0.14434 | 0.14434 | 0.14644 | 0.14415 | 0.14245 | 1.6667 | 1.6667 | 1.6667 | 1.6909 | 1.6645 | 1.6449 | 0.99033 | 0.010533 | 0.010471 | -0.97881 | 6.0886e-12 | 6.0066e-12 | 2.1336 | 0.012884 | 0.011736 | -2.1588 | -1.9432e-12 | -1.7716e-12 | -77.7799 | 162.2203 | 42.22 | 101.8406 | -16.8639 | -138.3164 | 1.4114 | 0.009985 | 0.0094365 | 1.4018 | 0 | 0 | -12.6785 | -147.0471 | 90.4805 | -12.5493 | 0 | 0

## LLG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.29404 | 5.0866 | 2.8833 | 0.29288 | 5.0867 | 2.8824 | 3.3952 | 58.7347 | 33.2931 | 3.3819 | 58.7356 | 33.2825 | -1.1694 | 33.6739 | -0.71306 | 1.9576 | 1.9346e-10 | 1.2193e-10 | -3.2793 | 7.4688 | 16.1089 | 4.3176 | -1.1592e-10 | -3.4492e-11 | 101.7631 | 176.3509 | 41.0626 | -78.1594 | -3.6354 | -138.9536 | 1.0254 | 0.58726 | 0.48433 | 1.4018 | 0 | 0 | -7.8638 | -171.1435 | 133.5971 | -12.5493 | 0 | 0
Line_1 | 0.14434 | 0.14434 | 0.14434 | 0.14644 | 0.14415 | 0.14245 | 1.6667 | 1.6667 | 1.6667 | 1.6909 | 1.6645 | 1.6449 | 0.99033 | 0.010533 | 0.010471 | -0.97881 | 6.0886e-12 | 6.0066e-12 | 2.1336 | 0.012884 | 0.011736 | -2.1588 | -1.9432e-12 | -1.7716e-12 | -77.7799 | 162.2203 | 42.22 | 101.8406 | -16.8639 | -138.3164 | 1.4114 | 0.009985 | 0.0094365 | 1.4018 | 0 | 0 | -12.6785 | -147.0471 | 90.4805 | -12.5493 | 0 | 0
Line_2 | 0.14434 | 0.14434 | 0.14434 | 0.14644 | 0.14415 | 0.14245 | 1.6667 | 1.6667 | 1.6667 | 1.6909 | 1.6645 | 1.6449 | 0.99033 | 0.010533 | 0.010471 | -0.97881 | 6.0886e-12 | 6.0066e-12 | 2.1336 | 0.012884 | 0.011736 | -2.1588 | -1.9432e-12 | -1.7716e-12 | -77.7799 | 162.2203 | 42.22 | 101.8406 | -16.8639 | -138.3164 | 1.4114 | 0.009985 | 0.0094365 | 1.4018 | 0 | 0 | -12.6785 | -147.0471 | 90.4805 | -12.5493 | 0 | 0

## LLG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.2904 | 1.2277 | 0.99889 | 0.29003 | 1.2279 | 0.99849 | 3.3533 | 14.1766 | 11.5342 | 3.349 | 14.1788 | 11.5295 | -0.89725 | 12.0141 | 7.7183 | 1.206 | -9.9987 | -6.9456 | -3.6054 | 7.6924 | 7.4855 | 3.963 | -8.0181 | -5.5067 | 102.0465 | -163.5159 | 72.1592 | -77.9228 | 16.5009 | -107.8438 | 1.108 | 1.0063 | 0.93219 | 1.2369 | 0.90393 | 0.76878 | -1.9285 | -130.8852 | 116.282 | -4.8488 | -124.7726 | 110.5646
Line_1 | 0.14434 | 0.14434 | 0.14434 | 0.14501 | 0.14431 | 0.14369 | 1.6667 | 1.6667 | 1.6667 | 1.6745 | 1.6664 | 1.6592 | 0.61616 | 0.45104 | 0.48354 | -0.603 | -0.44786 | -0.46736 | 1.983 | 1.4533 | 1.203 | -1.9815 | -1.4382 | -1.1868 | -77.7799 | 162.2202 | 42.2201 | 102.0772 | -17.4755 | -137.9413 | 1.2459 | 0.91299 | 0.77791 | 1.2369 | 0.90393 | 0.76878 | -5.0409 | -125.022 | 110.3226 | -4.8488 | -124.7726 | 110.5646
Line_2 | 0.14434 | 0.14434 | 0.14434 | 0.14501 | 0.14431 | 0.14369 | 1.6667 | 1.6667 | 1.6667 | 1.6745 | 1.6664 | 1.6592 | 0.61616 | 0.45104 | 0.48354 | -0.603 | -0.44786 | -0.46736 | 1.983 | 1.4533 | 1.203 | -1.9815 | -1.4382 | -1.1868 | -77.7799 | 162.2202 | 42.2201 | 102.0772 | -17.4755 | -137.9413 | 1.2459 | 0.91299 | 0.77791 | 1.2369 | 0.90393 | 0.76878 | -5.0409 | -125.022 | 110.3226 | -4.8488 | -124.7726 | 110.5646

## LLG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.2904 | 1.2277 | 0.99889 | 0.29003 | 1.2279 | 0.99849 | 3.3533 | 14.1766 | 11.5342 | 3.349 | 14.1788 | 11.5295 | -0.89725 | 12.0141 | 7.7183 | 1.206 | -9.9987 | -6.9456 | -3.6054 | 7.6924 | 7.4855 | 3.963 | -8.0181 | -5.5067 | 102.0465 | -163.5159 | 72.1592 | -77.9228 | 16.5009 | -107.8438 | 1.108 | 1.0063 | 0.93219 | 1.2369 | 0.90393 | 0.76878 | -1.9285 | -130.8852 | 116.282 | -4.8488 | -124.7726 | 110.5646
Line_1 | 0.14434 | 0.14434 | 0.14434 | 0.14501 | 0.14431 | 0.14369 | 1.6667 | 1.6667 | 1.6667 | 1.6745 | 1.6664 | 1.6592 | 0.61616 | 0.45104 | 0.48354 | -0.603 | -0.44786 | -0.46736 | 1.983 | 1.4533 | 1.203 | -1.9815 | -1.4382 | -1.1868 | -77.7799 | 162.2202 | 42.2201 | 102.0772 | -17.4755 | -137.9413 | 1.2459 | 0.91299 | 0.77791 | 1.2369 | 0.90393 | 0.76878 | -5.0409 | -125.022 | 110.3226 | -4.8488 | -124.7726 | 110.5646
Line_2 | 0.14434 | 0.14434 | 0.14434 | 0.14501 | 0.14431 | 0.14369 | 1.6667 | 1.6667 | 1.6667 | 1.6745 | 1.6664 | 1.6592 | 0.61616 | 0.45104 | 0.48354 | -0.603 | -0.44786 | -0.46736 | 1.983 | 1.4533 | 1.203 | -1.9815 | -1.4382 | -1.1868 | -77.7799 | 162.2202 | 42.2201 | 102.0772 | -17.4755 | -137.9413 | 1.2459 | 0.91299 | 0.77791 | 1.2369 | 0.90393 | 0.76878 | -5.0409 | -125.022 | 110.3226 | -4.8488 | -124.7726 | 110.5646

## LLG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.00545 | 3.9226 | 2.4904 | 0.0043448 | 3.9229 | 2.4897 | 0.062931 | 45.2941 | 28.7571 | 0.05017 | 45.2975 | 28.7485 | 0.0021943 | 30.34 | -0.11431 | -5.0242e-05 | -1.6983e-10 | -2.5907e-11 | -0.059921 | 1.8331 | 12.1337 | 0.066045 | -1.9365e-10 | -1.6159e-10 | 81.7197 | -170.3056 | 37.2235 | -99.0075 | 9.71 | -142.7952 | 0.9528 | 0.67106 | 0.42195 | 1.3164 | 0 | 0 | -6.1832 | -166.8481 | 127.7633 | -8.9639 | 0 | 0
Line_1 | 0 | 0 | 0 | 0.0021724 | 0.0021724 | 0.0021724 | 0 | 0 | 0 | 0.025085 | 0.025085 | 0.025085 | -1.5876e-09 | 2.1026e-12 | -2.2218e-12 | 2.512e-05 | -1.3175e-13 | 1.1388e-13 | -7.5462e-10 | 1.3486e-12 | 1.148e-12 | -0.033023 | 5.4662e-14 | 8.6141e-14 | 0 | 0 | 0 | 80.9925 | 80.9925 | 80.9925 | 1.3166 | 0.00068164 | 0.00068164 | 1.3164 | 0 | 0 | -8.993 | -87.3447 | -87.3447 | -8.9639 | 0 | 0
Line_2 | 0 | 0 | 0 | 0.0021724 | 0.0021724 | 0.0021724 | 0 | 0 | 0 | 0.025085 | 0.025085 | 0.025085 | -1.5876e-09 | 2.1026e-12 | -2.2218e-12 | 2.512e-05 | -1.3175e-13 | 1.1388e-13 | -7.546e-10 | 1.3486e-12 | 1.148e-12 | -0.033023 | 5.4662e-14 | 8.6141e-14 | 0 | 0 | 0 | 80.9925 | 80.9925 | 80.9925 | 1.3166 | 0.00068164 | 0.00068164 | 1.3164 | 0 | 0 | -8.993 | -87.3447 | -87.3447 | -8.9639 | 0 | 0

## LLG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.00545 | 3.9226 | 2.4904 | 0.0043448 | 3.9229 | 2.4897 | 0.062931 | 45.2941 | 28.7571 | 0.05017 | 45.2975 | 28.7485 | 0.0021943 | 30.34 | -0.11431 | -5.0242e-05 | -1.6983e-10 | -2.5907e-11 | -0.059921 | 1.8331 | 12.1337 | 0.066045 | -1.9365e-10 | -1.6159e-10 | 81.7197 | -170.3056 | 37.2235 | -99.0075 | 9.71 | -142.7952 | 0.9528 | 0.67106 | 0.42195 | 1.3164 | 0 | 0 | -6.1832 | -166.8481 | 127.7633 | -8.9639 | 0 | 0
Line_1 | 0 | 0 | 0 | 0.0021724 | 0.0021724 | 0.0021724 | 0 | 0 | 0 | 0.025085 | 0.025085 | 0.025085 | -1.5876e-09 | 2.1026e-12 | -2.2218e-12 | 2.512e-05 | -1.3175e-13 | 1.1388e-13 | -7.5462e-10 | 1.3486e-12 | 1.148e-12 | -0.033023 | 5.4662e-14 | 8.6141e-14 | 0 | 0 | 0 | 80.9925 | 80.9925 | 80.9925 | 1.3166 | 0.00068164 | 0.00068164 | 1.3164 | 0 | 0 | -8.993 | -87.3447 | -87.3447 | -8.9639 | 0 | 0
Line_2 | 0 | 0 | 0 | 0.0021724 | 0.0021724 | 0.0021724 | 0 | 0 | 0 | 0.025085 | 0.025085 | 0.025085 | -1.5876e-09 | 2.1026e-12 | -2.2218e-12 | 2.512e-05 | -1.3175e-13 | 1.1388e-13 | -7.546e-10 | 1.3486e-12 | 1.148e-12 | -0.033023 | 5.4662e-14 | 8.6141e-14 | 0 | 0 | 0 | 80.9925 | 80.9925 | 80.9925 | 1.3166 | 0.00068164 | 0.00068164 | 1.3164 | 0 | 0 | -8.993 | -87.3447 | -87.3447 | -8.9639 | 0 | 0

## LLG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.0024496 | 1.2103 | 0.96782 | 0.0019529 | 1.2106 | 0.96733 | 0.028286 | 13.9751 | 11.1754 | 0.02255 | 13.9783 | 11.1697 | 0.0083193 | 10.4505 | 5.6921 | -0.00643 | -7.3248 | -4.6699 | -0.026092 | 6.614 | 7.0663 | 0.024413 | -7.3438 | -4.6684 | 69.9296 | -164.1843 | 64.7098 | -110.7976 | 15.8354 | -115.2943 | 0.96821 | 0.88497 | 0.81194 | 1.1195 | 0.74202 | 0.59117 | -2.3861 | -131.8552 | 115.8573 | -6.0417 | -119.0905 | 109.6966
Line_1 | 0 | 0 | 0 | 0.00097643 | 0.00097643 | 0.00097643 | 0 | 0 | 0 | 0.011275 | 0.011275 | 0.011275 | -5.1354e-10 | 7.0103e-10 | 8.5152e-10 | 0.003215 | -0.0082787 | 0.0050688 | -4.3317e-10 | 4.3589e-11 | -3.8699e-10 | -0.012206 | 0.0012067 | 0.0043283 | 0 | 0 | 0 | 69.2024 | 69.2024 | 69.2024 | 1.1195 | 0.74231 | 0.5909 | 1.1195 | 0.74202 | 0.59117 | -6.0574 | -119.0824 | 109.7109 | -6.0417 | -119.0905 | 109.6966
Line_2 | 0 | 0 | 0 | 0.00097643 | 0.00097643 | 0.00097643 | 0 | 0 | 0 | 0.011275 | 0.011275 | 0.011275 | -5.1353e-10 | 7.0103e-10 | 8.5153e-10 | 0.003215 | -0.0082787 | 0.0050688 | -4.3317e-10 | 4.3589e-11 | -3.8699e-10 | -0.012206 | 0.0012067 | 0.0043283 | 0 | 0 | 0 | 69.2024 | 69.2024 | 69.2024 | 1.1195 | 0.74231 | 0.5909 | 1.1195 | 0.74202 | 0.59117 | -6.0574 | -119.0824 | 109.7109 | -6.0417 | -119.0905 | 109.6966

## LLG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.0024496 | 1.2103 | 0.96782 | 0.0019529 | 1.2106 | 0.96733 | 0.028286 | 13.9751 | 11.1754 | 0.02255 | 13.9783 | 11.1697 | 0.0083193 | 10.4505 | 5.6921 | -0.00643 | -7.3248 | -4.6699 | -0.026092 | 6.614 | 7.0663 | 0.024413 | -7.3438 | -4.6684 | 69.9296 | -164.1843 | 64.7098 | -110.7976 | 15.8354 | -115.2943 | 0.96821 | 0.88497 | 0.81194 | 1.1195 | 0.74202 | 0.59117 | -2.3861 | -131.8552 | 115.8573 | -6.0417 | -119.0905 | 109.6966
Line_1 | 0 | 0 | 0 | 0.00097643 | 0.00097643 | 0.00097643 | 0 | 0 | 0 | 0.011275 | 0.011275 | 0.011275 | -5.1354e-10 | 7.0103e-10 | 8.5152e-10 | 0.003215 | -0.0082787 | 0.0050688 | -4.3317e-10 | 4.3589e-11 | -3.8699e-10 | -0.012206 | 0.0012067 | 0.0043283 | 0 | 0 | 0 | 69.2024 | 69.2024 | 69.2024 | 1.1195 | 0.74231 | 0.5909 | 1.1195 | 0.74202 | 0.59117 | -6.0574 | -119.0824 | 109.7109 | -6.0417 | -119.0905 | 109.6966
Line_2 | 0 | 0 | 0 | 0.00097643 | 0.00097643 | 0.00097643 | 0 | 0 | 0 | 0.011275 | 0.011275 | 0.011275 | -5.1353e-10 | 7.0103e-10 | 8.5153e-10 | 0.003215 | -0.0082787 | 0.0050688 | -4.3317e-10 | 4.3589e-11 | -3.8699e-10 | -0.012206 | 0.0012067 | 0.0043283 | 0 | 0 | 0 | 69.2024 | 69.2024 | 69.2024 | 1.1195 | 0.74231 | 0.5909 | 1.1195 | 0.74202 | 0.59117 | -6.0574 | -119.0824 | 109.7109 | -6.0417 | -119.0905 | 109.6966