## LLL_max_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 3.6999 | 3.6999 | 0 | 0 | 128.1693 | 128.1693 | 35.5926 | -14.237 | 40.3839 | -16.1536 | -73.5107 | 106.4893 | 0.41999 | 0.168 | -24.9022 | -24.9022
Line_1 | 2.4666 | 2.4666 | 4.9647 | 0 | 85.4462 | 85.4462 | -1e-07 | 9.4914 | -1e-07 | 10.769 | 106.4893 | -73.5107 | 0 | 0.168 | 0 | -24.9022
Line_2 | 1.2333 | 1.2333 | 0 | 0 | 42.7231 | 42.7231 | -2.3728 | 4.7457 | -2.6923 | 5.3845 | 106.4893 | -73.5107 | 0.083999 | 0.168 | -24.9022 | -24.9022
Line_3 | 1.2333 | 1.2333 | 2.4824 | 0 | 42.7231 | 42.7231 | -1e-07 | 2.3728 | -1e-07 | 2.6923 | 106.4893 | -73.5107 | 0 | 0.083999 | 0 | -24.9022

## LLL_max_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 3.6999 | 3.6999 | 0 | 0 | 128.1693 | 128.1693 | 35.5926 | -14.237 | 40.3839 | -16.1536 | -73.5107 | 106.4893 | 0.41999 | 0.168 | -24.9022 | -24.9022
Line_1 | 2.4666 | 2.4666 | 4.9647 | 0 | 85.4462 | 85.4462 | -1e-07 | 9.4914 | -1e-07 | 10.769 | 106.4893 | -73.5107 | 0 | 0.168 | 0 | -24.9022
Line_2 | 1.2333 | 1.2333 | 0 | 0 | 42.7231 | 42.7231 | -2.3728 | 4.7457 | -2.6923 | 5.3845 | 106.4893 | -73.5107 | 0.083999 | 0.168 | -24.9022 | -24.9022
Line_3 | 1.2333 | 1.2333 | 2.4824 | 0 | 42.7231 | 42.7231 | -1e-07 | 2.3728 | -1e-07 | 2.6923 | 106.4893 | -73.5107 | 0 | 0.083999 | 0 | -24.9022

## LLL_max_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 1.2428 | 1.2428 | 0 | 0 | 43.0531 | 43.0531 | 27.1857 | -24.7761 | 27.7264 | -24.9923 | -54.2264 | 125.7736 | 0.90192 | 0.81741 | -8.6624 | -8.9775
Line_1 | 0.82856 | 0.82856 | 1.6677 | 0 | 28.7021 | 28.7021 | -15.4464 | 16.5174 | -15.4464 | 16.6616 | 125.7736 | -54.2264 | 0.76108 | 0.81741 | -9.2264 | -8.9775
Line_2 | 0.41428 | 0.41428 | 0 | 0 | 14.351 | 14.351 | -7.991 | 8.2587 | -8.027 | 8.3308 | 125.7736 | -54.2264 | 0.78924 | 0.81741 | -9.0975 | -8.9775
Line_3 | 0.41428 | 0.41428 | 0.83384 | 0 | 14.351 | 14.351 | -7.7232 | 7.991 | -7.7232 | 8.027 | 125.7736 | -54.2264 | 0.76108 | 0.78924 | -9.2264 | -9.0975

## LLL_max_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 1.2428 | 1.2428 | 0 | 0 | 43.0531 | 43.0531 | 27.1857 | -24.7761 | 27.7264 | -24.9923 | -54.2264 | 125.7736 | 0.90192 | 0.81741 | -8.6624 | -8.9775
Line_1 | 0.82856 | 0.82856 | 1.6677 | 0 | 28.7021 | 28.7021 | -15.4464 | 16.5174 | -15.4464 | 16.6616 | 125.7736 | -54.2264 | 0.76108 | 0.81741 | -9.2264 | -8.9775
Line_2 | 0.41428 | 0.41428 | 0 | 0 | 14.351 | 14.351 | -7.991 | 8.2587 | -8.027 | 8.3308 | 125.7736 | -54.2264 | 0.78924 | 0.81741 | -9.0975 | -8.9775
Line_3 | 0.41428 | 0.41428 | 0.83384 | 0 | 14.351 | 14.351 | -7.7232 | 7.991 | -7.7232 | 8.027 | 125.7736 | -54.2264 | 0.76108 | 0.78924 | -9.2264 | -9.0975

## LLL_min_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 3.0092 | 3.0092 | 0 | 0 | 104.2421 | 104.2421 | 45.2043 | -18.0817 | 26.7133 | -10.6853 | -62.3733 | 117.6267 | 0.50371 | 0.20148 | -31.7926 | -31.7926
Line_1 | 2.0061 | 2.0061 | 3.4722 | 0 | 69.4947 | 69.4947 | -1e-07 | 12.0545 | -1e-07 | 7.1235 | 117.6267 | -62.3733 | 0 | 0.20148 | 0 | -31.7926
Line_2 | 1.0031 | 1.0031 | 0 | 0 | 34.7474 | 34.7474 | -3.0136 | 6.0272 | -1.7809 | 3.5618 | 117.6267 | -62.3733 | 0.10074 | 0.20148 | -31.7926 | -31.7926
Line_3 | 1.0031 | 1.0031 | 1.7361 | 0 | 34.7474 | 34.7474 | -1e-07 | 3.0136 | -1e-07 | 1.7809 | 117.6267 | -62.3733 | 0 | 0.10074 | 0 | -31.7926

## LLL_min_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 3.0092 | 3.0092 | 0 | 0 | 104.2421 | 104.2421 | 45.2043 | -18.0817 | 26.7133 | -10.6853 | -62.3733 | 117.6267 | 0.50371 | 0.20148 | -31.7926 | -31.7926
Line_1 | 2.0061 | 2.0061 | 3.4722 | 0 | 69.4947 | 69.4947 | -1e-07 | 12.0545 | -1e-07 | 7.1235 | 117.6267 | -62.3733 | 0 | 0.20148 | 0 | -31.7926
Line_2 | 1.0031 | 1.0031 | 0 | 0 | 34.7474 | 34.7474 | -3.0136 | 6.0272 | -1.7809 | 3.5618 | 117.6267 | -62.3733 | 0.10074 | 0.20148 | -31.7926 | -31.7926
Line_3 | 1.0031 | 1.0031 | 1.7361 | 0 | 34.7474 | 34.7474 | -1e-07 | 3.0136 | -1e-07 | 1.7809 | 117.6267 | -62.3733 | 0 | 0.10074 | 0 | -31.7926

## LLL_min_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 1.0697 | 1.0697 | 0 | 0 | 37.0569 | 37.0569 | 22.8777 | -19.4502 | 20.541 | -18.5155 | -51.0933 | 128.9067 | 0.8297 | 0.72467 | -9.1739 | -7.5036
Line_1 | 0.71316 | 0.71316 | 1.2343 | 0 | 24.7046 | 24.7046 | -11.4434 | 12.9668 | -11.4434 | 12.3437 | 128.9067 | -51.0933 | 0.65508 | 0.72467 | -6.0933 | -7.5036
Line_2 | 0.35658 | 0.35658 | 0 | 0 | 12.3523 | 12.3523 | -6.1026 | 6.4834 | -5.9468 | 6.1718 | 128.9067 | -51.0933 | 0.68982 | 0.72467 | -6.834 | -7.5036
Line_3 | 0.35658 | 0.35658 | 0.61717 | 0 | 12.3523 | 12.3523 | -5.7217 | 6.1026 | -5.7217 | 5.9468 | 128.9067 | -51.0933 | 0.65508 | 0.68982 | -6.0933 | -6.834

## LLL_min_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 1.0697 | 1.0697 | 0 | 0 | 37.0569 | 37.0569 | 22.8777 | -19.4502 | 20.541 | -18.5155 | -51.0933 | 128.9067 | 0.8297 | 0.72467 | -9.1739 | -7.5036
Line_1 | 0.71316 | 0.71316 | 1.2343 | 0 | 24.7046 | 24.7046 | -11.4434 | 12.9668 | -11.4434 | 12.3437 | 128.9067 | -51.0933 | 0.65508 | 0.72467 | -6.0933 | -7.5036
Line_2 | 0.35658 | 0.35658 | 0 | 0 | 12.3523 | 12.3523 | -6.1026 | 6.4834 | -5.9468 | 6.1718 | 128.9067 | -51.0933 | 0.68982 | 0.72467 | -6.834 | -7.5036
Line_3 | 0.35658 | 0.35658 | 0.61717 | 0 | 12.3523 | 12.3523 | -5.7217 | 6.1026 | -5.7217 | 5.9468 | 128.9067 | -51.0933 | 0.65508 | 0.68982 | -6.0933 | -6.834

## LL_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 3.2042 | 3.2042 | 0 | 3.2042 | 3.2042 | 0 | 36.9993 | 36.9993 | 0 | 36.9993 | 36.9993 | 4.1685e-14 | 28.4108 | -10.6145 | -5.2106e-14 | -23.0719 | 15.9534 | -4.1685e-14 | 4.32 | 15.8719 | 3.6475e-14 | 1.7376 | -9.8143 | 0 | -163.5107 | 16.4893 | 0 | 16.4893 | -163.5107 | 1.1 | 0.7767 | 0.51607 | 1.1 | 0.62534 | 0.50624 | 8.9469e-13 | -154.8648 | 140.2623 | 8.8099e-13 | -167.8176 | 164.89
Line_1 | 0 | 2.1362 | 2.1362 | 0 | 2.1362 | 2.1362 | 0 | 24.6662 | 24.6662 | 0 | 24.6662 | 24.6662 | -2.6053e-14 | -13.0085 | 13.0085 | 1.5632e-14 | 15.3813 | -10.6356 | 5.2106e-15 | 3.8506 | -3.8506 | -1.0421e-14 | -1.1584 | 6.5429 | 0 | 16.4893 | -163.5107 | 0 | -163.5107 | 16.4893 | 1.1 | 0.55 | 0.55 | 1.1 | 0.62534 | 0.50624 | 8.7597e-13 | 180 | -180 | 8.8099e-13 | -167.8176 | 164.89
Line_2 | 0 | 1.0681 | 1.0681 | 0 | 1.0681 | 1.0681 | 0 | 12.3331 | 12.3331 | 0 | 12.3331 | 12.3331 | -2.0843e-14 | -7.0974 | 5.911 | 1.0421e-14 | 7.6906 | -5.3178 | 2.0843e-14 | 1.2523 | -2.5984 | -1.5632e-14 | -0.57919 | 3.2714 | 0 | 16.4893 | -163.5107 | 0 | -163.5107 | 16.4893 | 1.1 | 0.58437 | 0.52354 | 1.1 | 0.62534 | 0.50624 | 8.5956e-13 | -173.5168 | 172.7598 | 8.8099e-13 | -167.8176 | 164.89
Line_3 | 0 | 1.0681 | 1.0681 | 0 | 1.0681 | 1.0681 | 0 | 12.3331 | 12.3331 | 0 | 12.3331 | 12.3331 | -5.2106e-15 | -6.5042 | 6.5042 | -5.2106e-15 | 7.0974 | -5.911 | -1.0421e-14 | 1.9253 | -1.9253 | 1.0421e-14 | -1.2523 | 2.5984 | 0 | 16.4893 | -163.5107 | 0 | -163.5107 | 16.4893 | 1.1 | 0.55 | 0.55 | 1.1 | 0.58437 | 0.52354 | 8.7597e-13 | 180 | -180 | 8.5956e-13 | -173.5168 | 172.7598

## LL_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 3.2042 | 3.2042 | 0 | 3.2042 | 3.2042 | 0 | 36.9993 | 36.9993 | 0 | 36.9993 | 36.9993 | 4.1685e-14 | 28.4108 | -10.6145 | -5.2106e-14 | -23.0719 | 15.9534 | -4.1685e-14 | 4.32 | 15.8719 | 3.6475e-14 | 1.7376 | -9.8143 | 0 | -163.5107 | 16.4893 | 0 | 16.4893 | -163.5107 | 1.1 | 0.7767 | 0.51607 | 1.1 | 0.62534 | 0.50624 | 8.9469e-13 | -154.8648 | 140.2623 | 8.8099e-13 | -167.8176 | 164.89
Line_1 | 0 | 2.1362 | 2.1362 | 0 | 2.1362 | 2.1362 | 0 | 24.6662 | 24.6662 | 0 | 24.6662 | 24.6662 | -2.6053e-14 | -13.0085 | 13.0085 | 1.5632e-14 | 15.3813 | -10.6356 | 5.2106e-15 | 3.8506 | -3.8506 | -1.0421e-14 | -1.1584 | 6.5429 | 0 | 16.4893 | -163.5107 | 0 | -163.5107 | 16.4893 | 1.1 | 0.55 | 0.55 | 1.1 | 0.62534 | 0.50624 | 8.7597e-13 | 180 | -180 | 8.8099e-13 | -167.8176 | 164.89
Line_2 | 0 | 1.0681 | 1.0681 | 0 | 1.0681 | 1.0681 | 0 | 12.3331 | 12.3331 | 0 | 12.3331 | 12.3331 | -2.0843e-14 | -7.0974 | 5.911 | 1.0421e-14 | 7.6906 | -5.3178 | 2.0843e-14 | 1.2523 | -2.5984 | -1.5632e-14 | -0.57919 | 3.2714 | 0 | 16.4893 | -163.5107 | 0 | -163.5107 | 16.4893 | 1.1 | 0.58437 | 0.52354 | 1.1 | 0.62534 | 0.50624 | 8.5956e-13 | -173.5168 | 172.7598 | 8.8099e-13 | -167.8176 | 164.89
Line_3 | 0 | 1.0681 | 1.0681 | 0 | 1.0681 | 1.0681 | 0 | 12.3331 | 12.3331 | 0 | 12.3331 | 12.3331 | -5.2106e-15 | -6.5042 | 6.5042 | -5.2106e-15 | 7.0974 | -5.911 | -1.0421e-14 | 1.9253 | -1.9253 | 1.0421e-14 | -1.2523 | 2.5984 | 0 | 16.4893 | -163.5107 | 0 | -163.5107 | 16.4893 | 1.1 | 0.55 | 0.55 | 1.1 | 0.58437 | 0.52354 | 8.7597e-13 | 180 | -180 | 8.5956e-13 | -173.5168 | 172.7598

## LL_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 1.6287 | 1.6287 | 0 | 1.6287 | 1.6287 | 0 | 18.8063 | 18.8063 | 0 | 18.8063 | 18.8063 | 2.8659e-14 | 17.8002 | 0.06044 | -2.8659e-14 | -16.4209 | 1.3189 | -2.6053e-14 | 3.9189 | 14.5607 | 2.6053e-14 | -2.3539 | -12.9957 | 0 | -149.0411 | 30.9589 | 0 | 30.9589 | -149.0411 | 1.1 | 0.96917 | 0.77425 | 1.1 | 0.88208 | 0.69458 | 4.4602e-13 | -136.625 | 120.7211 | 4.3755e-13 | -140.8835 | 126.7539
Line_1 | 0 | 1.0858 | 1.0858 | 0 | 1.0858 | 1.0858 | 0 | 12.5375 | 12.5375 | 0 | 12.5375 | 12.5375 | -7.816e-15 | -10.3342 | 1.4923 | 7.816e-15 | 10.9473 | -0.87927 | -5.9205e-29 | -0.87368 | -7.9682 | -2.6053e-15 | 1.5692 | 8.6638 | 0 | 30.9589 | -149.0411 | 0 | -149.0411 | 30.9589 | 1.1 | 0.8272 | 0.6466 | 1.1 | 0.88208 | 0.69458 | 4.3401e-13 | -144.2087 | 131.5665 | 4.3755e-13 | -140.8835 | 126.7539
Line_2 | 0 | 0.54289 | 0.54289 | 0 | 0.54289 | 0.54289 | 0 | 6.2688 | 6.2688 | 0 | 6.2688 | 6.2688 | -2.6053e-15 | -5.3204 | 0.59289 | 5.2106e-15 | 5.4736 | -0.43963 | 7.816e-15 | -0.61073 | -4.158 | -7.816e-15 | 0.78462 | 4.3319 | 0 | 30.9589 | -149.0411 | 0 | -149.0411 | 30.9589 | 1.1 | 0.85428 | 0.67 | 1.1 | 0.88208 | 0.69458 | 4.2559e-13 | -142.4927 | 129.0741 | 4.3755e-13 | -140.8835 | 126.7539
Line_3 | 0 | 0.54289 | 0.54289 | 0 | 0.54289 | 0.54289 | 0 | 6.2688 | 6.2688 | 0 | 6.2688 | 6.2688 | -5.2106e-15 | -5.1671 | 0.74615 | 2.6053e-15 | 5.3204 | -0.59289 | -7.816e-15 | -0.43684 | -3.9841 | 5.2106e-15 | 0.61073 | 4.158 | 0 | 30.9589 | -149.0411 | 0 | -149.0411 | 30.9589 | 1.1 | 0.8272 | 0.6466 | 1.1 | 0.85428 | 0.67 | 4.3401e-13 | -144.2087 | 131.5665 | 4.2559e-13 | -142.4927 | 129.0741

## LL_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 1.6287 | 1.6287 | 0 | 1.6287 | 1.6287 | 0 | 18.8063 | 18.8063 | 0 | 18.8063 | 18.8063 | 2.8659e-14 | 17.8002 | 0.06044 | -2.8659e-14 | -16.4209 | 1.3189 | -2.6053e-14 | 3.9189 | 14.5607 | 2.6053e-14 | -2.3539 | -12.9957 | 0 | -149.0411 | 30.9589 | 0 | 30.9589 | -149.0411 | 1.1 | 0.96917 | 0.77425 | 1.1 | 0.88208 | 0.69458 | 4.4602e-13 | -136.625 | 120.7211 | 4.3755e-13 | -140.8835 | 126.7539
Line_1 | 0 | 1.0858 | 1.0858 | 0 | 1.0858 | 1.0858 | 0 | 12.5375 | 12.5375 | 0 | 12.5375 | 12.5375 | -7.816e-15 | -10.3342 | 1.4923 | 7.816e-15 | 10.9473 | -0.87927 | -5.9205e-29 | -0.87368 | -7.9682 | -2.6053e-15 | 1.5692 | 8.6638 | 0 | 30.9589 | -149.0411 | 0 | -149.0411 | 30.9589 | 1.1 | 0.8272 | 0.6466 | 1.1 | 0.88208 | 0.69458 | 4.3401e-13 | -144.2087 | 131.5665 | 4.3755e-13 | -140.8835 | 126.7539
Line_2 | 0 | 0.54289 | 0.54289 | 0 | 0.54289 | 0.54289 | 0 | 6.2688 | 6.2688 | 0 | 6.2688 | 6.2688 | -2.6053e-15 | -5.3204 | 0.59289 | 5.2106e-15 | 5.4736 | -0.43963 | 7.816e-15 | -0.61073 | -4.158 | -7.816e-15 | 0.78462 | 4.3319 | 0 | 30.9589 | -149.0411 | 0 | -149.0411 | 30.9589 | 1.1 | 0.85428 | 0.67 | 1.1 | 0.88208 | 0.69458 | 4.2559e-13 | -142.4927 | 129.0741 | 4.3755e-13 | -140.8835 | 126.7539
Line_3 | 0 | 0.54289 | 0.54289 | 0 | 0.54289 | 0.54289 | 0 | 6.2688 | 6.2688 | 0 | 6.2688 | 6.2688 | -5.2106e-15 | -5.1671 | 0.74615 | 2.6053e-15 | 5.3204 | -0.59289 | -7.816e-15 | -0.43684 | -3.9841 | 5.2106e-15 | 0.61073 | 4.158 | 0 | 30.9589 | -149.0411 | 0 | -149.0411 | 30.9589 | 1.1 | 0.8272 | 0.6466 | 1.1 | 0.85428 | 0.67 | 4.3401e-13 | -144.2087 | 131.5665 | 4.2559e-13 | -142.4927 | 129.0741

## LL_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 2.6061 | 2.6061 | 0 | 2.6061 | 2.6061 | 0 | 30.0921 | 30.0921 | 0 | 30.0921 | 30.0921 | 7.1054e-15 | 24.6317 | -2.0295 | -9.4739e-15 | -17.851 | 8.8102 | 9.4739e-15 | -0.29866 | 13.6553 | -9.4739e-15 | 4.3057 | -9.6483 | 0 | -152.3733 | 27.6267 | 0 | 27.6267 | -152.3733 | 1 | 0.8186 | 0.45877 | 1 | 0.61023 | 0.43419 | 9.5796e-13 | -153.068 | 126.0805 | 9.6773e-13 | -165.934 | 160.0269
Line_1 | 0 | 1.7374 | 1.7374 | 0 | 1.7374 | 1.7374 | 0 | 20.0614 | 20.0614 | 0 | 20.0614 | 20.0614 | -2.4869e-14 | -8.8871 | 8.8871 | 1.7764e-14 | 11.9007 | -5.8735 | 2.3685e-15 | 4.6513 | -4.6513 | -4.737e-15 | -2.8704 | 6.4322 | 0 | 27.6267 | -152.3733 | 0 | -152.3733 | 27.6267 | 1 | 0.5 | 0.5 | 1 | 0.61023 | 0.43419 | 9.7457e-13 | -180 | 180 | 9.6773e-13 | -165.934 | 160.0269
Line_2 | 0 | 0.86868 | 0.86868 | 0 | 0.86868 | 0.86868 | 0 | 10.0307 | 10.0307 | 0 | 10.0307 | 10.0307 | -2.2501e-14 | -5.1969 | 3.6901 | 2.0132e-14 | 5.9503 | -2.9367 | 1.1842e-14 | 1.8804 | -2.7709 | -1.4211e-14 | -1.4352 | 3.2161 | 0 | 27.6267 | -152.3733 | 0 | -152.3733 | 27.6267 | 1 | 0.55098 | 0.46005 | 1 | 0.61023 | 0.43419 | 9.3067e-13 | -172.2653 | 170.7242 | 9.6773e-13 | -165.934 | 160.0269
Line_3 | 0 | 0.86868 | 0.86868 | 0 | 0.86868 | 0.86868 | 0 | 10.0307 | 10.0307 | 0 | 10.0307 | 10.0307 | -2.3685e-15 | -4.4435 | 4.4435 | -4.737e-15 | 5.1969 | -3.6901 | -9.4739e-15 | 2.3257 | -2.3257 | 9.4739e-15 | -1.8804 | 2.7709 | 0 | 27.6267 | -152.3733 | 0 | -152.3733 | 27.6267 | 1 | 0.5 | 0.5 | 1 | 0.55098 | 0.46005 | 9.7457e-13 | -180 | 180 | 9.3067e-13 | -172.2653 | 170.7242

## LL_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 2.6061 | 2.6061 | 0 | 2.6061 | 2.6061 | 0 | 30.0921 | 30.0921 | 0 | 30.0921 | 30.0921 | 7.1054e-15 | 24.6317 | -2.0295 | -9.4739e-15 | -17.851 | 8.8102 | 9.4739e-15 | -0.29866 | 13.6553 | -9.4739e-15 | 4.3057 | -9.6483 | 0 | -152.3733 | 27.6267 | 0 | 27.6267 | -152.3733 | 1 | 0.8186 | 0.45877 | 1 | 0.61023 | 0.43419 | 9.5796e-13 | -153.068 | 126.0805 | 9.6773e-13 | -165.934 | 160.0269
Line_1 | 0 | 1.7374 | 1.7374 | 0 | 1.7374 | 1.7374 | 0 | 20.0614 | 20.0614 | 0 | 20.0614 | 20.0614 | -2.4869e-14 | -8.8871 | 8.8871 | 1.7764e-14 | 11.9007 | -5.8735 | 2.3685e-15 | 4.6513 | -4.6513 | -4.737e-15 | -2.8704 | 6.4322 | 0 | 27.6267 | -152.3733 | 0 | -152.3733 | 27.6267 | 1 | 0.5 | 0.5 | 1 | 0.61023 | 0.43419 | 9.7457e-13 | -180 | 180 | 9.6773e-13 | -165.934 | 160.0269
Line_2 | 0 | 0.86868 | 0.86868 | 0 | 0.86868 | 0.86868 | 0 | 10.0307 | 10.0307 | 0 | 10.0307 | 10.0307 | -2.2501e-14 | -5.1969 | 3.6901 | 2.0132e-14 | 5.9503 | -2.9367 | 1.1842e-14 | 1.8804 | -2.7709 | -1.4211e-14 | -1.4352 | 3.2161 | 0 | 27.6267 | -152.3733 | 0 | -152.3733 | 27.6267 | 1 | 0.55098 | 0.46005 | 1 | 0.61023 | 0.43419 | 9.3067e-13 | -172.2653 | 170.7242 | 9.6773e-13 | -165.934 | 160.0269
Line_3 | 0 | 0.86868 | 0.86868 | 0 | 0.86868 | 0.86868 | 0 | 10.0307 | 10.0307 | 0 | 10.0307 | 10.0307 | -2.3685e-15 | -4.4435 | 4.4435 | -4.737e-15 | 5.1969 | -3.6901 | -9.4739e-15 | 2.3257 | -2.3257 | 9.4739e-15 | -1.8804 | 2.7709 | 0 | 27.6267 | -152.3733 | 0 | -152.3733 | 27.6267 | 1 | 0.5 | 0.5 | 1 | 0.55098 | 0.46005 | 9.7457e-13 | -180 | 180 | 9.3067e-13 | -172.2653 | 170.7242

## LL_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 1.3721 | 1.3721 | 0 | 1.3721 | 1.3721 | 0 | 15.8432 | 15.8432 | 0 | 15.8432 | 15.8432 | 7.1054e-15 | 14.2512 | 1.4266 | -7.6975e-15 | -12.3717 | 0.45296 | 6.3699e-29 | 1.9064 | 11.2087 | -6.9387e-29 | -0.79565 | -10.098 | 0 | -144.0449 | 35.9551 | 0 | 35.9551 | -144.0449 | 1 | 0.90753 | 0.71319 | 1 | 0.7825 | 0.63801 | 5.1365e-13 | -136.4258 | 118.7019 | 5.1648e-13 | -140.3651 | 128.5235
Line_1 | 0 | 0.9147 | 0.9147 | 0 | 0.9147 | 0.9147 | 0 | 10.5621 | 10.5621 | 0 | 10.5621 | 10.5621 | -1.2434e-14 | -7.4125 | 1.1373 | 1.1842e-14 | 8.2478 | -0.30197 | -1.1291e-28 | -0.036791 | -6.2383 | 2.3685e-15 | 0.53044 | 6.732 | 0 | 35.9551 | -144.0449 | 0 | -144.0449 | 35.9551 | 1 | 0.70181 | 0.60037 | 1 | 0.7825 | 0.63801 | 5.2027e-13 | -143.7605 | 136.2873 | 5.1648e-13 | -140.3651 | 128.5235
Line_2 | 0 | 0.45735 | 0.45735 | 0 | 0.45735 | 0.45735 | 0 | 5.2811 | 5.2811 | 0 | 5.2811 | 5.2811 | -1.3027e-14 | -3.9151 | 0.35982 | 1.2434e-14 | 4.1239 | -0.15099 | 4.737e-15 | -0.14181 | -3.2426 | -7.1054e-15 | 0.26522 | 3.366 | 0 | 35.9551 | -144.0449 | 0 | -144.0449 | 35.9551 | 1 | 0.74183 | 0.61777 | 1 | 0.7825 | 0.63801 | 4.9456e-13 | -141.9705 | 132.2872 | 5.1648e-13 | -140.3651 | 128.5235
Line_3 | 0 | 0.45735 | 0.45735 | 0 | 0.45735 | 0.45735 | 0 | 5.2811 | 5.2811 | 0 | 5.2811 | 5.2811 | 1.1842e-15 | -3.7062 | 0.56866 | -1.1842e-15 | 3.9151 | -0.35982 | -7.1054e-15 | -0.018396 | -3.1192 | 9.4739e-15 | 0.14181 | 3.2426 | 0 | 35.9551 | -144.0449 | 0 | -144.0449 | 35.9551 | 1 | 0.70181 | 0.60037 | 1 | 0.74183 | 0.61777 | 5.2027e-13 | -143.7605 | 136.2873 | 4.9456e-13 | -141.9705 | 132.2872

## LL_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 1.3721 | 1.3721 | 0 | 1.3721 | 1.3721 | 0 | 15.8432 | 15.8432 | 0 | 15.8432 | 15.8432 | 7.1054e-15 | 14.2512 | 1.4266 | -7.6975e-15 | -12.3717 | 0.45296 | 6.3699e-29 | 1.9064 | 11.2087 | -6.9387e-29 | -0.79565 | -10.098 | 0 | -144.0449 | 35.9551 | 0 | 35.9551 | -144.0449 | 1 | 0.90753 | 0.71319 | 1 | 0.7825 | 0.63801 | 5.1365e-13 | -136.4258 | 118.7019 | 5.1648e-13 | -140.3651 | 128.5235
Line_1 | 0 | 0.9147 | 0.9147 | 0 | 0.9147 | 0.9147 | 0 | 10.5621 | 10.5621 | 0 | 10.5621 | 10.5621 | -1.2434e-14 | -7.4125 | 1.1373 | 1.1842e-14 | 8.2478 | -0.30197 | -1.1291e-28 | -0.036791 | -6.2383 | 2.3685e-15 | 0.53044 | 6.732 | 0 | 35.9551 | -144.0449 | 0 | -144.0449 | 35.9551 | 1 | 0.70181 | 0.60037 | 1 | 0.7825 | 0.63801 | 5.2027e-13 | -143.7605 | 136.2873 | 5.1648e-13 | -140.3651 | 128.5235
Line_2 | 0 | 0.45735 | 0.45735 | 0 | 0.45735 | 0.45735 | 0 | 5.2811 | 5.2811 | 0 | 5.2811 | 5.2811 | -1.3027e-14 | -3.9151 | 0.35982 | 1.2434e-14 | 4.1239 | -0.15099 | 4.737e-15 | -0.14181 | -3.2426 | -7.1054e-15 | 0.26522 | 3.366 | 0 | 35.9551 | -144.0449 | 0 | -144.0449 | 35.9551 | 1 | 0.74183 | 0.61777 | 1 | 0.7825 | 0.63801 | 4.9456e-13 | -141.9705 | 132.2872 | 5.1648e-13 | -140.3651 | 128.5235
Line_3 | 0 | 0.45735 | 0.45735 | 0 | 0.45735 | 0.45735 | 0 | 5.2811 | 5.2811 | 0 | 5.2811 | 5.2811 | 1.1842e-15 | -3.7062 | 0.56866 | -1.1842e-15 | 3.9151 | -0.35982 | -7.1054e-15 | -0.018396 | -3.1192 | 9.4739e-15 | 0.14181 | 3.2426 | 0 | 35.9551 | -144.0449 | 0 | -144.0449 | 35.9551 | 1 | 0.70181 | 0.60037 | 1 | 0.74183 | 0.61777 | 5.2027e-13 | -143.7605 | 136.2873 | 4.9456e-13 | -141.9705 | 132.2872

## LG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 3.0398 | 1.5199 | 1.5199 | 3.0398 | 1.5199 | 1.5199 | 35.1002 | 17.5501 | 17.5501 | 35.1004 | 17.55 | 17.55 | 10.3379 | -2.2075 | 24.7176 | -5.5389 | 3.4223 | -23.5239 | 9.837 | 12.3149 | -7.512 | -4.3732 | -10.9528 | 8.845 | -53.6331 | 126.3669 | 126.3669 | 126.3976 | -53.6946 | -53.6946 |  | 0.40656 | 0.71288 | 1.472 | 0.20106 | 0.65385 | 1.432 | -10.0552 | -133.4705 | 109.4622 | -15.31 | -126.3429 | 105.6991
Line_1 | 2.2285 | 0.81139 | 0.81139 | 2.2286 | 0.81137 | 0.81137 | 25.7329 | 9.3691 | 9.3691 | 25.7335 | 9.3689 | 9.3689 | 1.6208e-10 | 1.5336 | -12.664 | 4.0372 | -1.7111 | 12.4623 | -2.1816e-10 | -5.588 | 5.2318 | 3.2359 | 5.882 | -4.969 | 126.0233 | -52.6894 | -52.6894 | -54.0229 | 127.4373 | 127.4373 |  | 0 | 0.61849 | 1.4625 | 0.20106 | 0.65385 | 1.432 | 0 | -127.343 | 104.864 | -15.31 | -126.3429 | 105.6991
Line_2 | 0.81151 | 0.70882 | 0.70882 | 0.81142 | 0.70884 | 0.70884 | 9.3705 | 8.1847 | 8.1847 | 9.3694 | 8.185 | 8.185 | -1.6964 | 2.4458 | -10.345 | 1.5017 | -1.7112 | 11.0616 | -0.83338 | -4.672 | 4.2481 | 1.1373 | 5.0708 | -3.876 | 127.6557 | -55.1087 | -55.1087 | -52.4476 | 125.0097 | 125.0097 |  | 0.2017 | 0.64431 | 1.3664 | 0.20106 | 0.65385 | 1.432 | -26.1807 | -117.4766 | 102.5663 | -15.31 | -126.3429 | 105.6991
Line_3 | 1.4176 | 0.10721 | 0.10721 | 1.4176 | 0.1077 | 0.1077 | 16.3689 | 1.2379 | 1.2379 | 16.3692 | 1.2436 | 1.2436 | 1.0529e-10 | -0.0066664 | -1.421 | 2.8941 | -0.11897 | 1.2742 | -1.3712e-10 | -0.76562 | 1.1219 | 1.5891 | 0.79237 | -1.1241 | 125.1151 | -36.8441 | -36.8441 | -54.9507 | 143.9844 | 143.9844 |  | 0 | 0.61849 | 1.4625 | 0.2017 | 0.64431 | 1.3664 | 0 | -127.343 | 104.864 | -26.1807 | -117.4766 | 102.5663

## LG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 3.0398 | 1.5199 | 1.5199 | 3.0398 | 1.5199 | 1.5199 | 35.1002 | 17.5501 | 17.5501 | 35.1004 | 17.55 | 17.55 | 10.3379 | -2.2075 | 24.7176 | -5.5389 | 3.4223 | -23.5239 | 9.837 | 12.3149 | -7.512 | -4.3732 | -10.9528 | 8.845 | -53.6331 | 126.3669 | 126.3669 | 126.3976 | -53.6946 | -53.6946 |  | 0.40656 | 0.71288 | 1.472 | 0.20106 | 0.65385 | 1.432 | -10.0552 | -133.4705 | 109.4622 | -15.31 | -126.3429 | 105.6991
Line_1 | 2.2285 | 0.81139 | 0.81139 | 2.2286 | 0.81137 | 0.81137 | 25.7329 | 9.3691 | 9.3691 | 25.7335 | 9.3689 | 9.3689 | 1.6208e-10 | 1.5336 | -12.664 | 4.0372 | -1.7111 | 12.4623 | -2.1816e-10 | -5.588 | 5.2318 | 3.2359 | 5.882 | -4.969 | 126.0233 | -52.6894 | -52.6894 | -54.0229 | 127.4373 | 127.4373 |  | 0 | 0.61849 | 1.4625 | 0.20106 | 0.65385 | 1.432 | 0 | -127.343 | 104.864 | -15.31 | -126.3429 | 105.6991
Line_2 | 0.81151 | 0.70882 | 0.70882 | 0.81142 | 0.70884 | 0.70884 | 9.3705 | 8.1847 | 8.1847 | 9.3694 | 8.185 | 8.185 | -1.6964 | 2.4458 | -10.345 | 1.5017 | -1.7112 | 11.0616 | -0.83338 | -4.672 | 4.2481 | 1.1373 | 5.0708 | -3.876 | 127.6557 | -55.1087 | -55.1087 | -52.4476 | 125.0097 | 125.0097 |  | 0.2017 | 0.64431 | 1.3664 | 0.20106 | 0.65385 | 1.432 | -26.1807 | -117.4766 | 102.5663 | -15.31 | -126.3429 | 105.6991
Line_3 | 1.4176 | 0.10721 | 0.10721 | 1.4176 | 0.1077 | 0.1077 | 16.3689 | 1.2379 | 1.2379 | 16.3692 | 1.2436 | 1.2436 | 1.0529e-10 | -0.0066664 | -1.421 | 2.8941 | -0.11897 | 1.2742 | -1.3712e-10 | -0.76562 | 1.1219 | 1.5891 | 0.79237 | -1.1241 | 125.1151 | -36.8441 | -36.8441 | -54.9507 | 143.9844 | 143.9844 |  | 0 | 0.61849 | 1.4625 | 0.2017 | 0.64431 | 1.3664 | 0 | -127.343 | 104.864 | -26.1807 | -117.4766 | 102.5663

## LG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.86107 | 0.43053 | 0.43053 | 0.86107 | 0.43053 | 0.43053 | 9.9428 | 4.9714 | 4.9714 | 9.9428 | 4.9713 | 4.9713 | 6.3903 | -1.1948 | 5.7814 | -6.0082 | 1.2964 | -5.6867 | 6.3501 | 4.7862 | -1.6205 | -5.9087 | -4.6758 | 1.7233 | -47.437 | 132.563 | 132.563 | 132.5937 | -47.4984 | -47.4984 |  | 0.90607 | 0.9923 | 1.2078 | 0.84753 | 0.97604 | 1.1953 | -2.6177 | -123.4203 | 116.9056 | -2.8846 | -122.0025 | 115.6423
Line_1 | 0.63127 | 0.22984 | 0.22984 | 0.63129 | 0.22984 | 0.22984 | 7.2893 | 2.654 | 2.654 | 7.2895 | 2.6539 | 2.6539 | -4.0522 | 0.63288 | -3.0345 | 4.373 | -0.64261 | 3.017 | -4.1011 | -2.4847 | 0.99641 | 4.3641 | 2.5093 | -0.97978 | 132.2194 | -46.4933 | -46.4933 | -47.8267 | 133.6335 | 133.6335 |  | 0.79094 | 0.9661 | 1.2035 | 0.84753 | 0.97604 | 1.1953 | -2.437 | -122.203 | 115.3288 | -2.8846 | -122.0025 | 115.6423
Line_2 | 0.22987 | 0.20079 | 0.20079 | 0.22985 | 0.20079 | 0.20079 | 2.6544 | 2.3185 | 2.3185 | 2.6541 | 2.3185 | 2.3185 | -1.6537 | 0.71632 | -2.613 | 1.6353 | -0.65375 | 2.6697 | -1.5176 | -2.1334 | 0.76971 | 1.5446 | 2.1665 | -0.74356 | 133.8518 | -48.9125 | -48.9125 | -46.2515 | 131.2059 | 131.2059 |  | 0.84559 | 0.97065 | 1.1749 | 0.84753 | 0.97604 | 1.1953 | -3.6043 | -120.352 | 114.6741 | -2.8846 | -122.0025 | 115.6423
Line_3 | 0.40156 | 0.030369 | 0.030369 | 0.40156 | 0.030507 | 0.030507 | 4.6368 | 0.35067 | 0.35067 | 4.6369 | 0.35226 | 0.35226 | -2.536 | -0.0091938 | -0.34977 | 2.7652 | 0.0031782 | 0.33692 | -2.6493 | -0.33865 | 0.23613 | 2.7798 | 0.34191 | -0.24038 | 131.3113 | -30.6479 | -30.6479 | -48.7545 | 150.1806 | 150.1806 |  | 0.79094 | 0.9661 | 1.2035 | 0.84559 | 0.97065 | 1.1749 | -2.437 | -122.203 | 115.3288 | -3.6043 | -120.352 | 114.6741

## LG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.86107 | 0.43053 | 0.43053 | 0.86107 | 0.43053 | 0.43053 | 9.9428 | 4.9714 | 4.9714 | 9.9428 | 4.9713 | 4.9713 | 6.3903 | -1.1948 | 5.7814 | -6.0082 | 1.2964 | -5.6867 | 6.3501 | 4.7862 | -1.6205 | -5.9087 | -4.6758 | 1.7233 | -47.437 | 132.563 | 132.563 | 132.5937 | -47.4984 | -47.4984 |  | 0.90607 | 0.9923 | 1.2078 | 0.84753 | 0.97604 | 1.1953 | -2.6177 | -123.4203 | 116.9056 | -2.8846 | -122.0025 | 115.6423
Line_1 | 0.63127 | 0.22984 | 0.22984 | 0.63129 | 0.22984 | 0.22984 | 7.2893 | 2.654 | 2.654 | 7.2895 | 2.6539 | 2.6539 | -4.0522 | 0.63288 | -3.0345 | 4.373 | -0.64261 | 3.017 | -4.1011 | -2.4847 | 0.99641 | 4.3641 | 2.5093 | -0.97978 | 132.2194 | -46.4933 | -46.4933 | -47.8267 | 133.6335 | 133.6335 |  | 0.79094 | 0.9661 | 1.2035 | 0.84753 | 0.97604 | 1.1953 | -2.437 | -122.203 | 115.3288 | -2.8846 | -122.0025 | 115.6423
Line_2 | 0.22987 | 0.20079 | 0.20079 | 0.22985 | 0.20079 | 0.20079 | 2.6544 | 2.3185 | 2.3185 | 2.6541 | 2.3185 | 2.3185 | -1.6537 | 0.71632 | -2.613 | 1.6353 | -0.65375 | 2.6697 | -1.5176 | -2.1334 | 0.76971 | 1.5446 | 2.1665 | -0.74356 | 133.8518 | -48.9125 | -48.9125 | -46.2515 | 131.2059 | 131.2059 |  | 0.84559 | 0.97065 | 1.1749 | 0.84753 | 0.97604 | 1.1953 | -3.6043 | -120.352 | 114.6741 | -2.8846 | -122.0025 | 115.6423
Line_3 | 0.40156 | 0.030369 | 0.030369 | 0.40156 | 0.030507 | 0.030507 | 4.6368 | 0.35067 | 0.35067 | 4.6369 | 0.35226 | 0.35226 | -2.536 | -0.0091938 | -0.34977 | 2.7652 | 0.0031782 | 0.33692 | -2.6493 | -0.33865 | 0.23613 | 2.7798 | 0.34191 | -0.24038 | 131.3113 | -30.6479 | -30.6479 | -48.7545 | 150.1806 | 150.1806 |  | 0.79094 | 0.9661 | 1.2035 | 0.84559 | 0.97065 | 1.1749 | -2.437 | -122.203 | 115.3288 | -3.6043 | -120.352 | 114.6741

## LG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 2.3719 | 1.1859 | 1.1859 | 2.3719 | 1.1859 | 1.1859 | 27.388 | 13.694 | 13.694 | 27.3881 | 13.6939 | 13.6939 | 11.6344 | -0.21764 | 16.5925 | -6.0211 | 1.6325 | -15.1954 | 5.8789 | 9.7895 | -6.9436 | -2.5457 | -8.9633 | 7.7517 | -45.1315 | 134.8685 | 134.8685 | 134.8992 | -45.1929 | -45.1929 |  | 0.47595 | 0.71505 | 1.3135 | 0.23869 | 0.66531 | 1.2457 | -18.324 | -133.8579 | 112.1603 | -22.1823 | -124.8707 | 107.7795
Line_1 | 1.7148 | 0.65707 | 0.65707 | 1.7149 | 0.65707 | 0.65707 | 19.8014 | 7.5872 | 7.5872 | 19.8017 | 7.5872 | 7.5872 | -8.2228e-11 | 0.7378 | -8.4785 | 4.3433 | -0.836 | 8.3591 | 2.8711e-12 | -4.7617 | 4.6062 | 1.8641 | 4.9781 | -4.4104 | 134.639 | -44.5325 | -44.5325 | -45.4104 | 135.5963 | 135.5963 |  | 0 | 0.63509 | 1.2717 | 0.23869 | 0.66531 | 1.2457 | 0 | -125.7249 | 106.9532 | -22.1823 | -124.8707 | 107.7795
Line_2 | 0.65715 | 0.52898 | 0.52898 | 0.65709 | 0.529 | 0.529 | 7.5881 | 6.1082 | 6.1082 | 7.5875 | 6.1084 | 6.1084 | -1.7894 | 1.5187 | -6.1287 | 1.6778 | -0.7965 | 6.8363 | -0.45188 | -3.7802 | 3.5306 | 0.68166 | 3.9852 | -3.3413 | 135.8 | -46.2887 | -46.2887 | -44.2928 | 133.8267 | 133.8267 |  | 0.24322 | 0.66695 | 1.1579 | 0.23869 | 0.66531 | 1.2457 | -30.0274 | -114.4014 | 103.7657 | -22.1823 | -124.8707 | 107.7795
Line_3 | 1.0579 | 0.12927 | 0.12927 | 1.058 | 0.12945 | 0.12945 | 12.2161 | 1.4926 | 1.4926 | 12.2163 | 1.4947 | 1.4947 | -5.0747e-11 | 0.029687 | -1.5449 | 2.8547 | -0.2168 | 1.3399 | 1.1533e-12 | -0.9475 | 1.1031 | 0.82399 | 0.97304 | -1.0956 | 133.9411 | -37.5195 | -37.5195 | -46.1277 | 143.0378 | 143.0378 |  | 0 | 0.63509 | 1.2717 | 0.24322 | 0.66695 | 1.1579 | 0 | -125.7249 | 106.9532 | -30.0274 | -114.4014 | 103.7657

## LG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 2.3719 | 1.1859 | 1.1859 | 2.3719 | 1.1859 | 1.1859 | 27.388 | 13.694 | 13.694 | 27.3881 | 13.6939 | 13.6939 | 11.6344 | -0.21764 | 16.5925 | -6.0211 | 1.6325 | -15.1954 | 5.8789 | 9.7895 | -6.9436 | -2.5457 | -8.9633 | 7.7517 | -45.1315 | 134.8685 | 134.8685 | 134.8992 | -45.1929 | -45.1929 |  | 0.47595 | 0.71505 | 1.3135 | 0.23869 | 0.66531 | 1.2457 | -18.324 | -133.8579 | 112.1603 | -22.1823 | -124.8707 | 107.7795
Line_1 | 1.7148 | 0.65707 | 0.65707 | 1.7149 | 0.65707 | 0.65707 | 19.8014 | 7.5872 | 7.5872 | 19.8017 | 7.5872 | 7.5872 | -8.2228e-11 | 0.7378 | -8.4785 | 4.3433 | -0.836 | 8.3591 | 2.8711e-12 | -4.7617 | 4.6062 | 1.8641 | 4.9781 | -4.4104 | 134.639 | -44.5325 | -44.5325 | -45.4104 | 135.5963 | 135.5963 |  | 0 | 0.63509 | 1.2717 | 0.23869 | 0.66531 | 1.2457 | 0 | -125.7249 | 106.9532 | -22.1823 | -124.8707 | 107.7795
Line_2 | 0.65715 | 0.52898 | 0.52898 | 0.65709 | 0.529 | 0.529 | 7.5881 | 6.1082 | 6.1082 | 7.5875 | 6.1084 | 6.1084 | -1.7894 | 1.5187 | -6.1287 | 1.6778 | -0.7965 | 6.8363 | -0.45188 | -3.7802 | 3.5306 | 0.68166 | 3.9852 | -3.3413 | 135.8 | -46.2887 | -46.2887 | -44.2928 | 133.8267 | 133.8267 |  | 0.24322 | 0.66695 | 1.1579 | 0.23869 | 0.66531 | 1.2457 | -30.0274 | -114.4014 | 103.7657 | -22.1823 | -124.8707 | 107.7795
Line_3 | 1.0579 | 0.12927 | 0.12927 | 1.058 | 0.12945 | 0.12945 | 12.2161 | 1.4926 | 1.4926 | 12.2163 | 1.4947 | 1.4947 | -5.0747e-11 | 0.029687 | -1.5449 | 2.8547 | -0.2168 | 1.3399 | 1.1533e-12 | -0.9475 | 1.1031 | 0.82399 | 0.97304 | -1.0956 | 133.9411 | -37.5195 | -37.5195 | -46.1277 | 143.0378 | 143.0378 |  | 0 | 0.63509 | 1.2717 | 0.24322 | 0.66695 | 1.1579 | 0 | -125.7249 | 106.9532 | -30.0274 | -114.4014 | 103.7657

## LG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.74618 | 0.37309 | 0.37309 | 0.74618 | 0.37309 | 0.37309 | 8.6161 | 4.3081 | 4.3081 | 8.6161 | 4.308 | 4.308 | 5.3273 | -0.78577 | 4.4943 | -4.774 | 0.92885 | -4.3568 | 4.7577 | 3.821 | -1.4514 | -4.4256 | -3.7384 | 1.5283 | -45.0414 | 134.9586 | 134.9586 | 134.9894 | -45.1028 | -45.1028 |  | 0.82897 | 0.90551 | 1.0963 | 0.75553 | 0.89416 | 1.0718 | -3.2741 | -123.4208 | 117.0608 | -2.1797 | -121.1495 | 115.5667
Line_1 | 0.53948 | 0.20671 | 0.20671 | 0.53949 | 0.20671 | 0.20671 | 6.2294 | 2.3869 | 2.3869 | 6.2295 | 2.3869 | 2.3869 | -3.007 | 0.4799 | -2.4148 | 3.4343 | -0.48605 | 2.402 | -3.0312 | -2.0558 | 0.89579 | 3.2183 | 2.0782 | -0.87996 | 134.7291 | -44.4424 | -44.4424 | -45.3202 | 135.6865 | 135.6865 |  | 0.68541 | 0.88446 | 1.0791 | 0.75553 | 0.89416 | 1.0718 | -0.041369 | -121.303 | 115.2051 | -2.1797 | -121.1495 | 115.5667
Line_2 | 0.20673 | 0.16642 | 0.16642 | 0.20672 | 0.16642 | 0.16642 | 2.3872 | 1.9216 | 1.9216 | 2.387 | 1.9217 | 1.9217 | -1.3527 | 0.51681 | -1.8854 | 1.3397 | -0.4428 | 1.9548 | -1.1827 | -1.6392 | 0.66454 | 1.2073 | 1.6602 | -0.64839 | 135.8902 | -46.1986 | -46.1986 | -44.2027 | 133.9168 | 133.9168 |  | 0.75271 | 0.89442 | 1.0403 | 0.75553 | 0.89416 | 1.0718 | -2.9456 | -118.6993 | 114.3851 | -2.1797 | -121.1495 | 115.5667
Line_3 | 0.33282 | 0.040667 | 0.040667 | 0.33283 | 0.040723 | 0.040723 | 3.8431 | 0.46958 | 0.46958 | 3.8432 | 0.47023 | 0.47023 | -1.8322 | 0.044324 | -0.45001 | 2.1125 | -0.05979 | 0.42891 | -1.8925 | -0.41295 | 0.23292 | 1.9763 | 0.41631 | -0.23524 | 134.0312 | -37.4294 | -37.4294 | -46.0376 | 143.1279 | 143.1279 |  | 0.68541 | 0.88446 | 1.0791 | 0.75271 | 0.89442 | 1.0403 | -0.041369 | -121.303 | 115.2051 | -2.9456 | -118.6993 | 114.3851

## LG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.74618 | 0.37309 | 0.37309 | 0.74618 | 0.37309 | 0.37309 | 8.6161 | 4.3081 | 4.3081 | 8.6161 | 4.308 | 4.308 | 5.3273 | -0.78577 | 4.4943 | -4.774 | 0.92885 | -4.3568 | 4.7577 | 3.821 | -1.4514 | -4.4256 | -3.7384 | 1.5283 | -45.0414 | 134.9586 | 134.9586 | 134.9894 | -45.1028 | -45.1028 |  | 0.82897 | 0.90551 | 1.0963 | 0.75553 | 0.89416 | 1.0718 | -3.2741 | -123.4208 | 117.0608 | -2.1797 | -121.1495 | 115.5667
Line_1 | 0.53948 | 0.20671 | 0.20671 | 0.53949 | 0.20671 | 0.20671 | 6.2294 | 2.3869 | 2.3869 | 6.2295 | 2.3869 | 2.3869 | -3.007 | 0.4799 | -2.4148 | 3.4343 | -0.48605 | 2.402 | -3.0312 | -2.0558 | 0.89579 | 3.2183 | 2.0782 | -0.87996 | 134.7291 | -44.4424 | -44.4424 | -45.3202 | 135.6865 | 135.6865 |  | 0.68541 | 0.88446 | 1.0791 | 0.75553 | 0.89416 | 1.0718 | -0.041369 | -121.303 | 115.2051 | -2.1797 | -121.1495 | 115.5667
Line_2 | 0.20673 | 0.16642 | 0.16642 | 0.20672 | 0.16642 | 0.16642 | 2.3872 | 1.9216 | 1.9216 | 2.387 | 1.9217 | 1.9217 | -1.3527 | 0.51681 | -1.8854 | 1.3397 | -0.4428 | 1.9548 | -1.1827 | -1.6392 | 0.66454 | 1.2073 | 1.6602 | -0.64839 | 135.8902 | -46.1986 | -46.1986 | -44.2027 | 133.9168 | 133.9168 |  | 0.75271 | 0.89442 | 1.0403 | 0.75553 | 0.89416 | 1.0718 | -2.9456 | -118.6993 | 114.3851 | -2.1797 | -121.1495 | 115.5667
Line_3 | 0.33282 | 0.040667 | 0.040667 | 0.33283 | 0.040723 | 0.040723 | 3.8431 | 0.46958 | 0.46958 | 3.8432 | 0.47023 | 0.47023 | -1.8322 | 0.044324 | -0.45001 | 2.1125 | -0.05979 | 0.42891 | -1.8925 | -0.41295 | 0.23292 | 1.9763 | 0.41631 | -0.23524 | 134.0312 | -37.4294 | -37.4294 | -46.0376 | 143.1279 | 143.1279 |  | 0.68541 | 0.88446 | 1.0791 | 0.75271 | 0.89442 | 1.0403 | -0.041369 | -121.303 | 115.2051 | -2.9456 | -118.6993 | 114.3851

## LLG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.6175 | 3.8304 | 2.6778 | 1.6175 | 3.8314 | 2.6763 | 18.6771 | 44.2296 | 30.9201 | 18.677 | 44.2413 | 30.9035 | 24.5458 | 15.8479 | 4.4014 | -23.1813 | -8.2192 | -0.67609 | 3.2921 | 13.4459 | 8.4575 | -1.7786 | -4.7749 | -4.2326 | -27.1506 | -171.8892 | 28.5198 | 152.788 | 8.1319 | -151.5009 |  | 1.326 | 0.4699 | 0.30835 | 1.2448 | 0.21486 | 0.1387 | -19.5116 | -131.5767 | 91.0269 | -22.8246 | -141.7139 | 109.4237
Line_1 | 0.86349 | 2.7243 | 1.6859 | 0.86348 | 2.7233 | 1.6876 | 9.9707 | 31.4573 | 19.4675 | 9.9706 | 31.4459 | 19.4867 | -12.6059 | 1.1616e-10 | 9.2833e-11 | 12.3915 | 5.6622 | 0.71982 | -0.40349 | -9.9933e-11 | -1.7254e-11 | 0.70483 | 3.6862 | 2.6051 | 153.7931 | 5.2555 | -145.1623 | -26.0801 | -174.7789 | 34.8696 |  | 1.2649 | 0 | 0 | 1.2448 | 0.21486 | 0.1387 | -24.3735 | 0 | 0 | -22.8246 | -141.7139 | 109.4237
Line_2 | 0.75434 | 1.1213 | 1.0154 | 0.75436 | 1.1202 | 1.0165 | 8.7103 | 12.9475 | 11.7247 | 8.7106 | 12.9348 | 11.738 | -9.967 | -2.5835 | 1.1767 | 10.7898 | 2.557 | -0.043735 | -0.64861 | 0.075461 | -1.4252 | 1.0737 | 1.0887 | 1.6274 | 151.3739 | 15.2801 | -162.1753 | -28.5077 | -164.7766 | 17.8843 |  | 1.1467 | 0.19962 | 0.15764 | 1.2448 | 0.21486 | 0.1387 | -24.9028 | -166.393 | 147.3693 | -22.8246 | -141.7139 | 109.4237
Line_3 | 0.11409 | 1.6322 | 0.77356 | 0.11461 | 1.6314 | 0.77528 | 1.3174 | 18.8468 | 8.9322 | 1.3234 | 18.8381 | 8.9522 | -1.6169 | 7.6238e-11 | 3.6296e-11 | 1.4633 | 3.628 | 0.0010765 | 0.40349 | -5.1146e-11 | -2.3655e-11 | -0.40223 | 0.98942 | 1.4112 | 169.6385 | -1.593 | -122.5986 | -9.533 | 178.3521 | 57.413 |  | 1.2649 | 0 | 0 | 1.1467 | 0.19962 | 0.15764 | -24.3735 | 0 | 0 | -24.9028 | -166.393 | 147.3693

## LLG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.6175 | 3.8304 | 2.6778 | 1.6175 | 3.8314 | 2.6763 | 18.6771 | 44.2296 | 30.9201 | 18.677 | 44.2413 | 30.9035 | 24.5458 | 15.8479 | 4.4014 | -23.1813 | -8.2192 | -0.67609 | 3.2921 | 13.4459 | 8.4575 | -1.7786 | -4.7749 | -4.2326 | -27.1506 | -171.8892 | 28.5198 | 152.788 | 8.1319 | -151.5009 |  | 1.326 | 0.4699 | 0.30835 | 1.2448 | 0.21486 | 0.1387 | -19.5116 | -131.5767 | 91.0269 | -22.8246 | -141.7139 | 109.4237
Line_1 | 0.86349 | 2.7243 | 1.6859 | 0.86348 | 2.7233 | 1.6876 | 9.9707 | 31.4573 | 19.4675 | 9.9706 | 31.4459 | 19.4867 | -12.6059 | 1.1616e-10 | 9.2833e-11 | 12.3915 | 5.6622 | 0.71982 | -0.40349 | -9.9933e-11 | -1.7254e-11 | 0.70483 | 3.6862 | 2.6051 | 153.7931 | 5.2555 | -145.1623 | -26.0801 | -174.7789 | 34.8696 |  | 1.2649 | 0 | 0 | 1.2448 | 0.21486 | 0.1387 | -24.3735 | 0 | 0 | -22.8246 | -141.7139 | 109.4237
Line_2 | 0.75434 | 1.1213 | 1.0154 | 0.75436 | 1.1202 | 1.0165 | 8.7103 | 12.9475 | 11.7247 | 8.7106 | 12.9348 | 11.738 | -9.967 | -2.5835 | 1.1767 | 10.7898 | 2.557 | -0.043735 | -0.64861 | 0.075461 | -1.4252 | 1.0737 | 1.0887 | 1.6274 | 151.3739 | 15.2801 | -162.1753 | -28.5077 | -164.7766 | 17.8843 |  | 1.1467 | 0.19962 | 0.15764 | 1.2448 | 0.21486 | 0.1387 | -24.9028 | -166.393 | 147.3693 | -22.8246 | -141.7139 | 109.4237
Line_3 | 0.11409 | 1.6322 | 0.77356 | 0.11461 | 1.6314 | 0.77528 | 1.3174 | 18.8468 | 8.9322 | 1.3234 | 18.8381 | 8.9522 | -1.6169 | 7.6238e-11 | 3.6296e-11 | 1.4633 | 3.628 | 0.0010765 | 0.40349 | -5.1146e-11 | -2.3655e-11 | -0.40223 | 0.98942 | 1.4112 | 169.6385 | -1.593 | -122.5986 | -9.533 | 178.3521 | 57.413 |  | 1.2649 | 0 | 0 | 1.1467 | 0.19962 | 0.15764 | -24.3735 | 0 | 0 | -24.9028 | -166.393 | 147.3693

## LLG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.4412 | 1.1499 | 1.045 | 0.4412 | 1.1503 | 1.0446 | 5.0946 | 13.2776 | 12.0669 | 5.0946 | 13.2826 | 12.0615 | 4.7462 | 11.3046 | 3.9308 | -4.6415 | -10.6212 | -3.3621 | 3.1649 | 6.4718 | 8.9787 | -3.0554 | -5.6912 | -8.3311 | -40.204 | -154.9536 | 47.5917 | 139.7346 | 25.0562 | -132.4091 |  | 1.1197 | 0.98105 | 0.81226 | 1.0908 | 0.9072 | 0.74484 | -6.5079 | -125.1628 | 113.9486 | -6.91 | -126.7599 | 115.6135
Line_1 | 0.23554 | 0.78952 | 0.70077 | 0.23553 | 0.78907 | 0.70129 | 2.7197 | 9.1165 | 8.0918 | 2.7197 | 9.1113 | 8.0978 | -2.5222 | -6.5773 | -2.4816 | 2.5096 | 6.9946 | 2.7181 | -1.5629 | -4.1538 | -4.9564 | 1.5818 | 4.4044 | 5.3844 | 140.7398 | 21.0612 | -127.6001 | -39.1335 | -158.9578 | 52.3989 |  | 1.091 | 0.8533 | 0.685 | 1.0908 | 0.9072 | 0.74484 | -7.4749 | -126.6647 | 115.8035 | -6.91 | -126.7599 | 115.6135
Line_2 | 0.20576 | 0.36777 | 0.35027 | 0.20577 | 0.36735 | 0.35069 | 2.3759 | 4.2466 | 4.0446 | 2.376 | 4.2418 | 4.0494 | -2.0678 | -3.5927 | -0.55293 | 2.132 | 3.6266 | 0.64399 | -1.4446 | -1.1438 | -2.9336 | 1.4735 | 1.2868 | 2.9466 | 138.3205 | 33.7196 | -142.0699 | -41.5611 | -146.2962 | 37.9417 |  | 1.0617 | 0.88785 | 0.73809 | 1.0908 | 0.9072 | 0.74484 | -6.7406 | -128.6212 | 117.2562 | -6.91 | -126.7599 | 115.6135
Line_3 | 0.031121 | 0.43832 | 0.37188 | 0.031263 | 0.43795 | 0.37233 | 0.35936 | 5.0613 | 4.2941 | 0.36099 | 5.0571 | 4.2993 | -0.37698 | -3.1658 | -1.8991 | 0.36869 | 3.3916 | 1.9858 | -0.10767 | -2.9376 | -2.2462 | 0.10465 | 2.9422 | 2.4752 | 156.5851 | 10.4765 | -113.984 | -22.5864 | -169.5625 | 65.9954 |  | 1.091 | 0.8533 | 0.685 | 1.0617 | 0.88785 | 0.73809 | -7.4749 | -126.6647 | 115.8035 | -6.7406 | -128.6212 | 117.2562

## LLG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.4412 | 1.1499 | 1.045 | 0.4412 | 1.1503 | 1.0446 | 5.0946 | 13.2776 | 12.0669 | 5.0946 | 13.2826 | 12.0615 | 4.7462 | 11.3046 | 3.9308 | -4.6415 | -10.6212 | -3.3621 | 3.1649 | 6.4718 | 8.9787 | -3.0554 | -5.6912 | -8.3311 | -40.204 | -154.9536 | 47.5917 | 139.7346 | 25.0562 | -132.4091 |  | 1.1197 | 0.98105 | 0.81226 | 1.0908 | 0.9072 | 0.74484 | -6.5079 | -125.1628 | 113.9486 | -6.91 | -126.7599 | 115.6135
Line_1 | 0.23554 | 0.78952 | 0.70077 | 0.23553 | 0.78907 | 0.70129 | 2.7197 | 9.1165 | 8.0918 | 2.7197 | 9.1113 | 8.0978 | -2.5222 | -6.5773 | -2.4816 | 2.5096 | 6.9946 | 2.7181 | -1.5629 | -4.1538 | -4.9564 | 1.5818 | 4.4044 | 5.3844 | 140.7398 | 21.0612 | -127.6001 | -39.1335 | -158.9578 | 52.3989 |  | 1.091 | 0.8533 | 0.685 | 1.0908 | 0.9072 | 0.74484 | -7.4749 | -126.6647 | 115.8035 | -6.91 | -126.7599 | 115.6135
Line_2 | 0.20576 | 0.36777 | 0.35027 | 0.20577 | 0.36735 | 0.35069 | 2.3759 | 4.2466 | 4.0446 | 2.376 | 4.2418 | 4.0494 | -2.0678 | -3.5927 | -0.55293 | 2.132 | 3.6266 | 0.64399 | -1.4446 | -1.1438 | -2.9336 | 1.4735 | 1.2868 | 2.9466 | 138.3205 | 33.7196 | -142.0699 | -41.5611 | -146.2962 | 37.9417 |  | 1.0617 | 0.88785 | 0.73809 | 1.0908 | 0.9072 | 0.74484 | -6.7406 | -128.6212 | 117.2562 | -6.91 | -126.7599 | 115.6135
Line_3 | 0.031121 | 0.43832 | 0.37188 | 0.031263 | 0.43795 | 0.37233 | 0.35936 | 5.0613 | 4.2941 | 0.36099 | 5.0571 | 4.2993 | -0.37698 | -3.1658 | -1.8991 | 0.36869 | 3.3916 | 1.9858 | -0.10767 | -2.9376 | -2.2462 | 0.10465 | 2.9422 | 2.4752 | 156.5851 | 10.4765 | -113.984 | -22.5864 | -169.5625 | 65.9954 |  | 1.091 | 0.8533 | 0.685 | 1.0617 | 0.88785 | 0.73809 | -7.4749 | -126.6647 | 115.8035 | -6.7406 | -128.6212 | 117.2562

## LLG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.2634 | 3.0446 | 2.2608 | 1.2634 | 3.0455 | 2.2596 | 14.5884 | 35.1565 | 26.1056 | 14.5882 | 35.1669 | 26.0916 | 17.2174 | 18.065 | 7.155 | -15.6215 | -8.8057 | -2.0586 | 1.8571 | 7.4072 | 6.931 | -0.93821 | -1.9228 | -3.9206 | -23.2104 | -161.6306 | 40.1385 | 156.7281 | 18.3883 | -139.8766 |  | 1.1871 | 0.55536 | 0.38159 | 1.0728 | 0.2563 | 0.16972 | -17.0542 | -139.3355 | 84.2275 | -19.8349 | -149.2942 | 102.4213
Line_1 | 0.69998 | 2.1337 | 1.4558 | 0.69998 | 2.1327 | 1.4572 | 8.0827 | 24.6378 | 16.8098 | 8.0827 | 24.6266 | 16.8266 | -8.7848 | -1.2581e-10 | -3.8438e-11 | 8.6615 | 6.0951 | 1.5505 | -0.17654 | -1.0509e-10 | -1.0543e-10 | 0.40054 | 1.6393 | 2.3982 | 157.3886 | 15.6852 | -134.7193 | -22.4826 | -164.3481 | 45.3042 |  | 1.0871 | 0 | 0 | 1.0728 | 0.2563 | 0.16972 | -21.4602 | 0 | 0 | -19.8349 | -149.2942 | 102.4213
Line_2 | 0.56353 | 0.92176 | 0.81802 | 0.56355 | 0.9209 | 0.81896 | 6.5071 | 10.6436 | 9.4457 | 6.5073 | 10.6336 | 9.4566 | -6.1482 | -2.4465 | 0.62213 | 6.96 | 2.7106 | 0.50809 | -0.32101 | 0.78391 | -1.6785 | 0.53766 | 0.28344 | 1.5224 | 155.6323 | 24.7816 | -149.1671 | -24.2522 | -155.2639 | 30.8774 |  | 0.94614 | 0.24137 | 0.18952 | 1.0728 | 0.2563 | 0.16972 | -21.3789 | -172.9848 | 141.1698 | -19.8349 | -149.2942 | 102.4213
Line_3 | 0.13771 | 1.2324 | 0.69384 | 0.1379 | 1.2317 | 0.69519 | 1.5901 | 14.2311 | 8.0117 | 1.5923 | 14.2227 | 8.0273 | -1.7196 | -6.5002e-11 | -3.2282e-11 | 1.4974 | 3.4312 | 0.29585 | 0.17654 | -6.8851e-11 | -4.2644e-11 | -0.16631 | -0.11033 | 1.4923 | 164.4016 | 8.9102 | -117.6244 | -15.0412 | -171.143 | 62.3837 |  | 1.0871 | 0 | 0 | 0.94614 | 0.24137 | 0.18952 | -21.4602 | 0 | 0 | -21.3789 | -172.9848 | 141.1698

## LLG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.2634 | 3.0446 | 2.2608 | 1.2634 | 3.0455 | 2.2596 | 14.5884 | 35.1565 | 26.1056 | 14.5882 | 35.1669 | 26.0916 | 17.2174 | 18.065 | 7.155 | -15.6215 | -8.8057 | -2.0586 | 1.8571 | 7.4072 | 6.931 | -0.93821 | -1.9228 | -3.9206 | -23.2104 | -161.6306 | 40.1385 | 156.7281 | 18.3883 | -139.8766 |  | 1.1871 | 0.55536 | 0.38159 | 1.0728 | 0.2563 | 0.16972 | -17.0542 | -139.3355 | 84.2275 | -19.8349 | -149.2942 | 102.4213
Line_1 | 0.69998 | 2.1337 | 1.4558 | 0.69998 | 2.1327 | 1.4572 | 8.0827 | 24.6378 | 16.8098 | 8.0827 | 24.6266 | 16.8266 | -8.7848 | -1.2581e-10 | -3.8438e-11 | 8.6615 | 6.0951 | 1.5505 | -0.17654 | -1.0509e-10 | -1.0543e-10 | 0.40054 | 1.6393 | 2.3982 | 157.3886 | 15.6852 | -134.7193 | -22.4826 | -164.3481 | 45.3042 |  | 1.0871 | 0 | 0 | 1.0728 | 0.2563 | 0.16972 | -21.4602 | 0 | 0 | -19.8349 | -149.2942 | 102.4213
Line_2 | 0.56353 | 0.92176 | 0.81802 | 0.56355 | 0.9209 | 0.81896 | 6.5071 | 10.6436 | 9.4457 | 6.5073 | 10.6336 | 9.4566 | -6.1482 | -2.4465 | 0.62213 | 6.96 | 2.7106 | 0.50809 | -0.32101 | 0.78391 | -1.6785 | 0.53766 | 0.28344 | 1.5224 | 155.6323 | 24.7816 | -149.1671 | -24.2522 | -155.2639 | 30.8774 |  | 0.94614 | 0.24137 | 0.18952 | 1.0728 | 0.2563 | 0.16972 | -21.3789 | -172.9848 | 141.1698 | -19.8349 | -149.2942 | 102.4213
Line_3 | 0.13771 | 1.2324 | 0.69384 | 0.1379 | 1.2317 | 0.69519 | 1.5901 | 14.2311 | 8.0117 | 1.5923 | 14.2227 | 8.0273 | -1.7196 | -6.5002e-11 | -3.2282e-11 | 1.4974 | 3.4312 | 0.29585 | 0.17654 | -6.8851e-11 | -4.2644e-11 | -0.16631 | -0.11033 | 1.4923 | 164.4016 | 8.9102 | -117.6244 | -15.0412 | -171.143 | 62.3837 |  | 1.0871 | 0 | 0 | 0.94614 | 0.24137 | 0.18952 | -21.4602 | 0 | 0 | -21.3789 | -172.9848 | 141.1698

## LLG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.38628 | 0.98675 | 0.90412 | 0.38627 | 0.98714 | 0.90371 | 4.4603 | 11.3941 | 10.4399 | 4.4603 | 11.3985 | 10.4351 | 3.8477 | 9.1649 | 3.6378 | -3.696 | -8.1954 | -2.8217 | 2.4118 | 4.58 | 6.9013 | -2.3282 | -4.0049 | -6.4163 | -38.4833 | -152.105 | 50.9393 | 141.4553 | 27.9044 | -129.0608 |  | 1.0181 | 0.8992 | 0.74726 | 0.97936 | 0.80025 | 0.67171 | -6.4033 | -125.552 | 113.1449 | -6.3368 | -126.0517 | 117.2011
Line_1 | 0.21402 | 0.67445 | 0.60611 | 0.21402 | 0.67403 | 0.60659 | 2.4713 | 7.7879 | 6.9988 | 2.4713 | 7.783 | 7.0043 | -2.0742 | -4.8733 | -1.8336 | 2.0654 | 5.4189 | 2.1983 | -1.2435 | -2.956 | -3.7768 | 1.2616 | 3.0705 | 4.1597 | 142.1157 | 24.43 | -124.9421 | -37.7555 | -155.5891 | 55.0558 |  | 0.97859 | 0.73187 | 0.59988 | 0.97936 | 0.80025 | 0.67171 | -6.9403 | -124.3301 | 119.1618 | -6.3368 | -126.0517 | 117.2011
Line_2 | 0.1723 | 0.31737 | 0.30149 | 0.1723 | 0.31703 | 0.30184 | 1.9895 | 3.6646 | 3.4813 | 1.9896 | 3.6608 | 3.4853 | -1.5527 | -2.7083 | -0.51377 | 1.6307 | 2.7765 | 0.62341 | -1.0483 | -0.79507 | -2.2795 | 1.0666 | 0.93439 | 2.2566 | 140.3595 | 35.3637 | -137.3635 | -39.5251 | -144.6517 | 42.6445 |  | 0.94165 | 0.77023 | 0.6712 | 0.97936 | 0.80025 | 0.67171 | -5.6157 | -128.2758 | 119.9351 | -6.3368 | -126.0517 | 117.2011
Line_3 | 0.042104 | 0.36793 | 0.31822 | 0.042163 | 0.36759 | 0.31862 | 0.48618 | 4.2484 | 3.6745 | 0.48685 | 4.2446 | 3.6791 | -0.43487 | -2.3591 | -1.3467 | 0.41651 | 2.6199 | 1.4815 | -0.19299 | -2.0254 | -1.745 | 0.19156 | 1.9557 | 1.9757 | 149.1287 | 15.0223 | -113.1797 | -30.314 | -165.0159 | 66.8003 |  | 0.97859 | 0.73187 | 0.59988 | 0.94165 | 0.77023 | 0.6712 | -6.9403 | -124.3301 | 119.1618 | -5.6157 | -128.2758 | 119.9351

## LLG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.38628 | 0.98675 | 0.90412 | 0.38627 | 0.98714 | 0.90371 | 4.4603 | 11.3941 | 10.4399 | 4.4603 | 11.3985 | 10.4351 | 3.8477 | 9.1649 | 3.6378 | -3.696 | -8.1954 | -2.8217 | 2.4118 | 4.58 | 6.9013 | -2.3282 | -4.0049 | -6.4163 | -38.4833 | -152.105 | 50.9393 | 141.4553 | 27.9044 | -129.0608 |  | 1.0181 | 0.8992 | 0.74726 | 0.97936 | 0.80025 | 0.67171 | -6.4033 | -125.552 | 113.1449 | -6.3368 | -126.0517 | 117.2011
Line_1 | 0.21402 | 0.67445 | 0.60611 | 0.21402 | 0.67403 | 0.60659 | 2.4713 | 7.7879 | 6.9988 | 2.4713 | 7.783 | 7.0043 | -2.0742 | -4.8733 | -1.8336 | 2.0654 | 5.4189 | 2.1983 | -1.2435 | -2.956 | -3.7768 | 1.2616 | 3.0705 | 4.1597 | 142.1157 | 24.43 | -124.9421 | -37.7555 | -155.5891 | 55.0558 |  | 0.97859 | 0.73187 | 0.59988 | 0.97936 | 0.80025 | 0.67171 | -6.9403 | -124.3301 | 119.1618 | -6.3368 | -126.0517 | 117.2011
Line_2 | 0.1723 | 0.31737 | 0.30149 | 0.1723 | 0.31703 | 0.30184 | 1.9895 | 3.6646 | 3.4813 | 1.9896 | 3.6608 | 3.4853 | -1.5527 | -2.7083 | -0.51377 | 1.6307 | 2.7765 | 0.62341 | -1.0483 | -0.79507 | -2.2795 | 1.0666 | 0.93439 | 2.2566 | 140.3595 | 35.3637 | -137.3635 | -39.5251 | -144.6517 | 42.6445 |  | 0.94165 | 0.77023 | 0.6712 | 0.97936 | 0.80025 | 0.67171 | -5.6157 | -128.2758 | 119.9351 | -6.3368 | -126.0517 | 117.2011
Line_3 | 0.042104 | 0.36793 | 0.31822 | 0.042163 | 0.36759 | 0.31862 | 0.48618 | 4.2484 | 3.6745 | 0.48685 | 4.2446 | 3.6791 | -0.43487 | -2.3591 | -1.3467 | 0.41651 | 2.6199 | 1.4815 | -0.19299 | -2.0254 | -1.745 | 0.19156 | 1.9557 | 1.9757 | 149.1287 | 15.0223 | -113.1797 | -30.314 | -165.0159 | 66.8003 |  | 0.97859 | 0.73187 | 0.59988 | 0.94165 | 0.77023 | 0.6712 | -6.9403 | -124.3301 | 119.1618 | -5.6157 | -128.2758 | 119.9351