## LLL_max_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 3.6999 | 3.6999 | 0 | 0 | 128.1693 | 128.1693 | 35.5926 | -14.237 | 40.3839 | -16.1536 | -73.5107 | 106.4893 | 0.41999 | 0.168 | -24.9022 | -24.9022
Line_1 | 2.4666 | 2.4666 | 4.9647 | 0 | 85.4462 | 85.4462 | -1e-07 | 9.4914 | -1e-07 | 10.769 | 106.4893 | -73.5107 | 0 | 0.168 | 0 | -24.9022
Line_2 | 1.2333 | 1.2333 | 0 | 0 | 42.7231 | 42.7231 | -2.3728 | 4.7457 | -2.6923 | 5.3845 | 106.4893 | -73.5107 | 0.083999 | 0.168 | -24.9022 | -24.9022
Line_3 | 1.2333 | 1.2333 | 2.4824 | 0 | 42.7231 | 42.7231 | -1e-07 | 2.3728 | -1e-07 | 2.6923 | 106.4893 | -73.5107 | 0 | 0.083999 | 0 | -24.9022

## LLL_max_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 3.6999 | 3.6999 | 0 | 0 | 128.1693 | 128.1693 | 35.5926 | -14.237 | 40.3839 | -16.1536 | -73.5107 | 106.4893 | 0.41999 | 0.168 | -24.9022 | -24.9022
Line_1 | 2.4666 | 2.4666 | 4.9647 | 0 | 85.4462 | 85.4462 | -1e-07 | 9.4914 | -1e-07 | 10.769 | 106.4893 | -73.5107 | 0 | 0.168 | 0 | -24.9022
Line_2 | 1.2333 | 1.2333 | 0 | 0 | 42.7231 | 42.7231 | -2.3728 | 4.7457 | -2.6923 | 5.3845 | 106.4893 | -73.5107 | 0.083999 | 0.168 | -24.9022 | -24.9022
Line_3 | 1.2333 | 1.2333 | 2.4824 | 0 | 42.7231 | 42.7231 | -1e-07 | 2.3728 | -1e-07 | 2.6923 | 106.4893 | -73.5107 | 0 | 0.083999 | 0 | -24.9022

## LLL_max_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 1.2428 | 1.2428 | 0 | 0 | 43.0531 | 43.0531 | 27.1857 | -24.7761 | 27.7264 | -24.9923 | -54.2264 | 125.7736 | 0.90192 | 0.81741 | -8.6624 | -8.9775
Line_1 | 0.82856 | 0.82856 | 1.6677 | 0 | 28.7021 | 28.7021 | -15.4464 | 16.5174 | -15.4464 | 16.6616 | 125.7736 | -54.2264 | 0.76108 | 0.81741 | -9.2264 | -8.9775
Line_2 | 0.41428 | 0.41428 | 0 | 0 | 14.351 | 14.351 | -7.991 | 8.2587 | -8.027 | 8.3308 | 125.7736 | -54.2264 | 0.78924 | 0.81741 | -9.0975 | -8.9775
Line_3 | 0.41428 | 0.41428 | 0.83384 | 0 | 14.351 | 14.351 | -7.7232 | 7.991 | -7.7232 | 8.027 | 125.7736 | -54.2264 | 0.76108 | 0.78924 | -9.2264 | -9.0975

## LLL_max_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 1.2428 | 1.2428 | 0 | 0 | 43.0531 | 43.0531 | 27.1857 | -24.7761 | 27.7264 | -24.9923 | -54.2264 | 125.7736 | 0.90192 | 0.81741 | -8.6624 | -8.9775
Line_1 | 0.82856 | 0.82856 | 1.6677 | 0 | 28.7021 | 28.7021 | -15.4464 | 16.5174 | -15.4464 | 16.6616 | 125.7736 | -54.2264 | 0.76108 | 0.81741 | -9.2264 | -8.9775
Line_2 | 0.41428 | 0.41428 | 0 | 0 | 14.351 | 14.351 | -7.991 | 8.2587 | -8.027 | 8.3308 | 125.7736 | -54.2264 | 0.78924 | 0.81741 | -9.0975 | -8.9775
Line_3 | 0.41428 | 0.41428 | 0.83384 | 0 | 14.351 | 14.351 | -7.7232 | 7.991 | -7.7232 | 8.027 | 125.7736 | -54.2264 | 0.76108 | 0.78924 | -9.2264 | -9.0975

## LLL_min_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 3.0092 | 3.0092 | 0 | 0 | 104.2421 | 104.2421 | 45.2043 | -18.0817 | 26.7133 | -10.6853 | -62.3733 | 117.6267 | 0.50371 | 0.20148 | -31.7926 | -31.7926
Line_1 | 2.0061 | 2.0061 | 3.4722 | 0 | 69.4947 | 69.4947 | -1e-07 | 12.0545 | -1e-07 | 7.1235 | 117.6267 | -62.3733 | 0 | 0.20148 | 0 | -31.7926
Line_2 | 1.0031 | 1.0031 | 0 | 0 | 34.7474 | 34.7474 | -3.0136 | 6.0272 | -1.7809 | 3.5618 | 117.6267 | -62.3733 | 0.10074 | 0.20148 | -31.7926 | -31.7926
Line_3 | 1.0031 | 1.0031 | 1.7361 | 0 | 34.7474 | 34.7474 | -1e-07 | 3.0136 | -1e-07 | 1.7809 | 117.6267 | -62.3733 | 0 | 0.10074 | 0 | -31.7926

## LLL_min_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 3.0092 | 3.0092 | 0 | 0 | 104.2421 | 104.2421 | 45.2043 | -18.0817 | 26.7133 | -10.6853 | -62.3733 | 117.6267 | 0.50371 | 0.20148 | -31.7926 | -31.7926
Line_1 | 2.0061 | 2.0061 | 3.4722 | 0 | 69.4947 | 69.4947 | -1e-07 | 12.0545 | -1e-07 | 7.1235 | 117.6267 | -62.3733 | 0 | 0.20148 | 0 | -31.7926
Line_2 | 1.0031 | 1.0031 | 0 | 0 | 34.7474 | 34.7474 | -3.0136 | 6.0272 | -1.7809 | 3.5618 | 117.6267 | -62.3733 | 0.10074 | 0.20148 | -31.7926 | -31.7926
Line_3 | 1.0031 | 1.0031 | 1.7361 | 0 | 34.7474 | 34.7474 | -1e-07 | 3.0136 | -1e-07 | 1.7809 | 117.6267 | -62.3733 | 0 | 0.10074 | 0 | -31.7926

## LLL_min_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 1.0697 | 1.0697 | 0 | 0 | 37.0569 | 37.0569 | 22.8777 | -19.4502 | 20.541 | -18.5155 | -51.0933 | 128.9067 | 0.8297 | 0.72467 | -9.1739 | -7.5036
Line_1 | 0.71316 | 0.71316 | 1.2343 | 0 | 24.7046 | 24.7046 | -11.4434 | 12.9668 | -11.4434 | 12.3437 | 128.9067 | -51.0933 | 0.65508 | 0.72467 | -6.0933 | -7.5036
Line_2 | 0.35658 | 0.35658 | 0 | 0 | 12.3523 | 12.3523 | -6.1026 | 6.4834 | -5.9468 | 6.1718 | 128.9067 | -51.0933 | 0.68982 | 0.72467 | -6.834 | -7.5036
Line_3 | 0.35658 | 0.35658 | 0.61717 | 0 | 12.3523 | 12.3523 | -5.7217 | 6.1026 | -5.7217 | 5.9468 | 128.9067 | -51.0933 | 0.65508 | 0.68982 | -6.0933 | -6.834

## LLL_min_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 1.0697 | 1.0697 | 0 | 0 | 37.0569 | 37.0569 | 22.8777 | -19.4502 | 20.541 | -18.5155 | -51.0933 | 128.9067 | 0.8297 | 0.72467 | -9.1739 | -7.5036
Line_1 | 0.71316 | 0.71316 | 1.2343 | 0 | 24.7046 | 24.7046 | -11.4434 | 12.9668 | -11.4434 | 12.3437 | 128.9067 | -51.0933 | 0.65508 | 0.72467 | -6.0933 | -7.5036
Line_2 | 0.35658 | 0.35658 | 0 | 0 | 12.3523 | 12.3523 | -6.1026 | 6.4834 | -5.9468 | 6.1718 | 128.9067 | -51.0933 | 0.68982 | 0.72467 | -6.834 | -7.5036
Line_3 | 0.35658 | 0.35658 | 0.61717 | 0 | 12.3523 | 12.3523 | -5.7217 | 6.1026 | -5.7217 | 5.9468 | 128.9067 | -51.0933 | 0.65508 | 0.68982 | -6.0933 | -6.834

## LL_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 3.2042 | 3.2042 | 0 | 3.2042 | 3.2042 | 0 | 36.9993 | 36.9993 | 0 | 36.9993 | 36.9993 | -6.2528e-14 | 28.4108 | -10.6145 | 5.2106e-14 | -23.0719 | 15.9534 | -5.2106e-14 | 4.32 | 15.8719 | 5.2106e-14 | 1.7376 | -9.8143 | 0 | -163.5107 | 16.4893 | 0 | 16.4893 | -163.5107 | 1.1 | 0.7767 | 0.51607 | 1.1 | 0.62534 | 0.50624 | 9.507e-13 | -154.8648 | 140.2623 | 9.5347e-13 | -167.8176 | 164.89
Line_1 | 0 | 2.1362 | 2.1362 | 0 | 2.1362 | 2.1362 | 0 | 24.6662 | 24.6662 | 0 | 24.6662 | 24.6662 | -3.4295e-28 | -13.0085 | 13.0085 | -1.0421e-14 | 15.3813 | -10.6356 | 2.0843e-14 | 3.8506 | -3.8506 | -2.0843e-14 | -1.1584 | 6.5429 | 0 | 16.4893 | -163.5107 | 0 | -163.5107 | 16.4893 | 1.1 | 0.55 | 0.55 | 1.1 | 0.62534 | 0.50624 | 9.4275e-13 | 180 | -180 | 9.5347e-13 | -167.8176 | 164.89
Line_2 | 0 | 1.0681 | 1.0681 | 0 | 1.0681 | 1.0681 | 0 | 12.3331 | 12.3331 | 0 | 12.3331 | 12.3331 | 5.2106e-15 | -7.0974 | 5.911 | -1.5632e-14 | 7.6906 | -5.3178 | 2.0843e-14 | 1.2523 | -2.5984 | -1.0421e-14 | -0.57919 | 3.2714 | 0 | 16.4893 | -163.5107 | 0 | -163.5107 | 16.4893 | 1.1 | 0.58437 | 0.52354 | 1.1 | 0.62534 | 0.50624 | 9.2979e-13 | -173.5168 | 172.7598 | 9.5347e-13 | -167.8176 | 164.89
Line_3 | 0 | 1.0681 | 1.0681 | 0 | 1.0681 | 1.0681 | 0 | 12.3331 | 12.3331 | 0 | 12.3331 | 12.3331 | -5.2106e-15 | -6.5042 | 6.5042 | -5.2106e-15 | 7.0974 | -5.911 | 5.2106e-15 | 1.9253 | -1.9253 | -5.2106e-15 | -1.2523 | 2.5984 | 0 | 16.4893 | -163.5107 | 0 | -163.5107 | 16.4893 | 1.1 | 0.55 | 0.55 | 1.1 | 0.58437 | 0.52354 | 9.4275e-13 | 180 | -180 | 9.2979e-13 | -173.5168 | 172.7598

## LL_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 3.2042 | 3.2042 | 0 | 3.2042 | 3.2042 | 0 | 36.9993 | 36.9993 | 0 | 36.9993 | 36.9993 | -6.2528e-14 | 28.4108 | -10.6145 | 5.2106e-14 | -23.0719 | 15.9534 | -5.2106e-14 | 4.32 | 15.8719 | 5.2106e-14 | 1.7376 | -9.8143 | 0 | -163.5107 | 16.4893 | 0 | 16.4893 | -163.5107 | 1.1 | 0.7767 | 0.51607 | 1.1 | 0.62534 | 0.50624 | 9.507e-13 | -154.8648 | 140.2623 | 9.5347e-13 | -167.8176 | 164.89
Line_1 | 0 | 2.1362 | 2.1362 | 0 | 2.1362 | 2.1362 | 0 | 24.6662 | 24.6662 | 0 | 24.6662 | 24.6662 | -3.4295e-28 | -13.0085 | 13.0085 | -1.0421e-14 | 15.3813 | -10.6356 | 2.0843e-14 | 3.8506 | -3.8506 | -2.0843e-14 | -1.1584 | 6.5429 | 0 | 16.4893 | -163.5107 | 0 | -163.5107 | 16.4893 | 1.1 | 0.55 | 0.55 | 1.1 | 0.62534 | 0.50624 | 9.4275e-13 | 180 | -180 | 9.5347e-13 | -167.8176 | 164.89
Line_2 | 0 | 1.0681 | 1.0681 | 0 | 1.0681 | 1.0681 | 0 | 12.3331 | 12.3331 | 0 | 12.3331 | 12.3331 | 5.2106e-15 | -7.0974 | 5.911 | -1.5632e-14 | 7.6906 | -5.3178 | 2.0843e-14 | 1.2523 | -2.5984 | -1.0421e-14 | -0.57919 | 3.2714 | 0 | 16.4893 | -163.5107 | 0 | -163.5107 | 16.4893 | 1.1 | 0.58437 | 0.52354 | 1.1 | 0.62534 | 0.50624 | 9.2979e-13 | -173.5168 | 172.7598 | 9.5347e-13 | -167.8176 | 164.89
Line_3 | 0 | 1.0681 | 1.0681 | 0 | 1.0681 | 1.0681 | 0 | 12.3331 | 12.3331 | 0 | 12.3331 | 12.3331 | -5.2106e-15 | -6.5042 | 6.5042 | -5.2106e-15 | 7.0974 | -5.911 | 5.2106e-15 | 1.9253 | -1.9253 | -5.2106e-15 | -1.2523 | 2.5984 | 0 | 16.4893 | -163.5107 | 0 | -163.5107 | 16.4893 | 1.1 | 0.55 | 0.55 | 1.1 | 0.58437 | 0.52354 | 9.4275e-13 | 180 | -180 | 9.2979e-13 | -173.5168 | 172.7598

## LL_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 1.6287 | 1.6287 | 0 | 1.6287 | 1.6287 | 0 | 18.8063 | 18.8063 | 0 | 18.8063 | 18.8063 | -3.6475e-14 | 17.8002 | 0.06044 | 3.3869e-14 | -16.4209 | 1.3189 | -2.6053e-14 | 3.9189 | 14.5607 | 2.3448e-14 | -2.3539 | -12.9957 | 0 | -149.0411 | 30.9589 | 0 | 30.9589 | -149.0411 | 1.1 | 0.96917 | 0.77425 | 1.1 | 0.88208 | 0.69458 | 4.7786e-13 | -136.625 | 120.7211 | 4.8005e-13 | -140.8835 | 126.7539
Line_1 | 0 | 1.0858 | 1.0858 | 0 | 1.0858 | 1.0858 | 0 | 12.5375 | 12.5375 | 0 | 12.5375 | 12.5375 | -5.2106e-15 | -10.3342 | 1.4923 | 1.0914e-28 | 10.9473 | -0.87927 | 1.5632e-14 | -0.87368 | -7.9682 | -1.3027e-14 | 1.5692 | 8.6638 | 0 | 30.9589 | -149.0411 | 0 | -149.0411 | 30.9589 | 1.1 | 0.8272 | 0.6466 | 1.1 | 0.88208 | 0.69458 | 4.7486e-13 | -144.2087 | 131.5665 | 4.8005e-13 | -140.8835 | 126.7539
Line_2 | 0 | 0.54289 | 0.54289 | 0 | 0.54289 | 0.54289 | 0 | 6.2688 | 6.2688 | 0 | 6.2688 | 6.2688 | -5.2106e-15 | -5.3204 | 0.59289 | 5.2106e-15 | 5.4736 | -0.43963 | 1.8237e-14 | -0.61073 | -4.158 | -1.5632e-14 | 0.78462 | 4.3319 | 0 | 30.9589 | -149.0411 | 0 | -149.0411 | 30.9589 | 1.1 | 0.85428 | 0.67 | 1.1 | 0.88208 | 0.69458 | 4.6827e-13 | -142.4927 | 129.0741 | 4.8005e-13 | -140.8835 | 126.7539
Line_3 | 0 | 0.54289 | 0.54289 | 0 | 0.54289 | 0.54289 | 0 | 6.2688 | 6.2688 | 0 | 6.2688 | 6.2688 | 2.6053e-15 | -5.1671 | 0.74615 | -7.816e-15 | 5.3204 | -0.59289 | 2.1593e-29 | -0.43684 | -3.9841 | 5.2106e-15 | 0.61073 | 4.158 | 0 | 30.9589 | -149.0411 | 0 | -149.0411 | 30.9589 | 1.1 | 0.8272 | 0.6466 | 1.1 | 0.85428 | 0.67 | 4.7486e-13 | -144.2087 | 131.5665 | 4.6827e-13 | -142.4927 | 129.0741

## LL_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 1.6287 | 1.6287 | 0 | 1.6287 | 1.6287 | 0 | 18.8063 | 18.8063 | 0 | 18.8063 | 18.8063 | -3.6475e-14 | 17.8002 | 0.06044 | 3.3869e-14 | -16.4209 | 1.3189 | -2.6053e-14 | 3.9189 | 14.5607 | 2.3448e-14 | -2.3539 | -12.9957 | 0 | -149.0411 | 30.9589 | 0 | 30.9589 | -149.0411 | 1.1 | 0.96917 | 0.77425 | 1.1 | 0.88208 | 0.69458 | 4.7786e-13 | -136.625 | 120.7211 | 4.8005e-13 | -140.8835 | 126.7539
Line_1 | 0 | 1.0858 | 1.0858 | 0 | 1.0858 | 1.0858 | 0 | 12.5375 | 12.5375 | 0 | 12.5375 | 12.5375 | -5.2106e-15 | -10.3342 | 1.4923 | 1.0914e-28 | 10.9473 | -0.87927 | 1.5632e-14 | -0.87368 | -7.9682 | -1.3027e-14 | 1.5692 | 8.6638 | 0 | 30.9589 | -149.0411 | 0 | -149.0411 | 30.9589 | 1.1 | 0.8272 | 0.6466 | 1.1 | 0.88208 | 0.69458 | 4.7486e-13 | -144.2087 | 131.5665 | 4.8005e-13 | -140.8835 | 126.7539
Line_2 | 0 | 0.54289 | 0.54289 | 0 | 0.54289 | 0.54289 | 0 | 6.2688 | 6.2688 | 0 | 6.2688 | 6.2688 | -5.2106e-15 | -5.3204 | 0.59289 | 5.2106e-15 | 5.4736 | -0.43963 | 1.8237e-14 | -0.61073 | -4.158 | -1.5632e-14 | 0.78462 | 4.3319 | 0 | 30.9589 | -149.0411 | 0 | -149.0411 | 30.9589 | 1.1 | 0.85428 | 0.67 | 1.1 | 0.88208 | 0.69458 | 4.6827e-13 | -142.4927 | 129.0741 | 4.8005e-13 | -140.8835 | 126.7539
Line_3 | 0 | 0.54289 | 0.54289 | 0 | 0.54289 | 0.54289 | 0 | 6.2688 | 6.2688 | 0 | 6.2688 | 6.2688 | 2.6053e-15 | -5.1671 | 0.74615 | -7.816e-15 | 5.3204 | -0.59289 | 2.1593e-29 | -0.43684 | -3.9841 | 5.2106e-15 | 0.61073 | 4.158 | 0 | 30.9589 | -149.0411 | 0 | -149.0411 | 30.9589 | 1.1 | 0.8272 | 0.6466 | 1.1 | 0.85428 | 0.67 | 4.7486e-13 | -144.2087 | 131.5665 | 4.6827e-13 | -142.4927 | 129.0741

## LL_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 2.6061 | 2.6061 | 0 | 2.6061 | 2.6061 | 0 | 30.0921 | 30.0921 | 0 | 30.0921 | 30.0921 | 2.4869e-14 | 24.6317 | -2.0295 | -2.6053e-14 | -17.851 | 8.8102 | 7.1054e-15 | -0.29866 | 13.6553 | -4.737e-15 | 4.3057 | -9.6483 | 0 | -152.3733 | 27.6267 | 0 | 27.6267 | -152.3733 | 1 | 0.8186 | 0.45877 | 1 | 0.61023 | 0.43419 | 9.3709e-13 | -153.068 | 126.0805 | 9.4959e-13 | -165.934 | 160.0269
Line_1 | 0 | 1.7374 | 1.7374 | 0 | 1.7374 | 1.7374 | 0 | 20.0614 | 20.0614 | 0 | 20.0614 | 20.0614 | -1.7764e-14 | -8.8871 | 8.8871 | 1.7764e-14 | 11.9007 | -5.8735 | -4.737e-15 | 4.6513 | -4.6513 | 2.9441e-28 | -2.8704 | 6.4322 | 0 | 27.6267 | -152.3733 | 0 | -152.3733 | 27.6267 | 1 | 0.5 | 0.5 | 1 | 0.61023 | 0.43419 | 9.5658e-13 | -180 | 180 | 9.4959e-13 | -165.934 | 160.0269
Line_2 | 0 | 0.86868 | 0.86868 | 0 | 0.86868 | 0.86868 | 0 | 10.0307 | 10.0307 | 0 | 10.0307 | 10.0307 | -3.1974e-14 | -5.1969 | 3.6901 | 2.9606e-14 | 5.9503 | -2.9367 | 4.737e-15 | 1.8804 | -2.7709 | -4.737e-15 | -1.4352 | 3.2161 | 0 | 27.6267 | -152.3733 | 0 | -152.3733 | 27.6267 | 1 | 0.55098 | 0.46005 | 1 | 0.61023 | 0.43419 | 9.4332e-13 | -172.2653 | 170.7242 | 9.4959e-13 | -165.934 | 160.0269
Line_3 | 0 | 0.86868 | 0.86868 | 0 | 0.86868 | 0.86868 | 0 | 10.0307 | 10.0307 | 0 | 10.0307 | 10.0307 | 1.4211e-14 | -4.4435 | 4.4435 | -1.4211e-14 | 5.1969 | -3.6901 | -9.4739e-15 | 2.3257 | -2.3257 | 4.737e-15 | -1.8804 | 2.7709 | 0 | 27.6267 | -152.3733 | 0 | -152.3733 | 27.6267 | 1 | 0.5 | 0.5 | 1 | 0.55098 | 0.46005 | 9.5658e-13 | -180 | 180 | 9.4332e-13 | -172.2653 | 170.7242

## LL_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 2.6061 | 2.6061 | 0 | 2.6061 | 2.6061 | 0 | 30.0921 | 30.0921 | 0 | 30.0921 | 30.0921 | 2.4869e-14 | 24.6317 | -2.0295 | -2.6053e-14 | -17.851 | 8.8102 | 7.1054e-15 | -0.29866 | 13.6553 | -4.737e-15 | 4.3057 | -9.6483 | 0 | -152.3733 | 27.6267 | 0 | 27.6267 | -152.3733 | 1 | 0.8186 | 0.45877 | 1 | 0.61023 | 0.43419 | 9.3709e-13 | -153.068 | 126.0805 | 9.4959e-13 | -165.934 | 160.0269
Line_1 | 0 | 1.7374 | 1.7374 | 0 | 1.7374 | 1.7374 | 0 | 20.0614 | 20.0614 | 0 | 20.0614 | 20.0614 | -1.7764e-14 | -8.8871 | 8.8871 | 1.7764e-14 | 11.9007 | -5.8735 | -4.737e-15 | 4.6513 | -4.6513 | 2.9441e-28 | -2.8704 | 6.4322 | 0 | 27.6267 | -152.3733 | 0 | -152.3733 | 27.6267 | 1 | 0.5 | 0.5 | 1 | 0.61023 | 0.43419 | 9.5658e-13 | -180 | 180 | 9.4959e-13 | -165.934 | 160.0269
Line_2 | 0 | 0.86868 | 0.86868 | 0 | 0.86868 | 0.86868 | 0 | 10.0307 | 10.0307 | 0 | 10.0307 | 10.0307 | -3.1974e-14 | -5.1969 | 3.6901 | 2.9606e-14 | 5.9503 | -2.9367 | 4.737e-15 | 1.8804 | -2.7709 | -4.737e-15 | -1.4352 | 3.2161 | 0 | 27.6267 | -152.3733 | 0 | -152.3733 | 27.6267 | 1 | 0.55098 | 0.46005 | 1 | 0.61023 | 0.43419 | 9.4332e-13 | -172.2653 | 170.7242 | 9.4959e-13 | -165.934 | 160.0269
Line_3 | 0 | 0.86868 | 0.86868 | 0 | 0.86868 | 0.86868 | 0 | 10.0307 | 10.0307 | 0 | 10.0307 | 10.0307 | 1.4211e-14 | -4.4435 | 4.4435 | -1.4211e-14 | 5.1969 | -3.6901 | -9.4739e-15 | 2.3257 | -2.3257 | 4.737e-15 | -1.8804 | 2.7709 | 0 | 27.6267 | -152.3733 | 0 | -152.3733 | 27.6267 | 1 | 0.5 | 0.5 | 1 | 0.55098 | 0.46005 | 9.5658e-13 | -180 | 180 | 9.4332e-13 | -172.2653 | 170.7242

## LL_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 1.3721 | 1.3721 | 0 | 1.3721 | 1.3721 | 0 | 15.8432 | 15.8432 | 0 | 15.8432 | 15.8432 | 1.125e-14 | 14.2512 | 1.4266 | -1.125e-14 | -12.3717 | 0.45296 | 4.737e-15 | 1.9064 | 11.2087 | -4.737e-15 | -0.79565 | -10.098 | 0 | -144.0449 | 35.9551 | 0 | 35.9551 | -144.0449 | 1 | 0.90753 | 0.71319 | 1 | 0.7825 | 0.63801 | 5.0014e-13 | -136.4258 | 118.7019 | 5.051e-13 | -140.3651 | 128.5235
Line_1 | 0 | 0.9147 | 0.9147 | 0 | 0.9147 | 0.9147 | 0 | 10.5621 | 10.5621 | 0 | 10.5621 | 10.5621 | -5.9212e-15 | -7.4125 | 1.1373 | 5.9212e-15 | 8.2478 | -0.30197 | -7.1054e-15 | -0.036791 | -6.2383 | 7.1054e-15 | 0.53044 | 6.732 | 0 | 35.9551 | -144.0449 | 0 | -144.0449 | 35.9551 | 1 | 0.70181 | 0.60037 | 1 | 0.7825 | 0.63801 | 5.0894e-13 | -143.7605 | 136.2873 | 5.051e-13 | -140.3651 | 128.5235
Line_2 | 0 | 0.45735 | 0.45735 | 0 | 0.45735 | 0.45735 | 0 | 5.2811 | 5.2811 | 0 | 5.2811 | 5.2811 | -1.4211e-14 | -3.9151 | 0.35982 | 1.4211e-14 | 4.1239 | -0.15099 | -1.2458e-28 | -0.14181 | -3.2426 | 1.2528e-28 | 0.26522 | 3.366 | 0 | 35.9551 | -144.0449 | 0 | -144.0449 | 35.9551 | 1 | 0.74183 | 0.61777 | 1 | 0.7825 | 0.63801 | 5.023e-13 | -141.9705 | 132.2872 | 5.051e-13 | -140.3651 | 128.5235
Line_3 | 0 | 0.45735 | 0.45735 | 0 | 0.45735 | 0.45735 | 0 | 5.2811 | 5.2811 | 0 | 5.2811 | 5.2811 | 9.4739e-15 | -3.7062 | 0.56866 | -9.4739e-15 | 3.9151 | -0.35982 | -7.1054e-15 | -0.018396 | -3.1192 | 7.1054e-15 | 0.14181 | 3.2426 | 0 | 35.9551 | -144.0449 | 0 | -144.0449 | 35.9551 | 1 | 0.70181 | 0.60037 | 1 | 0.74183 | 0.61777 | 5.0894e-13 | -143.7605 | 136.2873 | 5.023e-13 | -141.9705 | 132.2872

## LL_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 1.3721 | 1.3721 | 0 | 1.3721 | 1.3721 | 0 | 15.8432 | 15.8432 | 0 | 15.8432 | 15.8432 | 1.125e-14 | 14.2512 | 1.4266 | -1.125e-14 | -12.3717 | 0.45296 | 4.737e-15 | 1.9064 | 11.2087 | -4.737e-15 | -0.79565 | -10.098 | 0 | -144.0449 | 35.9551 | 0 | 35.9551 | -144.0449 | 1 | 0.90753 | 0.71319 | 1 | 0.7825 | 0.63801 | 5.0014e-13 | -136.4258 | 118.7019 | 5.051e-13 | -140.3651 | 128.5235
Line_1 | 0 | 0.9147 | 0.9147 | 0 | 0.9147 | 0.9147 | 0 | 10.5621 | 10.5621 | 0 | 10.5621 | 10.5621 | -5.9212e-15 | -7.4125 | 1.1373 | 5.9212e-15 | 8.2478 | -0.30197 | -7.1054e-15 | -0.036791 | -6.2383 | 7.1054e-15 | 0.53044 | 6.732 | 0 | 35.9551 | -144.0449 | 0 | -144.0449 | 35.9551 | 1 | 0.70181 | 0.60037 | 1 | 0.7825 | 0.63801 | 5.0894e-13 | -143.7605 | 136.2873 | 5.051e-13 | -140.3651 | 128.5235
Line_2 | 0 | 0.45735 | 0.45735 | 0 | 0.45735 | 0.45735 | 0 | 5.2811 | 5.2811 | 0 | 5.2811 | 5.2811 | -1.4211e-14 | -3.9151 | 0.35982 | 1.4211e-14 | 4.1239 | -0.15099 | -1.2458e-28 | -0.14181 | -3.2426 | 1.2528e-28 | 0.26522 | 3.366 | 0 | 35.9551 | -144.0449 | 0 | -144.0449 | 35.9551 | 1 | 0.74183 | 0.61777 | 1 | 0.7825 | 0.63801 | 5.023e-13 | -141.9705 | 132.2872 | 5.051e-13 | -140.3651 | 128.5235
Line_3 | 0 | 0.45735 | 0.45735 | 0 | 0.45735 | 0.45735 | 0 | 5.2811 | 5.2811 | 0 | 5.2811 | 5.2811 | 9.4739e-15 | -3.7062 | 0.56866 | -9.4739e-15 | 3.9151 | -0.35982 | -7.1054e-15 | -0.018396 | -3.1192 | 7.1054e-15 | 0.14181 | 3.2426 | 0 | 35.9551 | -144.0449 | 0 | -144.0449 | 35.9551 | 1 | 0.70181 | 0.60037 | 1 | 0.74183 | 0.61777 | 5.0894e-13 | -143.7605 | 136.2873 | 5.023e-13 | -141.9705 | 132.2872

## LG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 2.6092 | 1.3046 | 1.3046 | 2.6078 | 1.306 | 1.306 | 30.1288 | 15.0644 | 15.0644 | 30.1126 | 15.0806 | 15.0806 | 7.5365 | -11.9952 | 15.7939 | -4.0009 | 12.8975 | -14.9215 | 7.8172 | 11.9602 | 4.7806 | -3.801 | -10.9664 | -3.7792 | -75.5138 | 104.4862 | 104.4862 | 104.4862 | -75.514 | -75.514 |  | 0.3604 | 1.1244 | 1.0954 | 0.18326 | 1.1226 | 1.0207 | -29.4664 | -120.4302 | 121.3265 | -31.9811 | -115.8877 | 118.6985
Line_1 | 1.9264 | 0.68465 | 0.68465 | 1.9279 | 0.68314 | 0.68314 | 22.2438 | 7.9056 | 7.9056 | 22.261 | 7.8883 | 7.8883 | 2.0313e-10 | 6.9793 | -7.8093 | 3.0185 | -7.088 | 7.6679 | -1.3166e-10 | -5.271 | -2.413 | 2.7445 | 5.3082 | 2.4555 | 105.7465 | -79.0619 | -79.0619 | -74.2586 | 100.9418 | 100.9418 |  | 0 | 1.1063 | 1.0339 | 0.18326 | 1.1226 | 1.0207 | 0 | -116.1232 | 118.1084 | -31.9811 | -115.8877 | 118.6985
Line_2 | 0.68044 | 0.62693 | 0.62693 | 0.68174 | 0.62561 | 0.62561 | 7.857 | 7.2392 | 7.2392 | 7.8721 | 7.224 | 7.224 | -1.1109 | 6.3924 | -6.6979 | 0.98235 | -5.8095 | 7.2536 | -1.01 | -5.2745 | -0.92982 | 1.0565 | 5.6582 | 1.3237 | 100.9165 | -71.6391 | -71.6391 | -79.0653 | 108.3567 | 108.3567 |  | 0.19109 | 1.1448 | 0.93411 | 0.18326 | 1.1226 | 1.0207 | -36.8093 | -111.1657 | 116.2643 | -31.9811 | -115.8877 | 118.6985
Line_3 | 1.249 | 0.10282 | 0.10282 | 1.2504 | 0.10203 | 0.10203 | 14.4227 | 1.1873 | 1.1873 | 14.4388 | 1.1782 | 1.1782 | 1.2766e-10 | 1.2702 | -0.44024 | 2.265 | -1.2645 | 0.41603 | -9.1305e-11 | 0.33448 | -1.1459 | 1.5757 | -0.46924 | 1.0189 | 108.3699 | -130.8754 | -130.8754 | -71.6345 | 48.4758 | 48.4758 |  | 0 | 1.1063 | 1.0339 | 0.19109 | 1.1448 | 0.93411 | 0 | -116.1232 | 118.1084 | -36.8093 | -111.1657 | 116.2643

## LG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 2.6092 | 1.3046 | 1.3046 | 2.6078 | 1.306 | 1.306 | 30.1288 | 15.0644 | 15.0644 | 30.1126 | 15.0806 | 15.0806 | 7.5365 | -11.9952 | 15.7939 | -4.0009 | 12.8975 | -14.9215 | 7.8172 | 11.9602 | 4.7806 | -3.801 | -10.9664 | -3.7792 | -75.5138 | 104.4862 | 104.4862 | 104.4862 | -75.514 | -75.514 |  | 0.3604 | 1.1244 | 1.0954 | 0.18326 | 1.1226 | 1.0207 | -29.4664 | -120.4302 | 121.3265 | -31.9811 | -115.8877 | 118.6985
Line_1 | 1.9264 | 0.68465 | 0.68465 | 1.9279 | 0.68314 | 0.68314 | 22.2438 | 7.9056 | 7.9056 | 22.261 | 7.8883 | 7.8883 | 2.0313e-10 | 6.9793 | -7.8093 | 3.0185 | -7.088 | 7.6679 | -1.3166e-10 | -5.271 | -2.413 | 2.7445 | 5.3082 | 2.4555 | 105.7465 | -79.0619 | -79.0619 | -74.2586 | 100.9418 | 100.9418 |  | 0 | 1.1063 | 1.0339 | 0.18326 | 1.1226 | 1.0207 | 0 | -116.1232 | 118.1084 | -31.9811 | -115.8877 | 118.6985
Line_2 | 0.68044 | 0.62693 | 0.62693 | 0.68174 | 0.62561 | 0.62561 | 7.857 | 7.2392 | 7.2392 | 7.8721 | 7.224 | 7.224 | -1.1109 | 6.3924 | -6.6979 | 0.98235 | -5.8095 | 7.2536 | -1.01 | -5.2745 | -0.92982 | 1.0565 | 5.6582 | 1.3237 | 100.9165 | -71.6391 | -71.6391 | -79.0653 | 108.3567 | 108.3567 |  | 0.19109 | 1.1448 | 0.93411 | 0.18326 | 1.1226 | 1.0207 | -36.8093 | -111.1657 | 116.2643 | -31.9811 | -115.8877 | 118.6985
Line_3 | 1.249 | 0.10282 | 0.10282 | 1.2504 | 0.10203 | 0.10203 | 14.4227 | 1.1873 | 1.1873 | 14.4388 | 1.1782 | 1.1782 | 1.2766e-10 | 1.2702 | -0.44024 | 2.265 | -1.2645 | 0.41603 | -9.1305e-11 | 0.33448 | -1.1459 | 1.5757 | -0.46924 | 1.0189 | 108.3699 | -130.8754 | -130.8754 | -71.6345 | 48.4758 | 48.4758 |  | 0 | 1.1063 | 1.0339 | 0.19109 | 1.1448 | 0.93411 | 0 | -116.1232 | 118.1084 | -36.8093 | -111.1657 | 116.2643

## LG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.84648 | 0.42324 | 0.42324 | 0.84602 | 0.42369 | 0.42369 | 9.7743 | 4.8871 | 4.8871 | 9.769 | 4.8924 | 4.8924 | 6.1671 | -2.2459 | 5.3327 | -5.7921 | 2.342 | -5.2448 | 6.1967 | 4.9292 | -0.48036 | -5.7711 | -4.8286 | 0.58681 | -54.481 | 125.519 | 125.519 | 125.519 | -54.4812 | -54.4812 |  | 0.89444 | 1.1084 | 1.0956 | 0.83697 | 1.0969 | 1.0787 | -9.3441 | -119.9853 | 120.3718 | -9.5852 | -118.6067 | 119.135
Line_1 | 0.62494 | 0.22211 | 0.22211 | 0.62543 | 0.22162 | 0.22162 | 7.2162 | 2.5647 | 2.5647 | 7.2218 | 2.5591 | 2.5591 | -4.0538 | 1.3689 | -2.7764 | 4.3743 | -1.3788 | 2.7572 | -3.8793 | -2.4453 | 0.14198 | 4.1715 | 2.4451 | -0.13676 | 126.7793 | -58.0291 | -58.0291 | -53.2258 | 121.9746 | 121.9746 |  | 0.77754 | 1.0927 | 1.0839 | 0.83697 | 1.0969 | 1.0787 | -9.481 | -118.7892 | 119.0434 | -9.5852 | -118.6067 | 119.135
Line_2 | 0.22075 | 0.20339 | 0.20339 | 0.22117 | 0.20296 | 0.20296 | 2.5489 | 2.3485 | 2.3485 | 2.5538 | 2.3436 | 2.3436 | -1.4284 | 1.0251 | -2.4328 | 1.4178 | -0.96316 | 2.4877 | -1.5923 | -2.3469 | 0.49287 | 1.5996 | 2.3835 | -0.45005 | 121.9493 | -50.6063 | -50.6063 | -58.0325 | 129.3895 | 129.3895 |  | 0.83919 | 1.0905 | 1.0569 | 0.83697 | 1.0969 | 1.0787 | -9.9452 | -117.0103 | 117.9409 | -9.5852 | -118.6067 | 119.135
Line_3 | 0.40521 | 0.033358 | 0.033358 | 0.40566 | 0.033101 | 0.033101 | 4.6789 | 0.38518 | 0.38518 | 4.6842 | 0.38222 | 0.38222 | -2.7408 | 0.41576 | -0.27454 | 2.9821 | -0.4141 | 0.26804 | -2.3924 | -0.065453 | -0.31456 | 2.5611 | 0.04732 | 0.30225 | 129.4027 | -109.8426 | -109.8426 | -50.6017 | 69.5086 | 69.5086 |  | 0.77754 | 1.0927 | 1.0839 | 0.83919 | 1.0905 | 1.0569 | -9.481 | -118.7892 | 119.0434 | -9.9452 | -117.0103 | 117.9409

## LG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.84648 | 0.42324 | 0.42324 | 0.84602 | 0.42369 | 0.42369 | 9.7743 | 4.8871 | 4.8871 | 9.769 | 4.8924 | 4.8924 | 6.1671 | -2.2459 | 5.3327 | -5.7921 | 2.342 | -5.2448 | 6.1967 | 4.9292 | -0.48036 | -5.7711 | -4.8286 | 0.58681 | -54.481 | 125.519 | 125.519 | 125.519 | -54.4812 | -54.4812 |  | 0.89444 | 1.1084 | 1.0956 | 0.83697 | 1.0969 | 1.0787 | -9.3441 | -119.9853 | 120.3718 | -9.5852 | -118.6067 | 119.135
Line_1 | 0.62494 | 0.22211 | 0.22211 | 0.62543 | 0.22162 | 0.22162 | 7.2162 | 2.5647 | 2.5647 | 7.2218 | 2.5591 | 2.5591 | -4.0538 | 1.3689 | -2.7764 | 4.3743 | -1.3788 | 2.7572 | -3.8793 | -2.4453 | 0.14198 | 4.1715 | 2.4451 | -0.13676 | 126.7793 | -58.0291 | -58.0291 | -53.2258 | 121.9746 | 121.9746 |  | 0.77754 | 1.0927 | 1.0839 | 0.83697 | 1.0969 | 1.0787 | -9.481 | -118.7892 | 119.0434 | -9.5852 | -118.6067 | 119.135
Line_2 | 0.22075 | 0.20339 | 0.20339 | 0.22117 | 0.20296 | 0.20296 | 2.5489 | 2.3485 | 2.3485 | 2.5538 | 2.3436 | 2.3436 | -1.4284 | 1.0251 | -2.4328 | 1.4178 | -0.96316 | 2.4877 | -1.5923 | -2.3469 | 0.49287 | 1.5996 | 2.3835 | -0.45005 | 121.9493 | -50.6063 | -50.6063 | -58.0325 | 129.3895 | 129.3895 |  | 0.83919 | 1.0905 | 1.0569 | 0.83697 | 1.0969 | 1.0787 | -9.9452 | -117.0103 | 117.9409 | -9.5852 | -118.6067 | 119.135
Line_3 | 0.40521 | 0.033358 | 0.033358 | 0.40566 | 0.033101 | 0.033101 | 4.6789 | 0.38518 | 0.38518 | 4.6842 | 0.38222 | 0.38222 | -2.7408 | 0.41576 | -0.27454 | 2.9821 | -0.4141 | 0.26804 | -2.3924 | -0.065453 | -0.31456 | 2.5611 | 0.04732 | 0.30225 | 129.4027 | -109.8426 | -109.8426 | -50.6017 | 69.5086 | 69.5086 |  | 0.77754 | 1.0927 | 1.0839 | 0.83919 | 1.0905 | 1.0569 | -9.481 | -118.7892 | 119.0434 | -9.9452 | -117.0103 | 117.9409

## LG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 2.1346 | 1.0673 | 1.0673 | 2.1335 | 1.0685 | 1.0685 | 24.6487 | 12.3243 | 12.3243 | 24.6354 | 12.3376 | 12.3376 | 9.4428 | -7.376 | 12.1367 | -4.8995 | 8.527 | -11.0069 | 5.795 | 10.0708 | 1.4152 | -3.1066 | -9.4079 | -0.74306 | -66.0786 | 113.9214 | 113.9214 | 113.9215 | -66.0788 | -66.0788 |  | 0.44948 | 1.0129 | 0.99145 | 0.23549 | 1.0291 | 0.89417 | -34.5415 | -119.8588 | 120.5724 | -33.7011 | -113.8909 | 117.7833
Line_1 | 1.5591 | 0.57965 | 0.57965 | 1.5604 | 0.57835 | 0.57835 | 18.0031 | 6.6932 | 6.6932 | 18.0178 | 6.6782 | 6.6782 | -8.3141e-11 | 5.0376 | -5.9829 | 3.6665 | -5.1094 | 5.8862 | -2.428e-11 | -4.7297 | -1.1318 | 2.1355 | 4.5968 | 1.0058 | 116.0897 | -71.9195 | -71.9195 | -63.9191 | 108.0864 | 108.0864 |  | 0 | 1.0324 | 0.90974 | 0.23549 | 1.0291 | 0.89417 | 0 | -115.1143 | 118.793 | -33.7011 | -113.8909 | 117.7833
Line_2 | 0.57622 | 0.49764 | 0.49764 | 0.57721 | 0.4966 | 0.4966 | 6.6536 | 5.7462 | 5.7462 | 6.665 | 5.7343 | 5.7343 | -1.3227 | 4.0893 | -4.4661 | 1.233 | -3.4176 | 5.1207 | -1.0954 | -4.4851 | 0.60041 | 0.97114 | 4.8111 | -0.26275 | 108.0464 | -59.2717 | -59.2717 | -71.9247 | 120.7207 | 120.7207 |  | 0.25812 | 1.0563 | 0.78422 | 0.23549 | 1.0291 | 0.89417 | -32.323 | -106.9148 | 113.0715 | -33.7011 | -113.8909 | 117.7833
Line_3 | 0.99139 | 0.14406 | 0.14406 | 0.99253 | 0.1434 | 0.1434 | 11.4476 | 1.6635 | 1.6635 | 11.4607 | 1.6559 | 1.6559 | -5.3945e-11 | 1.7085 | -0.76317 | 2.6372 | -1.6942 | 0.75649 | -1.1097e-11 | 0.17377 | -1.3068 | 1.3403 | -0.43444 | 1.0554 | 120.7445 | -120.9219 | -120.9219 | -59.2634 | 58.7029 | 58.7029 |  | 0 | 1.0324 | 0.90974 | 0.25812 | 1.0563 | 0.78422 | 0 | -115.1143 | 118.793 | -32.323 | -106.9148 | 113.0715

## LG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 2.1346 | 1.0673 | 1.0673 | 2.1335 | 1.0685 | 1.0685 | 24.6487 | 12.3243 | 12.3243 | 24.6354 | 12.3376 | 12.3376 | 9.4428 | -7.376 | 12.1367 | -4.8995 | 8.527 | -11.0069 | 5.795 | 10.0708 | 1.4152 | -3.1066 | -9.4079 | -0.74306 | -66.0786 | 113.9214 | 113.9214 | 113.9215 | -66.0788 | -66.0788 |  | 0.44948 | 1.0129 | 0.99145 | 0.23549 | 1.0291 | 0.89417 | -34.5415 | -119.8588 | 120.5724 | -33.7011 | -113.8909 | 117.7833
Line_1 | 1.5591 | 0.57965 | 0.57965 | 1.5604 | 0.57835 | 0.57835 | 18.0031 | 6.6932 | 6.6932 | 18.0178 | 6.6782 | 6.6782 | -8.3141e-11 | 5.0376 | -5.9829 | 3.6665 | -5.1094 | 5.8862 | -2.428e-11 | -4.7297 | -1.1318 | 2.1355 | 4.5968 | 1.0058 | 116.0897 | -71.9195 | -71.9195 | -63.9191 | 108.0864 | 108.0864 |  | 0 | 1.0324 | 0.90974 | 0.23549 | 1.0291 | 0.89417 | 0 | -115.1143 | 118.793 | -33.7011 | -113.8909 | 117.7833
Line_2 | 0.57622 | 0.49764 | 0.49764 | 0.57721 | 0.4966 | 0.4966 | 6.6536 | 5.7462 | 5.7462 | 6.665 | 5.7343 | 5.7343 | -1.3227 | 4.0893 | -4.4661 | 1.233 | -3.4176 | 5.1207 | -1.0954 | -4.4851 | 0.60041 | 0.97114 | 4.8111 | -0.26275 | 108.0464 | -59.2717 | -59.2717 | -71.9247 | 120.7207 | 120.7207 |  | 0.25812 | 1.0563 | 0.78422 | 0.23549 | 1.0291 | 0.89417 | -32.323 | -106.9148 | 113.0715 | -33.7011 | -113.8909 | 117.7833
Line_3 | 0.99139 | 0.14406 | 0.14406 | 0.99253 | 0.1434 | 0.1434 | 11.4476 | 1.6635 | 1.6635 | 11.4607 | 1.6559 | 1.6559 | -5.3945e-11 | 1.7085 | -0.76317 | 2.6372 | -1.6942 | 0.75649 | -1.1097e-11 | 0.17377 | -1.3068 | 1.3403 | -0.43444 | 1.0554 | 120.7445 | -120.9219 | -120.9219 | -59.2634 | 58.7029 | 58.7029 |  | 0 | 1.0324 | 0.90974 | 0.25812 | 1.0563 | 0.78422 | 0 | -115.1143 | 118.793 | -32.323 | -106.9148 | 113.0715

## LG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.73201 | 0.366 | 0.366 | 0.73161 | 0.3664 | 0.3664 | 8.4525 | 4.2262 | 4.2262 | 8.4479 | 4.2308 | 4.2308 | 5.1292 | -1.6029 | 4.1721 | -4.5928 | 1.739 | -4.0422 | 4.7002 | 3.9291 | -0.56907 | -4.3819 | -3.8541 | 0.64889 | -52.0843 | 127.9157 | 127.9157 | 127.9158 | -52.0846 | -52.0846 |  | 0.82308 | 1.0041 | 0.99632 | 0.7514 | 0.99941 | 0.96765 | -9.5832 | -119.8917 | 120.1485 | -8.4301 | -117.7994 | 118.7956
Line_1 | 0.53465 | 0.19877 | 0.19877 | 0.53509 | 0.19833 | 0.19833 | 6.1736 | 2.2952 | 2.2952 | 6.1787 | 2.2901 | 2.2901 | -3.0442 | 1.1414 | -2.2272 | 3.4774 | -1.1485 | 2.2124 | -2.8221 | -1.9985 | 0.11256 | 3.076 | 1.9797 | -0.12699 | 130.084 | -57.9253 | -57.9253 | -49.9248 | 122.0807 | 122.0807 |  | 0.67239 | 1.0027 | 0.97159 | 0.7514 | 0.99941 | 0.96765 | -7.0843 | -118.1923 | 119.1816 | -8.4301 | -117.7994 | 118.7956
Line_2 | 0.1976 | 0.17065 | 0.17065 | 0.19794 | 0.1703 | 0.1703 | 2.2816 | 1.9705 | 1.9705 | 2.2856 | 1.9664 | 1.9664 | -1.1236 | 0.66969 | -1.7553 | 1.1153 | -0.59049 | 1.8298 | -1.319 | -1.8388 | 0.56279 | 1.3059 | 1.8744 | -0.5219 | 122.0406 | -45.2775 | -45.2775 | -57.9305 | 134.7149 | 134.7149 |  | 0.7594 | 0.99315 | 0.93547 | 0.7514 | 0.99941 | 0.96765 | -8.3867 | -115.2662 | 116.9455 | -8.4301 | -117.7994 | 118.7956
Line_3 | 0.33997 | 0.049401 | 0.049401 | 0.34036 | 0.049175 | 0.049175 | 3.9256 | 0.57043 | 0.57043 | 3.9301 | 0.56783 | 0.56783 | -2.075 | 0.56097 | -0.38424 | 2.3872 | -0.5585 | 0.3805 | -1.6315 | -0.11173 | -0.39941 | 1.7912 | 0.078127 | 0.37064 | 134.7387 | -106.9276 | -106.9276 | -45.2691 | 72.6971 | 72.6971 |  | 0.67239 | 1.0027 | 0.97159 | 0.7594 | 0.99315 | 0.93547 | -7.0843 | -118.1923 | 119.1816 | -8.3867 | -115.2662 | 116.9455

## LG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.73201 | 0.366 | 0.366 | 0.73161 | 0.3664 | 0.3664 | 8.4525 | 4.2262 | 4.2262 | 8.4479 | 4.2308 | 4.2308 | 5.1292 | -1.6029 | 4.1721 | -4.5928 | 1.739 | -4.0422 | 4.7002 | 3.9291 | -0.56907 | -4.3819 | -3.8541 | 0.64889 | -52.0843 | 127.9157 | 127.9157 | 127.9158 | -52.0846 | -52.0846 |  | 0.82308 | 1.0041 | 0.99632 | 0.7514 | 0.99941 | 0.96765 | -9.5832 | -119.8917 | 120.1485 | -8.4301 | -117.7994 | 118.7956
Line_1 | 0.53465 | 0.19877 | 0.19877 | 0.53509 | 0.19833 | 0.19833 | 6.1736 | 2.2952 | 2.2952 | 6.1787 | 2.2901 | 2.2901 | -3.0442 | 1.1414 | -2.2272 | 3.4774 | -1.1485 | 2.2124 | -2.8221 | -1.9985 | 0.11256 | 3.076 | 1.9797 | -0.12699 | 130.084 | -57.9253 | -57.9253 | -49.9248 | 122.0807 | 122.0807 |  | 0.67239 | 1.0027 | 0.97159 | 0.7514 | 0.99941 | 0.96765 | -7.0843 | -118.1923 | 119.1816 | -8.4301 | -117.7994 | 118.7956
Line_2 | 0.1976 | 0.17065 | 0.17065 | 0.19794 | 0.1703 | 0.1703 | 2.2816 | 1.9705 | 1.9705 | 2.2856 | 1.9664 | 1.9664 | -1.1236 | 0.66969 | -1.7553 | 1.1153 | -0.59049 | 1.8298 | -1.319 | -1.8388 | 0.56279 | 1.3059 | 1.8744 | -0.5219 | 122.0406 | -45.2775 | -45.2775 | -57.9305 | 134.7149 | 134.7149 |  | 0.7594 | 0.99315 | 0.93547 | 0.7514 | 0.99941 | 0.96765 | -8.3867 | -115.2662 | 116.9455 | -8.4301 | -117.7994 | 118.7956
Line_3 | 0.33997 | 0.049401 | 0.049401 | 0.34036 | 0.049175 | 0.049175 | 3.9256 | 0.57043 | 0.57043 | 3.9301 | 0.56783 | 0.56783 | -2.075 | 0.56097 | -0.38424 | 2.3872 | -0.5585 | 0.3805 | -1.6315 | -0.11173 | -0.39941 | 1.7912 | 0.078127 | 0.37064 | 134.7387 | -106.9276 | -106.9276 | -45.2691 | 72.6971 | 72.6971 |  | 0.67239 | 1.0027 | 0.97159 | 0.7594 | 0.99315 | 0.93547 | -7.0843 | -118.1923 | 119.1816 | -8.3867 | -115.2662 | 116.9455

## LLG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.3827 | 3.2275 | 3.3277 | 1.3842 | 3.2273 | 3.3272 | 15.9656 | 37.268 | 38.4245 | 15.9828 | 37.2656 | 38.4196 | 3.5289 | 10.7865 | 8.7571 | -2.5337 | -5.3752 | -2.9947 | 17.5543 | 8.3266 | 13.4357 | -16.4425 | -2.1698 | -6.9127 | -77.7597 | -175.8448 | 28.4466 | 102.2402 | 4.1814 | -151.578 |  | 1.1215 | 0.36564 | 0.41738 | 1.0409 | 0.15555 | 0.19609 | 0.8738 | -138.1786 | 85.3513 | 3.4803 | -153.836 | 94.999
Line_1 | 0.7256 | 2.232 | 2.2396 | 0.72401 | 2.2322 | 2.2403 | 8.3786 | 25.7724 | 25.8607 | 8.3602 | 25.7749 | 25.869 | -0.93228 | 1.5137e-10 | 1.8844e-10 | 0.79106 | 3.575 | 2.4332 | -8.6308 | -1.2241e-10 | -4.5686e-11 | 8.6661 | 1.8148 | 4.4508 | 98.6922 | -0.70964 | -146.3723 | -81.3041 | 179.2498 | 33.6641 |  | 1.0361 | 0 | 0 | 1.0409 | 0.15555 | 0.19609 | 2.5272 | 0 | 0 | 3.4803 | -153.836 | 94.999
Line_2 | 0.66444 | 1.0215 | 1.1152 | 0.66304 | 1.0216 | 1.1152 | 7.6722 | 11.7953 | 12.8777 | 7.6561 | 11.7962 | 12.8776 | -1.1054 | -1.5528 | 0.37783 | 1.7426 | 1.8002 | 0.56146 | -7.3478 | 0.89119 | -2.4288 | 7.7764 | 0.35501 | 2.4619 | 106.1151 | 15.0864 | -162.2257 | -73.8891 | -164.9919 | 17.8461 |  | 0.96848 | 0.15179 | 0.19088 | 1.0409 | 0.15555 | 0.19609 | 7.5599 | 165.2344 | 116.6163 | 3.4803 | -153.836 | 94.999
Line_3 | 0.10898 | 1.2792 | 1.2056 | 0.10814 | 1.2798 | 1.2065 | 1.2583 | 14.7709 | 13.9215 | 1.2487 | 14.7783 | 13.9317 | 0.93228 | 9.9907e-11 | 9.1964e-11 | -0.94417 | 2.2425 | 0.9821 | -0.91141 | -4.9667e-11 | -4.9378e-11 | 0.75562 | -0.057479 | 2.4712 | 46.8787 | -13.2372 | -131.7675 | -133.77 | 166.7027 | 48.2897 |  | 1.0361 | 0 | 0 | 0.96848 | 0.15179 | 0.19088 | 2.5272 | 0 | 0 | 7.5599 | 165.2344 | 116.6163

## LLG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.3827 | 3.2275 | 3.3277 | 1.3842 | 3.2273 | 3.3272 | 15.9656 | 37.268 | 38.4245 | 15.9828 | 37.2656 | 38.4196 | 3.5289 | 10.7865 | 8.7571 | -2.5337 | -5.3752 | -2.9947 | 17.5543 | 8.3266 | 13.4357 | -16.4425 | -2.1698 | -6.9127 | -77.7597 | -175.8448 | 28.4466 | 102.2402 | 4.1814 | -151.578 |  | 1.1215 | 0.36564 | 0.41738 | 1.0409 | 0.15555 | 0.19609 | 0.8738 | -138.1786 | 85.3513 | 3.4803 | -153.836 | 94.999
Line_1 | 0.7256 | 2.232 | 2.2396 | 0.72401 | 2.2322 | 2.2403 | 8.3786 | 25.7724 | 25.8607 | 8.3602 | 25.7749 | 25.869 | -0.93228 | 1.5137e-10 | 1.8844e-10 | 0.79106 | 3.575 | 2.4332 | -8.6308 | -1.2241e-10 | -4.5686e-11 | 8.6661 | 1.8148 | 4.4508 | 98.6922 | -0.70964 | -146.3723 | -81.3041 | 179.2498 | 33.6641 |  | 1.0361 | 0 | 0 | 1.0409 | 0.15555 | 0.19609 | 2.5272 | 0 | 0 | 3.4803 | -153.836 | 94.999
Line_2 | 0.66444 | 1.0215 | 1.1152 | 0.66304 | 1.0216 | 1.1152 | 7.6722 | 11.7953 | 12.8777 | 7.6561 | 11.7962 | 12.8776 | -1.1054 | -1.5528 | 0.37783 | 1.7426 | 1.8002 | 0.56146 | -7.3478 | 0.89119 | -2.4288 | 7.7764 | 0.35501 | 2.4619 | 106.1151 | 15.0864 | -162.2257 | -73.8891 | -164.9919 | 17.8461 |  | 0.96848 | 0.15179 | 0.19088 | 1.0409 | 0.15555 | 0.19609 | 7.5599 | 165.2344 | 116.6163 | 3.4803 | -153.836 | 94.999
Line_3 | 0.10898 | 1.2792 | 1.2056 | 0.10814 | 1.2798 | 1.2065 | 1.2583 | 14.7709 | 13.9215 | 1.2487 | 14.7783 | 13.9317 | 0.93228 | 9.9907e-11 | 9.1964e-11 | -0.94417 | 2.2425 | 0.9821 | -0.91141 | -4.9667e-11 | -4.9378e-11 | 0.75562 | -0.057479 | 2.4712 | 46.8787 | -13.2372 | -131.7675 | -133.77 | 166.7027 | 48.2897 |  | 1.0361 | 0 | 0 | 0.96848 | 0.15179 | 0.19088 | 2.5272 | 0 | 0 | 7.5599 | 165.2344 | 116.6163

## LLG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.43259 | 1.0959 | 1.0998 | 0.43305 | 1.0958 | 1.0997 | 4.9951 | 12.6546 | 12.6991 | 5.0004 | 12.6536 | 12.6979 | 3.1524 | 10.0172 | 5.1502 | -3.058 | -9.3943 | -4.5167 | 4.5252 | 5.1106 | 10.3097 | -4.4194 | -4.3969 | -9.5982 | -54.7469 | -155.6087 | 47.1154 | 125.253 | 24.4152 | -132.9083 |  | 1.1041 | 0.88865 | 0.90751 | 1.0748 | 0.81971 | 0.8354 | 0.39122 | -128.5785 | 110.571 | 0.5722 | -130.5032 | 111.8908
Line_1 | 0.22702 | 0.75828 | 0.73487 | 0.22652 | 0.75837 | 0.73506 | 2.6213 | 8.7559 | 8.4856 | 2.6156 | 8.7569 | 8.4878 | -1.4703 | -5.8386 | -3.3125 | 1.4536 | 6.2455 | 3.5676 | -2.4062 | -3.3101 | -5.6586 | 2.4061 | 3.5383 | 6.1278 | 121.705 | 20.0003 | -127.937 | -58.2913 | -160.0368 | 52.099 |  | 1.0757 | 0.76653 | 0.77271 | 1.0748 | 0.81971 | 0.8354 | 0.27784 | -130.4489 | 111.7185 | 0.5722 | -130.5032 | 111.8908
Line_2 | 0.20788 | 0.34476 | 0.37301 | 0.20744 | 0.34481 | 0.37298 | 2.4004 | 3.9809 | 4.3071 | 2.3953 | 3.9815 | 4.3068 | -1.5451 | -3.123 | -0.83788 | 1.6044 | 3.1488 | 0.94912 | -1.9739 | -0.72021 | -3.4609 | 2.0133 | 0.85855 | 3.4704 | 129.1279 | 34.3172 | -142.8804 | -50.8763 | -145.7549 | 37.1866 |  | 1.0443 | 0.80508 | 0.82674 | 1.0748 | 0.81971 | 0.8354 | 1.0741 | -132.6966 | 113.5101 | 0.5722 | -130.5032 | 111.8908
Line_3 | 0.034095 | 0.43258 | 0.38657 | 0.033832 | 0.43279 | 0.38681 | 0.39369 | 4.995 | 4.4637 | 0.39066 | 4.9974 | 4.4665 | 0.14753 | -2.8944 | -2.427 | -0.15171 | 3.1399 | 2.5178 | -0.39698 | -2.5065 | -2.4508 | 0.37871 | 2.5156 | 2.7012 | 69.8915 | 8.6587 | -113.5612 | -110.7572 | -171.3964 | 66.4978 |  | 1.0757 | 0.76653 | 0.77271 | 1.0443 | 0.80508 | 0.82674 | 0.27784 | -130.4489 | 111.7185 | 1.0741 | -132.6966 | 113.5101

## LLG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.43259 | 1.0959 | 1.0998 | 0.43305 | 1.0958 | 1.0997 | 4.9951 | 12.6546 | 12.6991 | 5.0004 | 12.6536 | 12.6979 | 3.1524 | 10.0172 | 5.1502 | -3.058 | -9.3943 | -4.5167 | 4.5252 | 5.1106 | 10.3097 | -4.4194 | -4.3969 | -9.5982 | -54.7469 | -155.6087 | 47.1154 | 125.253 | 24.4152 | -132.9083 |  | 1.1041 | 0.88865 | 0.90751 | 1.0748 | 0.81971 | 0.8354 | 0.39122 | -128.5785 | 110.571 | 0.5722 | -130.5032 | 111.8908
Line_1 | 0.22702 | 0.75828 | 0.73487 | 0.22652 | 0.75837 | 0.73506 | 2.6213 | 8.7559 | 8.4856 | 2.6156 | 8.7569 | 8.4878 | -1.4703 | -5.8386 | -3.3125 | 1.4536 | 6.2455 | 3.5676 | -2.4062 | -3.3101 | -5.6586 | 2.4061 | 3.5383 | 6.1278 | 121.705 | 20.0003 | -127.937 | -58.2913 | -160.0368 | 52.099 |  | 1.0757 | 0.76653 | 0.77271 | 1.0748 | 0.81971 | 0.8354 | 0.27784 | -130.4489 | 111.7185 | 0.5722 | -130.5032 | 111.8908
Line_2 | 0.20788 | 0.34476 | 0.37301 | 0.20744 | 0.34481 | 0.37298 | 2.4004 | 3.9809 | 4.3071 | 2.3953 | 3.9815 | 4.3068 | -1.5451 | -3.123 | -0.83788 | 1.6044 | 3.1488 | 0.94912 | -1.9739 | -0.72021 | -3.4609 | 2.0133 | 0.85855 | 3.4704 | 129.1279 | 34.3172 | -142.8804 | -50.8763 | -145.7549 | 37.1866 |  | 1.0443 | 0.80508 | 0.82674 | 1.0748 | 0.81971 | 0.8354 | 1.0741 | -132.6966 | 113.5101 | 0.5722 | -130.5032 | 111.8908
Line_3 | 0.034095 | 0.43258 | 0.38657 | 0.033832 | 0.43279 | 0.38681 | 0.39369 | 4.995 | 4.4637 | 0.39066 | 4.9974 | 4.4665 | 0.14753 | -2.8944 | -2.427 | -0.15171 | 3.1399 | 2.5178 | -0.39698 | -2.5065 | -2.4508 | 0.37871 | 2.5156 | 2.7012 | 69.8915 | 8.6587 | -113.5612 | -110.7572 | -171.3964 | 66.4978 |  | 1.0757 | 0.76653 | 0.77271 | 1.0443 | 0.80508 | 0.82674 | 0.27784 | -130.4489 | 111.7185 | 1.0741 | -132.6966 | 113.5101

## LLG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.1346 | 2.5898 | 2.7422 | 1.1358 | 2.5897 | 2.7418 | 13.1014 | 29.9045 | 31.6641 | 13.1155 | 29.9034 | 31.6593 | 4.2891 | 13.0439 | 11.6806 | -3.002 | -6.3507 | -4.1716 | 12.4568 | 4.3405 | 10.3916 | -11.7089 | -0.36934 | -5.9679 | -70.2705 | -164.9048 | 39.4514 | 109.7292 | 15.1221 | -140.5726 |  | 1.0056 | 0.4597 | 0.49375 | 0.92163 | 0.21273 | 0.22999 | 0.73014 | -146.4993 | 81.1094 | 5.349 | -161.5495 | 94.4738
Line_1 | 0.6162 | 1.8059 | 1.8242 | 0.61482 | 1.8059 | 1.8249 | 7.1152 | 20.8527 | 21.0639 | 7.0993 | 20.8529 | 21.0726 | -1.0683 | -1.2695e-10 | -7.1719e-11 | 0.97224 | 4.3953 | 3.1104 | -6.624 | -9.9822e-11 | -1.4759e-10 | 6.4703 | 0.60034 | 3.7167 | 103.8885 | 10.7164 | -135.6377 | -76.1056 | -169.3273 | 44.3985 |  | 0.943 | 0 | 0 | 0.92163 | 0.21273 | 0.22999 | 4.7268 | 0 | 0 | 5.349 | -161.5495 | 94.4738
Line_2 | 0.52901 | 0.80149 | 0.93714 | 0.52792 | 0.80158 | 0.93714 | 6.1085 | 9.2548 | 10.8212 | 6.0958 | 9.2559 | 10.8211 | -1.283 | -1.6552 | 0.15336 | 2.0298 | 1.9554 | 1.0612 | -4.869 | 1.3209 | -2.5905 | 5.2386 | -0.231 | 2.2512 | 116.5363 | 25.2662 | -150.3547 | -63.4713 | -154.8121 | 29.7125 |  | 0.82429 | 0.22881 | 0.23981 | 0.92163 | 0.21273 | 0.22999 | 11.7747 | 166.6754 | 123.0333 | 5.349 | -161.5495 | 94.4738
Line_3 | 0.15314 | 1.0493 | 0.94803 | 0.15244 | 1.0497 | 0.9488 | 1.7683 | 12.1158 | 10.9469 | 1.7603 | 12.1207 | 10.9558 | 1.0683 | -6.1289e-11 | -5.5304e-11 | -1.0657 | 2.7029 | 1.1475 | -1.2804 | -7.1049e-11 | -6.4916e-11 | 0.98466 | -0.62099 | 2.3634 | 54.8862 | -0.32302 | -121.1252 | -125.4891 | 179.6144 | 58.932 |  | 0.943 | 0 | 0 | 0.82429 | 0.22881 | 0.23981 | 4.7268 | 0 | 0 | 11.7747 | 166.6754 | 123.0333

## LLG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.1346 | 2.5898 | 2.7422 | 1.1358 | 2.5897 | 2.7418 | 13.1014 | 29.9045 | 31.6641 | 13.1155 | 29.9034 | 31.6593 | 4.2891 | 13.0439 | 11.6806 | -3.002 | -6.3507 | -4.1716 | 12.4568 | 4.3405 | 10.3916 | -11.7089 | -0.36934 | -5.9679 | -70.2705 | -164.9048 | 39.4514 | 109.7292 | 15.1221 | -140.5726 |  | 1.0056 | 0.4597 | 0.49375 | 0.92163 | 0.21273 | 0.22999 | 0.73014 | -146.4993 | 81.1094 | 5.349 | -161.5495 | 94.4738
Line_1 | 0.6162 | 1.8059 | 1.8242 | 0.61482 | 1.8059 | 1.8249 | 7.1152 | 20.8527 | 21.0639 | 7.0993 | 20.8529 | 21.0726 | -1.0683 | -1.2695e-10 | -7.1719e-11 | 0.97224 | 4.3953 | 3.1104 | -6.624 | -9.9822e-11 | -1.4759e-10 | 6.4703 | 0.60034 | 3.7167 | 103.8885 | 10.7164 | -135.6377 | -76.1056 | -169.3273 | 44.3985 |  | 0.943 | 0 | 0 | 0.92163 | 0.21273 | 0.22999 | 4.7268 | 0 | 0 | 5.349 | -161.5495 | 94.4738
Line_2 | 0.52901 | 0.80149 | 0.93714 | 0.52792 | 0.80158 | 0.93714 | 6.1085 | 9.2548 | 10.8212 | 6.0958 | 9.2559 | 10.8211 | -1.283 | -1.6552 | 0.15336 | 2.0298 | 1.9554 | 1.0612 | -4.869 | 1.3209 | -2.5905 | 5.2386 | -0.231 | 2.2512 | 116.5363 | 25.2662 | -150.3547 | -63.4713 | -154.8121 | 29.7125 |  | 0.82429 | 0.22881 | 0.23981 | 0.92163 | 0.21273 | 0.22999 | 11.7747 | 166.6754 | 123.0333 | 5.349 | -161.5495 | 94.4738
Line_3 | 0.15314 | 1.0493 | 0.94803 | 0.15244 | 1.0497 | 0.9488 | 1.7683 | 12.1158 | 10.9469 | 1.7603 | 12.1207 | 10.9558 | 1.0683 | -6.1289e-11 | -5.5304e-11 | -1.0657 | 2.7029 | 1.1475 | -1.2804 | -7.1049e-11 | -6.4916e-11 | 0.98466 | -0.62099 | 2.3634 | 54.8862 | -0.32302 | -121.1252 | -125.4891 | 179.6144 | 58.932 |  | 0.943 | 0 | 0 | 0.82429 | 0.22881 | 0.23981 | 4.7268 | 0 | 0 | 11.7747 | 166.6754 | 123.0333

## LLG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.37582 | 0.93872 | 0.95181 | 0.37622 | 0.93866 | 0.95171 | 4.3396 | 10.8394 | 10.9905 | 4.3442 | 10.8387 | 10.9894 | 2.5891 | 8.1516 | 4.5794 | -2.4502 | -7.2731 | -3.6716 | 3.4853 | 3.5735 | 7.9072 | -3.4055 | -3.049 | -7.3748 | -53.1288 | -152.6331 | 50.2858 | 126.8709 | 27.3913 | -129.7379 |  | 1.0005 | 0.82112 | 0.8314 | 0.96573 | 0.72761 | 0.74965 | 0.26301 | -128.9613 | 110.2087 | 1.1363 | -129.8644 | 113.7958
Line_1 | 0.2041 | 0.65558 | 0.62743 | 0.20365 | 0.65562 | 0.62764 | 2.3568 | 7.57 | 7.245 | 2.3515 | 7.5705 | 7.2473 | -1.1447 | -4.3488 | -2.464 | 1.132 | 4.9251 | 2.8138 | -1.9884 | -2.3587 | -4.2199 | 1.9686 | 2.4669 | 4.6476 | 121.0302 | 23.5693 | -125.0495 | -58.9638 | -156.4705 | 54.9877 |  | 0.97354 | 0.65353 | 0.67448 | 0.96573 | 0.72761 | 0.74965 | 1.1017 | -127.9562 | 114.6699 | 1.1363 | -129.8644 | 113.7958
Line_2 | 0.17522 | 0.28786 | 0.33032 | 0.17486 | 0.28793 | 0.33028 | 2.0233 | 3.3239 | 3.8142 | 2.0191 | 3.3247 | 3.8138 | -1.2387 | -2.3148 | -0.69727 | 1.3182 | 2.348 | 0.85778 | -1.3979 | -0.4507 | -2.7598 | 1.4368 | 0.58208 | 2.7273 | 133.678 | 36.2838 | -138.8078 | -46.3296 | -143.7873 | 41.255 |  | 0.92312 | 0.7095 | 0.7463 | 0.96573 | 0.72761 | 0.74965 | 2.1353 | -132.6986 | 117.0132 | 1.1363 | -129.8644 | 113.7958
Line_3 | 0.050726 | 0.37998 | 0.31647 | 0.050494 | 0.38014 | 0.31668 | 0.58573 | 4.3876 | 3.6542 | 0.58305 | 4.3894 | 3.6568 | 0.18634 | -2.258 | -1.7313 | -0.18834 | 2.601 | 1.8381 | -0.53892 | -1.7674 | -1.7543 | 0.5042 | 1.7128 | 2.0172 | 72.0279 | 13.992 | -110.708 | -108.3474 | -166.0642 | 69.3538 |  | 0.97354 | 0.65353 | 0.67448 | 0.92312 | 0.7095 | 0.7463 | 1.1017 | -127.9562 | 114.6699 | 2.1353 | -132.6986 | 117.0132

## LLG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.37582 | 0.93872 | 0.95181 | 0.37622 | 0.93866 | 0.95171 | 4.3396 | 10.8394 | 10.9905 | 4.3442 | 10.8387 | 10.9894 | 2.5891 | 8.1516 | 4.5794 | -2.4502 | -7.2731 | -3.6716 | 3.4853 | 3.5735 | 7.9072 | -3.4055 | -3.049 | -7.3748 | -53.1288 | -152.6331 | 50.2858 | 126.8709 | 27.3913 | -129.7379 |  | 1.0005 | 0.82112 | 0.8314 | 0.96573 | 0.72761 | 0.74965 | 0.26301 | -128.9613 | 110.2087 | 1.1363 | -129.8644 | 113.7958
Line_1 | 0.2041 | 0.65558 | 0.62743 | 0.20365 | 0.65562 | 0.62764 | 2.3568 | 7.57 | 7.245 | 2.3515 | 7.5705 | 7.2473 | -1.1447 | -4.3488 | -2.464 | 1.132 | 4.9251 | 2.8138 | -1.9884 | -2.3587 | -4.2199 | 1.9686 | 2.4669 | 4.6476 | 121.0302 | 23.5693 | -125.0495 | -58.9638 | -156.4705 | 54.9877 |  | 0.97354 | 0.65353 | 0.67448 | 0.96573 | 0.72761 | 0.74965 | 1.1017 | -127.9562 | 114.6699 | 1.1363 | -129.8644 | 113.7958
Line_2 | 0.17522 | 0.28786 | 0.33032 | 0.17486 | 0.28793 | 0.33028 | 2.0233 | 3.3239 | 3.8142 | 2.0191 | 3.3247 | 3.8138 | -1.2387 | -2.3148 | -0.69727 | 1.3182 | 2.348 | 0.85778 | -1.3979 | -0.4507 | -2.7598 | 1.4368 | 0.58208 | 2.7273 | 133.678 | 36.2838 | -138.8078 | -46.3296 | -143.7873 | 41.255 |  | 0.92312 | 0.7095 | 0.7463 | 0.96573 | 0.72761 | 0.74965 | 2.1353 | -132.6986 | 117.0132 | 1.1363 | -129.8644 | 113.7958
Line_3 | 0.050726 | 0.37998 | 0.31647 | 0.050494 | 0.38014 | 0.31668 | 0.58573 | 4.3876 | 3.6542 | 0.58305 | 4.3894 | 3.6568 | 0.18634 | -2.258 | -1.7313 | -0.18834 | 2.601 | 1.8381 | -0.53892 | -1.7674 | -1.7543 | 0.5042 | 1.7128 | 2.0172 | 72.0279 | 13.992 | -110.708 | -108.3474 | -166.0642 | 69.3538 |  | 0.97354 | 0.65353 | 0.67448 | 0.92312 | 0.7095 | 0.7463 | 1.1017 | -127.9562 | 114.6699 | 2.1353 | -132.6986 | 117.0132