## LLL_max_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.70184 | 0.70184 | -7.4193 | -7.4193
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.70184 | 0.70184 | -7.4193 | -7.4193
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.70184 | 0.70184 | -7.4193 | -7.4193
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.70184 | 0.70184 | -7.4193 | -7.4193
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.70184 | 0.70184 | -7.4193 | -7.4193
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.70184 | 0.70184 | -7.4193 | -7.4193
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.70184 | 0.70184 | -7.4193 | -7.4193
Line16_4_18 | 3.6243 | 3.6243 | 0 | 7.0007 | 2.511 | 2.511 | 0.39406 | -1e-07 | 0.78812 | -1e-07 | -70.8543 | 109.1457 | 0.35092 | 0 | -7.4193 | 0
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.70184 | 0.70184 | -7.4193 | -7.4193
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.70184 | 0.70184 | -7.4193 | -7.4193
Line2_1_4 | 3.6243 | 3.6243 | 0 | 0 | 2.511 | 2.511 | 0.78812 | -0.39406 | 1.5762 | -0.78812 | -70.8543 | 109.1457 | 0.70184 | 0.35092 | -7.4193 | -7.4193
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.70184 | 0.70184 | -7.4193 | -7.4193
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.70184 | 0.70184 | -7.4193 | -7.4193
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.70184 | 0.70184 | -7.4193 | -7.4193
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.70184 | 0.70184 | -7.4193 | -7.4193
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.70184 | 0.70184 | -7.4193 | -7.4193
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.70184 | 0.70184 | -7.4193 | -7.4193
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.70184 | 0.70184 | -7.4193 | -7.4193

## LLL_max_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72372 | 0.72372 | -7.6495 | -7.6495
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72372 | 0.72372 | -7.6495 | -7.6495
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72372 | 0.72372 | -7.6495 | -7.6495
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72372 | 0.72372 | -7.6495 | -7.6495
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72372 | 0.72372 | -7.6495 | -7.6495
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72372 | 0.72372 | -7.6495 | -7.6495
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72372 | 0.72372 | -7.6495 | -7.6495
Line16_4_18 | 3.7373 | 3.7373 | 0 | 7.2438 | 2.5893 | 2.5893 | 0.41902 | -1e-07 | 0.83803 | -1e-07 | -71.0844 | 108.9156 | 0.36186 | 0 | -7.6495 | 0
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72372 | 0.72372 | -7.6495 | -7.6495
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72372 | 0.72372 | -7.6495 | -7.6495
Line2_1_4 | 3.7373 | 3.7373 | 0 | 0 | 2.5893 | 2.5893 | 0.83803 | -0.41902 | 1.6761 | -0.83803 | -71.0844 | 108.9156 | 0.72372 | 0.36186 | -7.6495 | -7.6495
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72372 | 0.72372 | -7.6495 | -7.6495
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72372 | 0.72372 | -7.6495 | -7.6495
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72372 | 0.72372 | -7.6495 | -7.6495
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72372 | 0.72372 | -7.6495 | -7.6495
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72372 | 0.72372 | -7.6495 | -7.6495
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72372 | 0.72372 | -7.6495 | -7.6495
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72372 | 0.72372 | -7.6495 | -7.6495

## LLL_max_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.12051 | -0.12051
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.12051 | -0.12051
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.12051 | -0.12051
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.12051 | -0.12051
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.12051 | -0.12051
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.12051 | -0.12051
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.12051 | -0.12051
Line16_4_18 | 0.034003 | 0.034003 | 0 | 0.065681 | 0.023558 | 0.023558 | 0.017378 | -0.017343 | 0.017412 | -0.017343 | -45.2344 | 134.7656 | 1.0442 | 1.0411 | -0.17729 | -0.23442
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.12051 | -0.12051
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.12051 | -0.12051
Line2_1_4 | 0.034003 | 0.034003 | 0 | 0 | 0.023558 | 0.023558 | 0.017412 | -0.017378 | 0.017482 | -0.017412 | -45.2344 | 134.7656 | 1.0474 | 1.0442 | -0.12051 | -0.17729
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.12051 | -0.12051
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.12051 | -0.12051
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.12051 | -0.12051
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.12051 | -0.12051
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.12051 | -0.12051
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.12051 | -0.12051
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 1.0474 | -0.12051 | -0.12051

## LLL_max_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12619 | -0.12619
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12619 | -0.12619
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12619 | -0.12619
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12619 | -0.12619
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12619 | -0.12619
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12619 | -0.12619
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12619 | -0.12619
Line16_4_18 | 0.035618 | 0.035618 | 0 | 0.069037 | 0.024677 | 0.024677 | 0.019068 | -0.01903 | 0.019106 | -0.01903 | -45.2401 | 134.7599 | 1.0938 | 1.0906 | -0.18297 | -0.2401
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12619 | -0.12619
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12619 | -0.12619
Line2_1_4 | 0.035618 | 0.035618 | 0 | 0 | 0.024677 | 0.024677 | 0.019106 | -0.019068 | 0.019182 | -0.019106 | -45.2401 | 134.7599 | 1.0971 | 1.0938 | -0.12619 | -0.18297
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12619 | -0.12619
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12619 | -0.12619
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12619 | -0.12619
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12619 | -0.12619
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12619 | -0.12619
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12619 | -0.12619
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0971 | 1.0971 | -0.12619 | -0.12619

## LLL_min_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.695 | 0.695 | -11.6026 | -11.6026
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.695 | 0.695 | -11.6026 | -11.6026
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.695 | 0.695 | -11.6026 | -11.6026
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.695 | 0.695 | -11.6026 | -11.6026
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.695 | 0.695 | -11.6026 | -11.6026
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.695 | 0.695 | -11.6026 | -11.6026
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.695 | 0.695 | -11.6026 | -11.6026
Line16_4_18 | 2.8946 | 2.8946 | 0 | 4.7808 | 2.0055 | 2.0055 | 0.48263 | -1e-07 | 0.50274 | -1e-07 | -57.7717 | 122.2283 | 0.3475 | 0 | -11.6026 | 0
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.695 | 0.695 | -11.6026 | -11.6026
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.695 | 0.695 | -11.6026 | -11.6026
Line2_1_4 | 2.8946 | 2.8946 | 0 | 0 | 2.0055 | 2.0055 | 0.96525 | -0.48263 | 1.0055 | -0.50274 | -57.7717 | 122.2283 | 0.695 | 0.3475 | -11.6026 | -11.6026
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.695 | 0.695 | -11.6026 | -11.6026
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.695 | 0.695 | -11.6026 | -11.6026
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.695 | 0.695 | -11.6026 | -11.6026
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.695 | 0.695 | -11.6026 | -11.6026
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.695 | 0.695 | -11.6026 | -11.6026
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.695 | 0.695 | -11.6026 | -11.6026
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.695 | 0.695 | -11.6026 | -11.6026

## LLL_min_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65842 | 0.65842 | -11.6026 | -11.6026
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65842 | 0.65842 | -11.6026 | -11.6026
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65842 | 0.65842 | -11.6026 | -11.6026
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65842 | 0.65842 | -11.6026 | -11.6026
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65842 | 0.65842 | -11.6026 | -11.6026
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65842 | 0.65842 | -11.6026 | -11.6026
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65842 | 0.65842 | -11.6026 | -11.6026
Line16_4_18 | 2.7423 | 2.7423 | 0 | 4.5292 | 1.8999 | 1.8999 | 0.43316 | -1e-07 | 0.45121 | -1e-07 | -57.7717 | 122.2283 | 0.32921 | 0 | -11.6026 | 0
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65842 | 0.65842 | -11.6026 | -11.6026
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65842 | 0.65842 | -11.6026 | -11.6026
Line2_1_4 | 2.7423 | 2.7423 | 0 | 0 | 1.8999 | 1.8999 | 0.86632 | -0.43316 | 0.90242 | -0.45121 | -57.7717 | 122.2283 | 0.65842 | 0.32921 | -11.6026 | -11.6026
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65842 | 0.65842 | -11.6026 | -11.6026
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65842 | 0.65842 | -11.6026 | -11.6026
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65842 | 0.65842 | -11.6026 | -11.6026
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65842 | 0.65842 | -11.6026 | -11.6026
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65842 | 0.65842 | -11.6026 | -11.6026
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65842 | 0.65842 | -11.6026 | -11.6026
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65842 | 0.65842 | -11.6026 | -11.6026

## LLL_min_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94754 | 0.94754 | -0.12527 | -0.12527
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94754 | 0.94754 | -0.12527 | -0.12527
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94754 | 0.94754 | -0.12527 | -0.12527
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94754 | 0.94754 | -0.12527 | -0.12527
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94754 | 0.94754 | -0.12527 | -0.12527
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94754 | 0.94754 | -0.12527 | -0.12527
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94754 | 0.94754 | -0.12527 | -0.12527
Line16_4_18 | 0.030706 | 0.030706 | 0 | 0.050714 | 0.021274 | 0.021274 | 0.014197 | -0.014143 | 0.014199 | -0.014143 | -45.1344 | 134.8656 | 0.94385 | 0.94017 | -0.1298 | -0.13436
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94754 | 0.94754 | -0.12527 | -0.12527
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94754 | 0.94754 | -0.12527 | -0.12527
Line2_1_4 | 0.030706 | 0.030706 | 0 | 0 | 0.021274 | 0.021274 | 0.014251 | -0.014197 | 0.014256 | -0.014199 | -45.1344 | 134.8656 | 0.94754 | 0.94385 | -0.12527 | -0.1298
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94754 | 0.94754 | -0.12527 | -0.12527
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94754 | 0.94754 | -0.12527 | -0.12527
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94754 | 0.94754 | -0.12527 | -0.12527
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94754 | 0.94754 | -0.12527 | -0.12527
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94754 | 0.94754 | -0.12527 | -0.12527
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94754 | 0.94754 | -0.12527 | -0.12527
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94754 | 0.94754 | -0.12527 | -0.12527

## LLL_min_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89767 | 0.89767 | -0.12527 | -0.12527
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89767 | 0.89767 | -0.12527 | -0.12527
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89767 | 0.89767 | -0.12527 | -0.12527
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89767 | 0.89767 | -0.12527 | -0.12527
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89767 | 0.89767 | -0.12527 | -0.12527
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89767 | 0.89767 | -0.12527 | -0.12527
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89767 | 0.89767 | -0.12527 | -0.12527
Line16_4_18 | 0.02909 | 0.02909 | 0 | 0.048045 | 0.020154 | 0.020154 | 0.012742 | -0.012693 | 0.012744 | -0.012693 | -45.1344 | 134.8656 | 0.89418 | 0.89069 | -0.1298 | -0.13436
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89767 | 0.89767 | -0.12527 | -0.12527
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89767 | 0.89767 | -0.12527 | -0.12527
Line2_1_4 | 0.02909 | 0.02909 | 0 | 0 | 0.020154 | 0.020154 | 0.012791 | -0.012742 | 0.012795 | -0.012744 | -45.1344 | 134.8656 | 0.89767 | 0.89418 | -0.12527 | -0.1298
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89767 | 0.89767 | -0.12527 | -0.12527
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89767 | 0.89767 | -0.12527 | -0.12527
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89767 | 0.89767 | -0.12527 | -0.12527
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89767 | 0.89767 | -0.12527 | -0.12527
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89767 | 0.89767 | -0.12527 | -0.12527
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89767 | 0.89767 | -0.12527 | -0.12527
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89767 | 0.89767 | -0.12527 | -0.12527

## LL_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.1601e-16 | -3.0235e-09 | -4.8365e-09 | -8.1601e-16 | 3.0235e-09 | 4.8365e-09 | 3.3029e-16 | 5.1114e-09 | -1.9712e-09 | -3.4972e-16 | -5.1114e-09 | 1.9712e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.85292 | 0.7501 | 1.05 | 0.85292 | 0.7501 | -1.0102e-12 | -135.0364 | 126.5322 | -1.0186e-12 | -135.0364 | 126.5322
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8858e-16 | -3.0235e-09 | -4.8365e-09 | -3.4972e-16 | 3.0235e-09 | 4.8365e-09 | 2.72e-16 | 5.1114e-09 | -1.9712e-09 | -3.1086e-16 | -5.1114e-09 | 1.9712e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.85292 | 0.7501 | 1.05 | 0.85292 | 0.7501 | -1.0249e-12 | -135.0364 | 126.5322 | -1.0312e-12 | -135.0364 | 126.5322
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1086e-16 | -2.5196e-09 | -4.0305e-09 | -3.1086e-16 | 2.5196e-09 | 4.0305e-09 | 2.3315e-16 | 4.2595e-09 | -1.6426e-09 | -2.1372e-16 | -4.2595e-09 | 1.6426e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.85292 | 0.7501 | 1.05 | 0.85292 | 0.7501 | -1.0312e-12 | -135.0364 | 126.5322 | -1.0367e-12 | -135.0364 | 126.5322
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.72e-16 | -1.5118e-09 | -2.4183e-09 | -3.1086e-16 | 1.5118e-09 | 2.4183e-09 | 1.9429e-17 | 2.5557e-09 | -9.8558e-10 | -5.8287e-17 | -2.5557e-09 | 9.8558e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.85292 | 0.7501 | 1.05 | 0.85292 | 0.7501 | -1.0367e-12 | -135.0364 | 126.5322 | -1.0402e-12 | -135.0364 | 126.5322
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8858e-17 | -5.0392e-10 | -8.0609e-10 | -1.1657e-16 | 5.0392e-10 | 8.0609e-10 | 2.1372e-16 | 8.5191e-10 | -3.2853e-10 | -2.5258e-16 | -8.5191e-10 | 3.2853e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.85292 | 0.7501 | 1.05 | 0.85292 | 0.7501 | -1.0367e-12 | -135.0364 | 126.5322 | -1.0369e-12 | -135.0364 | 126.5322
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5543e-16 | -1.0078e-09 | -1.6122e-09 | -1.1657e-16 | 1.0078e-09 | 1.6122e-09 | 3.8858e-17 | 1.7038e-09 | -6.5706e-10 | -1.9429e-17 | -1.7038e-09 | 6.5706e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.85292 | 0.7501 | 1.05 | 0.85292 | 0.7501 | -1.0402e-12 | -135.0364 | 126.5322 | -1.042e-12 | -135.0364 | 126.5322
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.8858e-17 | -5.0392e-10 | -8.0609e-10 | 3.8858e-17 | 5.0392e-10 | 8.0609e-10 | 1.9429e-17 | 8.5191e-10 | -3.2853e-10 | -7.0702e-31 | -8.5191e-10 | 3.2853e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.85292 | 0.7501 | 1.05 | 0.85292 | 0.7501 | -1.042e-12 | -135.0364 | 126.5322 | -1.0425e-12 | -135.0364 | 126.5322
Line16_4_18 | 0 | 3.1387 | 3.1387 | 0 | 3.1387 | 3.1387 | 0 | 0.72485 | 0.72485 | 0 | 0.72485 | 0.72485 | -3.1086e-16 | 0.45801 | -0.26098 | 3.1086e-16 | -0.3595 | 0.3595 | 3.8858e-17 | 0.072221 | 0.32184 | -3.8858e-17 | 0.12481 | -0.12481 | 0 | -160.8543 | 19.1457 | 0 | 19.1457 | -160.8543 | 1.05 | 0.63968 | 0.57164 | 1.05 | 0.525 | 0.525 | -1.0158e-12 | -151.8935 | 148.1848 | -1.0181e-12 | 180 | -180
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.4358e-31 | -5.0392e-10 | -8.0609e-10 | 0 | 5.0392e-10 | 8.0609e-10 | -1.9429e-17 | 8.5191e-10 | -3.2853e-10 | 0 | -8.5191e-10 | 3.2853e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.85292 | 0.7501 | 1.05 | 0.85292 | 0.7501 | -1.0132e-12 | -135.0364 | 126.5322 | -1.0137e-12 | -135.0364 | 126.5322
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.6058e-16 | -4.0313e-09 | -6.4487e-09 | -6.6058e-16 | 4.0313e-09 | 6.4487e-09 | 2.9143e-16 | 6.8153e-09 | -2.6282e-09 | -2.9143e-16 | -6.8153e-09 | 2.6282e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.85292 | 0.7501 | 1.05 | 0.85292 | 0.7501 | -1.0102e-12 | -135.0364 | 126.5322 | -1.0173e-12 | -135.0364 | 126.5322
Line2_1_4 | 0 | 3.1387 | 3.1387 | 0 | 3.1387 | 3.1387 | 0 | 0.72485 | 0.72485 | 0 | 0.72485 | 0.72485 | 3.8858e-16 | 0.55653 | -0.16247 | -3.8858e-16 | -0.45801 | 0.26098 | 2.72e-16 | 0.26925 | 0.51887 | -2.72e-16 | -0.072221 | -0.32184 | 0 | -160.8543 | 19.1457 | 0 | 19.1457 | -160.8543 | 1.05 | 0.85292 | 0.7501 | 1.05 | 0.63968 | 0.57164 | -1.0102e-12 | -135.0364 | 126.5322 | -1.0158e-12 | -151.8935 | 148.1848
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9429e-16 | -1.0078e-09 | -1.6122e-09 | -1.9429e-16 | 1.0078e-09 | 1.6122e-09 | 3.8858e-17 | 1.7038e-09 | -6.5705e-10 | -3.8858e-17 | -1.7038e-09 | 6.5706e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.85292 | 0.7501 | 1.05 | 0.85292 | 0.7501 | -1.0102e-12 | -135.0364 | 126.5322 | -1.0132e-12 | -135.0364 | 126.5322
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.2172e-16 | -2.5196e-09 | -4.0305e-09 | -6.2172e-16 | 2.5196e-09 | 4.0305e-09 | 2.5258e-16 | 4.2595e-09 | -1.6426e-09 | -2.5258e-16 | -4.2595e-09 | 1.6426e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.85292 | 0.7501 | 1.05 | 0.85292 | 0.7501 | -1.0186e-12 | -135.0364 | 126.5322 | -1.0252e-12 | -135.0364 | 126.5322
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.0515e-16 | -2.0157e-09 | -3.2244e-09 | -5.0515e-16 | 2.0157e-09 | 3.2244e-09 | 2.3315e-16 | 3.4076e-09 | -1.3141e-09 | -1.7486e-16 | -3.4076e-09 | 1.3141e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.85292 | 0.7501 | 1.05 | 0.85292 | 0.7501 | -1.0252e-12 | -135.0364 | 126.5322 | -1.029e-12 | -135.0364 | 126.5322
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9429e-16 | -1.5118e-09 | -2.4183e-09 | -2.3315e-16 | 1.5118e-09 | 2.4183e-09 | -1.1657e-16 | 2.5557e-09 | -9.8558e-10 | 9.7145e-17 | -2.5557e-09 | 9.8558e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.85292 | 0.7501 | 1.05 | 0.85292 | 0.7501 | -1.029e-12 | -135.0364 | 126.5322 | -1.0314e-12 | -135.0364 | 126.5322
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.7716e-17 | -5.0392e-10 | -8.0609e-10 | 1.1657e-16 | 5.0392e-10 | 8.0609e-10 | 1.399e-30 | 8.5191e-10 | -3.2853e-10 | 1.9429e-17 | -8.5191e-10 | 3.2853e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.85292 | 0.7501 | 1.05 | 0.85292 | 0.7501 | -1.0314e-12 | -135.0364 | 126.5322 | -1.0324e-12 | -135.0364 | 126.5322
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.0392e-10 | -8.0609e-10 | 3.8858e-17 | 5.0392e-10 | 8.0609e-10 | 0 | 8.5191e-10 | -3.2853e-10 | -6.9996e-31 | -8.5191e-10 | 3.2853e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.85292 | 0.7501 | 1.05 | 0.85292 | 0.7501 | -1.0314e-12 | -135.0364 | 126.5322 | -1.0321e-12 | -135.0364 | 126.5322
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.6629e-16 | -3.5274e-09 | -5.6426e-09 | -4.6629e-16 | 3.5274e-09 | 5.6426e-09 | 2.9143e-16 | 5.9633e-09 | -2.2997e-09 | -2.72e-16 | -5.9633e-09 | 2.2997e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.85292 | 0.7501 | 1.05 | 0.85292 | 0.7501 | -1.0173e-12 | -135.0364 | 126.5322 | -1.0249e-12 | -135.0364 | 126.5322

## LL_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.5133e-16 | -3.3669e-09 | -5.3859e-09 | -6.1062e-16 | 3.3669e-09 | 5.3859e-09 | 5.6991e-16 | 5.759e-09 | -2.262e-09 | -6.1062e-16 | -5.759e-09 | 2.262e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.88719 | 0.77689 | 1.1 | 0.88719 | 0.77689 | -1.8668e-12 | -135.5593 | 126.9102 | -1.8728e-12 | -135.5593 | 126.9102
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4779e-16 | -3.3669e-09 | -5.3859e-09 | -4.4779e-16 | 3.3669e-09 | 5.3859e-09 | 4.4779e-16 | 5.759e-09 | -2.262e-09 | -4.0708e-16 | -5.759e-09 | 2.262e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.88719 | 0.77689 | 1.1 | 0.88719 | 0.77689 | -1.8789e-12 | -135.5593 | 126.9102 | -1.8842e-12 | -135.5593 | 126.9102
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4779e-16 | -2.8058e-09 | -4.4883e-09 | -4.4779e-16 | 2.8058e-09 | 4.4883e-09 | 4.4779e-16 | 4.7992e-09 | -1.885e-09 | -4.4779e-16 | -4.7992e-09 | 1.885e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.88719 | 0.77689 | 1.1 | 0.88719 | 0.77689 | -1.8842e-12 | -135.5593 | 126.9102 | -1.8888e-12 | -135.5593 | 126.9102
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8496e-16 | -1.6835e-09 | -2.693e-09 | -2.4425e-16 | 1.6835e-09 | 2.693e-09 | -9.3938e-30 | 2.8795e-09 | -1.131e-09 | -4.0708e-17 | -2.8795e-09 | 1.131e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.88719 | 0.77689 | 1.1 | 0.88719 | 0.77689 | -1.8888e-12 | -135.5593 | 126.9102 | -1.8924e-12 | -135.5593 | 126.9102
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0708e-17 | -5.6115e-10 | -8.9765e-10 | 4.0708e-17 | 5.6115e-10 | 8.9765e-10 | 4.0708e-16 | 9.5983e-10 | -3.77e-10 | -4.0708e-16 | -9.5983e-10 | 3.77e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.88719 | 0.77689 | 1.1 | 0.88719 | 0.77689 | -1.8888e-12 | -135.5593 | 126.9102 | -1.8874e-12 | -135.5593 | 126.9102
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6283e-16 | -1.1223e-09 | -1.7953e-09 | -1.2212e-16 | 1.1223e-09 | 1.7953e-09 | 4.0708e-17 | 1.9197e-09 | -7.5399e-10 | -4.0708e-17 | -1.9197e-09 | 7.54e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.88719 | 0.77689 | 1.1 | 0.88719 | 0.77689 | -1.8924e-12 | -135.5593 | 126.9102 | -1.8943e-12 | -135.5593 | 126.9102
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.6115e-10 | -8.9765e-10 | -1.3462e-30 | 5.6115e-10 | 8.9765e-10 | 0 | 9.5983e-10 | -3.77e-10 | -4.0708e-17 | -9.5983e-10 | 3.77e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.88719 | 0.77689 | 1.1 | 0.88719 | 0.77689 | -1.8943e-12 | -135.5593 | 126.9102 | -1.8948e-12 | -135.5593 | 126.9102
Line16_4_18 | 0 | 3.2366 | 3.2366 | 0 | 3.2366 | 3.2366 | 0 | 0.74746 | 0.74746 | 0 | 0.74746 | 0.74746 | 0 | 0.49365 | -0.28415 | 1.6283e-16 | -0.3889 | 0.3889 | 0 | 0.07624 | 0.34278 | -5.3216e-30 | 0.13327 | -0.13327 | 0 | -161.0844 | 18.9156 | 0 | 18.9156 | -161.0844 | 1.1 | 0.66828 | 0.59567 | 1.1 | 0.55 | 0.55 | -1.8703e-12 | -152.305 | 148.5727 | -1.8725e-12 | -180 | -180
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.0708e-17 | -5.6115e-10 | -8.9765e-10 | 4.0708e-17 | 5.6115e-10 | 8.9765e-10 | 4.0708e-17 | 9.5983e-10 | -3.77e-10 | -1.3277e-30 | -9.5983e-10 | 3.77e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.88719 | 0.77689 | 1.1 | 0.88719 | 0.77689 | -1.8682e-12 | -135.5593 | 126.9102 | -1.8687e-12 | -135.5593 | 126.9102
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.1062e-16 | -4.4892e-09 | -7.1812e-09 | -5.2921e-16 | 4.4892e-09 | 7.1812e-09 | 4.4779e-16 | 7.6787e-09 | -3.016e-09 | -4.885e-16 | -7.6787e-09 | 3.016e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.88719 | 0.77689 | 1.1 | 0.88719 | 0.77689 | -1.8668e-12 | -135.5593 | 126.9102 | -1.8721e-12 | -135.5593 | 126.9102
Line2_1_4 | 0 | 3.2366 | 3.2366 | 0 | 3.2366 | 3.2366 | 0 | 0.74746 | 0.74746 | 0 | 0.74746 | 0.74746 | 3.2567e-16 | 0.59841 | -0.17939 | -3.2567e-16 | -0.49365 | 0.28415 | 4.0708e-16 | 0.28575 | 0.55229 | -4.885e-16 | -0.07624 | -0.34278 | 0 | -161.0844 | 18.9156 | 0 | 18.9156 | -161.0844 | 1.1 | 0.88719 | 0.77689 | 1.1 | 0.66828 | 0.59567 | -1.8668e-12 | -135.5593 | 126.9102 | -1.8703e-12 | -152.305 | 148.5727
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0354e-16 | -1.1223e-09 | -1.7953e-09 | -1.6283e-16 | 1.1223e-09 | 1.7953e-09 | -8.1416e-17 | 1.9197e-09 | -7.5399e-10 | 8.1416e-17 | -1.9197e-09 | 7.5399e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.88719 | 0.77689 | 1.1 | 0.88719 | 0.77689 | -1.8668e-12 | -135.5593 | 126.9102 | -1.8682e-12 | -135.5593 | 126.9102
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.1062e-16 | -2.8058e-09 | -4.4883e-09 | -6.1062e-16 | 2.8058e-09 | 4.4883e-09 | 4.885e-16 | 4.7992e-09 | -1.885e-09 | -4.885e-16 | -4.7992e-09 | 1.885e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.88719 | 0.77689 | 1.1 | 0.88719 | 0.77689 | -1.8728e-12 | -135.5593 | 126.9102 | -1.8778e-12 | -135.5593 | 126.9102
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6637e-16 | -2.2446e-09 | -3.5906e-09 | -4.0708e-16 | 2.2446e-09 | 3.5906e-09 | 5.2921e-16 | 3.8393e-09 | -1.508e-09 | -5.2921e-16 | -3.8393e-09 | 1.508e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.88719 | 0.77689 | 1.1 | 0.88719 | 0.77689 | -1.8778e-12 | -135.5593 | 126.9102 | -1.8825e-12 | -135.5593 | 126.9102
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2567e-16 | -1.6835e-09 | -2.693e-09 | -3.2567e-16 | 1.6835e-09 | 2.693e-09 | -1.07e-29 | 2.8795e-09 | -1.131e-09 | 1.0726e-29 | -2.8795e-09 | 1.131e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.88719 | 0.77689 | 1.1 | 0.88719 | 0.77689 | -1.8825e-12 | -135.5593 | 126.9102 | -1.8871e-12 | -135.5593 | 126.9102
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.6115e-10 | -8.9765e-10 | 0 | 5.6115e-10 | 8.9765e-10 | 0 | 9.5983e-10 | -3.77e-10 | 0 | -9.5983e-10 | 3.77e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.88719 | 0.77689 | 1.1 | 0.88719 | 0.77689 | -1.8871e-12 | -135.5593 | 126.9102 | -1.8882e-12 | -135.5593 | 126.9102
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.2212e-16 | -5.6115e-10 | -8.9765e-10 | 1.2212e-16 | 5.6115e-10 | 8.9765e-10 | 4.0223e-30 | 9.5983e-10 | -3.77e-10 | -4.024e-30 | -9.5983e-10 | 3.77e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.88719 | 0.77689 | 1.1 | 0.88719 | 0.77689 | -1.8871e-12 | -135.5593 | 126.9102 | -1.8879e-12 | -135.5593 | 126.9102
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4779e-16 | -3.9281e-09 | -6.2836e-09 | -4.0708e-16 | 3.9281e-09 | 6.2836e-09 | 5.2921e-16 | 6.7188e-09 | -2.639e-09 | -5.2921e-16 | -6.7188e-09 | 2.639e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.88719 | 0.77689 | 1.1 | 0.88719 | 0.77689 | -1.8721e-12 | -135.5593 | 126.9102 | -1.8789e-12 | -135.5593 | 126.9102

## LL_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0625e-17 | -4.6325e-11 | -1.333e-10 | -1.0625e-17 | 4.6325e-11 | 1.333e-10 | 4.8572e-18 | 1.2762e-10 | 2.3032e-11 | -4.2501e-18 | -1.2762e-10 | -2.3032e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0442 | 1.05 | 1.048 | 1.0442 | 1.2217e-14 | -120.3021 | 119.9453 | 1.2106e-14 | -120.3021 | 119.9453
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5536e-18 | -4.6325e-11 | -1.333e-10 | -4.5536e-18 | 4.6325e-11 | 1.333e-10 | -6.0715e-19 | 1.2762e-10 | 2.3032e-11 | -9.4042e-34 | -1.2762e-10 | -2.3032e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0442 | 1.05 | 1.048 | 1.0442 | 1.1946e-14 | -120.3021 | 119.9453 | 1.1833e-14 | -120.3021 | 119.9453
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9465e-18 | -3.8604e-11 | -1.1109e-10 | -4.5536e-18 | 3.8604e-11 | 1.1109e-10 | -6.0715e-19 | 1.0635e-10 | 1.9193e-11 | 1.2143e-18 | -1.0635e-10 | -1.9193e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0442 | 1.05 | 1.048 | 1.0442 | 1.1833e-14 | -120.3021 | 119.9453 | 1.172e-14 | -120.3021 | 119.9453
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9465e-18 | -2.3162e-11 | -6.6652e-11 | -3.9465e-18 | 2.3162e-11 | 6.6652e-11 | 1.2143e-18 | 6.3811e-11 | 1.1516e-11 | -1.8215e-18 | -6.3811e-11 | -1.1516e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0442 | 1.05 | 1.048 | 1.0442 | 1.172e-14 | -120.3021 | 119.9453 | 1.166e-14 | -120.3021 | 119.9453
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0358e-19 | -7.7208e-12 | -2.2217e-11 | -3.0358e-19 | 7.7208e-12 | 2.2217e-11 | -4.2501e-18 | 2.127e-11 | 3.8387e-12 | 3.6429e-18 | -2.127e-11 | -3.8387e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0442 | 1.05 | 1.048 | 1.0442 | 1.172e-14 | -120.3021 | 119.9453 | 1.1691e-14 | -120.3021 | 119.9453
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5179e-18 | -1.5442e-11 | -4.4435e-11 | -9.1073e-19 | 1.5442e-11 | 4.4435e-11 | 3.089e-34 | 4.2541e-11 | 7.6773e-12 | -1.8487e-34 | -4.2541e-11 | -7.6773e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0442 | 1.05 | 1.048 | 1.0442 | 1.166e-14 | -120.3021 | 119.9453 | 1.1631e-14 | -120.3021 | 119.9453
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.0715e-19 | -7.7208e-12 | -2.2217e-11 | 6.0715e-19 | 7.7208e-12 | 2.2217e-11 | -1.2143e-18 | 2.127e-11 | 3.8387e-12 | 1.2143e-18 | -2.127e-11 | -3.8387e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0442 | 1.05 | 1.048 | 1.0442 | 1.1631e-14 | -120.3021 | 119.9453 | 1.1612e-14 | -120.3021 | 119.9453
Line16_4_18 | 0 | 0.0584 | 0.0584 | 0 | 0.0584 | 0.0584 | 0 | 0.013487 | 0.013487 | 0 | 0.013487 | 0.013487 | -4.8572e-18 | 0.013608 | 0.0035134 | 4.8572e-18 | -0.013574 | -0.0034793 | -2.4286e-18 | 0.0036287 | 0.013561 | 1.0243e-33 | -0.0035605 | -0.013493 | 0 | -135.4649 | 44.5351 | 0 | 44.5351 | -135.4649 | 1.05 | 1.0442 | 1.0387 | 1.05 | 1.0405 | 1.0331 | 1.2119e-14 | -120.5336 | 120.01 | 1.2082e-14 | -120.7668 | 120.0754
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.0715e-19 | -7.7208e-12 | -2.2217e-11 | 6.0715e-19 | 7.7208e-12 | 2.2217e-11 | -1.289e-34 | 2.127e-11 | 3.8387e-12 | 6.0715e-19 | -2.127e-11 | -3.8387e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0442 | 1.05 | 1.048 | 1.0442 | 1.2164e-14 | -120.3021 | 119.9453 | 1.2145e-14 | -120.3021 | 119.9453
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.5894e-18 | -6.1766e-11 | -1.7774e-10 | -7.5894e-18 | 6.1766e-11 | 1.7774e-10 | 1.8215e-18 | 1.7016e-10 | 3.0709e-11 | -2.4286e-18 | -1.7016e-10 | -3.0709e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0442 | 1.05 | 1.048 | 1.0442 | 1.2217e-14 | -120.3021 | 119.9453 | 1.2086e-14 | -120.3021 | 119.9453
Line2_1_4 | 0 | 0.0584 | 0.0584 | 0 | 0.0584 | 0.0584 | 0 | 0.013487 | 0.013487 | 0 | 0.013487 | 0.013487 | 4.8572e-18 | 0.013642 | 0.0035475 | -6.0715e-18 | -0.013608 | -0.0035134 | 1.2143e-18 | 0.003697 | 0.013629 | -2.4286e-18 | -0.0036287 | -0.013561 | 0 | -135.4649 | 44.5351 | 0 | 44.5351 | -135.4649 | 1.05 | 1.048 | 1.0442 | 1.05 | 1.0442 | 1.0387 | 1.2217e-14 | -120.3021 | 119.9453 | 1.2119e-14 | -120.5336 | 120.01
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0358e-18 | -1.5442e-11 | -4.4435e-11 | -3.0358e-18 | 1.5442e-11 | 4.4435e-11 | 1.8215e-18 | 4.2541e-11 | 7.6773e-12 | -1.8215e-18 | -4.2541e-11 | -7.6773e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0442 | 1.05 | 1.048 | 1.0442 | 1.2217e-14 | -120.3021 | 119.9453 | 1.2164e-14 | -120.3021 | 119.9453
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.6787e-18 | -3.8604e-11 | -1.1109e-10 | -6.6787e-18 | 3.8604e-11 | 1.1109e-10 | 1.8215e-18 | 1.0635e-10 | 1.9193e-11 | -2.4286e-18 | -1.0635e-10 | -1.9193e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0442 | 1.05 | 1.048 | 1.0442 | 1.2106e-14 | -120.3021 | 119.9453 | 1.2005e-14 | -120.3021 | 119.9453
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.6787e-18 | -3.0883e-11 | -8.887e-11 | -6.6787e-18 | 3.0883e-11 | 8.887e-11 | -6.0715e-19 | 8.5081e-11 | 1.5355e-11 | 6.0715e-19 | -8.5081e-11 | -1.5355e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0442 | 1.05 | 1.048 | 1.0442 | 1.2005e-14 | -120.3021 | 119.9453 | 1.193e-14 | -120.3021 | 119.9453
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.125e-18 | -2.3162e-11 | -6.6652e-11 | -2.7322e-18 | 2.3162e-11 | 6.6652e-11 | 4.4248e-34 | 6.3811e-11 | 1.1516e-11 | 6.0715e-19 | -6.3811e-11 | -1.1516e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0442 | 1.05 | 1.048 | 1.0442 | 1.193e-14 | -120.3021 | 119.9453 | 1.1885e-14 | -120.3021 | 119.9453
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0715e-19 | -7.7208e-12 | -2.2217e-11 | -6.0715e-19 | 7.7208e-12 | 2.2217e-11 | 1.2595e-34 | 2.127e-11 | 3.8387e-12 | -6.0715e-19 | -2.127e-11 | -3.8387e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0442 | 1.05 | 1.048 | 1.0442 | 1.1885e-14 | -120.3021 | 119.9453 | 1.1871e-14 | -120.3021 | 119.9453
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.8215e-18 | -7.7208e-12 | -2.2217e-11 | 2.4286e-18 | 7.7208e-12 | 2.2217e-11 | 6.0715e-19 | 2.127e-11 | 3.8386e-12 | -1.2143e-18 | -2.127e-11 | -3.8386e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0442 | 1.05 | 1.048 | 1.0442 | 1.1885e-14 | -120.3021 | 119.9453 | 1.1876e-14 | -120.3021 | 119.9453
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.1608e-18 | -5.4045e-11 | -1.5552e-10 | -4.5536e-18 | 5.4045e-11 | 1.5552e-10 | 6.0715e-19 | 1.4889e-10 | 2.6871e-11 | 6.0715e-19 | -1.4889e-10 | -2.6871e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.048 | 1.0442 | 1.05 | 1.048 | 1.0442 | 1.2086e-14 | -120.3021 | 119.9453 | 1.1946e-14 | -120.3021 | 119.9453

## LL_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0495e-17 | -5.3219e-11 | -1.5314e-10 | -1.1131e-17 | 5.3219e-11 | 1.5314e-10 | 8.9049e-18 | 1.4664e-10 | 2.6437e-11 | -9.541e-18 | -1.4664e-10 | -2.6437e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0936 | 1.1 | 1.0978 | 1.0936 | -9.4872e-15 | -120.3163 | 119.9428 | -9.5983e-15 | -120.3163 | 119.9428
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.7246e-18 | -5.3219e-11 | -1.5314e-10 | -5.7246e-18 | 5.3219e-11 | 1.5314e-10 | 3.1803e-18 | 1.4664e-10 | 2.6437e-11 | -3.8164e-18 | -1.4664e-10 | -2.6437e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0936 | 1.1 | 1.0978 | 1.0936 | -9.7453e-15 | -120.3163 | 119.9428 | -9.8603e-15 | -120.3163 | 119.9428
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.5869e-18 | -4.4349e-11 | -1.2762e-10 | -7.9508e-18 | 4.4349e-11 | 1.2762e-10 | 2.5443e-18 | 1.222e-10 | 2.2031e-11 | -1.2721e-18 | -1.222e-10 | -2.2031e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0936 | 1.1 | 1.0978 | 1.0936 | -9.8603e-15 | -120.3163 | 119.9428 | -9.9742e-15 | -120.3163 | 119.9428
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4066e-18 | -2.6609e-11 | -7.6572e-11 | -5.4066e-18 | 2.6609e-11 | 7.6572e-11 | 2.5443e-18 | 7.332e-11 | 1.3218e-11 | -3.8164e-18 | -7.332e-11 | -1.3218e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0936 | 1.1 | 1.0978 | 1.0936 | -9.9742e-15 | -120.3163 | 119.9428 | -1.0037e-14 | -120.3163 | 119.9428
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2721e-18 | -8.8698e-12 | -2.5524e-11 | -1.2721e-18 | 8.8698e-12 | 2.5524e-11 | 1.2721e-18 | 2.444e-11 | 4.4061e-12 | -2.5443e-18 | -2.444e-11 | -4.4061e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0936 | 1.1 | 1.0978 | 1.0936 | -9.9742e-15 | -120.3163 | 119.9428 | -9.9863e-15 | -120.3163 | 119.9428
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.541e-19 | -1.7739e-11 | -5.1048e-11 | -9.541e-19 | 1.7739e-11 | 5.1048e-11 | 1.2721e-18 | 4.888e-11 | 8.8123e-12 | -3.1803e-18 | -4.888e-11 | -8.8122e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0936 | 1.1 | 1.0978 | 1.0936 | -1.0037e-14 | -120.3163 | 119.9428 | -1.0068e-14 | -120.3163 | 119.9428
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.3607e-19 | -8.8697e-12 | -2.5524e-11 | 0 | 8.8698e-12 | 2.5524e-11 | -6.3607e-19 | 2.444e-11 | 4.4061e-12 | 0 | -2.444e-11 | -4.4061e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0936 | 1.1 | 1.0978 | 1.0936 | -1.0068e-14 | -120.3163 | 119.9428 | -1.0088e-14 | -120.3163 | 119.9428
Line16_4_18 | 0 | 0.061167 | 0.061167 | 0 | 0.061167 | 0.061167 | 0 | 0.014126 | 0.014126 | 0 | 0.014126 | 0.014126 | -1.2721e-18 | 0.01493 | 0.0038518 | -1.2721e-18 | -0.014893 | -0.0038144 | -2.5443e-18 | 0.0039805 | 0.014876 | -2.5443e-18 | -0.0039057 | -0.014801 | 0 | -135.4761 | 44.5239 | 0 | 44.5239 | -135.4761 | 1.1 | 1.0938 | 1.0878 | 1.1 | 1.0899 | 1.0821 | -9.5699e-15 | -120.5478 | 120.0075 | -9.6106e-15 | -120.781 | 120.073
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8623e-18 | -8.8697e-12 | -2.5524e-11 | -2.2262e-18 | 8.8698e-12 | 2.5524e-11 | 1.9082e-18 | 2.444e-11 | 4.4061e-12 | -6.3607e-19 | -2.444e-11 | -4.4061e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0936 | 1.1 | 1.0978 | 1.0936 | -9.5145e-15 | -120.3163 | 119.9428 | -9.5342e-15 | -120.3163 | 119.9428
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.9508e-18 | -7.0958e-11 | -2.0419e-10 | -7.9508e-18 | 7.0958e-11 | 2.0419e-10 | 6.3607e-18 | 1.9552e-10 | 3.5249e-11 | -6.3607e-18 | -1.9552e-10 | -3.5249e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0936 | 1.1 | 1.0978 | 1.0936 | -9.4872e-15 | -120.3163 | 119.9428 | -9.6022e-15 | -120.3163 | 119.9428
Line2_1_4 | 0 | 0.061167 | 0.061167 | 0 | 0.061167 | 0.061167 | 0 | 0.014126 | 0.014126 | 0 | 0.014126 | 0.014126 | 7.6328e-18 | 0.014968 | 0.0038892 | -7.6328e-18 | -0.01493 | -0.0038518 | 5.0885e-18 | 0.0040553 | 0.014951 | -5.0885e-18 | -0.0039805 | -0.014876 | 0 | -135.4761 | 44.5239 | 0 | 44.5239 | -135.4761 | 1.1 | 1.0978 | 1.0936 | 1.1 | 1.0938 | 1.0878 | -9.4872e-15 | -120.3163 | 119.9428 | -9.5699e-15 | -120.5478 | 120.0075
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5902e-18 | -1.7739e-11 | -5.1048e-11 | -1.5902e-18 | 1.7739e-11 | 5.1048e-11 | -6.3607e-19 | 4.888e-11 | 8.8123e-12 | 6.3607e-19 | -4.888e-11 | -8.8123e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0936 | 1.1 | 1.0978 | 1.0936 | -9.4872e-15 | -120.3163 | 119.9428 | -9.5145e-15 | -120.3163 | 119.9428
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.859e-18 | -4.4349e-11 | -1.2762e-10 | -9.859e-18 | 4.4349e-11 | 1.2762e-10 | 7.6328e-18 | 1.222e-10 | 2.2031e-11 | -6.9967e-18 | -1.222e-10 | -2.2031e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0936 | 1.1 | 1.0978 | 1.0936 | -9.5983e-15 | -120.3163 | 119.9428 | -9.7014e-15 | -120.3163 | 119.9428
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.3148e-18 | -3.5479e-11 | -1.021e-10 | -7.9508e-18 | 3.5479e-11 | 1.021e-10 | 6.3607e-18 | 9.776e-11 | 1.7625e-11 | -6.9967e-18 | -9.776e-11 | -1.7624e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0936 | 1.1 | 1.0978 | 1.0936 | -9.7014e-15 | -120.3163 | 119.9428 | -9.8102e-15 | -120.3163 | 119.9428
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1344e-18 | -2.6609e-11 | -7.6572e-11 | -4.1344e-18 | 2.6609e-11 | 7.6572e-11 | 6.3607e-19 | 7.332e-11 | 1.3218e-11 | -1.2721e-18 | -7.332e-11 | -1.3218e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0936 | 1.1 | 1.0978 | 1.0936 | -9.8102e-15 | -120.3163 | 119.9428 | -9.8902e-15 | -120.3163 | 119.9428
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.3607e-19 | -8.8698e-12 | -2.5524e-11 | 0 | 8.8698e-12 | 2.5524e-11 | -1.098e-34 | 2.444e-11 | 4.4061e-12 | 0 | -2.444e-11 | -4.4061e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0936 | 1.1 | 1.0978 | 1.0936 | -9.8902e-15 | -120.3163 | 119.9428 | -9.9053e-15 | -120.3163 | 119.9428
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.3607e-19 | -8.8697e-12 | -2.5524e-11 | 1.2721e-18 | 8.8697e-12 | 2.5524e-11 | 6.3607e-19 | 2.444e-11 | 4.4061e-12 | -6.3607e-19 | -2.444e-11 | -4.4061e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0936 | 1.1 | 1.0978 | 1.0936 | -9.8902e-15 | -120.3163 | 119.9428 | -9.9075e-15 | -120.3163 | 119.9428
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.5869e-18 | -6.2088e-11 | -1.7867e-10 | -8.5869e-18 | 6.2088e-11 | 1.7867e-10 | 5.7246e-18 | 1.7108e-10 | 3.0843e-11 | -5.7246e-18 | -1.7108e-10 | -3.0843e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0978 | 1.0936 | 1.1 | 1.0978 | 1.0936 | -9.6022e-15 | -120.3163 | 119.9428 | -9.7453e-15 | -120.3163 | 119.9428

## LL_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7579e-17 | -1.4366e-09 | -3.9666e-09 | -3.5157e-17 | 1.4366e-09 | 3.9666e-09 | 4.7462e-16 | 4.6273e-09 | -2.4518e-10 | -4.7462e-16 | -4.6273e-09 | 2.4518e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.83839 | 0.68767 | 0.95 | 0.83839 | 0.68767 | -1.678e-12 | -135.3123 | 120.9775 | -1.6698e-12 | -135.3123 | 120.9775
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.7893e-18 | -1.4366e-09 | -3.9666e-09 | -8.7893e-18 | 1.4366e-09 | 3.9666e-09 | 4.3946e-16 | 4.6273e-09 | -2.4519e-10 | -4.2188e-16 | -4.6273e-09 | 2.4519e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.83839 | 0.68767 | 0.95 | 0.83839 | 0.68767 | -1.661e-12 | -135.3123 | 120.9775 | -1.6534e-12 | -135.3123 | 120.9775
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1667e-29 | -1.1971e-09 | -3.3055e-09 | -1.1109e-29 | 1.1971e-09 | 3.3055e-09 | 4.0431e-16 | 3.8561e-09 | -2.0432e-10 | -3.8673e-16 | -3.8561e-09 | 2.0432e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.83839 | 0.68767 | 0.95 | 0.83839 | 0.68767 | -1.6534e-12 | -135.3123 | 120.9775 | -1.6459e-12 | -135.3123 | 120.9775
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6368e-17 | -7.1829e-10 | -1.9833e-09 | -2.6368e-17 | 7.1829e-10 | 1.9833e-09 | -3.5157e-17 | 2.3136e-09 | -1.2259e-10 | 1.7579e-17 | -2.3137e-09 | 1.2259e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.83839 | 0.68767 | 0.95 | 0.83839 | 0.68767 | -1.6459e-12 | -135.3123 | 120.9775 | -1.6448e-12 | -135.3123 | 120.9775
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.9103e-17 | -2.3943e-10 | -6.611e-10 | 9.6682e-17 | 2.3943e-10 | 6.611e-10 | 3.3399e-16 | 7.7122e-10 | -4.0864e-11 | -3.3399e-16 | -7.7122e-10 | 4.0864e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.83839 | 0.68767 | 0.95 | 0.83839 | 0.68767 | -1.6459e-12 | -135.3123 | 120.9775 | -1.6402e-12 | -135.3123 | 120.9775
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6368e-17 | -4.7886e-10 | -1.3222e-09 | -8.7893e-18 | 4.7886e-10 | 1.3222e-09 | -7.5697e-31 | 1.5424e-09 | -8.1728e-11 | -1.7579e-17 | -1.5424e-09 | 8.1728e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.83839 | 0.68767 | 0.95 | 0.83839 | 0.68767 | -1.6448e-12 | -135.3123 | 120.9775 | -1.6442e-12 | -135.3123 | 120.9775
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.7893e-18 | -2.3943e-10 | -6.611e-10 | -8.7893e-18 | 2.3943e-10 | 6.611e-10 | 3.5157e-17 | 7.7122e-10 | -4.0864e-11 | -1.7579e-17 | -7.7122e-10 | 4.0864e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.83839 | 0.68767 | 0.95 | 0.83839 | 0.68767 | -1.6442e-12 | -135.3123 | 120.9775 | -1.6445e-12 | -135.3123 | 120.9775
Line16_4_18 | 0 | 2.5068 | 2.5068 | 0 | 2.5068 | 2.5068 | 0 | 0.57893 | 0.57893 | 0 | 0.57893 | 0.57893 | -2.0505e-30 | 0.35328 | -0.11197 | 2.0515e-30 | -0.23262 | 0.23262 | -7.0314e-17 | -0.020967 | 0.27233 | 7.0314e-17 | 0.14665 | -0.14665 | 0 | -147.7717 | 32.2283 | 0 | 32.2283 | -147.7717 | 0.95 | 0.6113 | 0.50862 | 0.95 | 0.475 | 0.475 | -1.6709e-12 | -151.1682 | 144.5775 | -1.6716e-12 | -180 | -180
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6368e-17 | -2.3943e-10 | -6.611e-10 | -2.6368e-17 | 2.3943e-10 | 6.611e-10 | 3.5157e-17 | 7.7122e-10 | -4.0864e-11 | -1.7579e-17 | -7.7122e-10 | 4.0864e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.83839 | 0.68767 | 0.95 | 0.83839 | 0.68767 | -1.6777e-12 | -135.3123 | 120.9775 | -1.6781e-12 | -135.3123 | 120.9775
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2871e-29 | -1.9154e-09 | -5.2888e-09 | 1.7579e-17 | 1.9154e-09 | 5.2888e-09 | 4.3946e-16 | 6.1697e-09 | -3.2691e-10 | -4.3946e-16 | -6.1697e-09 | 3.2691e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.83839 | 0.68767 | 0.95 | 0.83839 | 0.68767 | -1.678e-12 | -135.3123 | 120.9775 | -1.6695e-12 | -135.3123 | 120.9775
Line2_1_4 | 0 | 2.5068 | 2.5068 | 0 | 2.5068 | 2.5068 | 0 | 0.57893 | 0.57893 | 0 | 0.57893 | 0.57893 | -7.0314e-17 | 0.47394 | 0.0086903 | 7.0314e-17 | -0.35328 | 0.11197 | 3.8673e-16 | 0.10472 | 0.39802 | -3.5157e-16 | 0.020967 | -0.27233 | 0 | -147.7717 | 32.2283 | 0 | 32.2283 | -147.7717 | 0.95 | 0.83839 | 0.68767 | 0.95 | 0.6113 | 0.50862 | -1.678e-12 | -135.3123 | 120.9775 | -1.6709e-12 | -151.1682 | 144.5775
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.7893e-18 | -4.7886e-10 | -1.3222e-09 | 8.7893e-18 | 4.7886e-10 | 1.3222e-09 | 7.0314e-17 | 1.5424e-09 | -8.1728e-11 | -5.2736e-17 | -1.5424e-09 | 8.1728e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.83839 | 0.68767 | 0.95 | 0.83839 | 0.68767 | -1.678e-12 | -135.3123 | 120.9775 | -1.6777e-12 | -135.3123 | 120.9775
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.7893e-18 | -1.1971e-09 | -3.3055e-09 | -8.7893e-18 | 1.1971e-09 | 3.3055e-09 | 4.2188e-16 | 3.8561e-09 | -2.0432e-10 | -4.3946e-16 | -3.8561e-09 | 2.0432e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.83839 | 0.68767 | 0.95 | 0.83839 | 0.68767 | -1.6698e-12 | -135.3123 | 120.9775 | -1.6622e-12 | -135.3123 | 120.9775
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.7893e-17 | -9.5772e-10 | -2.6444e-09 | 7.0314e-17 | 9.5772e-10 | 2.6444e-09 | 4.2188e-16 | 3.0849e-09 | -1.6346e-10 | -4.0431e-16 | -3.0849e-09 | 1.6346e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.83839 | 0.68767 | 0.95 | 0.83839 | 0.68767 | -1.6622e-12 | -135.3123 | 120.9775 | -1.6551e-12 | -135.3123 | 120.9775
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.1525e-17 | -7.1829e-10 | -1.9833e-09 | -6.1525e-17 | 7.1829e-10 | 1.9833e-09 | 1.4063e-16 | 2.3136e-09 | -1.2259e-10 | -8.7893e-17 | -2.3136e-09 | 1.2259e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.83839 | 0.68767 | 0.95 | 0.83839 | 0.68767 | -1.6551e-12 | -135.3123 | 120.9775 | -1.6538e-12 | -135.3123 | 120.9775
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.7579e-17 | -2.3943e-10 | -6.611e-10 | 1.7579e-17 | 2.3943e-10 | 6.611e-10 | 5.2736e-17 | 7.7122e-10 | -4.0864e-11 | -5.2736e-17 | -7.7122e-10 | 4.0864e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.83839 | 0.68767 | 0.95 | 0.83839 | 0.68767 | -1.6538e-12 | -135.3123 | 120.9775 | -1.6539e-12 | -135.3123 | 120.9775
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7579e-17 | -2.3943e-10 | -6.611e-10 | -1.7579e-17 | 2.3943e-10 | 6.611e-10 | 7.0314e-17 | 7.7122e-10 | -4.0864e-11 | -7.0314e-17 | -7.7122e-10 | 4.0864e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.83839 | 0.68767 | 0.95 | 0.83839 | 0.68767 | -1.6538e-12 | -135.3123 | 120.9775 | -1.6538e-12 | -135.3123 | 120.9775
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.6368e-17 | -1.676e-09 | -4.6277e-09 | 2.6368e-17 | 1.676e-09 | 4.6277e-09 | 3.6915e-16 | 5.3985e-09 | -2.8605e-10 | -3.6915e-16 | -5.3985e-09 | 2.8605e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.83839 | 0.68767 | 0.95 | 0.83839 | 0.68767 | -1.6695e-12 | -135.3123 | 120.9775 | -1.661e-12 | -135.3123 | 120.9775

## LL_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3307e-17 | -1.2893e-09 | -3.56e-09 | -4.996e-17 | 1.2893e-09 | 3.56e-09 | 3.4972e-16 | 4.153e-09 | -2.2005e-10 | -3.4972e-16 | -4.153e-09 | 2.2005e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.79426 | 0.65148 | 0.9 | 0.79426 | 0.65148 | -1.5607e-12 | -135.3123 | 120.9775 | -1.5528e-12 | -135.3123 | 120.9775
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3267e-18 | -1.2893e-09 | -3.56e-09 | -2.498e-17 | 1.2893e-09 | 3.56e-09 | 3.6637e-16 | 4.153e-09 | -2.2006e-10 | -3.1641e-16 | -4.153e-09 | 2.2006e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.79426 | 0.65148 | 0.9 | 0.79426 | 0.65148 | -1.5441e-12 | -135.3123 | 120.9775 | -1.5366e-12 | -135.3123 | 120.9775
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.498e-17 | -1.0744e-09 | -2.9667e-09 | 2.498e-17 | 1.0744e-09 | 2.9667e-09 | 3.4972e-16 | 3.4609e-09 | -1.8338e-10 | -3.6637e-16 | -3.4609e-09 | 1.8338e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.79426 | 0.65148 | 0.9 | 0.79426 | 0.65148 | -1.5366e-12 | -135.3123 | 120.9775 | -1.5293e-12 | -135.3123 | 120.9775
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.3267e-18 | -6.4467e-10 | -1.78e-09 | 8.3267e-18 | 6.4467e-10 | 1.78e-09 | 1.6653e-17 | 2.0765e-09 | -1.1003e-10 | -1.6653e-17 | -2.0765e-09 | 1.1003e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.79426 | 0.65148 | 0.9 | 0.79426 | 0.65148 | -1.5293e-12 | -135.3123 | 120.9775 | -1.5282e-12 | -135.3123 | 120.9775
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.3307e-17 | -2.1489e-10 | -5.9334e-10 | 3.3307e-17 | 2.1489e-10 | 5.9334e-10 | 2.9976e-16 | 6.9217e-10 | -3.6676e-11 | -2.8311e-16 | -6.9217e-10 | 3.6676e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.79426 | 0.65148 | 0.9 | 0.79426 | 0.65148 | -1.5293e-12 | -135.3123 | 120.9775 | -1.526e-12 | -135.3123 | 120.9775
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3267e-18 | -4.2978e-10 | -1.1867e-09 | -8.3267e-18 | 4.2978e-10 | 1.1867e-09 | 4.996e-17 | 1.3843e-09 | -7.3352e-11 | -6.6613e-17 | -1.3843e-09 | 7.3352e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.79426 | 0.65148 | 0.9 | 0.79426 | 0.65148 | -1.5282e-12 | -135.3123 | 120.9775 | -1.5276e-12 | -135.3123 | 120.9775
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3267e-18 | -2.1489e-10 | -5.9334e-10 | -4.1633e-17 | 2.1489e-10 | 5.9334e-10 | 3.3307e-17 | 6.9217e-10 | -3.6676e-11 | -1.6653e-17 | -6.9217e-10 | 3.6676e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.79426 | 0.65148 | 0.9 | 0.79426 | 0.65148 | -1.5276e-12 | -135.3123 | 120.9775 | -1.5279e-12 | -135.3123 | 120.9775
Line16_4_18 | 0 | 2.3749 | 2.3749 | 0 | 2.3749 | 2.3749 | 0 | 0.54846 | 0.54846 | 0 | 0.54846 | 0.54846 | 6.6613e-17 | 0.31707 | -0.10049 | -6.6613e-17 | -0.20878 | 0.20878 | -6.6613e-17 | -0.018818 | 0.24442 | 6.6613e-17 | 0.13162 | -0.13162 | 0 | -147.7717 | 32.2283 | 0 | 32.2283 | -147.7717 | 0.9 | 0.57913 | 0.48185 | 0.9 | 0.45 | 0.45 | -1.5551e-12 | -151.1682 | 144.5775 | -1.5568e-12 | -180 | -180
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0711e-31 | -2.1489e-10 | -5.9334e-10 | -9.0733e-31 | 2.1489e-10 | 5.9334e-10 | 3.3307e-17 | 6.9217e-10 | -3.6676e-11 | -3.3307e-17 | -6.9217e-10 | 3.6676e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.79426 | 0.65148 | 0.9 | 0.79426 | 0.65148 | -1.5605e-12 | -135.3123 | 120.9775 | -1.5608e-12 | -135.3123 | 120.9775
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.498e-17 | -1.7191e-09 | -4.7467e-09 | -2.498e-17 | 1.7191e-09 | 4.7467e-09 | 3.3307e-16 | 5.5374e-09 | -2.9341e-10 | -3.4972e-16 | -5.5374e-09 | 2.9341e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.79426 | 0.65148 | 0.9 | 0.79426 | 0.65148 | -1.5607e-12 | -135.3123 | 120.9775 | -1.5523e-12 | -135.3123 | 120.9775
Line2_1_4 | 0 | 2.3749 | 2.3749 | 0 | 2.3749 | 2.3749 | 0 | 0.54846 | 0.54846 | 0 | 0.54846 | 0.54846 | -3.3307e-17 | 0.42536 | 0.0077996 | 6.6613e-17 | -0.31707 | 0.10049 | 3.3307e-16 | 0.093984 | 0.35722 | -3.6637e-16 | 0.018818 | -0.24442 | 0 | -147.7717 | 32.2283 | 0 | 32.2283 | -147.7717 | 0.9 | 0.79426 | 0.65148 | 0.9 | 0.57913 | 0.48185 | -1.5607e-12 | -135.3123 | 120.9775 | -1.5551e-12 | -151.1682 | 144.5775
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.6653e-17 | -4.2978e-10 | -1.1867e-09 | 1.6653e-17 | 4.2978e-10 | 1.1867e-09 | 3.3307e-17 | 1.3843e-09 | -7.3352e-11 | -4.5355e-31 | -1.3843e-09 | 7.3352e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.79426 | 0.65148 | 0.9 | 0.79426 | 0.65148 | -1.5607e-12 | -135.3123 | 120.9775 | -1.5605e-12 | -135.3123 | 120.9775
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3267e-18 | -1.0744e-09 | -2.9667e-09 | -2.498e-17 | 1.0744e-09 | 2.9667e-09 | 3.6637e-16 | 3.4609e-09 | -1.8338e-10 | -3.6637e-16 | -3.4609e-09 | 1.8338e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.79426 | 0.65148 | 0.9 | 0.79426 | 0.65148 | -1.5528e-12 | -135.3123 | 120.9775 | -1.5454e-12 | -135.3123 | 120.9775
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.6653e-17 | -8.5956e-10 | -2.3734e-09 | 1.6653e-17 | 8.5956e-10 | 2.3734e-09 | 3.3307e-16 | 2.7687e-09 | -1.467e-10 | -3.1641e-16 | -2.7687e-09 | 1.467e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.79426 | 0.65148 | 0.9 | 0.79426 | 0.65148 | -1.5454e-12 | -135.3123 | 120.9775 | -1.5384e-12 | -135.3123 | 120.9775
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3267e-18 | -6.4467e-10 | -1.78e-09 | -8.3267e-18 | 6.4467e-10 | 1.78e-09 | 1.1657e-16 | 2.0765e-09 | -1.1003e-10 | -1.3323e-16 | -2.0765e-09 | 1.1003e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.79426 | 0.65148 | 0.9 | 0.79426 | 0.65148 | -1.5384e-12 | -135.3123 | 120.9775 | -1.5369e-12 | -135.3123 | 120.9775
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.1489e-10 | -5.9334e-10 | 0 | 2.1489e-10 | 5.9334e-10 | 0 | 6.9217e-10 | -3.6676e-11 | 0 | -6.9217e-10 | 3.6676e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.79426 | 0.65148 | 0.9 | 0.79426 | 0.65148 | -1.5369e-12 | -135.3123 | 120.9775 | -1.5371e-12 | -135.3123 | 120.9775
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3267e-18 | -2.1489e-10 | -5.9334e-10 | -2.498e-17 | 2.1489e-10 | 5.9334e-10 | 1.6653e-17 | 6.9217e-10 | -3.6676e-11 | -1.6653e-17 | -6.9217e-10 | 3.6676e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.79426 | 0.65148 | 0.9 | 0.79426 | 0.65148 | -1.5369e-12 | -135.3123 | 120.9775 | -1.537e-12 | -135.3123 | 120.9775
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.6653e-17 | -1.5042e-09 | -4.1534e-09 | 1.6653e-17 | 1.5042e-09 | 4.1534e-09 | 2.8311e-16 | 4.8452e-09 | -2.5673e-10 | -2.9976e-16 | -4.8452e-09 | 2.5673e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.79426 | 0.65148 | 0.9 | 0.79426 | 0.65148 | -1.5523e-12 | -135.3123 | 120.9775 | -1.5441e-12 | -135.3123 | 120.9775

## LL_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4033e-18 | -3.8862e-11 | -1.1288e-10 | -2.4033e-18 | 3.8862e-11 | 1.1288e-10 | 8.2399e-18 | 1.0829e-10 | 1.9912e-11 | -8.2399e-18 | -1.0829e-10 | -1.9912e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94812 | 0.94457 | 0.95 | 0.94812 | 0.94457 | -3.2307e-14 | -120.3131 | 119.9422 | -3.2172e-14 | -120.3131 | 119.9422
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.266e-18 | -3.8862e-11 | -1.1288e-10 | -2.266e-18 | 3.8862e-11 | 1.1288e-10 | 8.7893e-18 | 1.0829e-10 | 1.9912e-11 | -9.3386e-18 | -1.0829e-10 | -1.9912e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94812 | 0.94457 | 0.95 | 0.94812 | 0.94457 | -3.2029e-14 | -120.3131 | 119.9422 | -3.1898e-14 | -120.3131 | 119.9422
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9913e-18 | -3.2385e-11 | -9.4068e-11 | -1.9913e-18 | 3.2385e-11 | 9.4068e-11 | 8.7893e-18 | 9.0245e-11 | 1.6593e-11 | -8.7893e-18 | -9.0245e-11 | -1.6593e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94812 | 0.94457 | 0.95 | 0.94812 | 0.94457 | -3.1898e-14 | -120.3131 | 119.9422 | -3.1762e-14 | -120.3131 | 119.9422
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7466e-19 | -1.9431e-11 | -5.6441e-11 | -5.4933e-19 | 1.9431e-11 | 5.6441e-11 | 1.648e-18 | 5.4147e-11 | 9.9561e-12 | -1.648e-18 | -5.4147e-11 | -9.9561e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94812 | 0.94457 | 0.95 | 0.94812 | 0.94457 | -3.1762e-14 | -120.3131 | 119.9422 | -3.1742e-14 | -120.3131 | 119.9422
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.6133e-19 | -6.477e-12 | -1.8814e-11 | -1.236e-18 | 6.477e-12 | 1.8814e-11 | 6.0426e-18 | 1.8049e-11 | 3.3187e-12 | -6.5919e-18 | -1.8049e-11 | -3.3187e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94812 | 0.94457 | 0.95 | 0.94812 | 0.94457 | -3.1762e-14 | -120.3131 | 119.9422 | -3.1686e-14 | -120.3131 | 119.9422
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8066e-19 | -1.2954e-11 | -3.7627e-11 | -4.8066e-19 | 1.2954e-11 | 3.7627e-11 | 1.0987e-18 | 3.6098e-11 | 6.6374e-12 | -5.4933e-19 | -3.6098e-11 | -6.6374e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94812 | 0.94457 | 0.95 | 0.94812 | 0.94457 | -3.1742e-14 | -120.3131 | 119.9422 | -3.1726e-14 | -120.3131 | 119.9422
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4933e-19 | -6.477e-12 | -1.8814e-11 | -8.2399e-19 | 6.477e-12 | 1.8814e-11 | 5.4933e-19 | 1.8049e-11 | 3.3187e-12 | 5.4933e-19 | -1.8049e-11 | -3.3187e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94812 | 0.94457 | 0.95 | 0.94812 | 0.94457 | -3.1726e-14 | -120.3131 | 119.9422 | -3.1733e-14 | -120.3131 | 119.9422
Line16_4_18 | 0 | 0.052639 | 0.052639 | 0 | 0.052639 | 0.052639 | 0 | 0.012156 | 0.012156 | 0 | 0.012156 | 0.012156 | 2.1973e-18 | 0.011082 | 0.0028784 | -3.296e-18 | -0.011029 | -0.0028252 | -2.1973e-18 | 0.0029185 | 0.011047 | 2.1973e-18 | -0.0028631 | -0.010991 | 0 | -135.266 | 44.734 | 0 | 44.734 | -135.266 | 0.95 | 0.94272 | 0.93905 | 0.95 | 0.93734 | 0.93354 | -3.2209e-14 | -120.5122 | 120.1294 | -3.225e-14 | -120.7135 | 120.3187
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4933e-19 | -6.477e-12 | -1.8814e-11 | -5.4933e-19 | 6.477e-12 | 1.8814e-11 | 1.648e-18 | 1.8049e-11 | 3.3187e-12 | -1.0987e-18 | -1.8049e-11 | -3.3187e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94812 | 0.94457 | 0.95 | 0.94812 | 0.94457 | -3.2304e-14 | -120.3131 | 119.9422 | -3.2311e-14 | -120.3131 | 119.9422
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5406e-18 | -5.1816e-11 | -1.5051e-10 | -2.266e-18 | 5.1816e-11 | 1.5051e-10 | 7.6906e-18 | 1.4439e-10 | 2.655e-11 | -7.6906e-18 | -1.4439e-10 | -2.655e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94812 | 0.94457 | 0.95 | 0.94812 | 0.94457 | -3.2307e-14 | -120.3131 | 119.9422 | -3.217e-14 | -120.3131 | 119.9422
Line2_1_4 | 0 | 0.052639 | 0.052639 | 0 | 0.052639 | 0.052639 | 0 | 0.012156 | 0.012156 | 0 | 0.012156 | 0.012156 | 5.4933e-19 | 0.011136 | 0.0029316 | -5.4933e-19 | -0.011082 | -0.0028784 | 7.6906e-18 | 0.0029739 | 0.011102 | -7.6906e-18 | -0.0029185 | -0.011047 | 0 | -135.266 | 44.734 | 0 | 44.734 | -135.266 | 0.95 | 0.94812 | 0.94457 | 0.95 | 0.94272 | 0.93905 | -3.2307e-14 | -120.3131 | 119.9422 | -3.2209e-14 | -120.5122 | 120.1294
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.18e-19 | -1.2954e-11 | -3.7627e-11 | 8.9266e-19 | 1.2954e-11 | 3.7627e-11 | 1.0987e-18 | 3.6098e-11 | 6.6374e-12 | -1.0987e-18 | -3.6098e-11 | -6.6374e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94812 | 0.94457 | 0.95 | 0.94812 | 0.94457 | -3.2307e-14 | -120.3131 | 119.9422 | -3.2304e-14 | -120.3131 | 119.9422
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.678e-18 | -3.2385e-11 | -9.4068e-11 | -2.4033e-18 | 3.2385e-11 | 9.4068e-11 | 8.2399e-18 | 9.0245e-11 | 1.6593e-11 | -8.2399e-18 | -9.0245e-11 | -1.6593e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94812 | 0.94457 | 0.95 | 0.94812 | 0.94457 | -3.2172e-14 | -120.3131 | 119.9422 | -3.2055e-14 | -120.3131 | 119.9422
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5107e-18 | -2.5908e-11 | -7.5255e-11 | -1.5107e-18 | 2.5908e-11 | 7.5255e-11 | 8.2399e-18 | 7.2196e-11 | 1.3275e-11 | -7.6906e-18 | -7.2196e-11 | -1.3275e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94812 | 0.94457 | 0.95 | 0.94812 | 0.94457 | -3.2055e-14 | -120.3131 | 119.9422 | -3.1939e-14 | -120.3131 | 119.9422
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1673e-18 | -1.9431e-11 | -5.6441e-11 | -1.442e-18 | 1.9431e-11 | 5.6441e-11 | 2.1973e-18 | 5.4147e-11 | 9.9561e-12 | -1.648e-18 | -5.4147e-11 | -9.9561e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94812 | 0.94457 | 0.95 | 0.94812 | 0.94457 | -3.1939e-14 | -120.3131 | 119.9422 | -3.1907e-14 | -120.3131 | 119.9422
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.9266e-19 | -6.477e-12 | -1.8814e-11 | 8.9266e-19 | 6.477e-12 | 1.8814e-11 | 5.4933e-19 | 1.8049e-11 | 3.3187e-12 | -4.9713e-34 | -1.8049e-11 | -3.3187e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94812 | 0.94457 | 0.95 | 0.94812 | 0.94457 | -3.1907e-14 | -120.3131 | 119.9422 | -3.1909e-14 | -120.3131 | 119.9422
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.3733e-19 | -6.477e-12 | -1.8814e-11 | 1.3733e-19 | 6.477e-12 | 1.8814e-11 | 2.1973e-18 | 1.8049e-11 | 3.3187e-12 | -5.4933e-19 | -1.8049e-11 | -3.3187e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94812 | 0.94457 | 0.95 | 0.94812 | 0.94457 | -3.1907e-14 | -120.3131 | 119.9422 | -3.1907e-14 | -120.3131 | 119.9422
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.472e-18 | -4.5339e-11 | -1.317e-10 | -1.9227e-18 | 4.5339e-11 | 1.317e-10 | 8.2399e-18 | 1.2634e-10 | 2.3231e-11 | -7.6906e-18 | -1.2634e-10 | -2.3231e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94812 | 0.94457 | 0.95 | 0.94812 | 0.94457 | -3.217e-14 | -120.3131 | 119.9422 | -3.2029e-14 | -120.3131 | 119.9422

## LL_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9516e-18 | -3.4879e-11 | -1.0131e-10 | -1.9516e-18 | 3.4879e-11 | 1.0131e-10 | 8.3267e-18 | 9.7195e-11 | 1.7871e-11 | -7.8063e-18 | -9.7195e-11 | -1.7871e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89822 | 0.89485 | 0.9 | 0.89822 | 0.89485 | -3.3106e-14 | -120.3131 | 119.9422 | -3.2972e-14 | -120.3131 | 119.9422
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2768e-18 | -3.4879e-11 | -1.0131e-10 | -2.0166e-18 | 3.4879e-11 | 1.0131e-10 | 8.8471e-18 | 9.7195e-11 | 1.7871e-11 | -7.8063e-18 | -9.7195e-11 | -1.7871e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89822 | 0.89485 | 0.9 | 0.89822 | 0.89485 | -3.2825e-14 | -120.3131 | 119.9422 | -3.2692e-14 | -120.3131 | 119.9422
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7564e-18 | -2.9066e-11 | -8.4427e-11 | -1.7564e-18 | 2.9066e-11 | 8.4427e-11 | 8.8471e-18 | 8.0996e-11 | 1.4893e-11 | -8.3267e-18 | -8.0996e-11 | -1.4893e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89822 | 0.89485 | 0.9 | 0.89822 | 0.89485 | -3.2692e-14 | -120.3131 | 119.9422 | -3.2554e-14 | -120.3131 | 119.9422
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9516e-19 | -1.7439e-11 | -5.0656e-11 | -1.9516e-19 | 1.7439e-11 | 5.0656e-11 | 5.2042e-19 | 4.8598e-11 | 8.9356e-12 | -1.0408e-18 | -4.8598e-11 | -8.9356e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89822 | 0.89485 | 0.9 | 0.89822 | 0.89485 | -3.2554e-14 | -120.3131 | 119.9422 | -3.2534e-14 | -120.3131 | 119.9422
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.301e-19 | -5.8131e-12 | -1.6885e-11 | 1.301e-19 | 5.8131e-12 | 1.6885e-11 | 5.2042e-18 | 1.6199e-11 | 2.9785e-12 | -5.7246e-18 | -1.6199e-11 | -2.9785e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89822 | 0.89485 | 0.9 | 0.89822 | 0.89485 | -3.2554e-14 | -120.3131 | 119.9422 | -3.2467e-14 | -120.3131 | 119.9422
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5536e-19 | -1.1626e-11 | -3.3771e-11 | -7.1557e-19 | 1.1626e-11 | 3.3771e-11 | 1.5613e-18 | 3.2398e-11 | 5.9571e-12 | -1.0408e-18 | -3.2398e-11 | -5.9571e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89822 | 0.89485 | 0.9 | 0.89822 | 0.89485 | -3.2534e-14 | -120.3131 | 119.9422 | -3.2518e-14 | -120.3131 | 119.9422
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.2526e-19 | -5.8131e-12 | -1.6885e-11 | 6.5052e-20 | 5.8131e-12 | 1.6885e-11 | 5.2042e-19 | 1.6199e-11 | 2.9785e-12 | -1.0408e-18 | -1.6199e-11 | -2.9785e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89822 | 0.89485 | 0.9 | 0.89822 | 0.89485 | -3.2518e-14 | -120.3131 | 119.9422 | -3.2525e-14 | -120.3131 | 119.9422
Line16_4_18 | 0 | 0.049869 | 0.049869 | 0 | 0.049869 | 0.049869 | 0 | 0.011517 | 0.011517 | 0 | 0.011517 | 0.011517 | 5.9967e-34 | 0.0099465 | 0.0025834 | 1.0408e-18 | -0.0098987 | -0.0025356 | 1.0408e-18 | 0.0026194 | 0.0099144 | -2.0817e-18 | -0.0025697 | -0.0098647 | 0 | -135.266 | 44.734 | 0 | 44.734 | -135.266 | 0.9 | 0.89311 | 0.88962 | 0.9 | 0.888 | 0.8844 | -3.3011e-14 | -120.5122 | 120.1294 | -3.3053e-14 | -120.7135 | 120.3187
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.8131e-12 | -1.6885e-11 | -2.6021e-19 | 5.8131e-12 | 1.6885e-11 | 0 | 1.6199e-11 | 2.9785e-12 | -5.2042e-19 | -1.6199e-11 | -2.9785e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89822 | 0.89485 | 0.9 | 0.89822 | 0.89485 | -3.3103e-14 | -120.3131 | 119.9422 | -3.311e-14 | -120.3131 | 119.9422
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2118e-18 | -4.6505e-11 | -1.3508e-10 | -2.2118e-18 | 4.6505e-11 | 1.3508e-10 | 6.7654e-18 | 1.2959e-10 | 2.3828e-11 | -7.2858e-18 | -1.2959e-10 | -2.3828e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89822 | 0.89485 | 0.9 | 0.89822 | 0.89485 | -3.3106e-14 | -120.3131 | 119.9422 | -3.2968e-14 | -120.3131 | 119.9422
Line2_1_4 | 0 | 0.049869 | 0.049869 | 0 | 0.049869 | 0.049869 | 0 | 0.011517 | 0.011517 | 0 | 0.011517 | 0.011517 | -5.2042e-19 | 0.0099942 | 0.0026311 | 5.2042e-19 | -0.0099465 | -0.0025834 | 8.3267e-18 | 0.0026691 | 0.0099642 | -9.3675e-18 | -0.0026194 | -0.0099144 | 0 | -135.266 | 44.734 | 0 | 44.734 | -135.266 | 0.9 | 0.89822 | 0.89485 | 0.9 | 0.89311 | 0.88962 | -3.3106e-14 | -120.3131 | 119.9422 | -3.3011e-14 | -120.5122 | 120.1294
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.301e-19 | -1.1626e-11 | -3.3771e-11 | -3.9031e-19 | 1.1626e-11 | 3.3771e-11 | 1.0408e-18 | 3.2398e-11 | 5.9571e-12 | -1.0408e-18 | -3.2398e-11 | -5.9571e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89822 | 0.89485 | 0.9 | 0.89822 | 0.89485 | -3.3106e-14 | -120.3131 | 119.9422 | -3.3103e-14 | -120.3131 | 119.9422
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1225e-18 | -2.9066e-11 | -8.4427e-11 | -3.1225e-18 | 2.9066e-11 | 8.4427e-11 | 6.7654e-18 | 8.0996e-11 | 1.4893e-11 | -7.2858e-18 | -8.0996e-11 | -1.4893e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89822 | 0.89485 | 0.9 | 0.89822 | 0.89485 | -3.2972e-14 | -120.3131 | 119.9422 | -3.2855e-14 | -120.3131 | 119.9422
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1059e-18 | -2.3253e-11 | -6.7542e-11 | -8.4568e-19 | 2.3253e-11 | 6.7542e-11 | 7.2858e-18 | 6.4797e-11 | 1.1914e-11 | -7.8063e-18 | -6.4797e-11 | -1.1914e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89822 | 0.89485 | 0.9 | 0.89822 | 0.89485 | -3.2855e-14 | -120.3131 | 119.9422 | -3.2742e-14 | -120.3131 | 119.9422
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4311e-18 | -1.7439e-11 | -5.0656e-11 | -9.1073e-19 | 1.7439e-11 | 5.0656e-11 | 3.1225e-18 | 4.8598e-11 | 8.9356e-12 | -3.1225e-18 | -4.8598e-11 | -8.9356e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89822 | 0.89485 | 0.9 | 0.89822 | 0.89485 | -3.2742e-14 | -120.3131 | 119.9422 | -3.2717e-14 | -120.3131 | 119.9422
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5536e-19 | -5.8131e-12 | -1.6885e-11 | 6.5052e-20 | 5.8131e-12 | 1.6885e-11 | 1.5613e-18 | 1.6199e-11 | 2.9786e-12 | -1.5613e-18 | -1.6199e-11 | -2.9786e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89822 | 0.89485 | 0.9 | 0.89822 | 0.89485 | -3.2717e-14 | -120.3131 | 119.9422 | -3.2718e-14 | -120.3131 | 119.9422
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0408e-18 | -5.8131e-12 | -1.6885e-11 | -5.2042e-19 | 5.8131e-12 | 1.6885e-11 | 1.0408e-18 | 1.6199e-11 | 2.9786e-12 | -1.0408e-18 | -1.6199e-11 | -2.9786e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89822 | 0.89485 | 0.9 | 0.89822 | 0.89485 | -3.2717e-14 | -120.3131 | 119.9422 | -3.2712e-14 | -120.3131 | 119.9422
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9516e-18 | -4.0692e-11 | -1.182e-10 | -1.6914e-18 | 4.0692e-11 | 1.182e-10 | 6.7654e-18 | 1.1339e-10 | 2.085e-11 | -7.2858e-18 | -1.1339e-10 | -2.085e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89822 | 0.89485 | 0.9 | 0.89822 | 0.89485 | -3.2968e-14 | -120.3131 | 119.9422 | -3.2825e-14 | -120.3131 | 119.9422

## LG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.046709 | 0.046709 | 0.046709 | 0.046709 | 0.046709 | 0.046709 | 0.010787 | 0.010787 | 0.010787 | 0.010787 | 0.010787 | 0.010787 | -0.00031553 | 0.015702 | 0.017439 | 0.00032643 | -0.015691 | -0.017428 | -0.0006338 | 0.010185 | -0.0093561 | 0.00065562 | -0.010163 | 0.0093778 | 174.9202 | 174.9202 | 174.9202 | -5.0802 | -5.0802 | -5.0802 |  | 0.065634 | 1.735 | 1.8346 | 0.067895 | 1.733 | 1.8347 | 58.4546 | -152.1105 | 146.7059 | 58.4513 | -152.1484 | 146.6353
Line10_11_12 | 0.046615 | 0.046615 | 0.046615 | 0.046615 | 0.046615 | 0.046615 | 0.010765 | 0.010765 | 0.010765 | 0.010765 | 0.010765 | 0.010765 | -0.00033411 | 0.015608 | 0.017419 | 0.00034497 | -0.015597 | -0.017408 | -0.00067723 | 0.010183 | -0.0093116 | 0.00069896 | -0.010161 | 0.0093332 | 174.6929 | 174.6929 | 174.6929 | -5.3076 | -5.3076 | -5.3076 |  | 0.070148 | 1.7311 | 1.8347 | 0.072404 | 1.7291 | 1.8348 | 58.4336 | -152.1857 | 146.5649 | 58.4241 | -152.2235 | 146.4945
Line11_12_13 | 0.046615 | 0.046615 | 0.046615 | 0.046615 | 0.046615 | 0.046615 | 0.010765 | 0.010765 | 0.010765 | 0.010765 | 0.010765 | 0.010765 | -0.00034497 | 0.015597 | 0.017408 | 0.00035583 | -0.015586 | -0.017397 | -0.00069896 | 0.010161 | -0.0093332 | 0.00072069 | -0.01014 | 0.0093547 | 174.6924 | 174.6924 | 174.6924 | -5.308 | -5.308 | -5.308 |  | 0.072404 | 1.7291 | 1.8348 | 0.074661 | 1.7272 | 1.8348 | 58.4241 | -152.2235 | 146.4945 | 58.4151 | -152.2613 | 146.4241
Line12_13_15 | 1.1018e-06 | 1.0998e-06 | 1.0998e-06 | 0 | 0 | 0 | 2.5446e-07 | 2.5399e-07 | 2.5399e-07 | 0 | 0 | 0 | -1.7372e-08 | 2.5437e-07 | -2.0339e-07 | 1.1711e-08 | -1.749e-07 | 1.2957e-07 | 7.6912e-09 | -3.5742e-07 | -4.1931e-07 | -4.8826e-09 | 2.3473e-07 | 2.8269e-07 | -97.7039 | -97.7002 | -97.7002 | 0 | 0 | 0 |  | 0.074661 | 1.7272 | 1.8348 | 0.074661 | 1.7272 | 1.8348 | 58.4151 | -152.2613 | 146.4241 | 58.4151 | -152.2613 | 146.4241
Line13_13_14 | 0.046615 | 0.046615 | 0.046615 | 0.046615 | 0.046615 | 0.046615 | 0.010765 | 0.010765 | 0.010765 | 0.010765 | 0.010765 | 0.010765 | -0.00035581 | 0.015586 | 0.017397 | 0.00036667 | -0.015575 | -0.017386 | -0.0007207 | 0.01014 | -0.0093543 | 0.00074243 | -0.010118 | 0.0093759 | 174.6906 | 174.6906 | 174.6906 | -5.3098 | -5.3098 | -5.3098 |  | 0.074661 | 1.7272 | 1.8348 | 0.076918 | 1.7253 | 1.8349 | 58.4151 | -152.2613 | 146.4241 | 58.4066 | -152.2992 | 146.3536
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.1581e-08 | 1.6958e-07 | -1.3559e-07 | 5.9207e-09 | -9.0105e-08 | 6.1778e-08 | 5.1274e-09 | -2.3828e-07 | -2.7954e-07 | -2.3189e-09 | 1.1559e-07 | 1.4291e-07 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.074661 | 1.7272 | 1.8348 | 0.074661 | 1.7272 | 1.8348 | 58.4151 | -152.2613 | 146.4241 | 58.4151 | -152.2613 | 146.4241
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.7906e-09 | 8.479e-08 | -6.7796e-08 | 1.3011e-10 | -5.3153e-09 | -6.0183e-09 | 2.5637e-09 | -1.1914e-07 | -1.3977e-07 | 2.4486e-10 | -3.5495e-09 | 3.1436e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.074661 | 1.7272 | 1.8348 | 0.074661 | 1.7272 | 1.8348 | 58.4151 | -152.2613 | 146.4241 | 58.4152 | -152.2613 | 146.4241
Line16_4_18 | 0.4208 | 0 | 0 | 0.4208 | 0 | 0 | 0.09718 | 0 | 0 | 0.09718 | 0 | 0 | 0.0014756 | 8.3504e-08 | -7.0402e-08 | -5.8325e-16 | -5.2679e-09 | -6.0099e-09 | 0.0029513 | -1.2123e-07 | -1.3965e-07 | 1.4781e-15 | -3.5491e-09 | 3.1207e-09 | -4.9647 | 0 | 0 | 175.0353 | 0 | 0 |  | 0.033953 | 1.7272 | 1.8349 | 0 | 1.7214 | 1.8352 | 58.4703 | -152.264 | 146.423 | 0 | -152.3795 | 146.2111
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.0945e-09 | 8.4876e-08 | -6.8487e-08 | 1.1641e-10 | -5.3795e-09 | -6.0314e-09 | 2.2999e-09 | -1.2062e-07 | -1.4011e-07 | 2.1535e-10 | -3.5506e-09 | 3.1743e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.065634 | 1.735 | 1.8346 | 0.065634 | 1.735 | 1.8346 | 58.4546 | -152.1105 | 146.7059 | 58.4546 | -152.1105 | 146.7059
Line1_1_3 | 0.046615 | 0.046615 | 0.046615 | 0.046615 | 0.046615 | 0.046615 | 0.010765 | 0.010765 | 0.010765 | 0.010765 | 0.010765 | 0.010765 | -0.00031239 | 0.01563 | 0.01744 | 0.00032325 | -0.015619 | -0.017429 | -0.00063376 | 0.010226 | -0.0092684 | 0.00065549 | -0.010204 | 0.00929 | 174.6938 | 174.6938 | 174.6938 | -5.3067 | -5.3067 | -5.3067 |  | 0.065634 | 1.735 | 1.8346 | 0.067891 | 1.733 | 1.8347 | 58.4546 | -152.1105 | 146.7059 | 58.4438 | -152.1481 | 146.6354
Line2_1_4 | 0.37386 | 0.046946 | 0.046946 | 0.37386 | 0.046946 | 0.046946 | 0.086339 | 0.010842 | 0.010842 | 0.086339 | 0.010842 | 0.010842 | 0.0025306 | 0.015882 | 0.017433 | -0.0013084 | -0.015837 | -0.017388 | 0.0050704 | 0.010079 | -0.0095767 | -0.0026233 | -0.0099918 | 0.0096642 | -5.0215 | 175.4881 | 175.4881 | 174.9785 | -4.5124 | -4.5124 |  | 0.065634 | 1.735 | 1.8346 | 0.033953 | 1.7272 | 1.8349 | 58.4546 | -152.1105 | 146.7059 | 58.4703 | -152.264 | 146.423
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.0189e-08 | 1.6975e-07 | -1.3697e-07 | 5.2109e-09 | -9.0256e-08 | 6.2456e-08 | 4.5997e-09 | -2.4123e-07 | -2.8022e-07 | -2.0845e-09 | 1.1706e-07 | 1.4328e-07 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.065634 | 1.735 | 1.8346 | 0.065634 | 1.735 | 1.8346 | 58.4546 | -152.1105 | 146.7059 | 58.4546 | -152.1105 | 146.7059
Line4_2_6 | 0.046709 | 0.046709 | 0.046709 | 0.046709 | 0.046709 | 0.046709 | 0.010787 | 0.010787 | 0.010787 | 0.010787 | 0.010787 | 0.010787 | -0.00032643 | 0.015691 | 0.017428 | 0.00033734 | -0.01568 | -0.017417 | -0.00065562 | 0.010163 | -0.0093778 | 0.00067744 | -0.010141 | 0.0093995 | 174.9198 | 174.9198 | 174.9198 | -5.0807 | -5.0807 | -5.0807 |  | 0.067895 | 1.733 | 1.8347 | 0.070157 | 1.7311 | 1.8347 | 58.4513 | -152.1484 | 146.6353 | 58.4482 | -152.1864 | 146.5647
Line5_6_7 | 0.046709 | 0.046709 | 0.046709 | 0.046709 | 0.046709 | 0.046709 | 0.010787 | 0.010787 | 0.010787 | 0.010787 | 0.010787 | 0.010787 | -0.00033734 | 0.01568 | 0.017417 | 0.00034824 | -0.015669 | -0.017406 | -0.00067744 | 0.010141 | -0.0093995 | 0.00069926 | -0.01012 | 0.0094212 | 174.9193 | 174.9193 | 174.9193 | -5.0811 | -5.0811 | -5.0811 |  | 0.070157 | 1.7311 | 1.8347 | 0.072418 | 1.7291 | 1.8348 | 58.4482 | -152.1864 | 146.5647 | 58.4452 | -152.2245 | 146.4941
Line6_7_8 | 1.103e-06 | 1.1009e-06 | 1.1009e-06 | 0 | 0 | 0 | 2.5472e-07 | 2.5425e-07 | 2.5425e-07 | 0 | 0 | 0 | -1.6856e-08 | 2.5444e-07 | -2.0391e-07 | 1.1364e-08 | -1.7496e-07 | 1.2992e-07 | 7.492e-09 | -3.5853e-07 | -4.1958e-07 | -4.7571e-09 | 2.3547e-07 | 2.8287e-07 | -97.5912 | -97.5872 | -97.5872 | 0 | 0 | 0 |  | 0.072418 | 1.7291 | 1.8348 | 0.072418 | 1.7291 | 1.8348 | 58.4452 | -152.2245 | 146.4941 | 58.4453 | -152.2245 | 146.4941
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.6187e-09 | 8.4814e-08 | -6.7969e-08 | 1.2668e-10 | -5.3314e-09 | -6.0217e-09 | 2.4973e-09 | -1.1951e-07 | -1.3986e-07 | 2.3758e-10 | -3.5499e-09 | 3.1513e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.072418 | 1.7291 | 1.8348 | 0.072418 | 1.7291 | 1.8348 | 58.4453 | -152.2245 | 146.4941 | 58.4453 | -152.2245 | 146.4941
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.6187e-09 | 8.4814e-08 | -6.7969e-08 | 1.2668e-10 | -5.3314e-09 | -6.0217e-09 | 2.4973e-09 | -1.1951e-07 | -1.3986e-07 | 2.3758e-10 | -3.5499e-09 | 3.1513e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.072418 | 1.7291 | 1.8348 | 0.072418 | 1.7291 | 1.8348 | 58.4453 | -152.2245 | 146.4941 | 58.4453 | -152.2245 | 146.4941
Line9_3_11 | 0.046615 | 0.046615 | 0.046615 | 0.046615 | 0.046615 | 0.046615 | 0.010765 | 0.010765 | 0.010765 | 0.010765 | 0.010765 | 0.010765 | -0.00032325 | 0.015619 | 0.017429 | 0.00033411 | -0.015608 | -0.017419 | -0.00065549 | 0.010204 | -0.00929 | 0.00067723 | -0.010183 | 0.0093116 | 174.6933 | 174.6933 | 174.6933 | -5.3071 | -5.3071 | -5.3071 |  | 0.067891 | 1.733 | 1.8347 | 0.070148 | 1.7311 | 1.8347 | 58.4438 | -152.1481 | 146.6354 | 58.4336 | -152.1857 | 146.5649

## LG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.048923 | 0.048923 | 0.048923 | 0.048923 | 0.048923 | 0.048923 | 0.011298 | 0.011298 | 0.011298 | 0.011298 | 0.011298 | 0.011298 | -0.00034614 | 0.017211 | 0.019144 | 0.00035811 | -0.017199 | -0.019132 | -0.0006953 | 0.011174 | -0.010265 | 0.00071924 | -0.01115 | 0.010289 | 174.8484 | 174.8484 | 174.8484 | -5.1521 | -5.1521 | -5.1521 |  | 0.068745 | 1.8163 | 1.9227 | 0.071113 | 1.8142 | 1.9227 | 58.3827 | -152.159 | 146.6484 | 58.3794 | -152.1969 | 146.5779
Line10_11_12 | 0.048824 | 0.048824 | 0.048824 | 0.048824 | 0.048824 | 0.048824 | 0.011275 | 0.011275 | 0.011275 | 0.011275 | 0.011275 | 0.011275 | -0.00036653 | 0.017108 | 0.019122 | 0.00037844 | -0.017096 | -0.019111 | -0.00074294 | 0.011172 | -0.010216 | 0.00076678 | -0.011148 | 0.01024 | 174.621 | 174.621 | 174.621 | -5.3794 | -5.3794 | -5.3794 |  | 0.073472 | 1.8122 | 1.9228 | 0.075836 | 1.8101 | 1.9228 | 58.3617 | -152.2343 | 146.5076 | 58.3522 | -152.272 | 146.4372
Line11_12_13 | 0.048824 | 0.048824 | 0.048824 | 0.048824 | 0.048824 | 0.048824 | 0.011275 | 0.011275 | 0.011275 | 0.011275 | 0.011275 | 0.011275 | -0.00037844 | 0.017096 | 0.01911 | 0.00039035 | -0.017084 | -0.019099 | -0.00076678 | 0.011148 | -0.01024 | 0.00079062 | -0.011125 | 0.010264 | 174.6206 | 174.6206 | 174.6206 | -5.3799 | -5.3799 | -5.3799 |  | 0.075836 | 1.8101 | 1.9228 | 0.078199 | 1.8081 | 1.9229 | 58.3522 | -152.272 | 146.4372 | 58.3432 | -152.3098 | 146.3668
Line12_13_15 | 1.1541e-06 | 1.1519e-06 | 1.1519e-06 | 0 | 0 | 0 | 2.6653e-07 | 2.6602e-07 | 2.6602e-07 | 0 | 0 | 0 | -1.9058e-08 | 2.7906e-07 | -2.2313e-07 | 1.2849e-08 | -1.9186e-07 | 1.4214e-07 | 8.4379e-09 | -3.9177e-07 | -4.6031e-07 | -5.3568e-09 | 2.5728e-07 | 3.1032e-07 | -97.7759 | -97.772 | -97.772 | 0 | 0 | 0 |  | 0.078199 | 1.8081 | 1.9229 | 0.078199 | 1.8081 | 1.9229 | 58.3432 | -152.3098 | 146.3668 | 58.3432 | -152.3098 | 146.3668
Line13_13_14 | 0.048824 | 0.048824 | 0.048824 | 0.048824 | 0.048824 | 0.048824 | 0.011275 | 0.011275 | 0.011275 | 0.011275 | 0.011275 | 0.011275 | -0.00039033 | 0.017084 | 0.019099 | 0.00040225 | -0.017072 | -0.019087 | -0.00079063 | 0.011125 | -0.010263 | 0.00081447 | -0.011101 | 0.010287 | 174.6188 | 174.6188 | 174.6188 | -5.3817 | -5.3817 | -5.3817 |  | 0.078199 | 1.8081 | 1.9229 | 0.080563 | 1.8061 | 1.923 | 58.3432 | -152.3098 | 146.3668 | 58.3347 | -152.3477 | 146.2964
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.2706e-08 | 1.8604e-07 | -1.4875e-07 | 6.4959e-09 | -9.8842e-08 | 6.7767e-08 | 5.6253e-09 | -2.6118e-07 | -3.0687e-07 | -2.5442e-09 | 1.2669e-07 | 1.5688e-07 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.078199 | 1.8081 | 1.9229 | 0.078199 | 1.8081 | 1.9229 | 58.3432 | -152.3098 | 146.3668 | 58.3433 | -152.3098 | 146.3668
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.3528e-09 | 9.3018e-08 | -7.4376e-08 | 1.4311e-10 | -5.8235e-09 | -6.6089e-09 | 2.8126e-09 | -1.3059e-07 | -1.5344e-07 | 2.6847e-10 | -3.8979e-09 | 3.4445e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.078199 | 1.8081 | 1.9229 | 0.078199 | 1.8081 | 1.9229 | 58.3433 | -152.3098 | 146.3668 | 58.3433 | -152.3098 | 146.3668
Line16_4_18 | 0.44075 | 0 | 0 | 0.44075 | 0 | 0 | 0.10179 | 0 | 0 | 0.10179 | 0 | 0 | 0.0016188 | 9.1609e-08 | -7.7237e-08 | -3.7714e-16 | -5.7716e-09 | -6.5998e-09 | 0.0032376 | -1.3289e-07 | -1.533e-07 | 1.1901e-15 | -3.8974e-09 | 3.4192e-09 | -5.0366 | 0 | 0 | 174.9634 | 0 | 0 |  | 0.035563 | 1.8081 | 1.923 | 0 | 1.802 | 1.9233 | 58.3984 | -152.3125 | 146.3657 | 0 | -152.428 | 146.154
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.5891e-09 | 9.3114e-08 | -7.5135e-08 | 1.2803e-10 | -5.8939e-09 | -6.6233e-09 | 2.5232e-09 | -1.3221e-07 | -1.5381e-07 | 2.3611e-10 | -3.8992e-09 | 3.4781e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.068745 | 1.8163 | 1.9227 | 0.068745 | 1.8163 | 1.9227 | 58.3827 | -152.159 | 146.6484 | 58.3827 | -152.159 | 146.6484
Line1_1_3 | 0.048824 | 0.048824 | 0.048824 | 0.048824 | 0.048824 | 0.048824 | 0.011275 | 0.011275 | 0.011275 | 0.011275 | 0.011275 | 0.011275 | -0.0003427 | 0.017133 | 0.019146 | 0.00035461 | -0.017121 | -0.019134 | -0.00069526 | 0.011219 | -0.010169 | 0.0007191 | -0.011196 | 0.010192 | 174.6219 | 174.6219 | 174.6219 | -5.3785 | -5.3785 | -5.3785 |  | 0.068745 | 1.8163 | 1.9227 | 0.071108 | 1.8142 | 1.9227 | 58.3827 | -152.159 | 146.6484 | 58.3719 | -152.1966 | 146.578
Line2_1_4 | 0.39158 | 0.04917 | 0.04917 | 0.39158 | 0.04917 | 0.04917 | 0.090431 | 0.011355 | 0.011355 | 0.090431 | 0.011355 | 0.011355 | 0.0027762 | 0.017409 | 0.019138 | -0.0014354 | -0.01736 | -0.019089 | 0.0055623 | 0.011059 | -0.010507 | -0.0028779 | -0.010963 | 0.010603 | -5.0934 | 175.4162 | 175.4162 | 174.9067 | -4.5843 | -4.5843 |  | 0.068745 | 1.8163 | 1.9227 | 0.035563 | 1.8081 | 1.923 | 58.3827 | -152.159 | 146.6484 | 58.3984 | -152.3125 | 146.3657
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.1178e-08 | 1.8623e-07 | -1.5027e-07 | 5.7171e-09 | -9.9008e-08 | 6.8512e-08 | 5.0463e-09 | -2.6441e-07 | -3.0762e-07 | -2.287e-09 | 1.2831e-07 | 1.5729e-07 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.068745 | 1.8163 | 1.9227 | 0.068745 | 1.8163 | 1.9227 | 58.3827 | -152.159 | 146.6484 | 58.3827 | -152.159 | 146.6484
Line4_2_6 | 0.048923 | 0.048923 | 0.048923 | 0.048923 | 0.048923 | 0.048923 | 0.011298 | 0.011298 | 0.011298 | 0.011298 | 0.011298 | 0.011298 | -0.00035811 | 0.017199 | 0.019132 | 0.00037007 | -0.017187 | -0.019121 | -0.00071924 | 0.01115 | -0.010289 | 0.00074318 | -0.011127 | 0.010313 | 174.8479 | 174.8479 | 174.8479 | -5.1525 | -5.1525 | -5.1525 |  | 0.071113 | 1.8142 | 1.9227 | 0.073482 | 1.8122 | 1.9228 | 58.3794 | -152.1969 | 146.5779 | 58.3763 | -152.2349 | 146.5073
Line5_6_7 | 0.048923 | 0.048923 | 0.048923 | 0.048923 | 0.048923 | 0.048923 | 0.011298 | 0.011298 | 0.011298 | 0.011298 | 0.011298 | 0.011298 | -0.00037007 | 0.017187 | 0.019121 | 0.00038203 | -0.017175 | -0.019109 | -0.00074318 | 0.011127 | -0.010313 | 0.00076711 | -0.011103 | 0.010336 | 174.8475 | 174.8475 | 174.8475 | -5.153 | -5.153 | -5.153 |  | 0.073482 | 1.8122 | 1.9228 | 0.07585 | 1.8101 | 1.9229 | 58.3763 | -152.2349 | 146.5073 | 58.3733 | -152.273 | 146.4368
Line6_7_8 | 1.1553e-06 | 1.1531e-06 | 1.1531e-06 | 0 | 0 | 0 | 2.6681e-07 | 2.6629e-07 | 2.6629e-07 | 0 | 0 | 0 | -1.8493e-08 | 2.7913e-07 | -2.237e-07 | 1.2468e-08 | -1.9193e-07 | 1.4252e-07 | 8.2194e-09 | -3.9298e-07 | -4.606e-07 | -5.2191e-09 | 2.5809e-07 | 3.1052e-07 | -97.6632 | -97.6591 | -97.6591 | 0 | 0 | 0 |  | 0.07585 | 1.8101 | 1.9229 | 0.07585 | 1.8101 | 1.9229 | 58.3733 | -152.273 | 146.4368 | 58.3734 | -152.273 | 146.4368
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.1643e-09 | 9.3045e-08 | -7.4566e-08 | 1.3933e-10 | -5.8412e-09 | -6.6127e-09 | 2.7398e-09 | -1.3099e-07 | -1.5353e-07 | 2.6049e-10 | -3.8983e-09 | 3.4529e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.07585 | 1.8101 | 1.9229 | 0.07585 | 1.8101 | 1.9229 | 58.3734 | -152.273 | 146.4368 | 58.3734 | -152.273 | 146.4368
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.1643e-09 | 9.3045e-08 | -7.4566e-08 | 1.3933e-10 | -5.8412e-09 | -6.6127e-09 | 2.7398e-09 | -1.3099e-07 | -1.5353e-07 | 2.6049e-10 | -3.8983e-09 | 3.4529e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.07585 | 1.8101 | 1.9229 | 0.07585 | 1.8101 | 1.9229 | 58.3734 | -152.273 | 146.4368 | 58.3734 | -152.273 | 146.4368
Line9_3_11 | 0.048824 | 0.048824 | 0.048824 | 0.048824 | 0.048824 | 0.048824 | 0.011275 | 0.011275 | 0.011275 | 0.011275 | 0.011275 | 0.011275 | -0.00035461 | 0.01712 | 0.019134 | 0.00036653 | -0.017108 | -0.019122 | -0.0007191 | 0.011196 | -0.010192 | 0.00074294 | -0.011172 | 0.010216 | 174.6215 | 174.6215 | 174.6215 | -5.379 | -5.379 | -5.379 |  | 0.071108 | 1.8142 | 1.9227 | 0.073472 | 1.8122 | 1.9228 | 58.3719 | -152.1966 | 146.578 | 58.3617 | -152.2343 | 146.5076

## LG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.0035786 | 0.0035786 | 0.0035786 | 0.0035786 | 0.0035786 | 0.0035786 | 0.00082645 | 0.00082645 | 0.00082645 | 0.00082645 | 0.00082645 | 0.00082645 | -0.00057756 | -0.00012057 | 0.0008908 | 0.00057762 | 0.00012064 | -0.00089073 | -0.00058174 | 0.00084737 | -0.00026448 | 0.00058188 | -0.00084724 | 0.0002646 | 137.7098 | 137.7098 | 137.7098 | -42.2907 | -42.2907 | -42.2907 |  | 0.9919 | 1.0356 | 1.1244 | 0.99207 | 1.0355 | 1.1243 | 2.9166 | -124.1925 | 121.1733 | 2.9198 | -124.187 | 121.1646
Line10_11_12 | 0.0035714 | 0.0035714 | 0.0035714 | 0.0035714 | 0.0035714 | 0.0035714 | 0.00082478 | 0.00082478 | 0.00082478 | 0.00082478 | 0.00082478 | 0.00082478 | -0.00057421 | -0.0001238 | 0.00088991 | 0.00057427 | 0.00012387 | -0.00088985 | -0.00058311 | 0.00084492 | -0.00026067 | 0.00058324 | -0.00084479 | 0.00026079 | 137.4824 | 137.4824 | 137.4824 | -42.518 | -42.518 | -42.518 |  | 0.99223 | 1.0354 | 1.1243 | 0.9924 | 1.0352 | 1.1243 | 2.9228 | -124.1815 | 121.156 | 2.9259 | -124.176 | 121.1473
Line11_12_13 | 0.0035714 | 0.0035714 | 0.0035714 | 0.0035714 | 0.0035714 | 0.0035714 | 0.00082478 | 0.00082478 | 0.00082478 | 0.00082478 | 0.00082478 | 0.00082478 | -0.00057427 | -0.00012387 | 0.00088985 | 0.00057433 | 0.00012394 | -0.00088978 | -0.00058324 | 0.00084479 | -0.00026079 | 0.00058337 | -0.00084466 | 0.00026091 | 137.482 | 137.482 | 137.482 | -42.5185 | -42.5185 | -42.5185 |  | 0.9924 | 1.0352 | 1.1243 | 0.99256 | 1.0351 | 1.1242 | 2.9259 | -124.176 | 121.1473 | 2.929 | -124.1706 | 121.1386
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.4345e-08 | 1.9789e-08 | -5.2743e-09 | 9.7671e-09 | -1.3147e-08 | 3.2093e-09 | 1.2987e-08 | 3.7536e-09 | -2.1232e-08 | -8.4628e-09 | -2.7922e-09 | 1.4241e-08 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.99256 | 1.0351 | 1.1242 | 0.99256 | 1.0351 | 1.1242 | 2.929 | -124.1706 | 121.1386 | 2.929 | -124.1706 | 121.1386
Line13_13_14 | 0.0035714 | 0.0035714 | 0.0035714 | 0.0035714 | 0.0035714 | 0.0035714 | 0.00082477 | 0.00082477 | 0.00082477 | 0.00082477 | 0.00082477 | 0.00082477 | -0.00057431 | -0.00012396 | 0.00088979 | 0.00057437 | 0.00012403 | -0.00088973 | -0.00058338 | 0.00084466 | -0.00026089 | 0.00058351 | -0.00084453 | 0.00026101 | 137.4802 | 137.4802 | 137.4802 | -42.5203 | -42.5203 | -42.5203 |  | 0.99256 | 1.0351 | 1.1242 | 0.99273 | 1.0349 | 1.1242 | 2.929 | -124.1706 | 121.1386 | 2.932 | -124.1651 | 121.1299
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -9.563e-09 | 1.3193e-08 | -3.5162e-09 | 4.9856e-09 | -6.5503e-09 | 1.4512e-09 | 8.658e-09 | 2.5024e-09 | -1.4155e-08 | -4.1338e-09 | -1.541e-09 | 7.1633e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.99256 | 1.0351 | 1.1242 | 0.99256 | 1.0351 | 1.1242 | 2.929 | -124.1706 | 121.1386 | 2.929 | -124.1706 | 121.1386
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.7815e-09 | 6.5964e-09 | -1.7581e-09 | 2.0405e-10 | 4.6087e-11 | -3.0691e-10 | 4.329e-09 | 1.2512e-09 | -7.0773e-09 | 1.9526e-10 | -2.8982e-10 | 8.601e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.99256 | 1.0351 | 1.1242 | 0.99256 | 1.0351 | 1.1242 | 2.929 | -124.1706 | 121.1386 | 2.929 | -124.1706 | 121.1386
Line16_4_18 | 0.03224 | 0 | 0 | 0.03224 | 0 | 0 | 0.0074454 | 0 | 0 | 0.0074454 | 0 | 0 | 0.0052056 | 6.659e-09 | -1.8788e-09 | -0.005197 | 4.7795e-11 | -3.065e-10 | 0.0052143 | 1.1576e-09 | -7.0967e-09 | -0.005197 | -2.8857e-10 | 8.4016e-11 | -42.1752 | 0 | 0 | 137.8249 | 0 | 0 |  | 0.9896 | 1.0351 | 1.1243 | 0.98713 | 1.0346 | 1.1242 | 2.8725 | -124.1707 | 121.1384 | 2.8249 | -124.1544 | 121.1123
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.762e-09 | 6.637e-09 | -1.8176e-09 | 2.0635e-10 | 4.3848e-11 | -3.0751e-10 | 4.3826e-09 | 1.2016e-09 | -7.0935e-09 | 1.9431e-10 | -2.9149e-10 | 8.8639e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.9919 | 1.0356 | 1.1244 | 0.9919 | 1.0356 | 1.1244 | 2.9166 | -124.1925 | 121.1733 | 2.9166 | -124.1925 | 121.1733
Line1_1_3 | 0.0035714 | 0.0035714 | 0.0035714 | 0.0035714 | 0.0035714 | 0.0035714 | 0.00082478 | 0.00082478 | 0.00082478 | 0.00082478 | 0.00082478 | 0.00082478 | -0.00057409 | -0.00012366 | 0.00089003 | 0.00057415 | 0.00012373 | -0.00088997 | -0.00058284 | 0.00084517 | -0.00026043 | 0.00058297 | -0.00084505 | 0.00026055 | 137.4833 | 137.4833 | 137.4833 | -42.5171 | -42.5171 | -42.5171 |  | 0.9919 | 1.0356 | 1.1244 | 0.99207 | 1.0355 | 1.1243 | 2.9166 | -124.1925 | 121.1733 | 2.9197 | -124.187 | 121.1646
Line2_1_4 | 0.028643 | 0.0035967 | 0.0035967 | 0.028643 | 0.0035967 | 0.0035967 | 0.0066148 | 0.00083062 | 0.00083062 | 0.0066148 | 0.00083062 | 0.00083062 | 0.0046275 | -0.00011273 | 0.00089262 | -0.0046203 | 0.000113 | -0.00089236 | 0.0046515 | 0.00085281 | -0.00027468 | -0.0046372 | -0.0008523 | 0.00027519 | -42.232 | 138.2776 | 138.2776 | 137.7681 | -41.7229 | -41.7229 |  | 0.9919 | 1.0356 | 1.1244 | 0.9896 | 1.0351 | 1.1243 | 2.9166 | -124.1925 | 121.1733 | 2.8725 | -124.1707 | 121.1384
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -9.5241e-09 | 1.3274e-08 | -3.6352e-09 | 4.9684e-09 | -6.5931e-09 | 1.5101e-09 | 8.7652e-09 | 2.4033e-09 | -1.4187e-08 | -4.1883e-09 | -1.4931e-09 | 7.1822e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.9919 | 1.0356 | 1.1244 | 0.9919 | 1.0356 | 1.1244 | 2.9166 | -124.1925 | 121.1733 | 2.9166 | -124.1925 | 121.1733
Line4_2_6 | 0.0035786 | 0.0035786 | 0.0035786 | 0.0035786 | 0.0035786 | 0.0035786 | 0.00082645 | 0.00082645 | 0.00082645 | 0.00082645 | 0.00082645 | 0.00082645 | -0.00057762 | -0.00012064 | 0.00089073 | 0.00057768 | 0.00012071 | -0.00089067 | -0.00058188 | 0.00084724 | -0.0002646 | 0.00058201 | -0.00084711 | 0.00026472 | 137.7093 | 137.7093 | 137.7093 | -42.2911 | -42.2911 | -42.2911 |  | 0.99207 | 1.0355 | 1.1243 | 0.99223 | 1.0354 | 1.1243 | 2.9198 | -124.187 | 121.1646 | 2.9229 | -124.1815 | 121.1559
Line5_6_7 | 0.0035786 | 0.0035786 | 0.0035786 | 0.0035786 | 0.0035786 | 0.0035786 | 0.00082645 | 0.00082645 | 0.00082645 | 0.00082645 | 0.00082645 | 0.00082645 | -0.00057768 | -0.00012071 | 0.00089067 | 0.00057774 | 0.00012078 | -0.00089061 | -0.00058201 | 0.00084711 | -0.00026472 | 0.00058214 | -0.00084698 | 0.00026485 | 137.7089 | 137.7089 | 137.7089 | -42.2916 | -42.2916 | -42.2916 |  | 0.99223 | 1.0354 | 1.1243 | 0.9924 | 1.0352 | 1.1243 | 2.9229 | -124.1815 | 121.1559 | 2.926 | -124.1761 | 121.1472
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.4331e-08 | 1.982e-08 | -5.3186e-09 | 9.7583e-09 | -1.3168e-08 | 3.2386e-09 | 1.3027e-08 | 3.7169e-09 | -2.1245e-08 | -8.4897e-09 | -2.7682e-09 | 1.425e-08 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.9924 | 1.0352 | 1.1243 | 0.9924 | 1.0352 | 1.1243 | 2.926 | -124.1761 | 121.1472 | 2.926 | -124.1761 | 121.1472
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.7768e-09 | 6.6066e-09 | -1.7729e-09 | 2.0462e-10 | 4.5535e-11 | -3.0707e-10 | 4.3424e-09 | 1.239e-09 | -7.0815e-09 | 1.9503e-10 | -2.9024e-10 | 8.6662e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.9924 | 1.0352 | 1.1243 | 0.9924 | 1.0352 | 1.1243 | 2.926 | -124.1761 | 121.1472 | 2.926 | -124.1761 | 121.1472
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.7768e-09 | 6.6066e-09 | -1.7729e-09 | 2.0462e-10 | 4.5535e-11 | -3.0707e-10 | 4.3424e-09 | 1.239e-09 | -7.0815e-09 | 1.9503e-10 | -2.9024e-10 | 8.6662e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.9924 | 1.0352 | 1.1243 | 0.9924 | 1.0352 | 1.1243 | 2.926 | -124.1761 | 121.1472 | 2.926 | -124.1761 | 121.1472
Line9_3_11 | 0.0035714 | 0.0035714 | 0.0035714 | 0.0035714 | 0.0035714 | 0.0035714 | 0.00082478 | 0.00082478 | 0.00082478 | 0.00082478 | 0.00082478 | 0.00082478 | -0.00057415 | -0.00012373 | 0.00088997 | 0.00057421 | 0.0001238 | -0.00088991 | -0.00058297 | 0.00084505 | -0.00026055 | 0.00058311 | -0.00084492 | 0.00026067 | 137.4829 | 137.4829 | 137.4829 | -42.5176 | -42.5176 | -42.5176 |  | 0.99207 | 1.0355 | 1.1243 | 0.99223 | 1.0354 | 1.1243 | 2.9197 | -124.187 | 121.1646 | 2.9228 | -124.1815 | 121.156

## LG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.0037488 | 0.0037488 | 0.0037488 | 0.0037488 | 0.0037488 | 0.0037488 | 0.00086574 | 0.00086574 | 0.00086574 | 0.00086574 | 0.00086574 | 0.00086574 | -0.00063378 | -0.00013238 | 0.00097759 | 0.00063385 | 0.00013246 | -0.00097753 | -0.00063838 | 0.00092987 | -0.00029024 | 0.00063852 | -0.00092973 | 0.00029037 | 137.7059 | 137.7059 | 137.7059 | -42.2945 | -42.2945 | -42.2945 |  | 1.0391 | 1.0849 | 1.1779 | 1.0392 | 1.0848 | 1.1779 | 2.9128 | -124.1915 | 121.1704 | 2.9159 | -124.186 | 121.1617
Line10_11_12 | 0.0037412 | 0.0037412 | 0.0037412 | 0.0037412 | 0.0037412 | 0.0037412 | 0.00086399 | 0.00086399 | 0.00086399 | 0.00086399 | 0.00086399 | 0.00086399 | -0.00063011 | -0.00013594 | 0.00097662 | 0.00063017 | 0.00013601 | -0.00097655 | -0.00063987 | 0.00092718 | -0.00028606 | 0.00064001 | -0.00092703 | 0.00028619 | 137.4786 | 137.4786 | 137.4786 | -42.5219 | -42.5219 | -42.5219 |  | 1.0394 | 1.0846 | 1.1779 | 1.0396 | 1.0845 | 1.1778 | 2.919 | -124.1805 | 121.1531 | 2.9221 | -124.1751 | 121.1444
Line11_12_13 | 0.0037412 | 0.0037412 | 0.0037412 | 0.0037412 | 0.0037412 | 0.0037412 | 0.00086399 | 0.00086399 | 0.00086399 | 0.00086399 | 0.00086399 | 0.00086399 | -0.00063017 | -0.00013601 | 0.00097655 | 0.00063024 | 0.00013609 | -0.00097648 | -0.00064001 | 0.00092703 | -0.00028619 | 0.00064016 | -0.00092689 | 0.00028632 | 137.4781 | 137.4781 | 137.4781 | -42.5223 | -42.5223 | -42.5223 |  | 1.0396 | 1.0845 | 1.1778 | 1.0398 | 1.0843 | 1.1778 | 2.9221 | -124.1751 | 121.1444 | 2.9252 | -124.1696 | 121.1357
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.5742e-08 | 2.1715e-08 | -5.7877e-09 | 1.0719e-08 | -1.4426e-08 | 3.5216e-09 | 1.4252e-08 | 4.1207e-09 | -2.33e-08 | -9.2874e-09 | -3.0651e-09 | 1.5628e-08 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0398 | 1.0843 | 1.1778 | 1.0398 | 1.0843 | 1.1778 | 2.9252 | -124.1696 | 121.1357 | 2.9252 | -124.1696 | 121.1357
Line13_13_14 | 0.0037412 | 0.0037412 | 0.0037412 | 0.0037412 | 0.0037412 | 0.0037412 | 0.00086399 | 0.00086399 | 0.00086399 | 0.00086399 | 0.00086399 | 0.00086399 | -0.00063022 | -0.00013611 | 0.00097649 | 0.00063029 | 0.00013619 | -0.00097642 | -0.00064017 | 0.00092689 | -0.0002863 | 0.00064032 | -0.00092675 | 0.00028643 | 137.4763 | 137.4763 | 137.4763 | -42.5241 | -42.5241 | -42.5241 |  | 1.0398 | 1.0843 | 1.1778 | 1.0399 | 1.0842 | 1.1778 | 2.9252 | -124.1696 | 121.1357 | 2.9282 | -124.1641 | 121.1271
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.0495e-08 | 1.4477e-08 | -3.8585e-09 | 5.4715e-09 | -7.1876e-09 | 1.5924e-09 | 9.5014e-09 | 2.7471e-09 | -1.5533e-08 | -4.5367e-09 | -1.6916e-09 | 7.8608e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0398 | 1.0843 | 1.1778 | 1.0398 | 1.0843 | 1.1778 | 2.9252 | -124.1696 | 121.1357 | 2.9252 | -124.1696 | 121.1357
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.2473e-09 | 7.2384e-09 | -1.9292e-09 | 2.2423e-10 | 5.081e-11 | -3.3687e-10 | 4.7507e-09 | 1.3736e-09 | -7.7667e-09 | 2.1401e-10 | -3.1798e-10 | 9.4158e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0398 | 1.0843 | 1.1778 | 1.0398 | 1.0843 | 1.1778 | 2.9252 | -124.1696 | 121.1357 | 2.9252 | -124.1696 | 121.1357
Line16_4_18 | 0.033772 | 0 | 0 | 0.033772 | 0 | 0 | 0.0077994 | 0 | 0 | 0.0077994 | 0 | 0 | 0.0057124 | 7.307e-09 | -2.0617e-09 | -0.0057029 | 5.2684e-11 | -3.3642e-10 | 0.0057219 | 1.2709e-09 | -7.788e-09 | -0.0057029 | -3.1662e-10 | 9.197e-11 | -42.179 | 0 | 0 | 137.821 | 0 | 0 |  | 1.0366 | 1.0843 | 1.1778 | 1.0341 | 1.0839 | 1.1777 | 2.8687 | -124.1697 | 121.1355 | 2.821 | -124.1534 | 121.1094
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.2259e-09 | 7.2829e-09 | -1.9945e-09 | 2.2675e-10 | 4.8352e-11 | -3.3752e-10 | 4.8095e-09 | 1.3192e-09 | -7.7845e-09 | 2.1297e-10 | -3.1983e-10 | 9.7043e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0391 | 1.0849 | 1.1779 | 1.0391 | 1.0849 | 1.1779 | 2.9128 | -124.1915 | 121.1704 | 2.9128 | -124.1915 | 121.1704
Line1_1_3 | 0.0037412 | 0.0037412 | 0.0037412 | 0.0037412 | 0.0037412 | 0.0037412 | 0.00086399 | 0.00086399 | 0.00086399 | 0.00086399 | 0.00086399 | 0.00086399 | -0.00062998 | -0.00013578 | 0.00097676 | 0.00063004 | 0.00013586 | -0.00097669 | -0.00063958 | 0.00092746 | -0.00028579 | 0.00063973 | -0.00092732 | 0.00028592 | 137.4795 | 137.4795 | 137.4795 | -42.5209 | -42.521 | -42.521 |  | 1.0391 | 1.0849 | 1.1779 | 1.0392 | 1.0848 | 1.1779 | 2.9128 | -124.1915 | 121.1704 | 2.9159 | -124.186 | 121.1617
Line2_1_4 | 0.030005 | 0.0037677 | 0.0037677 | 0.030005 | 0.0037677 | 0.0037677 | 0.0069293 | 0.00087011 | 0.00087011 | 0.0069293 | 0.00087011 | 0.00087011 | 0.0050779 | -0.00012378 | 0.0009796 | -0.0050701 | 0.00012408 | -0.00097931 | 0.0051044 | 0.00093584 | -0.00030143 | -0.0050886 | -0.00093527 | 0.00030198 | -42.2358 | 138.2738 | 138.2738 | 137.7642 | -41.7267 | -41.7267 |  | 1.0391 | 1.0849 | 1.1779 | 1.0366 | 1.0843 | 1.1778 | 2.9128 | -124.1915 | 121.1704 | 2.8687 | -124.1697 | 121.1355
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.0452e-08 | 1.4566e-08 | -3.9891e-09 | 5.4527e-09 | -7.2345e-09 | 1.657e-09 | 9.619e-09 | 2.6384e-09 | -1.5569e-08 | -4.5966e-09 | -1.639e-09 | 7.8815e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0391 | 1.0849 | 1.1779 | 1.0391 | 1.0849 | 1.1779 | 2.9128 | -124.1915 | 121.1704 | 2.9128 | -124.1915 | 121.1704
Line4_2_6 | 0.0037488 | 0.0037488 | 0.0037488 | 0.0037488 | 0.0037488 | 0.0037488 | 0.00086574 | 0.00086574 | 0.00086574 | 0.00086574 | 0.00086574 | 0.00086574 | -0.00063385 | -0.00013246 | 0.00097753 | 0.00063391 | 0.00013254 | -0.00097746 | -0.00063852 | 0.00092972 | -0.00029037 | 0.00063867 | -0.00092958 | 0.0002905 | 137.7055 | 137.7055 | 137.7055 | -42.295 | -42.295 | -42.295 |  | 1.0392 | 1.0848 | 1.1779 | 1.0394 | 1.0846 | 1.1779 | 2.9159 | -124.186 | 121.1617 | 2.9191 | -124.1806 | 121.153
Line5_6_7 | 0.0037488 | 0.0037488 | 0.0037488 | 0.0037488 | 0.0037488 | 0.0037488 | 0.00086574 | 0.00086574 | 0.00086574 | 0.00086574 | 0.00086574 | 0.00086574 | -0.00063391 | -0.00013254 | 0.00097746 | 0.00063398 | 0.00013261 | -0.00097739 | -0.00063867 | 0.00092958 | -0.0002905 | 0.00063881 | -0.00092944 | 0.00029063 | 137.705 | 137.705 | 137.705 | -42.2954 | -42.2954 | -42.2954 |  | 1.0394 | 1.0846 | 1.1779 | 1.0396 | 1.0845 | 1.1778 | 2.9191 | -124.1806 | 121.153 | 2.9222 | -124.1751 | 121.1443
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.5727e-08 | 2.1749e-08 | -5.8363e-09 | 1.0709e-08 | -1.4449e-08 | 3.5538e-09 | 1.4296e-08 | 4.0805e-09 | -2.3314e-08 | -9.317e-09 | -3.0388e-09 | 1.5638e-08 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0396 | 1.0845 | 1.1778 | 1.0396 | 1.0845 | 1.1778 | 2.9222 | -124.1751 | 121.1443 | 2.9222 | -124.1751 | 121.1443
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.2422e-09 | 7.2496e-09 | -1.9454e-09 | 2.2486e-10 | 5.0204e-11 | -3.3704e-10 | 4.7654e-09 | 1.3602e-09 | -7.7713e-09 | 2.1376e-10 | -3.1845e-10 | 9.4874e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0396 | 1.0845 | 1.1778 | 1.0396 | 1.0845 | 1.1778 | 2.9222 | -124.1751 | 121.1443 | 2.9222 | -124.1751 | 121.1443
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.2422e-09 | 7.2496e-09 | -1.9454e-09 | 2.2486e-10 | 5.0204e-11 | -3.3704e-10 | 4.7654e-09 | 1.3602e-09 | -7.7713e-09 | 2.1376e-10 | -3.1845e-10 | 9.4874e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0396 | 1.0845 | 1.1778 | 1.0396 | 1.0845 | 1.1778 | 2.9222 | -124.1751 | 121.1443 | 2.9222 | -124.1751 | 121.1443
Line9_3_11 | 0.0037412 | 0.0037412 | 0.0037412 | 0.0037412 | 0.0037412 | 0.0037412 | 0.00086399 | 0.00086399 | 0.00086399 | 0.00086399 | 0.00086399 | 0.00086399 | -0.00063004 | -0.00013586 | 0.00097669 | 0.00063011 | 0.00013594 | -0.00097662 | -0.00063973 | 0.00092732 | -0.00028592 | 0.00063987 | -0.00092718 | 0.00028606 | 137.4791 | 137.479 | 137.479 | -42.5214 | -42.5214 | -42.5214 |  | 1.0392 | 1.0848 | 1.1779 | 1.0394 | 1.0846 | 1.1779 | 2.9159 | -124.186 | 121.1617 | 2.919 | -124.1805 | 121.1531

## LG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.04109 | 0.04109 | 0.04109 | 0.04109 | 0.04109 | 0.04109 | 0.0094893 | 0.0094893 | 0.0094893 | 0.0094893 | 0.0094893 | 0.0094893 | -0.00046997 | 0.01229 | 0.013652 | 0.00048617 | -0.012273 | -0.013636 | -0.00049126 | 0.0080983 | -0.0074563 | 0.00050815 | -0.0080815 | 0.0074731 | 174.996 | 174.996 | 174.996 | -5.0044 | -5.0044 | -5.0044 |  | 0.071645 | 1.551 | 1.6392 | 0.074111 | 1.5486 | 1.6386 | 41.2651 | -151.6211 | 146.3535 | 41.2617 | -151.6413 | 146.2702
Line10_11_12 | 0.040932 | 0.040932 | 0.040932 | 0.040932 | 0.040932 | 0.040932 | 0.0094529 | 0.0094529 | 0.0094529 | 0.0094529 | 0.0094529 | 0.0094529 | -0.0004984 | 0.012179 | 0.013596 | 0.00051448 | -0.012162 | -0.01358 | -0.00052473 | 0.0080819 | -0.0074076 | 0.00054149 | -0.0080653 | 0.0074243 | 174.7703 | 174.7703 | 174.7703 | -5.2301 | -5.2301 | -5.2301 |  | 0.076559 | 1.5462 | 1.6379 | 0.079015 | 1.5438 | 1.6373 | 41.2442 | -151.6607 | 146.1877 | 41.2347 | -151.6806 | 146.1048
Line11_12_13 | 0.040932 | 0.040932 | 0.040932 | 0.040932 | 0.040932 | 0.040932 | 0.0094529 | 0.0094529 | 0.0094529 | 0.0094529 | 0.0094529 | 0.0094529 | -0.00051448 | 0.012162 | 0.01358 | 0.00053056 | -0.012146 | -0.013564 | -0.00054149 | 0.0080653 | -0.0074242 | 0.00055824 | -0.0080486 | 0.0074409 | 174.7699 | 174.7699 | 174.7699 | -5.2306 | -5.2306 | -5.2306 |  | 0.079015 | 1.5438 | 1.6373 | 0.081472 | 1.5414 | 1.6367 | 41.2347 | -151.6806 | 146.1048 | 41.2258 | -151.7006 | 146.0218
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.3721e-08 | 2.0187e-07 | -1.6219e-07 | 9.3366e-09 | -1.3873e-07 | 1.0343e-07 | 1.199e-08 | -2.7865e-07 | -3.2737e-07 | -7.8062e-09 | 1.8294e-07 | 2.2075e-07 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.081472 | 1.5414 | 1.6367 | 0.081472 | 1.5414 | 1.6367 | 41.2258 | -151.7006 | 146.0218 | 41.2258 | -151.7006 | 146.0218
Line13_13_14 | 0.040932 | 0.040932 | 0.040932 | 0.040932 | 0.040932 | 0.040932 | 0.0094529 | 0.0094529 | 0.0094529 | 0.0094529 | 0.0094529 | 0.0094529 | -0.00053055 | 0.012146 | 0.013564 | 0.00054663 | -0.01213 | -0.013548 | -0.00055826 | 0.0080489 | -0.0074406 | 0.00057501 | -0.0080322 | 0.0074572 | 174.7681 | 174.7681 | 174.7681 | -5.2324 | -5.2324 | -5.2324 |  | 0.081472 | 1.5414 | 1.6367 | 0.083929 | 1.539 | 1.636 | 41.2258 | -151.7006 | 146.0218 | 41.2173 | -151.7206 | 145.9387
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -9.1475e-09 | 1.3458e-07 | -1.0813e-07 | 4.7629e-09 | -7.1435e-08 | 4.9365e-08 | 7.9932e-09 | -1.8577e-07 | -2.1825e-07 | -3.8096e-09 | 9.0061e-08 | 1.1163e-07 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.081472 | 1.5414 | 1.6367 | 0.081472 | 1.5414 | 1.6367 | 41.2258 | -151.7006 | 146.0218 | 41.2258 | -151.7006 | 146.0218
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.5738e-09 | 6.7291e-08 | -5.4064e-08 | 1.8911e-10 | -4.1437e-09 | -4.6986e-09 | 3.9966e-09 | -9.2883e-08 | -1.0912e-07 | 1.8703e-10 | -2.8215e-09 | 2.5011e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.081472 | 1.5414 | 1.6367 | 0.081472 | 1.5414 | 1.6367 | 41.2258 | -151.7006 | 146.0218 | 41.2258 | -151.7006 | 146.0218
Line16_4_18 | 0.37052 | 0 | 0 | 0.37052 | 0 | 0 | 0.085568 | 0 | 0 | 0.085568 | 0 | 0 | 0.0021966 | 6.6716e-08 | -5.6528e-08 | -7.0886e-16 | -4.0864e-09 | -4.6715e-09 | 0.0022881 | -9.5198e-08 | -1.0974e-07 | -4.0739e-16 | -2.8133e-09 | 2.4756e-09 | -4.8885 | 0 | 0 | 175.1115 | 0 | 0 |  | 0.037067 | 1.5414 | 1.6367 | 0 | 1.5341 | 1.6348 | 41.2807 | -151.704 | 146.0185 | 0 | -151.7663 | 145.7672
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.0274e-09 | 6.7616e-08 | -5.4801e-08 | 1.6877e-10 | -4.2201e-09 | -4.7361e-09 | 3.5707e-09 | -9.4625e-08 | -1.1002e-07 | 1.646e-10 | -2.8326e-09 | 2.5347e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.071645 | 1.551 | 1.6392 | 0.071645 | 1.551 | 1.6392 | 41.2651 | -151.6211 | 146.3535 | 41.2651 | -151.6211 | 146.3535
Line1_1_3 | 0.040932 | 0.040932 | 0.040932 | 0.040932 | 0.040932 | 0.040932 | 0.0094529 | 0.0094529 | 0.0094529 | 0.0094529 | 0.0094529 | 0.0094529 | -0.00046624 | 0.012211 | 0.013628 | 0.00048232 | -0.012195 | -0.013612 | -0.00049121 | 0.0081153 | -0.0073743 | 0.00050797 | -0.0080986 | 0.007391 | 174.7712 | 174.7712 | 174.7712 | -5.2292 | -5.2292 | -5.2292 |  | 0.071645 | 1.551 | 1.6392 | 0.074102 | 1.5486 | 1.6386 | 41.2651 | -151.6211 | 146.3535 | 41.2543 | -151.6409 | 146.2706
Line2_1_4 | 0.32903 | 0.041486 | 0.041486 | 0.32903 | 0.041486 | 0.041486 | 0.075987 | 0.0095809 | 0.0095809 | 0.075987 | 0.0095809 | 0.0095809 | 0.0037674 | 0.012488 | 0.013709 | -0.0019486 | -0.012422 | -0.013642 | 0.00393 | 0.0080537 | -0.0076638 | -0.0020338 | -0.0079858 | 0.0077317 | -4.9451 | 175.5609 | 175.5609 | 175.0549 | -4.4396 | -4.4396 |  | 0.071645 | 1.551 | 1.6392 | 0.037067 | 1.5414 | 1.6367 | 41.2651 | -151.6211 | 146.3535 | 41.2807 | -151.704 | 146.0185
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.0547e-09 | 1.3523e-07 | -1.096e-07 | 4.1961e-09 | -7.1836e-08 | 5.0065e-08 | 7.1415e-09 | -1.8925e-07 | -2.2005e-07 | -3.4061e-09 | 9.1793e-08 | 1.1256e-07 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.071645 | 1.551 | 1.6392 | 0.071645 | 1.551 | 1.6392 | 41.2651 | -151.6211 | 146.3535 | 41.2651 | -151.6211 | 146.3535
Line4_2_6 | 0.04109 | 0.04109 | 0.04109 | 0.04109 | 0.04109 | 0.04109 | 0.0094893 | 0.0094893 | 0.0094893 | 0.0094893 | 0.0094893 | 0.0094893 | -0.00048617 | 0.012273 | 0.013636 | 0.00050238 | -0.012257 | -0.013619 | -0.00050815 | 0.0080815 | -0.0074731 | 0.00052504 | -0.0080648 | 0.0074899 | 174.9956 | 174.9956 | 174.9956 | -5.0049 | -5.0049 | -5.0049 |  | 0.074111 | 1.5486 | 1.6386 | 0.076577 | 1.5462 | 1.638 | 41.2617 | -151.6413 | 146.2702 | 41.2586 | -151.6616 | 146.1869
Line5_6_7 | 0.04109 | 0.04109 | 0.04109 | 0.04109 | 0.04109 | 0.04109 | 0.0094893 | 0.0094893 | 0.0094893 | 0.0094893 | 0.0094893 | 0.0094893 | -0.00050238 | 0.012257 | 0.013619 | 0.00051858 | -0.012241 | -0.013603 | -0.00052504 | 0.0080648 | -0.0074899 | 0.00054192 | -0.008048 | 0.0075066 | 174.9951 | 174.9951 | 174.9951 | -5.0053 | -5.0053 | -5.0053 |  | 0.076577 | 1.5462 | 1.638 | 0.079044 | 1.5438 | 1.6373 | 41.2586 | -151.6616 | 146.1869 | 41.2556 | -151.6819 | 146.1036
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.3321e-08 | 2.0212e-07 | -1.6274e-07 | 9.065e-09 | -1.3891e-07 | 1.0378e-07 | 1.1674e-08 | -2.7994e-07 | -3.2805e-07 | -7.6009e-09 | 1.838e-07 | 2.2121e-07 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.079044 | 1.5438 | 1.6373 | 0.079044 | 1.5438 | 1.6373 | 41.2556 | -151.6819 | 146.1036 | 41.2557 | -151.6819 | 146.1036
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.4404e-09 | 6.7373e-08 | -5.4246e-08 | 1.8408e-10 | -4.1627e-09 | -4.708e-09 | 3.8912e-09 | -9.3314e-08 | -1.0935e-07 | 1.8156e-10 | -2.8243e-09 | 2.5094e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.079044 | 1.5438 | 1.6373 | 0.079044 | 1.5438 | 1.6373 | 41.2557 | -151.6819 | 146.1036 | 41.2557 | -151.6819 | 146.1036
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.4404e-09 | 6.7373e-08 | -5.4246e-08 | 1.8408e-10 | -4.1627e-09 | -4.708e-09 | 3.8912e-09 | -9.3314e-08 | -1.0935e-07 | 1.8156e-10 | -2.8243e-09 | 2.5094e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.079044 | 1.5438 | 1.6373 | 0.079044 | 1.5438 | 1.6373 | 41.2557 | -151.6819 | 146.1036 | 41.2557 | -151.6819 | 146.1036
Line9_3_11 | 0.040932 | 0.040932 | 0.040932 | 0.040932 | 0.040932 | 0.040932 | 0.0094529 | 0.0094529 | 0.0094529 | 0.0094529 | 0.0094529 | 0.0094529 | -0.00048232 | 0.012195 | 0.013612 | 0.0004984 | -0.012179 | -0.013596 | -0.00050797 | 0.0080986 | -0.007391 | 0.00052473 | -0.0080819 | 0.0074076 | 174.7708 | 174.7708 | 174.7708 | -5.2297 | -5.2297 | -5.2297 |  | 0.074102 | 1.5486 | 1.6386 | 0.076559 | 1.5462 | 1.6379 | 41.2543 | -151.6409 | 146.2706 | 41.2442 | -151.6607 | 146.1877

## LG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.038927 | 0.038927 | 0.038927 | 0.038927 | 0.038927 | 0.038927 | 0.0089899 | 0.0089899 | 0.0089899 | 0.0089899 | 0.0089899 | 0.0089899 | -0.0004218 | 0.01103 | 0.012253 | 0.00043634 | -0.011016 | -0.012238 | -0.00044091 | 0.0072683 | -0.0066921 | 0.00045607 | -0.0072532 | 0.0067072 | 174.996 | 174.996 | 174.996 | -5.0044 | -5.0044 | -5.0044 |  | 0.067874 | 1.4694 | 1.553 | 0.07021 | 1.4671 | 1.5524 | 41.2651 | -151.6211 | 146.3535 | 41.2617 | -151.6413 | 146.2702
Line10_11_12 | 0.038778 | 0.038778 | 0.038778 | 0.038778 | 0.038778 | 0.038778 | 0.0089554 | 0.0089554 | 0.0089554 | 0.0089554 | 0.0089554 | 0.0089554 | -0.00044732 | 0.01093 | 0.012203 | 0.00046175 | -0.010916 | -0.012188 | -0.00047095 | 0.0072536 | -0.0066484 | 0.00048599 | -0.0072386 | 0.0066633 | 174.7703 | 174.7703 | 174.7703 | -5.2301 | -5.2301 | -5.2301 |  | 0.072529 | 1.4648 | 1.5517 | 0.074857 | 1.4626 | 1.5511 | 41.2442 | -151.6607 | 146.1877 | 41.2347 | -151.6806 | 146.1048
Line11_12_13 | 0.038778 | 0.038778 | 0.038778 | 0.038778 | 0.038778 | 0.038778 | 0.0089554 | 0.0089554 | 0.0089554 | 0.0089554 | 0.0089554 | 0.0089554 | -0.00046175 | 0.010916 | 0.012188 | 0.00047618 | -0.010901 | -0.012174 | -0.00048599 | 0.0072386 | -0.0066633 | 0.00050103 | -0.0072237 | 0.0066783 | 174.7699 | 174.7699 | 174.7699 | -5.2306 | -5.2306 | -5.2306 |  | 0.074857 | 1.4626 | 1.5511 | 0.077184 | 1.4603 | 1.5505 | 41.2347 | -151.6806 | 146.1048 | 41.2258 | -151.7006 | 146.0218
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.2315e-08 | 1.8118e-07 | -1.4557e-07 | 8.3797e-09 | -1.2451e-07 | 9.2828e-08 | 1.0761e-08 | -2.5009e-07 | -2.9382e-07 | -7.0061e-09 | 1.6419e-07 | 1.9812e-07 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.077184 | 1.4603 | 1.5505 | 0.077184 | 1.4603 | 1.5505 | 41.2258 | -151.7006 | 146.0218 | 41.2258 | -151.7006 | 146.0218
Line13_13_14 | 0.038778 | 0.038778 | 0.038778 | 0.038778 | 0.038778 | 0.038778 | 0.0089554 | 0.0089554 | 0.0089554 | 0.0089554 | 0.0089554 | 0.0089554 | -0.00047617 | 0.010901 | 0.012174 | 0.0004906 | -0.010887 | -0.01216 | -0.00050104 | 0.0072239 | -0.006678 | 0.00051608 | -0.007209 | 0.0066929 | 174.7681 | 174.7681 | 174.7681 | -5.2324 | -5.2324 | -5.2324 |  | 0.077184 | 1.4603 | 1.5505 | 0.079512 | 1.458 | 1.5499 | 41.2258 | -151.7006 | 146.0218 | 41.2173 | -151.7206 | 145.9387
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.21e-09 | 1.2079e-07 | -9.7045e-08 | 4.2747e-09 | -6.4113e-08 | 4.4306e-08 | 7.174e-09 | -1.6673e-07 | -1.9588e-07 | -3.4191e-09 | 8.0831e-08 | 1.0018e-07 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.077184 | 1.4603 | 1.5505 | 0.077184 | 1.4603 | 1.5505 | 41.2258 | -151.7006 | 146.0218 | 41.2258 | -151.7006 | 146.0218
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.105e-09 | 6.0394e-08 | -4.8523e-08 | 1.6973e-10 | -3.719e-09 | -4.217e-09 | 3.587e-09 | -8.3363e-08 | -9.794e-08 | 1.6786e-10 | -2.5323e-09 | 2.2448e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.077184 | 1.4603 | 1.5505 | 0.077184 | 1.4603 | 1.5505 | 41.2258 | -151.7006 | 146.0218 | 41.2258 | -151.7006 | 146.0218
Line16_4_18 | 0.35102 | 0 | 0 | 0.35102 | 0 | 0 | 0.081064 | 0 | 0 | 0.081064 | 0 | 0 | 0.0019714 | 5.9878e-08 | -5.0734e-08 | -6.979e-16 | -3.6676e-09 | -4.1927e-09 | 0.0020536 | -8.5441e-08 | -9.8488e-08 | -3.9468e-16 | -2.525e-09 | 2.2218e-09 | -4.8885 | 0 | 0 | 175.1115 | 0 | 0 |  | 0.035116 | 1.4602 | 1.5506 | 0 | 1.4534 | 1.5488 | 41.2807 | -151.704 | 146.0185 | 0 | -151.7663 | 145.7672
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.6146e-09 | 6.0686e-08 | -4.9184e-08 | 1.5147e-10 | -3.7876e-09 | -4.2507e-09 | 3.2048e-09 | -8.4927e-08 | -9.8747e-08 | 1.4773e-10 | -2.5423e-09 | 2.2749e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.067874 | 1.4694 | 1.553 | 0.067874 | 1.4694 | 1.553 | 41.2651 | -151.6211 | 146.3535 | 41.2651 | -151.6211 | 146.3535
Line1_1_3 | 0.038778 | 0.038778 | 0.038778 | 0.038778 | 0.038778 | 0.038778 | 0.0089554 | 0.0089554 | 0.0089554 | 0.0089554 | 0.0089554 | 0.0089554 | -0.00041846 | 0.010959 | 0.012232 | 0.00043289 | -0.010945 | -0.012217 | -0.00044086 | 0.0072835 | -0.0066185 | 0.00045591 | -0.0072685 | 0.0066334 | 174.7712 | 174.7712 | 174.7712 | -5.2292 | -5.2292 | -5.2292 |  | 0.067874 | 1.4694 | 1.553 | 0.070201 | 1.4671 | 1.5523 | 41.2651 | -151.6211 | 146.3535 | 41.2543 | -151.6409 | 146.2706
Line2_1_4 | 0.31172 | 0.039303 | 0.039303 | 0.31172 | 0.039303 | 0.039303 | 0.071988 | 0.0090766 | 0.0090766 | 0.071988 | 0.0090766 | 0.0090766 | 0.0033813 | 0.011208 | 0.012304 | -0.0017489 | -0.011149 | -0.012244 | 0.0035272 | 0.0072283 | -0.0068783 | -0.0018254 | -0.0071673 | 0.0069393 | -4.9451 | 175.5609 | 175.5609 | 175.0549 | -4.4396 | -4.4396 |  | 0.067874 | 1.4694 | 1.553 | 0.035116 | 1.4602 | 1.5506 | 41.2651 | -151.6211 | 146.3535 | 41.2807 | -151.704 | 146.0185
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.2292e-09 | 1.2137e-07 | -9.8369e-08 | 3.7661e-09 | -6.4473e-08 | 4.4934e-08 | 6.4095e-09 | -1.6985e-07 | -1.9749e-07 | -3.057e-09 | 8.2385e-08 | 1.0102e-07 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.067874 | 1.4694 | 1.553 | 0.067874 | 1.4694 | 1.553 | 41.2651 | -151.6211 | 146.3535 | 41.2651 | -151.6211 | 146.3535
Line4_2_6 | 0.038927 | 0.038927 | 0.038927 | 0.038927 | 0.038927 | 0.038927 | 0.0089899 | 0.0089899 | 0.0089899 | 0.0089899 | 0.0089899 | 0.0089899 | -0.00043634 | 0.011016 | 0.012238 | 0.00045089 | -0.011001 | -0.012224 | -0.00045607 | 0.0072532 | -0.0067071 | 0.00047122 | -0.0072382 | 0.0067222 | 174.9956 | 174.9956 | 174.9956 | -5.0049 | -5.0049 | -5.0049 |  | 0.07021 | 1.4671 | 1.5524 | 0.072547 | 1.4648 | 1.5517 | 41.2617 | -151.6413 | 146.2702 | 41.2586 | -151.6616 | 146.1869
Line5_6_7 | 0.038927 | 0.038927 | 0.038927 | 0.038927 | 0.038927 | 0.038927 | 0.0089899 | 0.0089899 | 0.0089899 | 0.0089899 | 0.0089899 | 0.0089899 | -0.00045089 | 0.011001 | 0.012224 | 0.00046543 | -0.010986 | -0.012209 | -0.00047122 | 0.0072382 | -0.0067222 | 0.00048638 | -0.0072231 | 0.0067373 | 174.9951 | 174.9951 | 174.9951 | -5.0053 | -5.0053 | -5.0053 |  | 0.072547 | 1.4648 | 1.5517 | 0.074884 | 1.4625 | 1.5511 | 41.2586 | -151.6616 | 146.1869 | 41.2556 | -151.6819 | 146.1036
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.1956e-08 | 1.814e-07 | -1.4606e-07 | 8.1359e-09 | -1.2467e-07 | 9.3147e-08 | 1.0477e-08 | -2.5125e-07 | -2.9443e-07 | -6.8219e-09 | 1.6497e-07 | 1.9854e-07 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.074884 | 1.4625 | 1.5511 | 0.074884 | 1.4625 | 1.5511 | 41.2556 | -151.6819 | 146.1036 | 41.2557 | -151.6819 | 146.1036
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.9853e-09 | 6.0468e-08 | -4.8686e-08 | 1.6521e-10 | -3.736e-09 | -4.2255e-09 | 3.4924e-09 | -8.375e-08 | -9.8143e-08 | 1.6295e-10 | -2.5348e-09 | 2.2522e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.074884 | 1.4625 | 1.5511 | 0.074884 | 1.4625 | 1.5511 | 41.2557 | -151.6819 | 146.1036 | 41.2557 | -151.6819 | 146.1036
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.9853e-09 | 6.0468e-08 | -4.8686e-08 | 1.6521e-10 | -3.736e-09 | -4.2255e-09 | 3.4924e-09 | -8.375e-08 | -9.8143e-08 | 1.6295e-10 | -2.5348e-09 | 2.2522e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.074884 | 1.4625 | 1.5511 | 0.074884 | 1.4625 | 1.5511 | 41.2557 | -151.6819 | 146.1036 | 41.2557 | -151.6819 | 146.1036
Line9_3_11 | 0.038778 | 0.038778 | 0.038778 | 0.038778 | 0.038778 | 0.038778 | 0.0089554 | 0.0089554 | 0.0089554 | 0.0089554 | 0.0089554 | 0.0089554 | -0.00043289 | 0.010945 | 0.012217 | 0.00044732 | -0.01093 | -0.012203 | -0.00045591 | 0.0072685 | -0.0066334 | 0.00047095 | -0.0072536 | 0.0066484 | 174.7708 | 174.7708 | 174.7708 | -5.2297 | -5.2297 | -5.2297 |  | 0.070201 | 1.4671 | 1.5523 | 0.072529 | 1.4648 | 1.5517 | 41.2543 | -151.6409 | 146.2706 | 41.2442 | -151.6607 | 146.1877

## LG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.0032296 | 0.0032296 | 0.0032296 | 0.0032296 | 0.0032296 | 0.0032296 | 0.00074584 | 0.00074584 | 0.00074584 | 0.00074584 | 0.00074584 | 0.00074584 | -0.00047221 | -9.75e-05 | 0.00072707 | 0.00047231 | 9.7606e-05 | -0.00072697 | -0.00047424 | 0.00069206 | -0.00021689 | 0.00047435 | -0.00069196 | 0.00021699 | 137.7871 | 137.7871 | 137.7871 | -42.2134 | -42.2134 | -42.2134 |  | 0.89731 | 0.93707 | 1.0173 | 0.8975 | 0.93695 | 1.0172 | 2.9099 | -124.1937 | 121.1766 | 2.9101 | -124.1844 | 121.1669
Line10_11_12 | 0.0032172 | 0.0032172 | 0.0032172 | 0.0032172 | 0.0032172 | 0.0032172 | 0.00074298 | 0.00074298 | 0.00074298 | 0.00074298 | 0.00074298 | 0.00074298 | -0.00046874 | -0.00010004 | 0.00072492 | 0.00046883 | 0.00010014 | -0.00072483 | -0.00047448 | 0.00068882 | -0.00021341 | 0.00047459 | -0.00068871 | 0.00021351 | 137.5614 | 137.5614 | 137.5614 | -42.4391 | -42.4391 | -42.4391 |  | 0.89769 | 0.93683 | 1.0171 | 0.89789 | 0.93671 | 1.017 | 2.9102 | -124.175 | 121.1573 | 2.9104 | -124.1657 | 121.1476
Line11_12_13 | 0.0032172 | 0.0032172 | 0.0032172 | 0.0032172 | 0.0032172 | 0.0032172 | 0.00074298 | 0.00074298 | 0.00074298 | 0.00074298 | 0.00074298 | 0.00074298 | -0.00046883 | -0.00010014 | 0.00072483 | 0.00046893 | 0.00010025 | -0.00072473 | -0.00047459 | 0.00068871 | -0.00021351 | 0.00047469 | -0.00068861 | 0.00021361 | 137.5609 | 137.5609 | 137.5609 | -42.4395 | -42.4395 | -42.4395 |  | 0.89789 | 0.93671 | 1.017 | 0.89808 | 0.93659 | 1.0169 | 2.9104 | -124.1657 | 121.1476 | 2.9106 | -124.1564 | 121.138
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.1685e-08 | 1.6148e-08 | -4.3256e-09 | 7.9571e-09 | -1.0728e-08 | 2.6335e-09 | 1.0616e-08 | 3.044e-09 | -1.731e-08 | -6.9182e-09 | -2.2658e-09 | 1.161e-08 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.89808 | 0.93659 | 1.0169 | 0.89808 | 0.93659 | 1.0169 | 2.9106 | -124.1564 | 121.138 | 2.9106 | -124.1564 | 121.138
Line13_13_14 | 0.0032172 | 0.0032172 | 0.0032172 | 0.0032172 | 0.0032172 | 0.0032172 | 0.00074298 | 0.00074298 | 0.00074298 | 0.00074298 | 0.00074298 | 0.00074298 | -0.00046892 | -0.00010027 | 0.00072473 | 0.00046901 | 0.00010037 | -0.00072464 | -0.0004747 | 0.0006886 | -0.00021359 | 0.00047481 | -0.0006885 | 0.00021369 | 137.5591 | 137.5591 | 137.5591 | -42.4413 | -42.4413 | -42.4413 |  | 0.89808 | 0.93659 | 1.0169 | 0.89827 | 0.93647 | 1.0168 | 2.9106 | -124.1564 | 121.138 | 2.9108 | -124.1471 | 121.1283
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.7901e-09 | 1.0766e-08 | -2.8837e-09 | 4.062e-09 | -5.3453e-09 | 1.1916e-09 | 7.077e-09 | 2.0294e-09 | -1.154e-08 | -3.3797e-09 | -1.2511e-09 | 5.8403e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.89808 | 0.93659 | 1.0169 | 0.89808 | 0.93659 | 1.0169 | 2.9106 | -124.1564 | 121.138 | 2.9106 | -124.1564 | 121.138
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.8951e-09 | 5.3828e-09 | -1.4419e-09 | 1.6694e-10 | 3.7468e-11 | -2.5025e-10 | 3.5385e-09 | 1.0147e-09 | -5.77e-09 | 1.5885e-10 | -2.3646e-10 | 7.0349e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.89808 | 0.93659 | 1.0169 | 0.89808 | 0.93659 | 1.0169 | 2.9106 | -124.1564 | 121.138 | 2.9106 | -124.1564 | 121.138
Line16_4_18 | 0.029122 | 0 | 0 | 0.029122 | 0 | 0 | 0.0067254 | 0 | 0 | 0.0067254 | 0 | 0 | 0.004254 | 5.4712e-09 | -1.5527e-09 | -0.0042405 | 3.8836e-11 | -2.4917e-10 | 0.0042546 | 9.4305e-10 | -5.8247e-09 | -0.0042405 | -2.3477e-10 | 6.8496e-11 | -42.0974 | 0 | 0 | 137.9026 | 0 | 0 |  | 0.89459 | 0.93658 | 1.0169 | 0.89168 | 0.93622 | 1.0167 | 2.9064 | -124.1564 | 121.1375 | 2.9026 | -124.1283 | 121.1083
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.8934e-09 | 5.4356e-09 | -1.4956e-09 | 1.6934e-10 | 3.5702e-11 | -2.5171e-10 | 3.5936e-09 | 9.7652e-10 | -5.8059e-09 | 1.5867e-10 | -2.387e-10 | 7.2762e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.89731 | 0.93707 | 1.0173 | 0.89731 | 0.93707 | 1.0173 | 2.9099 | -124.1937 | 121.1766 | 2.9099 | -124.1937 | 121.1766
Line1_1_3 | 0.0032172 | 0.0032172 | 0.0032172 | 0.0032172 | 0.0032172 | 0.0032172 | 0.00074298 | 0.00074298 | 0.00074298 | 0.00074298 | 0.00074298 | 0.00074298 | -0.00046854 | -9.983e-05 | 0.00072512 | 0.00046864 | 9.9935e-05 | -0.00072502 | -0.00047426 | 0.00068903 | -0.00021322 | 0.00047437 | -0.00068892 | 0.00021332 | 137.5623 | 137.5623 | 137.5623 | -42.4381 | -42.4382 | -42.4382 |  | 0.89731 | 0.93707 | 1.0173 | 0.8975 | 0.93695 | 1.0172 | 2.9099 | -124.1937 | 121.1766 | 2.91 | -124.1844 | 121.1669
Line2_1_4 | 0.025861 | 0.0032607 | 0.0032607 | 0.025861 | 0.0032607 | 0.0032607 | 0.0059724 | 0.00075303 | 0.00075303 | 0.0059724 | 0.00075303 | 0.00075303 | 0.0037852 | -9.1548e-05 | 0.00073189 | -0.003774 | 9.1962e-05 | -0.00073148 | 0.0037937 | 0.00069968 | -0.00022621 | -0.003782 | -0.00069926 | 0.00022663 | -42.154 | 138.3519 | 138.3519 | 137.846 | -41.6485 | -41.6485 |  | 0.89731 | 0.93707 | 1.0173 | 0.89459 | 0.93658 | 1.0169 | 2.9099 | -124.1937 | 121.1766 | 2.9064 | -124.1564 | 121.1375
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.7868e-09 | 1.0871e-08 | -2.9911e-09 | 4.0627e-09 | -5.3999e-09 | 1.2439e-09 | 7.1872e-09 | 1.953e-09 | -1.1612e-08 | -3.4349e-09 | -1.2152e-09 | 5.8786e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.89731 | 0.93707 | 1.0173 | 0.89731 | 0.93707 | 1.0173 | 2.9099 | -124.1937 | 121.1766 | 2.9099 | -124.1937 | 121.1766
Line4_2_6 | 0.0032296 | 0.0032296 | 0.0032296 | 0.0032296 | 0.0032296 | 0.0032296 | 0.00074584 | 0.00074584 | 0.00074584 | 0.00074584 | 0.00074584 | 0.00074584 | -0.00047231 | -9.7606e-05 | 0.00072697 | 0.00047241 | 9.7711e-05 | -0.00072687 | -0.00047435 | 0.00069196 | -0.00021699 | 0.00047446 | -0.00069185 | 0.00021709 | 137.7866 | 137.7866 | 137.7866 | -42.2138 | -42.2138 | -42.2138 |  | 0.8975 | 0.93695 | 1.0172 | 0.89769 | 0.93683 | 1.0171 | 2.9101 | -124.1844 | 121.1669 | 2.9103 | -124.175 | 121.1572
Line5_6_7 | 0.0032296 | 0.0032296 | 0.0032296 | 0.0032296 | 0.0032296 | 0.0032296 | 0.00074584 | 0.00074584 | 0.00074584 | 0.00074584 | 0.00074584 | 0.00074584 | -0.0004724 | -9.7711e-05 | 0.00072687 | 0.0004725 | 9.7817e-05 | -0.00072677 | -0.00047446 | 0.00069185 | -0.00021709 | 0.00047456 | -0.00069175 | 0.00021719 | 137.7862 | 137.7862 | 137.7862 | -42.2143 | -42.2143 | -42.2143 |  | 0.89769 | 0.93683 | 1.0171 | 0.89789 | 0.93671 | 1.017 | 2.9103 | -124.175 | 121.1572 | 2.9105 | -124.1657 | 121.1474
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.1685e-08 | 1.6188e-08 | -4.3651e-09 | 7.9572e-09 | -1.0755e-08 | 2.6595e-09 | 1.0656e-08 | 3.0162e-09 | -1.7337e-08 | -6.9454e-09 | -2.2478e-09 | 1.1629e-08 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.89789 | 0.93671 | 1.017 | 0.89789 | 0.93671 | 1.017 | 2.9105 | -124.1657 | 121.1474 | 2.9105 | -124.1657 | 121.1474
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.8948e-09 | 5.3959e-09 | -1.455e-09 | 1.6753e-10 | 3.7038e-11 | -2.5062e-10 | 3.5521e-09 | 1.0054e-09 | -5.779e-09 | 1.5881e-10 | -2.3702e-10 | 7.0942e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.89789 | 0.93671 | 1.017 | 0.89789 | 0.93671 | 1.017 | 2.9105 | -124.1657 | 121.1474 | 2.9105 | -124.1657 | 121.1474
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.8948e-09 | 5.3959e-09 | -1.455e-09 | 1.6753e-10 | 3.7038e-11 | -2.5062e-10 | 3.5521e-09 | 1.0054e-09 | -5.779e-09 | 1.5881e-10 | -2.3702e-10 | 7.0942e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.89789 | 0.93671 | 1.017 | 0.89789 | 0.93671 | 1.017 | 2.9105 | -124.1657 | 121.1474 | 2.9105 | -124.1657 | 121.1474
Line9_3_11 | 0.0032172 | 0.0032172 | 0.0032172 | 0.0032172 | 0.0032172 | 0.0032172 | 0.00074298 | 0.00074298 | 0.00074298 | 0.00074298 | 0.00074298 | 0.00074298 | -0.00046864 | -9.9935e-05 | 0.00072502 | 0.00046874 | 0.00010004 | -0.00072492 | -0.00047437 | 0.00068892 | -0.00021332 | 0.00047448 | -0.00068882 | 0.00021341 | 137.5619 | 137.5618 | 137.5618 | -42.4386 | -42.4386 | -42.4386 |  | 0.8975 | 0.93695 | 1.0172 | 0.89769 | 0.93683 | 1.0171 | 2.91 | -124.1844 | 121.1669 | 2.9102 | -124.175 | 121.1573

## LG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.0030596 | 0.0030596 | 0.0030596 | 0.0030596 | 0.0030596 | 0.0030596 | 0.00070658 | 0.00070658 | 0.00070658 | 0.00070658 | 0.00070658 | 0.00070658 | -0.00042381 | -8.7507e-05 | 0.00065255 | 0.0004239 | 8.7602e-05 | -0.00065246 | -0.00042563 | 0.00062113 | -0.00019466 | 0.00042573 | -0.00062104 | 0.00019475 | 137.7871 | 137.7871 | 137.7871 | -42.2134 | -42.2134 | -42.2134 |  | 0.85008 | 0.88775 | 0.96374 | 0.85026 | 0.88763 | 0.96366 | 2.9099 | -124.1937 | 121.1766 | 2.9101 | -124.1844 | 121.1669
Line10_11_12 | 0.0030479 | 0.0030479 | 0.0030479 | 0.0030479 | 0.0030479 | 0.0030479 | 0.00070387 | 0.00070387 | 0.00070387 | 0.00070387 | 0.00070387 | 0.00070387 | -0.00042069 | -8.9787e-05 | 0.00065062 | 0.00042078 | 8.9881e-05 | -0.00065054 | -0.00042585 | 0.00061822 | -0.00019154 | 0.00042594 | -0.00061812 | 0.00019163 | 137.5614 | 137.5614 | 137.5614 | -42.4391 | -42.4391 | -42.4391 |  | 0.85045 | 0.88752 | 0.96357 | 0.85063 | 0.88741 | 0.96349 | 2.9102 | -124.175 | 121.1573 | 2.9104 | -124.1657 | 121.1476
Line11_12_13 | 0.0030479 | 0.0030479 | 0.0030479 | 0.0030479 | 0.0030479 | 0.0030479 | 0.00070387 | 0.00070387 | 0.00070387 | 0.00070387 | 0.00070387 | 0.00070387 | -0.00042078 | -8.9881e-05 | 0.00065054 | 0.00042087 | 8.9975e-05 | -0.00065045 | -0.00042594 | 0.00061812 | -0.00019163 | 0.00042604 | -0.00061803 | 0.00019172 | 137.5609 | 137.5609 | 137.5609 | -42.4395 | -42.4395 | -42.4395 |  | 0.85063 | 0.88741 | 0.96349 | 0.85081 | 0.8873 | 0.9634 | 2.9104 | -124.1657 | 121.1476 | 2.9106 | -124.1564 | 121.138
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.0488e-08 | 1.4493e-08 | -3.8822e-09 | 7.1415e-09 | -9.6285e-09 | 2.3636e-09 | 9.5275e-09 | 2.7321e-09 | -1.5536e-08 | -6.2091e-09 | -2.0336e-09 | 1.042e-08 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.85081 | 0.8873 | 0.9634 | 0.85081 | 0.8873 | 0.9634 | 2.9106 | -124.1564 | 121.138 | 2.9106 | -124.1564 | 121.138
Line13_13_14 | 0.0030479 | 0.0030479 | 0.0030479 | 0.0030479 | 0.0030479 | 0.0030479 | 0.00070387 | 0.00070387 | 0.00070387 | 0.00070387 | 0.00070387 | 0.00070387 | -0.00042085 | -8.9989e-05 | 0.00065045 | 0.00042094 | 9.0083e-05 | -0.00065037 | -0.00042605 | 0.00061803 | -0.0001917 | 0.00042615 | -0.00061793 | 0.00019179 | 137.5591 | 137.5591 | 137.5591 | -42.4413 | -42.4413 | -42.4413 |  | 0.85081 | 0.8873 | 0.9634 | 0.85099 | 0.88718 | 0.96332 | 2.9106 | -124.1564 | 121.138 | 2.9108 | -124.1471 | 121.1283
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.9917e-09 | 9.6621e-09 | -2.5882e-09 | 3.6457e-09 | -4.7974e-09 | 1.0695e-09 | 6.3517e-09 | 1.8214e-09 | -1.0357e-08 | -3.0333e-09 | -1.1229e-09 | 5.2417e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.85081 | 0.8873 | 0.9634 | 0.85081 | 0.8873 | 0.9634 | 2.9106 | -124.1564 | 121.138 | 2.9106 | -124.1564 | 121.138
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.4959e-09 | 4.8311e-09 | -1.2941e-09 | 1.4983e-10 | 3.3628e-11 | -2.246e-10 | 3.1758e-09 | 9.1069e-10 | -5.1786e-09 | 1.4257e-10 | -2.1223e-10 | 6.3139e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.85081 | 0.8873 | 0.9634 | 0.85081 | 0.8873 | 0.9634 | 2.9106 | -124.1564 | 121.138 | 2.9106 | -124.1564 | 121.138
Line16_4_18 | 0.027589 | 0 | 0 | 0.027589 | 0 | 0 | 0.0063715 | 0 | 0 | 0.0063715 | 0 | 0 | 0.003818 | 4.9104e-09 | -1.3936e-09 | -0.0038058 | 3.4855e-11 | -2.2363e-10 | 0.0038185 | 8.4639e-10 | -5.2277e-09 | -0.0038058 | -2.1071e-10 | 6.1475e-11 | -42.0974 | 0 | 0 | 137.9026 | 0 | 0 |  | 0.8475 | 0.88729 | 0.96341 | 0.84475 | 0.88695 | 0.96315 | 2.9064 | -124.1564 | 121.1375 | 2.9026 | -124.1283 | 121.1083
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.4943e-09 | 4.8785e-09 | -1.3423e-09 | 1.5198e-10 | 3.2043e-11 | -2.2591e-10 | 3.2253e-09 | 8.7643e-10 | -5.2108e-09 | 1.4241e-10 | -2.1423e-10 | 6.5304e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.85008 | 0.88775 | 0.96374 | 0.85008 | 0.88775 | 0.96374 | 2.9099 | -124.1937 | 121.1766 | 2.9099 | -124.1937 | 121.1766
Line1_1_3 | 0.0030479 | 0.0030479 | 0.0030479 | 0.0030479 | 0.0030479 | 0.0030479 | 0.00070387 | 0.00070387 | 0.00070387 | 0.00070387 | 0.00070387 | 0.00070387 | -0.00042052 | -8.9598e-05 | 0.0006508 | 0.00042061 | 8.9693e-05 | -0.00065071 | -0.00042566 | 0.0006184 | -0.00019136 | 0.00042575 | -0.00061831 | 0.00019145 | 137.5623 | 137.5623 | 137.5623 | -42.4381 | -42.4382 | -42.4382 |  | 0.85008 | 0.88775 | 0.96374 | 0.85026 | 0.88763 | 0.96366 | 2.9099 | -124.1937 | 121.1766 | 2.91 | -124.1844 | 121.1669
Line2_1_4 | 0.0245 | 0.0030891 | 0.0030891 | 0.0245 | 0.0030891 | 0.0030891 | 0.0056581 | 0.0007134 | 0.0007134 | 0.0056581 | 0.0007134 | 0.0007134 | 0.0033973 | -8.2165e-05 | 0.00065687 | -0.0033872 | 8.2536e-05 | -0.00065651 | 0.0034049 | 0.00062797 | -0.00020303 | -0.0033943 | -0.00062759 | 0.0002034 | -42.154 | 138.3519 | 138.3519 | 137.846 | -41.6485 | -41.6485 |  | 0.85008 | 0.88775 | 0.96374 | 0.8475 | 0.88729 | 0.96341 | 2.9099 | -124.1937 | 121.1766 | 2.9064 | -124.1564 | 121.1375
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.9887e-09 | 9.757e-09 | -2.6846e-09 | 3.6463e-09 | -4.8465e-09 | 1.1164e-09 | 6.4506e-09 | 1.7529e-09 | -1.0422e-08 | -3.0829e-09 | -1.0907e-09 | 5.2761e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.85008 | 0.88775 | 0.96374 | 0.85008 | 0.88775 | 0.96374 | 2.9099 | -124.1937 | 121.1766 | 2.9099 | -124.1937 | 121.1766
Line4_2_6 | 0.0030596 | 0.0030596 | 0.0030596 | 0.0030596 | 0.0030596 | 0.0030596 | 0.00070658 | 0.00070658 | 0.00070658 | 0.00070658 | 0.00070658 | 0.00070658 | -0.0004239 | -8.7602e-05 | 0.00065246 | 0.00042399 | 8.7697e-05 | -0.00065237 | -0.00042573 | 0.00062104 | -0.00019475 | 0.00042583 | -0.00062094 | 0.00019484 | 137.7866 | 137.7866 | 137.7866 | -42.2138 | -42.2138 | -42.2138 |  | 0.85026 | 0.88763 | 0.96366 | 0.85045 | 0.88752 | 0.96357 | 2.9101 | -124.1844 | 121.1669 | 2.9103 | -124.175 | 121.1572
Line5_6_7 | 0.0030596 | 0.0030596 | 0.0030596 | 0.0030596 | 0.0030596 | 0.0030596 | 0.00070658 | 0.00070658 | 0.00070658 | 0.00070658 | 0.00070658 | 0.00070658 | -0.00042399 | -8.7697e-05 | 0.00065237 | 0.00042407 | 8.7791e-05 | -0.00065228 | -0.00042583 | 0.00062094 | -0.00019484 | 0.00042592 | -0.00062085 | 0.00019493 | 137.7862 | 137.7862 | 137.7862 | -42.2143 | -42.2143 | -42.2143 |  | 0.85045 | 0.88752 | 0.96357 | 0.85063 | 0.88741 | 0.96349 | 2.9103 | -124.175 | 121.1572 | 2.9105 | -124.1657 | 121.1474
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.0487e-08 | 1.4529e-08 | -3.9177e-09 | 7.1416e-09 | -9.6525e-09 | 2.3869e-09 | 9.5641e-09 | 2.7071e-09 | -1.556e-08 | -6.2336e-09 | -2.0174e-09 | 1.0437e-08 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.85063 | 0.88741 | 0.96349 | 0.85063 | 0.88741 | 0.96349 | 2.9105 | -124.1657 | 121.1474 | 2.9105 | -124.1657 | 121.1474
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.4956e-09 | 4.8429e-09 | -1.3059e-09 | 1.5036e-10 | 3.3242e-11 | -2.2493e-10 | 3.188e-09 | 9.0235e-10 | -5.1867e-09 | 1.4253e-10 | -2.1273e-10 | 6.3671e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.85063 | 0.88741 | 0.96349 | 0.85063 | 0.88741 | 0.96349 | 2.9105 | -124.1657 | 121.1474 | 2.9105 | -124.1657 | 121.1474
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.4956e-09 | 4.8429e-09 | -1.3059e-09 | 1.5036e-10 | 3.3242e-11 | -2.2493e-10 | 3.188e-09 | 9.0235e-10 | -5.1867e-09 | 1.4253e-10 | -2.1273e-10 | 6.3671e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.85063 | 0.88741 | 0.96349 | 0.85063 | 0.88741 | 0.96349 | 2.9105 | -124.1657 | 121.1474 | 2.9105 | -124.1657 | 121.1474
Line9_3_11 | 0.0030479 | 0.0030479 | 0.0030479 | 0.0030479 | 0.0030479 | 0.0030479 | 0.00070387 | 0.00070387 | 0.00070387 | 0.00070387 | 0.00070387 | 0.00070387 | -0.00042061 | -8.9693e-05 | 0.00065071 | 0.00042069 | 8.9787e-05 | -0.00065062 | -0.00042575 | 0.00061831 | -0.00019145 | 0.00042585 | -0.00061822 | 0.00019154 | 137.5619 | 137.5618 | 137.5618 | -42.4386 | -42.4386 | -42.4386 |  | 0.85026 | 0.88763 | 0.96366 | 0.85045 | 0.88752 | 0.96357 | 2.91 | -124.1844 | 121.1669 | 2.9102 | -124.175 | 121.1573

## LLG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.023887 | 0.023887 | 0.023887 | 0.023887 | 0.023887 | 0.023887 | 0.0055164 | 0.0055164 | 0.0055164 | 0.0055164 | 0.0055164 | 0.0055164 | 0.008647 | -0.00034956 | 0.00028691 | -0.0086442 | 0.00035239 | -0.00028403 | 0.00017664 | -0.0034006 | 0.003275 | -0.000171 | 0.0034064 | -0.0032693 | -1.973 | -1.973 | -1.9731 | 178.0265 | 178.0266 | 178.0265 |  | 1.5678 | 0.61971 | 0.59595 | 1.5673 | 0.62079 | 0.59487 | -0.80279 | -97.8419 | 83.0201 | -0.84021 | -97.8797 | 83.0611
Line10_11_12 | 0.023839 | 0.023839 | 0.023839 | 0.023839 | 0.023839 | 0.023839 | 0.0055053 | 0.0055053 | 0.0055053 | 0.0055053 | 0.0055053 | 0.0055053 | 0.0086231 | -0.00034107 | 0.00026768 | -0.0086203 | 0.00034388 | -0.00026481 | 0.00019915 | -0.0034065 | 0.0032581 | -0.00019354 | 0.0034122 | -0.0032524 | -2.2004 | -2.2003 | -2.2004 | 177.7992 | 177.7992 | 177.7991 |  | 1.5668 | 0.62186 | 0.5938 | 1.5662 | 0.62294 | 0.59273 | -0.87734 | -97.9179 | 83.1028 | -0.91466 | -97.9557 | 83.1443
Line11_12_13 | 0.023839 | 0.023839 | 0.023839 | 0.023839 | 0.023839 | 0.023839 | 0.0055053 | 0.0055053 | 0.0055053 | 0.0055053 | 0.0055053 | 0.0055053 | 0.0086203 | -0.00034388 | 0.00026481 | -0.0086174 | 0.0003467 | -0.00026194 | 0.00019354 | -0.0034122 | 0.0032524 | -0.00018792 | 0.0034179 | -0.0032467 | -2.2008 | -2.2008 | -2.2009 | 177.7987 | 177.7988 | 177.7987 |  | 1.5662 | 0.62294 | 0.59273 | 1.5657 | 0.62402 | 0.59166 | -0.91466 | -97.9557 | 83.1443 | -0.952 | -97.9933 | 83.186
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2916e-08 | -8.2995e-08 | 7.4943e-08 | -1.1572e-08 | 5.613e-08 | -4.9422e-08 | -2.0295e-07 | 5.6347e-09 | -2.2339e-09 | 1.352e-07 | -2.8562e-09 | 1.2429e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.5657 | 0.62402 | 0.59166 | 1.5657 | 0.62402 | 0.59166 | -0.952 | -97.9933 | 83.186 | -0.952 | -97.9933 | 83.186
Line13_13_14 | 0.023839 | 0.023839 | 0.023839 | 0.023839 | 0.023839 | 0.023839 | 0.0055053 | 0.0055053 | 0.0055053 | 0.0055053 | 0.0055053 | 0.0055053 | 0.0086174 | -0.00034661 | 0.00026187 | -0.0086146 | 0.00034943 | -0.000259 | 0.00018813 | -0.0034179 | 0.0032467 | -0.00018251 | 0.0034236 | -0.003241 | -2.2026 | -2.2026 | -2.2026 | 177.7969 | 177.7969 | 177.7969 |  | 1.5657 | 0.62402 | 0.59166 | 1.5651 | 0.6251 | 0.59059 | -0.952 | -97.9933 | 83.186 | -0.98937 | -98.0308 | 83.2279
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.6108e-09 | -5.533e-08 | 4.9962e-08 | -7.2666e-09 | 2.8465e-08 | -2.4441e-08 | -1.353e-07 | 3.7565e-09 | -1.4893e-09 | 6.7551e-08 | -9.78e-10 | -6.2034e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.5657 | 0.62402 | 0.59166 | 1.5657 | 0.62402 | 0.59166 | -0.952 | -97.9933 | 83.186 | -0.952 | -97.9933 | 83.186
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3054e-09 | -2.7665e-08 | 2.4981e-08 | -2.9612e-09 | 7.9963e-10 | 5.4008e-10 | -6.7651e-08 | 1.8782e-09 | -7.4463e-10 | -1.0015e-10 | 9.0024e-10 | -1.365e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.5657 | 0.62402 | 0.59166 | 1.5657 | 0.62402 | 0.59166 | -0.952 | -97.9933 | 83.186 | -0.952 | -97.9933 | 83.186
Line16_4_18 | 0 | 3.2394 | 3.0385 | 0 | 3.2394 | 3.0385 | 0 | 0.74811 | 0.70171 | 0 | 0.74811 | 0.70171 | 3.289e-09 | 0.10304 | 0.094145 | -2.9494e-09 | 3.5204e-14 | 1.059e-14 | -6.8163e-08 | 0.2081 | 0.18627 | -1.1204e-10 | 1.863e-14 | 1.3485e-14 | 0 | -161.5364 | 19.873 | 0 | 18.4636 | -160.127 |  | 1.5657 | 0.3104 | 0.29743 | 1.5641 | 0 | 0 | -0.95323 | -97.8788 | 83.0602 | -1.0661 | 0 | 0
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9646e-09 | -2.7574e-08 | 2.5255e-08 | -2.9775e-09 | 8.0153e-10 | 5.3064e-10 | -6.8041e-08 | 2.0128e-09 | -1.0331e-09 | -8.4571e-11 | 8.9986e-10 | -1.3802e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.5678 | 0.61971 | 0.59595 | 1.5678 | 0.61971 | 0.59595 | -0.80279 | -97.8419 | 83.0201 | -0.80279 | -97.8419 | 83.0201
Line1_1_3 | 0.023839 | 0.023839 | 0.023839 | 0.023839 | 0.023839 | 0.023839 | 0.0055053 | 0.0055053 | 0.0055053 | 0.0055053 | 0.0055053 | 0.0055053 | 0.0086288 | -0.00033544 | 0.00027341 | -0.008626 | 0.00033826 | -0.00027054 | 0.00021038 | -0.0033951 | 0.0032694 | -0.00020477 | 0.0034008 | -0.0032638 | -2.1995 | -2.1994 | -2.1996 | 177.8001 | 177.8002 | 177.8 |  | 1.5678 | 0.61971 | 0.59595 | 1.5673 | 0.62078 | 0.59488 | -0.80279 | -97.8419 | 83.0201 | -0.84005 | -97.88 | 83.0614
Line2_1_4 | 0.024008 | 3.2168 | 3.0609 | 0.024008 | 3.2168 | 3.0609 | 0.0055443 | 0.74289 | 0.70688 | 0.0055443 | 0.74289 | 0.70688 | 0.0086921 | 0.20506 | 0.18921 | -0.0086804 | -0.10285 | -0.094304 | 9.1391e-05 | 0.41218 | 0.37638 | -6.8542e-05 | -0.20639 | -0.18791 | -1.4052 | -161.3911 | 19.7099 | 178.5944 | 18.6089 | -160.2901 |  | 1.5678 | 0.61971 | 0.59595 | 1.5657 | 0.3104 | 0.29743 | -0.80279 | -97.8419 | 83.0201 | -0.95323 | -97.8788 | 83.0602
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.9293e-09 | -5.5148e-08 | 5.0509e-08 | -6.9421e-09 | 2.8375e-08 | -2.4724e-08 | -1.3608e-07 | 4.0256e-09 | -2.0663e-09 | 6.7956e-08 | -1.1129e-09 | -3.4701e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.5678 | 0.61971 | 0.59595 | 1.5678 | 0.61971 | 0.59595 | -0.80279 | -97.8419 | 83.0201 | -0.80279 | -97.8419 | 83.0201
Line4_2_6 | 0.023887 | 0.023887 | 0.023887 | 0.023887 | 0.023887 | 0.023887 | 0.0055164 | 0.0055164 | 0.0055164 | 0.0055164 | 0.0055164 | 0.0055164 | 0.0086442 | -0.00035239 | 0.00028403 | -0.0086413 | 0.00035521 | -0.00028116 | 0.000171 | -0.0034064 | 0.0032693 | -0.00016536 | 0.0034121 | -0.0032636 | -1.9735 | -1.9734 | -1.9735 | 178.0261 | 178.0261 | 178.026 |  | 1.5673 | 0.62079 | 0.59487 | 1.5668 | 0.62187 | 0.5938 | -0.84021 | -97.8797 | 83.0611 | -0.87765 | -97.9172 | 83.1021
Line5_6_7 | 0.023887 | 0.023887 | 0.023887 | 0.023887 | 0.023887 | 0.023887 | 0.0055164 | 0.0055164 | 0.0055164 | 0.0055164 | 0.0055164 | 0.0055164 | 0.0086413 | -0.00035521 | 0.00028116 | -0.0086385 | 0.00035804 | -0.00027828 | 0.00016536 | -0.0034121 | 0.0032636 | -0.00015972 | 0.0034178 | -0.0032578 | -1.9739 | -1.9739 | -1.974 | 178.0256 | 178.0257 | 178.0256 |  | 1.5668 | 0.62187 | 0.5938 | 1.5662 | 0.62295 | 0.59272 | -0.87765 | -97.9172 | 83.1021 | -0.91512 | -97.9547 | 83.1434
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2664e-08 | -8.293e-08 | 7.5148e-08 | -1.1408e-08 | 5.6087e-08 | -4.9561e-08 | -2.0325e-07 | 5.7335e-09 | -2.4487e-09 | 1.354e-07 | -2.9221e-09 | 2.637e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.5662 | 0.62295 | 0.59272 | 1.5662 | 0.62295 | 0.59272 | -0.91512 | -97.9547 | 83.1434 | -0.91512 | -97.9547 | 83.1434
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2214e-09 | -2.7643e-08 | 2.5049e-08 | -2.9653e-09 | 8.0009e-10 | 5.3773e-10 | -6.775e-08 | 1.9112e-09 | -8.1623e-10 | -9.6305e-11 | 9.002e-10 | -1.3688e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.5662 | 0.62295 | 0.59272 | 1.5662 | 0.62295 | 0.59272 | -0.91512 | -97.9547 | 83.1434 | -0.91512 | -97.9547 | 83.1434
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2214e-09 | -2.7643e-08 | 2.5049e-08 | -2.9653e-09 | 8.0009e-10 | 5.3773e-10 | -6.775e-08 | 1.9112e-09 | -8.1623e-10 | -9.6305e-11 | 9.002e-10 | -1.3688e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.5662 | 0.62295 | 0.59272 | 1.5662 | 0.62295 | 0.59272 | -0.91512 | -97.9547 | 83.1434 | -0.91512 | -97.9547 | 83.1434
Line9_3_11 | 0.023839 | 0.023839 | 0.023839 | 0.023839 | 0.023839 | 0.023839 | 0.0055053 | 0.0055053 | 0.0055053 | 0.0055053 | 0.0055053 | 0.0055053 | 0.008626 | -0.00033825 | 0.00027054 | -0.0086231 | 0.00034107 | -0.00026768 | 0.00020477 | -0.0034008 | 0.0032638 | -0.00019915 | 0.0034065 | -0.0032581 | -2.1999 | -2.1998 | -2.2 | 177.7996 | 177.7997 | 177.7995 |  | 1.5673 | 0.62078 | 0.59488 | 1.5668 | 0.62186 | 0.5938 | -0.84005 | -97.88 | 83.0614 | -0.87734 | -97.9179 | 83.1028

## LLG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.025023 | 0.025023 | 0.025023 | 0.025023 | 0.025023 | 0.025023 | 0.0057789 | 0.0057789 | 0.0057789 | 0.0057789 | 0.0057789 | 0.0057789 | 0.0094895 | -0.00039147 | 0.00032271 | -0.0094863 | 0.00039457 | -0.00031955 | 0.00019384 | -0.0036733 | 0.0035354 | -0.00018766 | 0.0036796 | -0.0035291 | -1.9916 | -1.9915 | -1.9916 | 178.008 | 178.0081 | 178.0079 |  | 1.6424 | 0.63924 | 0.61432 | 1.6419 | 0.64038 | 0.61319 | -0.82132 | -98.0745 | 82.7928 | -0.85873 | -98.1125 | 82.834
Line10_11_12 | 0.024973 | 0.024973 | 0.024973 | 0.024973 | 0.024973 | 0.024973 | 0.0057672 | 0.0057672 | 0.0057672 | 0.0057672 | 0.0057672 | 0.0057672 | 0.0094632 | -0.00038236 | 0.00030182 | -0.0094601 | 0.00038545 | -0.00029867 | 0.00021856 | -0.0036799 | 0.003517 | -0.00021239 | 0.0036861 | -0.0035108 | -2.2189 | -2.2188 | -2.219 | 177.7806 | 177.7807 | 177.7806 |  | 1.6413 | 0.6415 | 0.61207 | 1.6407 | 0.64263 | 0.61094 | -0.89587 | -98.1509 | 82.8761 | -0.93319 | -98.1889 | 82.9179
Line11_12_13 | 0.024973 | 0.024973 | 0.024973 | 0.024973 | 0.024973 | 0.024973 | 0.0057672 | 0.0057672 | 0.0057672 | 0.0057672 | 0.0057672 | 0.0057672 | 0.0094601 | -0.00038545 | 0.00029868 | -0.009457 | 0.00038854 | -0.00029553 | 0.00021239 | -0.0036861 | 0.0035108 | -0.00020623 | 0.0036924 | -0.0035045 | -2.2194 | -2.2193 | -2.2194 | 177.7802 | 177.7803 | 177.7801 |  | 1.6407 | 0.64263 | 0.61094 | 1.6402 | 0.64377 | 0.60982 | -0.93319 | -98.1889 | 82.9179 | -0.97053 | -98.2267 | 82.9599
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4174e-08 | -8.9743e-08 | 8.0843e-08 | -1.2699e-08 | 6.072e-08 | -5.3296e-08 | -2.2272e-07 | 6.4456e-09 | -2.688e-09 | 1.4837e-07 | -3.3339e-09 | 3.1041e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.6402 | 0.64377 | 0.60982 | 1.6402 | 0.64377 | 0.60982 | -0.97053 | -98.2267 | 82.9599 | -0.97053 | -98.2267 | 82.9599
Line13_13_14 | 0.024973 | 0.024973 | 0.024973 | 0.024973 | 0.024973 | 0.024973 | 0.0057672 | 0.0057672 | 0.0057672 | 0.0057672 | 0.0057672 | 0.0057672 | 0.0094569 | -0.00038845 | 0.00029545 | -0.0094538 | 0.00039154 | -0.0002923 | 0.00020646 | -0.0036924 | 0.0035045 | -0.00020029 | 0.0036986 | -0.0034983 | -2.2212 | -2.2211 | -2.2212 | 177.7784 | 177.7784 | 177.7784 |  | 1.6402 | 0.64377 | 0.60982 | 1.6396 | 0.6449 | 0.6087 | -0.97053 | -98.2267 | 82.9599 | -1.0079 | -98.2645 | 83.0021
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.4493e-09 | -5.9829e-08 | 5.3896e-08 | -7.9741e-09 | 3.0806e-08 | -2.6348e-08 | -1.4848e-07 | 4.2971e-09 | -1.792e-09 | 7.4128e-08 | -1.1854e-09 | -5.856e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.6402 | 0.64377 | 0.60982 | 1.6402 | 0.64377 | 0.60982 | -0.97053 | -98.2267 | 82.9599 | -0.97053 | -98.2267 | 82.9599
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7246e-09 | -2.9914e-08 | 2.6948e-08 | -3.2495e-09 | 8.9169e-10 | 5.9973e-10 | -7.424e-08 | 2.1485e-09 | -8.9601e-10 | -1.1205e-10 | 9.6314e-10 | -1.4816e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.6402 | 0.64377 | 0.60982 | 1.6402 | 0.64377 | 0.60982 | -0.97053 | -98.2267 | 82.9599 | -0.97053 | -98.2267 | 82.9599
Line16_4_18 | 0 | 3.3422 | 3.1315 | 0 | 3.3422 | 3.1315 | 0 | 0.77185 | 0.72318 | 0 | 0.77185 | 0.72318 | 3.6092e-09 | 0.10966 | 0.10002 | -3.2365e-09 | 3.6388e-14 | 3.6914e-14 | -7.4802e-08 | 0.22148 | 0.19788 | -1.251e-10 | -1.3608e-14 | 1.0266e-14 | 0 | -161.7704 | 19.6477 | 0 | 18.2296 | -160.3523 |  | 1.6402 | 0.32019 | 0.30659 | 1.6385 | 0 | 0 | -0.97175 | -98.1117 | 82.8332 | -1.0846 | 0 | 0
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3507e-09 | -2.9812e-08 | 2.7245e-08 | -3.2673e-09 | 8.9348e-10 | 5.8966e-10 | -7.4668e-08 | 2.2928e-09 | -1.2092e-09 | -9.4955e-11 | 9.6273e-10 | -1.4983e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.6424 | 0.63924 | 0.61432 | 1.6424 | 0.63924 | 0.61432 | -0.82132 | -98.0745 | 82.7928 | -0.82132 | -98.0745 | 82.7928
Line1_1_3 | 0.024973 | 0.024973 | 0.024973 | 0.024973 | 0.024973 | 0.024973 | 0.0057672 | 0.0057672 | 0.0057672 | 0.0057672 | 0.0057672 | 0.0057672 | 0.0094694 | -0.00037618 | 0.00030811 | -0.0094663 | 0.00037927 | -0.00030497 | 0.00023088 | -0.0036674 | 0.0035295 | -0.00022472 | 0.0036736 | -0.0035232 | -2.218 | -2.2179 | -2.2181 | 177.7815 | 177.7816 | 177.7815 |  | 1.6424 | 0.63924 | 0.61432 | 1.6419 | 0.64037 | 0.61319 | -0.82132 | -98.0745 | 82.7928 | -0.85858 | -98.1128 | 82.8344
Line2_1_4 | 0.02515 | 3.3185 | 3.1549 | 0.02515 | 3.3185 | 3.1549 | 0.0058081 | 0.76638 | 0.7286 | 0.0058081 | 0.76638 | 0.7286 | 0.0095389 | 0.21821 | 0.20105 | -0.0095261 | -0.10944 | -0.1002 | 0.00010029 | 0.43862 | 0.3999 | -7.522e-05 | -0.21963 | -0.19965 | -1.4237 | -161.6243 | 19.4835 | 178.5758 | 18.3757 | -160.5165 |  | 1.6424 | 0.63924 | 0.61432 | 1.6402 | 0.32019 | 0.30659 | -0.82132 | -98.0745 | 82.7928 | -0.97175 | -98.1117 | 82.8332
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.7013e-09 | -5.9624e-08 | 5.4491e-08 | -7.618e-09 | 3.0705e-08 | -2.6656e-08 | -1.4934e-07 | 4.5855e-09 | -2.4184e-09 | 7.4573e-08 | -1.33e-09 | -2.8908e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.6424 | 0.63924 | 0.61432 | 1.6424 | 0.63924 | 0.61432 | -0.82132 | -98.0745 | 82.7928 | -0.82132 | -98.0745 | 82.7928
Line4_2_6 | 0.025023 | 0.025023 | 0.025023 | 0.025023 | 0.025023 | 0.025023 | 0.0057789 | 0.0057789 | 0.0057789 | 0.0057789 | 0.0057789 | 0.0057789 | 0.0094863 | -0.00039457 | 0.00031955 | -0.0094832 | 0.00039767 | -0.0003164 | 0.00018766 | -0.0036796 | 0.0035291 | -0.00018147 | 0.0036858 | -0.0035229 | -1.992 | -1.9919 | -1.9921 | 178.0075 | 178.0076 | 178.0075 |  | 1.6419 | 0.64038 | 0.61319 | 1.6413 | 0.64151 | 0.61206 | -0.85873 | -98.1125 | 82.834 | -0.89618 | -98.1503 | 82.8754
Line5_6_7 | 0.025023 | 0.025023 | 0.025023 | 0.025023 | 0.025023 | 0.025023 | 0.0057789 | 0.0057789 | 0.0057789 | 0.0057789 | 0.0057789 | 0.0057789 | 0.0094832 | -0.00039767 | 0.0003164 | -0.0094801 | 0.00040077 | -0.00031324 | 0.00018147 | -0.0036858 | 0.0035229 | -0.00017528 | 0.0036921 | -0.0035166 | -1.9925 | -1.9924 | -1.9925 | 178.0071 | 178.0071 | 178.007 |  | 1.6413 | 0.64151 | 0.61206 | 1.6407 | 0.64265 | 0.61093 | -0.89618 | -98.1503 | 82.8754 | -0.93365 | -98.1879 | 82.9169
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3897e-08 | -8.967e-08 | 8.1066e-08 | -1.2519e-08 | 6.0672e-08 | -5.3447e-08 | -2.2304e-07 | 6.5515e-09 | -2.9212e-09 | 1.4859e-07 | -3.4046e-09 | 4.6171e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.6407 | 0.64265 | 0.61093 | 1.6407 | 0.64265 | 0.61093 | -0.93365 | -98.1879 | 82.9169 | -0.93365 | -98.1879 | 82.9169
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.6324e-09 | -2.989e-08 | 2.7022e-08 | -3.254e-09 | 8.9213e-10 | 5.9722e-10 | -7.4348e-08 | 2.1838e-09 | -9.7375e-10 | -1.0783e-10 | 9.6309e-10 | -1.4858e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.6407 | 0.64265 | 0.61093 | 1.6407 | 0.64265 | 0.61093 | -0.93365 | -98.1879 | 82.9169 | -0.93365 | -98.1879 | 82.9169
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.6324e-09 | -2.989e-08 | 2.7022e-08 | -3.254e-09 | 8.9213e-10 | 5.9722e-10 | -7.4348e-08 | 2.1838e-09 | -9.7375e-10 | -1.0783e-10 | 9.6309e-10 | -1.4858e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.6407 | 0.64265 | 0.61093 | 1.6407 | 0.64265 | 0.61093 | -0.93365 | -98.1879 | 82.9169 | -0.93365 | -98.1879 | 82.9169
Line9_3_11 | 0.024973 | 0.024973 | 0.024973 | 0.024973 | 0.024973 | 0.024973 | 0.0057672 | 0.0057672 | 0.0057672 | 0.0057672 | 0.0057672 | 0.0057672 | 0.0094663 | -0.00037927 | 0.00030497 | -0.0094632 | 0.00038236 | -0.00030182 | 0.00022472 | -0.0036736 | 0.0035232 | -0.00021856 | 0.0036799 | -0.003517 | -2.2185 | -2.2184 | -2.2185 | 177.7811 | 177.7812 | 177.781 |  | 1.6419 | 0.64037 | 0.61319 | 1.6413 | 0.6415 | 0.61207 | -0.85858 | -98.1128 | 82.8344 | -0.89587 | -98.1509 | 82.8761

## LLG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.0033939 | 0.0033939 | 0.0033939 | 0.0033939 | 0.0033939 | 0.0033939 | 0.00078379 | 0.00078379 | 0.00078379 | 0.00078379 | 0.00078379 | 0.00078379 | 0.00069237 | 0.0001919 | -0.00071097 | -0.0006923 | -0.00019185 | 0.00071103 | 0.00052346 | -0.00081043 | 0.000288 | -0.00052335 | 0.00081054 | -0.00028788 | -39.5396 | -39.5396 | -39.5396 | 140.4599 | 140.4599 | 140.4599 |  | 1.1074 | 1.0626 | 0.97869 | 1.1073 | 1.0627 | 0.97871 | -2.4489 | -116.2179 | 118.4085 | -2.4527 | -116.2236 | 118.4181
Line10_11_12 | 0.003387 | 0.003387 | 0.003387 | 0.003387 | 0.003387 | 0.003387 | 0.0007822 | 0.0007822 | 0.0007822 | 0.0007822 | 0.0007822 | 0.0007822 | 0.00068877 | 0.00019461 | -0.00071078 | -0.00068871 | -0.00019455 | 0.00071084 | 0.00052491 | -0.00080825 | 0.00028437 | -0.0005248 | 0.00080837 | -0.00028425 | -39.767 | -39.767 | -39.767 | 140.2326 | 140.2326 | 140.2326 |  | 1.1071 | 1.0628 | 0.97872 | 1.107 | 1.063 | 0.97874 | -2.4564 | -116.2293 | 118.4276 | -2.4601 | -116.235 | 118.4372
Line11_12_13 | 0.003387 | 0.003387 | 0.003387 | 0.003387 | 0.003387 | 0.003387 | 0.0007822 | 0.0007822 | 0.0007822 | 0.0007822 | 0.0007822 | 0.0007822 | 0.00068871 | 0.00019455 | -0.00071084 | -0.00068865 | -0.0001945 | 0.0007109 | 0.0005248 | -0.00080837 | 0.00028425 | -0.00052469 | 0.00080848 | -0.00028413 | -39.7674 | -39.7674 | -39.7674 | 140.2321 | 140.2321 | 140.2321 |  | 1.107 | 1.063 | 0.97874 | 1.1068 | 1.0631 | 0.97875 | -2.4601 | -116.235 | 118.4372 | -2.4638 | -116.2407 | 118.4468
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3047e-08 | -1.8898e-08 | 5.9714e-09 | -8.9323e-09 | 1.2539e-08 | -3.7266e-09 | -1.5717e-08 | -5.355e-09 | 1.706e-08 | 1.0295e-08 | 3.8384e-09 | -1.1476e-08 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1068 | 1.0631 | 0.97875 | 1.1068 | 1.0631 | 0.97875 | -2.4638 | -116.2407 | 118.4468 | -2.4638 | -116.2407 | 118.4468
Line13_13_14 | 0.003387 | 0.003387 | 0.003387 | 0.003387 | 0.003387 | 0.003387 | 0.0007822 | 0.0007822 | 0.0007822 | 0.0007822 | 0.0007822 | 0.0007822 | 0.00068864 | 0.00019452 | -0.00071091 | -0.00068858 | -0.00019447 | 0.00071097 | 0.0005247 | -0.00080847 | 0.00028411 | -0.00052459 | 0.00080859 | -0.00028399 | -39.7692 | -39.7692 | -39.7692 | 140.2303 | 140.2303 | 140.2303 |  | 1.1068 | 1.0631 | 0.97875 | 1.1067 | 1.0632 | 0.97876 | -2.4638 | -116.2407 | 118.4468 | -2.4676 | -116.2464 | 118.4563
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.6978e-09 | -1.2599e-08 | 3.9809e-09 | -4.5834e-09 | 6.2395e-09 | -1.7361e-09 | -1.0478e-08 | -3.57e-09 | 1.1373e-08 | 5.0558e-09 | 2.0534e-09 | -5.7889e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1068 | 1.0631 | 0.97875 | 1.1068 | 1.0631 | 0.97875 | -2.4638 | -116.2407 | 118.4468 | -2.4638 | -116.2407 | 118.4468
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3489e-09 | -6.2993e-09 | 1.9905e-09 | -2.3454e-10 | -5.9808e-11 | 2.5432e-10 | -5.239e-09 | -1.785e-09 | 5.6867e-09 | -1.8319e-10 | 2.6835e-10 | -1.0214e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1068 | 1.0631 | 0.97875 | 1.1068 | 1.0631 | 0.97875 | -2.4638 | -116.2407 | 118.4468 | -2.4638 | -116.2407 | 118.4468
Line16_4_18 | 0 | 0.034525 | 0.031776 | 0 | 0.034526 | 0.031776 | 0 | 0.0079733 | 0.0073384 | 0 | 0.0079733 | 0.0073384 | 4.2966e-09 | 0.0059681 | 0.0050611 | -2.3269e-10 | -0.0059601 | -0.0050486 | -5.3405e-09 | 0.0059835 | 0.0050661 | -1.8398e-10 | -0.0059601 | -0.0050486 | 0 | -161.3715 | 73.3618 | 0 | 18.6285 | -106.6382 |  | 1.1068 | 1.0599 | 0.97582 | 1.1064 | 1.0571 | 0.97294 | -2.4641 | -116.2973 | 118.3901 | -2.4755 | -116.3715 | 118.3618
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3282e-09 | -6.3352e-09 | 2.0475e-09 | -2.3701e-10 | -5.7932e-11 | 2.5443e-10 | -5.2964e-09 | -1.7437e-09 | 5.6919e-09 | -1.8217e-10 | 2.6985e-10 | -1.0465e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1074 | 1.0626 | 0.97869 | 1.1074 | 1.0626 | 0.97869 | -2.4489 | -116.2179 | 118.4085 | -2.4489 | -116.2179 | 118.4085
Line1_1_3 | 0.003387 | 0.003387 | 0.003387 | 0.003387 | 0.003387 | 0.003387 | 0.0007822 | 0.0007822 | 0.0007822 | 0.0007822 | 0.0007822 | 0.0007822 | 0.0006889 | 0.00019471 | -0.00071066 | -0.00068884 | -0.00019466 | 0.00071072 | 0.00052512 | -0.00080803 | 0.00028461 | -0.00052502 | 0.00080814 | -0.00028449 | -39.7661 | -39.7661 | -39.7661 | 140.2335 | 140.2335 | 140.2335 |  | 1.1074 | 1.0626 | 0.97869 | 1.1073 | 1.0627 | 0.97871 | -2.4489 | -116.2179 | 118.4085 | -2.4526 | -116.2236 | 118.4181
Line2_1_4 | 0.003411 | 0.032824 | 0.030643 | 0.003411 | 0.032824 | 0.030643 | 0.00078775 | 0.0075805 | 0.0070767 | 0.00078775 | 0.0075805 | 0.0070767 | 0.00070104 | 0.0061595 | 0.0043627 | -0.00070081 | -0.0061513 | -0.0043516 | 0.00051918 | 0.0051905 | 0.0053791 | -0.00051872 | -0.0051689 | -0.005362 | -38.9718 | -156.3378 | 67.4518 | 141.0278 | 23.6622 | -112.5481 |  | 1.1074 | 1.0626 | 0.97869 | 1.1068 | 1.0599 | 0.97582 | -2.4489 | -116.2179 | 118.4085 | -2.4641 | -116.2973 | 118.3901
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.6563e-09 | -1.267e-08 | 4.0951e-09 | -4.5652e-09 | 6.2773e-09 | -1.7931e-09 | -1.0593e-08 | -3.4873e-09 | 1.1384e-08 | 5.1143e-09 | 2.0135e-09 | -5.7965e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1074 | 1.0626 | 0.97869 | 1.1074 | 1.0626 | 0.97869 | -2.4489 | -116.2179 | 118.4085 | -2.4489 | -116.2179 | 118.4085
Line4_2_6 | 0.0033939 | 0.0033939 | 0.0033939 | 0.0033939 | 0.0033939 | 0.0033939 | 0.00078379 | 0.00078379 | 0.00078379 | 0.00078379 | 0.00078379 | 0.00078379 | 0.0006923 | 0.00019185 | -0.00071103 | -0.00069224 | -0.0001918 | 0.00071109 | 0.00052335 | -0.00081054 | 0.00028788 | -0.00052324 | 0.00081065 | -0.00028776 | -39.5401 | -39.5401 | -39.5401 | 140.4595 | 140.4595 | 140.4595 |  | 1.1073 | 1.0627 | 0.97871 | 1.1071 | 1.0628 | 0.97872 | -2.4527 | -116.2236 | 118.4181 | -2.4564 | -116.2293 | 118.4277
Line5_6_7 | 0.0033939 | 0.0033939 | 0.0033939 | 0.0033939 | 0.0033939 | 0.0033939 | 0.00078379 | 0.00078379 | 0.00078379 | 0.00078379 | 0.00078379 | 0.00078379 | 0.00069224 | 0.0001918 | -0.00071109 | -0.00069218 | -0.00019175 | 0.00071115 | 0.00052324 | -0.00081065 | 0.00028776 | -0.00052313 | 0.00081077 | -0.00028764 | -39.5405 | -39.5405 | -39.5405 | 140.459 | 140.459 | 140.459 |  | 1.1071 | 1.0628 | 0.97872 | 1.107 | 1.063 | 0.97873 | -2.4564 | -116.2293 | 118.4277 | -2.4602 | -116.235 | 118.4373
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3032e-08 | -1.8925e-08 | 6.0138e-09 | -8.923e-09 | 1.2557e-08 | -3.7549e-09 | -1.576e-08 | -5.3246e-09 | 1.7065e-08 | 1.0324e-08 | 3.8184e-09 | -1.1479e-08 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.107 | 1.063 | 0.97873 | 1.107 | 1.063 | 0.97873 | -2.4602 | -116.235 | 118.4373 | -2.4602 | -116.235 | 118.4373
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3439e-09 | -6.3084e-09 | 2.0046e-09 | -2.3515e-10 | -5.9347e-11 | 2.5435e-10 | -5.2533e-09 | -1.7749e-09 | 5.6882e-09 | -1.8294e-10 | 2.6873e-10 | -1.0276e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.107 | 1.063 | 0.97873 | 1.107 | 1.063 | 0.97873 | -2.4602 | -116.235 | 118.4373 | -2.4602 | -116.235 | 118.4373
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3439e-09 | -6.3084e-09 | 2.0046e-09 | -2.3515e-10 | -5.9347e-11 | 2.5435e-10 | -5.2533e-09 | -1.7749e-09 | 5.6882e-09 | -1.8294e-10 | 2.6873e-10 | -1.0276e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.107 | 1.063 | 0.97873 | 1.107 | 1.063 | 0.97873 | -2.4602 | -116.235 | 118.4373 | -2.4602 | -116.235 | 118.4373
Line9_3_11 | 0.003387 | 0.003387 | 0.003387 | 0.003387 | 0.003387 | 0.003387 | 0.0007822 | 0.0007822 | 0.0007822 | 0.0007822 | 0.0007822 | 0.0007822 | 0.00068883 | 0.00019466 | -0.00071072 | -0.00068877 | -0.00019461 | 0.00071078 | 0.00052502 | -0.00080814 | 0.00028449 | -0.00052491 | 0.00080825 | -0.00028437 | -39.7665 | -39.7665 | -39.7665 | 140.233 | 140.233 | 140.233 |  | 1.1073 | 1.0627 | 0.97871 | 1.1071 | 1.0628 | 0.97872 | -2.4526 | -116.2236 | 118.4181 | -2.4564 | -116.2293 | 118.4276

## LLG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.0035554 | 0.0035554 | 0.0035554 | 0.0035554 | 0.0035554 | 0.0035554 | 0.00082108 | 0.00082108 | 0.00082108 | 0.00082108 | 0.00082108 | 0.00082108 | 0.00075983 | 0.00021052 | -0.00078016 | -0.00075976 | -0.00021046 | 0.00078023 | 0.00057446 | -0.00088937 | 0.00031604 | -0.00057434 | 0.0008895 | -0.00031591 | -39.5415 | -39.5415 | -39.5415 | 140.458 | 140.458 | 140.458 |  | 1.1601 | 1.1131 | 1.0252 | 1.16 | 1.1132 | 1.0252 | -2.4508 | -116.2246 | 118.4057 | -2.4546 | -116.2302 | 118.4153
Line10_11_12 | 0.0035482 | 0.0035482 | 0.0035482 | 0.0035482 | 0.0035482 | 0.0035482 | 0.00081942 | 0.00081942 | 0.00081942 | 0.00081942 | 0.00081942 | 0.00081942 | 0.00075588 | 0.00021349 | -0.00077996 | -0.00075582 | -0.00021343 | 0.00078002 | 0.00057605 | -0.00088699 | 0.00031206 | -0.00057593 | 0.00088711 | -0.00031193 | -39.7689 | -39.7689 | -39.7689 | 140.2307 | 140.2307 | 140.2307 |  | 1.1598 | 1.1134 | 1.0252 | 1.1596 | 1.1135 | 1.0252 | -2.4583 | -116.236 | 118.4248 | -2.462 | -116.2417 | 118.4344
Line11_12_13 | 0.0035482 | 0.0035482 | 0.0035482 | 0.0035482 | 0.0035482 | 0.0035482 | 0.00081942 | 0.00081942 | 0.00081942 | 0.00081942 | 0.00081942 | 0.00081942 | 0.00075582 | 0.00021343 | -0.00078002 | -0.00075575 | -0.00021337 | 0.00078009 | 0.00057593 | -0.00088711 | 0.00031193 | -0.00057581 | 0.00088723 | -0.0003118 | -39.7693 | -39.7693 | -39.7693 | 140.2302 | 140.2302 | 140.2302 |  | 1.1596 | 1.1135 | 1.0252 | 1.1595 | 1.1136 | 1.0252 | -2.462 | -116.2417 | 118.4344 | -2.4657 | -116.2473 | 118.444
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4317e-08 | -2.074e-08 | 6.5513e-09 | -9.8022e-09 | 1.3761e-08 | -4.088e-09 | -1.7248e-08 | -5.8733e-09 | 1.8721e-08 | 1.1297e-08 | 4.2095e-09 | -1.2593e-08 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1595 | 1.1136 | 1.0252 | 1.1595 | 1.1136 | 1.0252 | -2.4657 | -116.2473 | 118.444 | -2.4657 | -116.2473 | 118.444
Line13_13_14 | 0.0035482 | 0.0035482 | 0.0035482 | 0.0035482 | 0.0035482 | 0.0035482 | 0.00081942 | 0.00081942 | 0.00081942 | 0.00081942 | 0.00081942 | 0.00081942 | 0.00075573 | 0.00021339 | -0.00078009 | -0.00075567 | -0.00021334 | 0.00078016 | 0.00057583 | -0.00088723 | 0.00031178 | -0.00057571 | 0.00088735 | -0.00031164 | -39.7711 | -39.7711 | -39.7711 | 140.2284 | 140.2284 | 140.2284 |  | 1.1595 | 1.1136 | 1.0252 | 1.1593 | 1.1138 | 1.0252 | -2.4657 | -116.2473 | 118.444 | -2.4695 | -116.253 | 118.4535
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.545e-09 | -1.3827e-08 | 4.3675e-09 | -5.0297e-09 | 6.848e-09 | -1.9042e-09 | -1.1499e-08 | -3.9155e-09 | 1.2481e-08 | 5.5481e-09 | 2.2517e-09 | -6.3527e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1595 | 1.1136 | 1.0252 | 1.1595 | 1.1136 | 1.0252 | -2.4657 | -116.2473 | 118.444 | -2.4657 | -116.2473 | 118.444
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7725e-09 | -6.9133e-09 | 2.1838e-09 | -2.5725e-10 | -6.5267e-11 | 2.7958e-10 | -5.7493e-09 | -1.9578e-09 | 6.2404e-09 | -2.012e-10 | 2.9397e-10 | -1.1228e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1595 | 1.1136 | 1.0252 | 1.1595 | 1.1136 | 1.0252 | -2.4657 | -116.2473 | 118.444 | -2.4657 | -116.2473 | 118.444
Line16_4_18 | 0 | 0.036167 | 0.033285 | 0 | 0.036167 | 0.033285 | 0 | 0.0083524 | 0.0076868 | 0 | 0.0083524 | 0.0076868 | 4.7151e-09 | 0.006549 | 0.0055531 | -2.5522e-10 | -0.0065402 | -0.0055394 | -5.8606e-09 | 0.006566 | 0.0055586 | -2.0207e-10 | -0.0065402 | -0.0055394 | 0 | -161.3781 | 73.359 | 0 | 18.6219 | -106.641 |  | 1.1595 | 1.1103 | 1.0222 | 1.159 | 1.1074 | 1.0191 | -2.466 | -116.304 | 118.3873 | -2.4774 | -116.3781 | 118.3591
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7497e-09 | -6.9527e-09 | 2.2464e-09 | -2.5995e-10 | -6.3208e-11 | 2.797e-10 | -5.8123e-09 | -1.9124e-09 | 6.246e-09 | -2.0008e-10 | 2.9562e-10 | -1.1504e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1601 | 1.1131 | 1.0252 | 1.1601 | 1.1131 | 1.0252 | -2.4508 | -116.2246 | 118.4057 | -2.4508 | -116.2246 | 118.4057
Line1_1_3 | 0.0035482 | 0.0035482 | 0.0035482 | 0.0035482 | 0.0035482 | 0.0035482 | 0.00081942 | 0.00081942 | 0.00081942 | 0.00081942 | 0.00081942 | 0.00081942 | 0.00075602 | 0.0002136 | -0.00077983 | -0.00075595 | -0.00021354 | 0.00077989 | 0.00057629 | -0.00088674 | 0.00031232 | -0.00057617 | 0.00088686 | -0.00031219 | -39.768 | -39.768 | -39.768 | 140.2316 | 140.2316 | 140.2316 |  | 1.1601 | 1.1131 | 1.0252 | 1.16 | 1.1132 | 1.0252 | -2.4508 | -116.2246 | 118.4057 | -2.4545 | -116.2303 | 118.4153
Line2_1_4 | 0.0035734 | 0.034385 | 0.032098 | 0.0035734 | 0.034385 | 0.032098 | 0.00082523 | 0.0079408 | 0.0074127 | 0.00082523 | 0.0079408 | 0.0074127 | 0.00076935 | 0.0067591 | 0.0047867 | -0.00076909 | -0.00675 | -0.0047746 | 0.00056977 | 0.0056957 | 0.0059021 | -0.00056926 | -0.005672 | -0.0058833 | -38.9737 | -156.3445 | 67.4484 | 141.0259 | 23.6556 | -112.5516 |  | 1.1601 | 1.1131 | 1.0252 | 1.1595 | 1.1103 | 1.0222 | -2.4508 | -116.2246 | 118.4057 | -2.466 | -116.304 | 118.3873
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.4995e-09 | -1.3905e-08 | 4.4928e-09 | -5.0097e-09 | 6.8895e-09 | -1.9667e-09 | -1.1625e-08 | -3.8248e-09 | 1.2492e-08 | 5.6122e-09 | 2.208e-09 | -6.3611e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1601 | 1.1131 | 1.0252 | 1.1601 | 1.1131 | 1.0252 | -2.4508 | -116.2246 | 118.4057 | -2.4508 | -116.2246 | 118.4057
Line4_2_6 | 0.0035554 | 0.0035554 | 0.0035554 | 0.0035554 | 0.0035554 | 0.0035554 | 0.00082108 | 0.00082108 | 0.00082108 | 0.00082108 | 0.00082108 | 0.00082108 | 0.00075976 | 0.00021046 | -0.00078023 | -0.00075969 | -0.0002104 | 0.00078029 | 0.00057434 | -0.0008895 | 0.00031591 | -0.00057422 | 0.00088962 | -0.00031578 | -39.542 | -39.542 | -39.542 | 140.4576 | 140.4576 | 140.4576 |  | 1.16 | 1.1132 | 1.0252 | 1.1598 | 1.1134 | 1.0252 | -2.4546 | -116.2302 | 118.4153 | -2.4583 | -116.2359 | 118.4249
Line5_6_7 | 0.0035554 | 0.0035554 | 0.0035554 | 0.0035554 | 0.0035554 | 0.0035554 | 0.00082108 | 0.00082108 | 0.00082108 | 0.00082108 | 0.00082108 | 0.00082108 | 0.00075969 | 0.0002104 | -0.00078029 | -0.00075962 | -0.00021035 | 0.00078036 | 0.00057422 | -0.00088962 | 0.00031578 | -0.0005741 | 0.00088975 | -0.00031564 | -39.5424 | -39.5424 | -39.5424 | 140.4571 | 140.4571 | 140.4571 |  | 1.1598 | 1.1134 | 1.0252 | 1.1596 | 1.1135 | 1.0252 | -2.4583 | -116.2359 | 118.4249 | -2.4621 | -116.2416 | 118.4345
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4301e-08 | -2.077e-08 | 6.5979e-09 | -9.7919e-09 | 1.3782e-08 | -4.119e-09 | -1.7295e-08 | -5.8399e-09 | 1.8726e-08 | 1.1329e-08 | 4.1876e-09 | -1.2597e-08 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1596 | 1.1135 | 1.0252 | 1.1596 | 1.1135 | 1.0252 | -2.4621 | -116.2416 | 118.4345 | -2.4621 | -116.2416 | 118.4345
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.767e-09 | -6.9232e-09 | 2.1993e-09 | -2.5792e-10 | -6.4761e-11 | 2.7962e-10 | -5.765e-09 | -1.9466e-09 | 6.2419e-09 | -2.0093e-10 | 2.9439e-10 | -1.1297e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1596 | 1.1135 | 1.0252 | 1.1596 | 1.1135 | 1.0252 | -2.4621 | -116.2416 | 118.4345 | -2.4621 | -116.2416 | 118.4345
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.767e-09 | -6.9232e-09 | 2.1993e-09 | -2.5792e-10 | -6.4761e-11 | 2.7962e-10 | -5.765e-09 | -1.9466e-09 | 6.2419e-09 | -2.0093e-10 | 2.9439e-10 | -1.1297e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1596 | 1.1135 | 1.0252 | 1.1596 | 1.1135 | 1.0252 | -2.4621 | -116.2416 | 118.4345 | -2.4621 | -116.2416 | 118.4345
Line9_3_11 | 0.0035482 | 0.0035482 | 0.0035482 | 0.0035482 | 0.0035482 | 0.0035482 | 0.00081942 | 0.00081942 | 0.00081942 | 0.00081942 | 0.00081942 | 0.00081942 | 0.00075595 | 0.00021354 | -0.00077989 | -0.00075588 | -0.00021349 | 0.00077996 | 0.00057617 | -0.00088686 | 0.00031219 | -0.00057605 | 0.00088699 | -0.00031206 | -39.7684 | -39.7684 | -39.7684 | 140.2311 | 140.2311 | 140.2311 |  | 1.16 | 1.1132 | 1.0252 | 1.1598 | 1.1134 | 1.0252 | -2.4545 | -116.2303 | 118.4153 | -2.4583 | -116.236 | 118.4248

## LLG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.02134 | 0.02134 | 0.02134 | 0.02134 | 0.02134 | 0.02134 | 0.0049283 | 0.0049283 | 0.0049283 | 0.0049283 | 0.0049283 | 0.0049283 | 0.0069666 | -0.00054468 | 0.0004485 | -0.0069622 | 0.00054903 | -0.00044411 | 0.0001411 | -0.0029747 | 0.0028742 | -0.0001366 | 0.0029792 | -0.0028697 | -1.9653 | -1.9652 | -1.9653 | 178.0343 | 178.0343 | 178.0342 |  | 1.4139 | 0.61362 | 0.59026 | 1.413 | 0.61469 | 0.58921 | -0.80499 | -102.3415 | 79.1656 | -0.84172 | -102.4073 | 79.2369
Line10_11_12 | 0.021258 | 0.021258 | 0.021258 | 0.021258 | 0.021258 | 0.021258 | 0.0049094 | 0.0049094 | 0.0049094 | 0.0049094 | 0.0049094 | 0.0049094 | 0.0069306 | -0.00053959 | 0.00042682 | -0.0069263 | 0.0005439 | -0.00042246 | 0.00015886 | -0.0029744 | 0.0028559 | -0.00015439 | 0.0029789 | -0.0028514 | -2.191 | -2.1909 | -2.191 | 177.8086 | 177.8086 | 177.8085 |  | 1.4121 | 0.61575 | 0.58818 | 1.4112 | 0.61681 | 0.58714 | -0.87794 | -102.4732 | 79.3088 | -0.91448 | -102.5387 | 79.3808
Line11_12_13 | 0.021258 | 0.021258 | 0.021258 | 0.021258 | 0.021258 | 0.021258 | 0.0049094 | 0.0049094 | 0.0049094 | 0.0049094 | 0.0049094 | 0.0049094 | 0.0069262 | -0.0005439 | 0.00042246 | -0.0069219 | 0.00054822 | -0.0004181 | 0.00015439 | -0.0029789 | 0.0028514 | -0.00014993 | 0.0029834 | -0.0028469 | -2.1914 | -2.1914 | -2.1915 | 177.8081 | 177.8082 | 177.8081 |  | 1.4112 | 0.61681 | 0.58714 | 1.4103 | 0.61787 | 0.5861 | -0.91448 | -102.5387 | 79.3808 | -0.95107 | -102.604 | 79.4531
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.036e-08 | -7.2367e-08 | 6.6312e-08 | -9.2874e-09 | 4.8899e-08 | -4.3916e-08 | -1.6317e-07 | 1.115e-08 | -6.0208e-09 | 1.087e-07 | -6.7897e-09 | 2.6867e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.4103 | 0.61787 | 0.5861 | 1.4103 | 0.61787 | 0.5861 | -0.95107 | -102.604 | 79.4531 | -0.95107 | -102.604 | 79.4531
Line13_13_14 | 0.021258 | 0.021258 | 0.021258 | 0.021258 | 0.021258 | 0.021258 | 0.0049094 | 0.0049094 | 0.0049094 | 0.0049094 | 0.0049094 | 0.0049094 | 0.0069219 | -0.00054815 | 0.00041804 | -0.0069176 | 0.00055246 | -0.00041368 | 0.00015009 | -0.0029835 | 0.0028469 | -0.00014563 | 0.002988 | -0.0028424 | -2.1932 | -2.1932 | -2.1933 | 177.8063 | 177.8063 | 177.8063 |  | 1.4103 | 0.61787 | 0.5861 | 1.4094 | 0.61894 | 0.58506 | -0.95107 | -102.604 | 79.4531 | -0.9877 | -102.669 | 79.5256
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.9068e-09 | -4.8245e-08 | 4.4208e-08 | -5.834e-09 | 2.4776e-08 | -2.1812e-08 | -1.0878e-07 | 7.4332e-09 | -4.0139e-09 | 5.4308e-08 | -3.0731e-09 | 6.7976e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.4103 | 0.61787 | 0.5861 | 1.4103 | 0.61787 | 0.5861 | -0.95107 | -102.604 | 79.4531 | -0.95107 | -102.604 | 79.4531
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4534e-09 | -2.4122e-08 | 2.2104e-08 | -2.3806e-09 | 6.54e-10 | 2.918e-10 | -5.439e-08 | 3.7166e-09 | -2.0069e-09 | -8.1538e-11 | 6.4347e-10 | -1.3272e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.4103 | 0.61787 | 0.5861 | 1.4103 | 0.61787 | 0.5861 | -0.95107 | -102.604 | 79.4531 | -0.95107 | -102.604 | 79.4531
Line16_4_18 | 0 | 2.5871 | 2.4277 | 0 | 2.5871 | 2.4277 | 0 | 0.59746 | 0.56066 | 0 | 0.59746 | 0.56066 | 2.6359e-09 | 0.12627 | 0.11528 | -2.3623e-09 | -2.603e-14 | -5.1071e-14 | -5.5176e-08 | 0.13333 | 0.11828 | -9.1105e-11 | 3.0525e-14 | -3.9669e-15 | 0 | -148.9658 | 33.5007 | 0 | 31.0342 | -146.4993 |  | 1.4103 | 0.30735 | 0.2946 | 1.4075 | 0 | 0 | -0.95337 | -102.407 | 79.2366 | -1.0647 | 0 | 0
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1942e-09 | -2.4128e-08 | 2.2405e-08 | -2.4053e-09 | 6.5612e-10 | 2.7813e-10 | -5.4968e-08 | 3.7932e-09 | -2.3328e-09 | -6.9192e-11 | 6.4838e-10 | -1.3444e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.4139 | 0.61362 | 0.59026 | 1.4139 | 0.61362 | 0.59026 | -0.80499 | -102.3415 | 79.1656 | -0.80499 | -102.3415 | 79.1656
Line1_1_3 | 0.021258 | 0.021258 | 0.021258 | 0.021258 | 0.021258 | 0.021258 | 0.0049094 | 0.0049094 | 0.0049094 | 0.0049094 | 0.0049094 | 0.0049094 | 0.0069393 | -0.00053096 | 0.00043555 | -0.0069349 | 0.00053528 | -0.00043119 | 0.00016779 | -0.0029654 | 0.0028649 | -0.00016332 | 0.0029699 | -0.0028604 | -2.1901 | -2.19 | -2.1902 | 177.8095 | 177.8095 | 177.8094 |  | 1.4139 | 0.61362 | 0.59026 | 1.413 | 0.61468 | 0.58922 | -0.80499 | -102.3415 | 79.1656 | -0.84144 | -102.4075 | 79.2371
Line2_1_4 | 0.021546 | 2.5689 | 2.4454 | 0.021546 | 2.5689 | 2.4454 | 0.0049759 | 0.59327 | 0.56475 | 0.0049759 | 0.59327 | 0.56475 | 0.0070349 | 0.2512 | 0.23176 | -0.007017 | -0.12597 | -0.11552 | 7.3113e-05 | 0.26348 | 0.23961 | -5.481e-05 | -0.13183 | -0.11973 | -1.4004 | -148.708 | 33.2119 | 178.5991 | 31.292 | -146.7881 |  | 1.4139 | 0.61362 | 0.59026 | 1.4103 | 0.30735 | 0.2946 | -0.80499 | -102.3415 | 79.1656 | -0.95337 | -102.407 | 79.2366
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.3884e-09 | -4.8256e-08 | 4.481e-08 | -5.5995e-09 | 2.4784e-08 | -2.2127e-08 | -1.0994e-07 | 7.5864e-09 | -4.6656e-09 | 5.4899e-08 | -3.1448e-09 | 9.8837e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.4139 | 0.61362 | 0.59026 | 1.4139 | 0.61362 | 0.59026 | -0.80499 | -102.3415 | 79.1656 | -0.80499 | -102.3415 | 79.1656
Line4_2_6 | 0.02134 | 0.02134 | 0.02134 | 0.02134 | 0.02134 | 0.02134 | 0.0049283 | 0.0049283 | 0.0049283 | 0.0049283 | 0.0049283 | 0.0049283 | 0.0069622 | -0.00054903 | 0.00044411 | -0.0069578 | 0.00055337 | -0.00043971 | 0.0001366 | -0.0029792 | 0.0028697 | -0.0001321 | 0.0029838 | -0.0028651 | -1.9657 | -1.9657 | -1.9658 | 178.0338 | 178.0339 | 178.0338 |  | 1.413 | 0.61469 | 0.58921 | 1.4121 | 0.61576 | 0.58817 | -0.84172 | -102.4073 | 79.2369 | -0.87851 | -102.4729 | 79.3086
Line5_6_7 | 0.02134 | 0.02134 | 0.02134 | 0.02134 | 0.02134 | 0.02134 | 0.0049283 | 0.0049283 | 0.0049283 | 0.0049283 | 0.0049283 | 0.0049283 | 0.0069578 | -0.00055337 | 0.00043971 | -0.0069535 | 0.00055772 | -0.00043532 | 0.0001321 | -0.0029838 | 0.0028651 | -0.0001276 | 0.0029883 | -0.0028606 | -1.9662 | -1.9662 | -1.9662 | 178.0334 | 178.0334 | 178.0333 |  | 1.4121 | 0.61576 | 0.58817 | 1.4112 | 0.61683 | 0.58712 | -0.87851 | -102.4729 | 79.3086 | -0.91533 | -102.5383 | 79.3805
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0171e-08 | -7.2375e-08 | 6.6535e-08 | -9.1673e-09 | 4.8904e-08 | -4.4069e-08 | -1.636e-07 | 1.1205e-08 | -6.2611e-09 | 1.0899e-07 | -6.8253e-09 | 2.8426e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.4112 | 0.61683 | 0.58712 | 1.4112 | 0.61683 | 0.58712 | -0.91533 | -102.5383 | 79.3805 | -0.91533 | -102.5383 | 79.3805
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3903e-09 | -2.4125e-08 | 2.2178e-08 | -2.3868e-09 | 6.5452e-10 | 2.8842e-10 | -5.4534e-08 | 3.735e-09 | -2.087e-09 | -7.8525e-11 | 6.4474e-10 | -1.3314e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.4112 | 0.61683 | 0.58712 | 1.4112 | 0.61683 | 0.58712 | -0.91533 | -102.5383 | 79.3805 | -0.91533 | -102.5383 | 79.3805
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3903e-09 | -2.4125e-08 | 2.2178e-08 | -2.3868e-09 | 6.5452e-10 | 2.8842e-10 | -5.4534e-08 | 3.735e-09 | -2.087e-09 | -7.8525e-11 | 6.4473e-10 | -1.3314e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.4112 | 0.61683 | 0.58712 | 1.4112 | 0.61683 | 0.58712 | -0.91533 | -102.5383 | 79.3805 | -0.91533 | -102.5383 | 79.3805
Line9_3_11 | 0.021258 | 0.021258 | 0.021258 | 0.021258 | 0.021258 | 0.021258 | 0.0049094 | 0.0049094 | 0.0049094 | 0.0049094 | 0.0049094 | 0.0049094 | 0.0069349 | -0.00053527 | 0.00043119 | -0.0069306 | 0.00053959 | -0.00042682 | 0.00016332 | -0.0029699 | 0.0028604 | -0.00015886 | 0.0029744 | -0.0028559 | -2.1905 | -2.1905 | -2.1906 | 177.809 | 177.8091 | 177.8089 |  | 1.413 | 0.61468 | 0.58922 | 1.4121 | 0.61575 | 0.58818 | -0.84144 | -102.4075 | 79.2371 | -0.87794 | -102.4732 | 79.3088

## LLG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.020217 | 0.020217 | 0.020217 | 0.020217 | 0.020217 | 0.020217 | 0.0046689 | 0.0046689 | 0.0046689 | 0.0046689 | 0.0046689 | 0.0046689 | 0.0062526 | -0.00048885 | 0.00040253 | -0.0062486 | 0.00049275 | -0.00039859 | 0.00012664 | -0.0026698 | 0.0025796 | -0.0001226 | 0.0026739 | -0.0025756 | -1.9653 | -1.9652 | -1.9653 | 178.0343 | 178.0343 | 178.0342 |  | 1.3395 | 0.58132 | 0.5592 | 1.3386 | 0.58234 | 0.5582 | -0.80499 | -102.3415 | 79.1656 | -0.84172 | -102.4073 | 79.2369
Line10_11_12 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.004651 | 0.004651 | 0.004651 | 0.004651 | 0.004651 | 0.004651 | 0.0062203 | -0.00048428 | 0.00038308 | -0.0062164 | 0.00048816 | -0.00037916 | 0.00014258 | -0.0026695 | 0.0025632 | -0.00013857 | 0.0026736 | -0.0025591 | -2.191 | -2.1909 | -2.191 | 177.8086 | 177.8086 | 177.8085 |  | 1.3377 | 0.58334 | 0.55722 | 1.3369 | 0.58435 | 0.55624 | -0.87794 | -102.4732 | 79.3088 | -0.91448 | -102.5387 | 79.3808
Line11_12_13 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.004651 | 0.004651 | 0.004651 | 0.004651 | 0.004651 | 0.004651 | 0.0062164 | -0.00048816 | 0.00037916 | -0.0062125 | 0.00049203 | -0.00037525 | 0.00013857 | -0.0026736 | 0.0025591 | -0.00013456 | 0.0026777 | -0.0025551 | -2.1914 | -2.1914 | -2.1915 | 177.8081 | 177.8082 | 177.8081 |  | 1.3369 | 0.58435 | 0.55624 | 1.336 | 0.58535 | 0.55525 | -0.91448 | -102.5387 | 79.3808 | -0.95107 | -102.604 | 79.4531
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.2984e-09 | -6.495e-08 | 5.9515e-08 | -8.3355e-09 | 4.3887e-08 | -3.9415e-08 | -1.4645e-07 | 1.0007e-08 | -5.4037e-09 | 9.7557e-08 | -6.0938e-09 | 2.4113e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.336 | 0.58535 | 0.55525 | 1.336 | 0.58535 | 0.55525 | -0.95107 | -102.604 | 79.4531 | -0.95107 | -102.604 | 79.4531
Line13_13_14 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.004651 | 0.004651 | 0.004651 | 0.004651 | 0.004651 | 0.004651 | 0.0062124 | -0.00049196 | 0.00037519 | -0.0062086 | 0.00049584 | -0.00037128 | 0.00013471 | -0.0026777 | 0.0025551 | -0.0001307 | 0.0026817 | -0.002551 | -2.1932 | -2.1932 | -2.1933 | 177.8063 | 177.8063 | 177.8063 |  | 1.336 | 0.58535 | 0.55525 | 1.3352 | 0.58636 | 0.55427 | -0.95107 | -102.604 | 79.4531 | -0.9877 | -102.669 | 79.5256
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.1989e-09 | -4.33e-08 | 3.9677e-08 | -5.2361e-09 | 2.2237e-08 | -1.9576e-08 | -9.763e-08 | 6.6713e-09 | -3.6025e-09 | 4.8742e-08 | -2.7581e-09 | 6.1009e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.336 | 0.58535 | 0.55525 | 1.336 | 0.58535 | 0.55525 | -0.95107 | -102.604 | 79.4531 | -0.95107 | -102.604 | 79.4531
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0995e-09 | -2.165e-08 | 1.9838e-08 | -2.1366e-09 | 5.8697e-10 | 2.6189e-10 | -4.8815e-08 | 3.3357e-09 | -1.8012e-09 | -7.3181e-11 | 5.7752e-10 | -1.1911e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.336 | 0.58535 | 0.55525 | 1.336 | 0.58535 | 0.55525 | -0.95107 | -102.604 | 79.4531 | -0.95107 | -102.604 | 79.4531
Line16_4_18 | 0 | 2.4509 | 2.3 | 0 | 2.4509 | 2.3 | 0 | 0.56602 | 0.53115 | 0 | 0.56602 | 0.53115 | 2.3658e-09 | 0.11333 | 0.10347 | -2.1202e-09 | -2.5033e-14 | -4.4154e-14 | -4.9521e-08 | 0.11967 | 0.10616 | -8.1768e-11 | 2.8116e-14 | -4.153e-15 | 0 | -148.9658 | 33.5007 | 0 | 31.0342 | -146.4993 |  | 1.336 | 0.29118 | 0.27909 | 1.3335 | 0 | 0 | -0.95337 | -102.407 | 79.2366 | -1.0647 | 0 | 0
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8668e-09 | -2.1655e-08 | 2.0109e-08 | -2.1588e-09 | 5.8887e-10 | 2.4962e-10 | -4.9334e-08 | 3.4044e-09 | -2.0937e-09 | -6.2101e-11 | 5.8192e-10 | -1.2066e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3395 | 0.58132 | 0.5592 | 1.3395 | 0.58132 | 0.5592 | -0.80499 | -102.3415 | 79.1656 | -0.80499 | -102.3415 | 79.1656
Line1_1_3 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.004651 | 0.004651 | 0.004651 | 0.004651 | 0.004651 | 0.004651 | 0.006228 | -0.00047654 | 0.00039091 | -0.0062242 | 0.00048041 | -0.00038699 | 0.00015059 | -0.0026614 | 0.0025713 | -0.00014658 | 0.0026655 | -0.0025672 | -2.1901 | -2.19 | -2.1902 | 177.8095 | 177.8095 | 177.8094 |  | 1.3395 | 0.58132 | 0.5592 | 1.3386 | 0.58233 | 0.55821 | -0.80499 | -102.3415 | 79.1656 | -0.84144 | -102.4075 | 79.2371
Line2_1_4 | 0.020412 | 2.4337 | 2.3167 | 0.020412 | 2.4337 | 2.3167 | 0.004714 | 0.56204 | 0.53503 | 0.004714 | 0.56204 | 0.53503 | 0.0063138 | 0.22546 | 0.20801 | -0.0062978 | -0.11306 | -0.10368 | 6.562e-05 | 0.23648 | 0.21505 | -4.9192e-05 | -0.11832 | -0.10746 | -1.4004 | -148.708 | 33.2119 | 178.5991 | 31.292 | -146.7881 |  | 1.3395 | 0.58132 | 0.5592 | 1.336 | 0.29118 | 0.27909 | -0.80499 | -102.3415 | 79.1656 | -0.95337 | -102.407 | 79.2366
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.7336e-09 | -4.331e-08 | 4.0217e-08 | -5.0256e-09 | 2.2244e-08 | -1.9859e-08 | -9.8668e-08 | 6.8088e-09 | -4.1874e-09 | 4.9272e-08 | -2.8225e-09 | 8.8707e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3395 | 0.58132 | 0.5592 | 1.3395 | 0.58132 | 0.5592 | -0.80499 | -102.3415 | 79.1656 | -0.80499 | -102.3415 | 79.1656
Line4_2_6 | 0.020217 | 0.020217 | 0.020217 | 0.020217 | 0.020217 | 0.020217 | 0.0046689 | 0.0046689 | 0.0046689 | 0.0046689 | 0.0046689 | 0.0046689 | 0.0062486 | -0.00049275 | 0.00039859 | -0.0062447 | 0.00049666 | -0.00039465 | 0.0001226 | -0.0026739 | 0.0025756 | -0.00011856 | 0.002678 | -0.0025715 | -1.9657 | -1.9657 | -1.9658 | 178.0338 | 178.0339 | 178.0338 |  | 1.3386 | 0.58234 | 0.5582 | 1.3377 | 0.58335 | 0.55721 | -0.84172 | -102.4073 | 79.2369 | -0.87851 | -102.4729 | 79.3086
Line5_6_7 | 0.020217 | 0.020217 | 0.020217 | 0.020217 | 0.020217 | 0.020217 | 0.0046689 | 0.0046689 | 0.0046689 | 0.0046689 | 0.0046689 | 0.0046689 | 0.0062447 | -0.00049666 | 0.00039465 | -0.0062408 | 0.00050056 | -0.0003907 | 0.00011856 | -0.002678 | 0.0025715 | -0.00011452 | 0.002682 | -0.0025674 | -1.9662 | -1.9662 | -1.9662 | 178.0334 | 178.0334 | 178.0333 |  | 1.3377 | 0.58335 | 0.55721 | 1.3369 | 0.58437 | 0.55622 | -0.87851 | -102.4729 | 79.3086 | -0.91533 | -102.5383 | 79.3805
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.1283e-09 | -6.4957e-08 | 5.9716e-08 | -8.2277e-09 | 4.3892e-08 | -3.9552e-08 | -1.4683e-07 | 1.0057e-08 | -5.6194e-09 | 9.7818e-08 | -6.1258e-09 | 2.5513e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3369 | 0.58437 | 0.55622 | 1.3369 | 0.58437 | 0.55622 | -0.91533 | -102.5383 | 79.3805 | -0.91533 | -102.5383 | 79.3805
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0428e-09 | -2.1652e-08 | 1.9905e-08 | -2.1422e-09 | 5.8744e-10 | 2.5886e-10 | -4.8944e-08 | 3.3522e-09 | -1.8731e-09 | -7.0477e-11 | 5.7865e-10 | -1.195e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3369 | 0.58437 | 0.55622 | 1.3369 | 0.58437 | 0.55622 | -0.91533 | -102.5383 | 79.3805 | -0.91533 | -102.5383 | 79.3805
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0428e-09 | -2.1652e-08 | 1.9905e-08 | -2.1422e-09 | 5.8744e-10 | 2.5886e-10 | -4.8944e-08 | 3.3522e-09 | -1.8731e-09 | -7.0477e-11 | 5.7865e-10 | -1.195e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3369 | 0.58437 | 0.55622 | 1.3369 | 0.58437 | 0.55622 | -0.91533 | -102.5383 | 79.3805 | -0.91533 | -102.5383 | 79.3805
Line9_3_11 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.004651 | 0.004651 | 0.004651 | 0.004651 | 0.004651 | 0.004651 | 0.0062241 | -0.00048041 | 0.00038699 | -0.0062203 | 0.00048429 | -0.00038308 | 0.00014658 | -0.0026655 | 0.0025672 | -0.00014258 | 0.0026695 | -0.0025632 | -2.1905 | -2.1905 | -2.1906 | 177.809 | 177.8091 | 177.8089 |  | 1.3386 | 0.58233 | 0.55821 | 1.3377 | 0.58334 | 0.55722 | -0.84144 | -102.4075 | 79.2371 | -0.87794 | -102.4732 | 79.3088

## LLG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.0030638 | 0.0030638 | 0.0030638 | 0.0030638 | 0.0030638 | 0.0030638 | 0.00070755 | 0.00070755 | 0.00070755 | 0.00070755 | 0.00070755 | 0.00070755 | 0.00056596 | 0.00015601 | -0.00058036 | -0.00056587 | -0.00015593 | 0.00058045 | 0.00042698 | -0.00066202 | 0.00023588 | -0.00042689 | 0.00066211 | -0.00023578 | -39.4807 | -39.4807 | -39.4807 | 140.5189 | 140.5189 | 140.5189 |  | 1.002 | 0.96127 | 0.88539 | 1.0018 | 0.96137 | 0.88546 | -2.4485 | -116.2203 | 118.401 | -2.4502 | -116.2295 | 118.412
Line10_11_12 | 0.003052 | 0.003052 | 0.003052 | 0.003052 | 0.003052 | 0.003052 | 0.00070484 | 0.00070484 | 0.00070484 | 0.00070484 | 0.00070484 | 0.00070484 | 0.00056193 | 0.00015783 | -0.00057923 | -0.00056184 | -0.00015775 | 0.00057932 | 0.00042737 | -0.00065905 | 0.00023251 | -0.00042728 | 0.00065914 | -0.00023241 | -39.7064 | -39.7064 | -39.7064 | 140.2932 | 140.2932 | 140.2932 |  | 1.0016 | 0.96147 | 0.88553 | 1.0014 | 0.96157 | 0.88559 | -2.4517 | -116.2387 | 118.4229 | -2.4534 | -116.2479 | 118.4339
Line11_12_13 | 0.003052 | 0.003052 | 0.003052 | 0.003052 | 0.003052 | 0.003052 | 0.00070484 | 0.00070484 | 0.00070484 | 0.00070484 | 0.00070484 | 0.00070484 | 0.00056184 | 0.00015775 | -0.00057932 | -0.00056175 | -0.00015766 | 0.00057941 | 0.00042728 | -0.00065914 | 0.00023241 | -0.0004272 | 0.00065923 | -0.00023231 | -39.7068 | -39.7068 | -39.7068 | 140.2927 | 140.2927 | 140.2927 |  | 1.0014 | 0.96157 | 0.88559 | 1.0013 | 0.96167 | 0.88566 | -2.4534 | -116.2479 | 118.4339 | -2.455 | -116.2571 | 118.4449
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0633e-08 | -1.5425e-08 | 4.8877e-09 | -7.2801e-09 | 1.0235e-08 | -3.0507e-09 | -1.2833e-08 | -4.3474e-09 | 1.3919e-08 | 8.4058e-09 | 3.1169e-09 | -9.3629e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0013 | 0.96167 | 0.88566 | 1.0013 | 0.96167 | 0.88566 | -2.455 | -116.2571 | 118.4449 | -2.455 | -116.2571 | 118.4449
Line13_13_14 | 0.003052 | 0.003052 | 0.003052 | 0.003052 | 0.003052 | 0.003052 | 0.00070484 | 0.00070484 | 0.00070484 | 0.00070484 | 0.00070484 | 0.00070484 | 0.00056173 | 0.00015768 | -0.00057942 | -0.00056164 | -0.00015759 | 0.00057951 | 0.00042721 | -0.00065923 | 0.0002323 | -0.00042712 | 0.00065932 | -0.0002322 | -39.7086 | -39.7086 | -39.7086 | 140.2909 | 140.2909 | 140.2909 |  | 1.0013 | 0.96167 | 0.88566 | 1.0011 | 0.96177 | 0.88573 | -2.455 | -116.2571 | 118.4449 | -2.4566 | -116.2663 | 118.4559
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.0887e-09 | -1.0283e-08 | 3.2584e-09 | -3.7357e-09 | 5.0934e-09 | -1.4214e-09 | -8.5552e-09 | -2.8983e-09 | 9.2791e-09 | 4.1282e-09 | 1.6678e-09 | -4.7233e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0013 | 0.96167 | 0.88566 | 1.0013 | 0.96167 | 0.88566 | -2.455 | -116.2571 | 118.4449 | -2.455 | -116.2571 | 118.4449
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5443e-09 | -5.1417e-09 | 1.6292e-09 | -1.914e-10 | -4.8291e-11 | 2.0779e-10 | -4.2776e-09 | -1.4491e-09 | 4.6396e-09 | -1.494e-10 | 2.1868e-10 | -8.3722e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0013 | 0.96167 | 0.88566 | 1.0013 | 0.96167 | 0.88566 | -2.455 | -116.2571 | 118.4449 | -2.455 | -116.2571 | 118.4449
Line16_4_18 | 0 | 0.031174 | 0.028707 | 0 | 0.031174 | 0.028707 | 0 | 0.0071992 | 0.0066296 | 0 | 0.0071993 | 0.0066296 | 3.5242e-09 | 0.0048738 | 0.0041378 | -1.8929e-10 | -0.004859 | -0.0041205 | -4.3913e-09 | 0.0048792 | 0.0041336 | -1.4965e-10 | -0.004859 | -0.0041205 | 0 | -161.2939 | 73.4695 | 0 | 18.7061 | -106.5305 |  | 1.0013 | 0.95794 | 0.88221 | 1.0007 | 0.9545 | 0.87897 | -2.4554 | -116.2616 | 118.4407 | -2.4605 | -116.2939 | 118.4695
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5405e-09 | -5.1897e-09 | 1.6818e-09 | -1.9418e-10 | -4.7016e-11 | 2.0855e-10 | -4.3415e-09 | -1.4221e-09 | 4.6594e-09 | -1.4911e-10 | 2.2073e-10 | -8.6062e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.002 | 0.96127 | 0.88539 | 1.002 | 0.96127 | 0.88539 | -2.4485 | -116.2203 | 118.401 | -2.4485 | -116.2203 | 118.401
Line1_1_3 | 0.003052 | 0.003052 | 0.003052 | 0.003052 | 0.003052 | 0.003052 | 0.00070484 | 0.00070484 | 0.00070484 | 0.00070484 | 0.00070484 | 0.00070484 | 0.00056212 | 0.000158 | -0.00057905 | -0.00056202 | -0.00015791 | 0.00057914 | 0.00042755 | -0.00065886 | 0.0002327 | -0.00042746 | 0.00065896 | -0.0002326 | -39.7055 | -39.7054 | -39.7054 | 140.2941 | 140.2941 | 140.2941 |  | 1.002 | 0.96127 | 0.88539 | 1.0018 | 0.96137 | 0.88546 | -2.4485 | -116.2203 | 118.401 | -2.4501 | -116.2295 | 118.412
Line2_1_4 | 0.0030934 | 0.029633 | 0.027677 | 0.0030934 | 0.029633 | 0.027677 | 0.00071438 | 0.0068433 | 0.0063918 | 0.00071438 | 0.0068434 | 0.0063918 | 0.00057564 | 0.0050381 | 0.003572 | -0.00057527 | -0.0050237 | -0.0035561 | 0.00042544 | 0.0042298 | 0.0043895 | -0.00042507 | -0.0042115 | -0.0043762 | -38.9158 | -156.236 | 67.5378 | 141.0837 | 23.764 | -112.4621 |  | 1.002 | 0.96127 | 0.88539 | 1.0013 | 0.95794 | 0.88221 | -2.4485 | -116.2203 | 118.401 | -2.4554 | -116.2616 | 118.4407
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.081e-09 | -1.0379e-08 | 3.3636e-09 | -3.7347e-09 | 5.1427e-09 | -1.4733e-09 | -8.683e-09 | -2.8443e-09 | 9.3188e-09 | 4.1924e-09 | 1.6429e-09 | -4.7455e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.002 | 0.96127 | 0.88539 | 1.002 | 0.96127 | 0.88539 | -2.4485 | -116.2203 | 118.401 | -2.4485 | -116.2203 | 118.401
Line4_2_6 | 0.0030638 | 0.0030638 | 0.0030638 | 0.0030638 | 0.0030638 | 0.0030638 | 0.00070755 | 0.00070755 | 0.00070755 | 0.00070755 | 0.00070755 | 0.00070755 | 0.00056587 | 0.00015593 | -0.00058045 | -0.00056577 | -0.00015584 | 0.00058054 | 0.00042689 | -0.00066211 | 0.00023578 | -0.0004268 | 0.0006622 | -0.00023568 | -39.4811 | -39.4811 | -39.4811 | 140.5184 | 140.5184 | 140.5184 |  | 1.0018 | 0.96137 | 0.88546 | 1.0016 | 0.96147 | 0.88553 | -2.4502 | -116.2295 | 118.412 | -2.4518 | -116.2387 | 118.4231
Line5_6_7 | 0.0030638 | 0.0030638 | 0.0030638 | 0.0030638 | 0.0030638 | 0.0030638 | 0.00070755 | 0.00070755 | 0.00070755 | 0.00070755 | 0.00070755 | 0.00070755 | 0.00056577 | 0.00015584 | -0.00058054 | -0.00056568 | -0.00015576 | 0.00058063 | 0.0004268 | -0.0006622 | 0.00023568 | -0.00042671 | 0.00066229 | -0.00023558 | -39.4816 | -39.4816 | -39.4816 | 140.518 | 140.518 | 140.518 |  | 1.0016 | 0.96147 | 0.88553 | 1.0014 | 0.96157 | 0.88559 | -2.4518 | -116.2387 | 118.4231 | -2.4535 | -116.2479 | 118.4341
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0631e-08 | -1.5461e-08 | 4.9264e-09 | -7.2792e-09 | 1.0259e-08 | -3.0763e-09 | -1.288e-08 | -4.3278e-09 | 1.3934e-08 | 8.4375e-09 | 3.1044e-09 | -9.3735e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0014 | 0.96157 | 0.88559 | 1.0014 | 0.96157 | 0.88559 | -2.4535 | -116.2479 | 118.4341 | -2.4535 | -116.2479 | 118.4341
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5436e-09 | -5.1536e-09 | 1.6421e-09 | -1.9209e-10 | -4.7982e-11 | 2.0799e-10 | -4.2934e-09 | -1.4426e-09 | 4.6446e-09 | -1.4933e-10 | 2.1919e-10 | -8.4297e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0014 | 0.96157 | 0.88559 | 1.0014 | 0.96157 | 0.88559 | -2.4535 | -116.2479 | 118.4341 | -2.4535 | -116.2479 | 118.4341
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5436e-09 | -5.1536e-09 | 1.6421e-09 | -1.9209e-10 | -4.7982e-11 | 2.0799e-10 | -4.2934e-09 | -1.4426e-09 | 4.6446e-09 | -1.4933e-10 | 2.1919e-10 | -8.4297e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0014 | 0.96157 | 0.88559 | 1.0014 | 0.96157 | 0.88559 | -2.4535 | -116.2479 | 118.4341 | -2.4535 | -116.2479 | 118.4341
Line9_3_11 | 0.003052 | 0.003052 | 0.003052 | 0.003052 | 0.003052 | 0.003052 | 0.00070484 | 0.00070484 | 0.00070484 | 0.00070484 | 0.00070484 | 0.00070484 | 0.00056202 | 0.00015791 | -0.00057914 | -0.00056193 | -0.00015783 | 0.00057923 | 0.00042746 | -0.00065896 | 0.0002326 | -0.00042737 | 0.00065905 | -0.00023251 | -39.7059 | -39.7059 | -39.7059 | 140.2936 | 140.2936 | 140.2936 |  | 1.0018 | 0.96137 | 0.88546 | 1.0016 | 0.96147 | 0.88553 | -2.4501 | -116.2295 | 118.412 | -2.4517 | -116.2387 | 118.4229

## LLG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.0029025 | 0.0029025 | 0.0029025 | 0.0029025 | 0.0029025 | 0.0029025 | 0.00067031 | 0.00067031 | 0.00067031 | 0.00067031 | 0.00067031 | 0.00067031 | 0.00050795 | 0.00014002 | -0.00052087 | -0.00050787 | -0.00013994 | 0.00052096 | 0.00038322 | -0.00059416 | 0.0002117 | -0.00038314 | 0.00059425 | -0.00021161 | -39.4807 | -39.4807 | -39.4807 | 140.5189 | 140.5189 | 140.5189 |  | 0.94925 | 0.91068 | 0.83879 | 0.94908 | 0.91077 | 0.83885 | -2.4485 | -116.2203 | 118.401 | -2.4502 | -116.2295 | 118.412
Line10_11_12 | 0.0028914 | 0.0028914 | 0.0028914 | 0.0028914 | 0.0028914 | 0.0028914 | 0.00066774 | 0.00066774 | 0.00066774 | 0.00066774 | 0.00066774 | 0.00066774 | 0.00050434 | 0.00014165 | -0.00051986 | -0.00050425 | -0.00014158 | 0.00051995 | 0.00038357 | -0.0005915 | 0.00020868 | -0.00038349 | 0.00059158 | -0.00020859 | -39.7064 | -39.7064 | -39.7064 | 140.2932 | 140.2932 | 140.2932 |  | 0.94891 | 0.91087 | 0.83892 | 0.94874 | 0.91096 | 0.83898 | -2.4517 | -116.2387 | 118.4229 | -2.4534 | -116.2479 | 118.4339
Line11_12_13 | 0.0028914 | 0.0028914 | 0.0028914 | 0.0028914 | 0.0028914 | 0.0028914 | 0.00066774 | 0.00066774 | 0.00066774 | 0.00066774 | 0.00066774 | 0.00066774 | 0.00050425 | 0.00014158 | -0.00051995 | -0.00050417 | -0.0001415 | 0.00052003 | 0.00038349 | -0.00059158 | 0.00020859 | -0.00038341 | 0.00059166 | -0.0002085 | -39.7068 | -39.7068 | -39.7068 | 140.2927 | 140.2927 | 140.2927 |  | 0.94874 | 0.91096 | 0.83898 | 0.94856 | 0.91105 | 0.83905 | -2.4534 | -116.2479 | 118.4339 | -2.455 | -116.2571 | 118.4449
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.5432e-09 | -1.3844e-08 | 4.3867e-09 | -6.5339e-09 | 9.186e-09 | -2.738e-09 | -1.1518e-08 | -3.9018e-09 | 1.2492e-08 | 7.5443e-09 | 2.7975e-09 | -8.4032e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.94856 | 0.91105 | 0.83905 | 0.94856 | 0.91105 | 0.83905 | -2.455 | -116.2571 | 118.4449 | -2.455 | -116.2571 | 118.4449
Line13_13_14 | 0.0028914 | 0.0028914 | 0.0028914 | 0.0028914 | 0.0028914 | 0.0028914 | 0.00066774 | 0.00066774 | 0.00066774 | 0.00066774 | 0.00066774 | 0.00066774 | 0.00050416 | 0.00014152 | -0.00052003 | -0.00050408 | -0.00014144 | 0.00052011 | 0.00038342 | -0.00059166 | 0.00020849 | -0.00038334 | 0.00059174 | -0.0002084 | -39.7086 | -39.7086 | -39.7086 | 140.2909 | 140.2909 | 140.2909 |  | 0.94856 | 0.91105 | 0.83905 | 0.94839 | 0.91115 | 0.83911 | -2.455 | -116.2571 | 118.4449 | -2.4566 | -116.2663 | 118.4559
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.3621e-09 | -9.2294e-09 | 2.9245e-09 | -3.3529e-09 | 4.5713e-09 | -1.2757e-09 | -7.6784e-09 | -2.6012e-09 | 8.3281e-09 | 3.7051e-09 | 1.4969e-09 | -4.2392e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.94856 | 0.91105 | 0.83905 | 0.94856 | 0.91105 | 0.83905 | -2.455 | -116.2571 | 118.4449 | -2.455 | -116.2571 | 118.4449
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1811e-09 | -4.6147e-09 | 1.4622e-09 | -1.7179e-10 | -4.3341e-11 | 1.865e-10 | -3.8392e-09 | -1.3006e-09 | 4.164e-09 | -1.3408e-10 | 1.9626e-10 | -7.5141e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.94856 | 0.91105 | 0.83905 | 0.94856 | 0.91105 | 0.83905 | -2.455 | -116.2571 | 118.4449 | -2.455 | -116.2571 | 118.4449
Line16_4_18 | 0 | 0.029533 | 0.027196 | 0 | 0.029533 | 0.027196 | 0 | 0.0068203 | 0.0062807 | 0 | 0.0068203 | 0.0062807 | 3.163e-09 | 0.0043742 | 0.0037137 | -1.6989e-10 | -0.004361 | -0.0036982 | -3.9412e-09 | 0.0043792 | 0.00371 | -1.3431e-10 | -0.004361 | -0.0036982 | 0 | -161.2939 | 73.4695 | 0 | 18.7061 | -106.5305 |  | 0.94856 | 0.90752 | 0.83578 | 0.94804 | 0.90426 | 0.83271 | -2.4554 | -116.2616 | 118.4407 | -2.4605 | -116.2939 | 118.4695
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1776e-09 | -4.6578e-09 | 1.5094e-09 | -1.7428e-10 | -4.2198e-11 | 1.8718e-10 | -3.8965e-09 | -1.2764e-09 | 4.1818e-09 | -1.3383e-10 | 1.9811e-10 | -7.7241e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.94925 | 0.91068 | 0.83879 | 0.94925 | 0.91068 | 0.83879 | -2.4485 | -116.2203 | 118.401 | -2.4485 | -116.2203 | 118.401
Line1_1_3 | 0.0028914 | 0.0028914 | 0.0028914 | 0.0028914 | 0.0028914 | 0.0028914 | 0.00066774 | 0.00066774 | 0.00066774 | 0.00066774 | 0.00066774 | 0.00066774 | 0.0005045 | 0.0001418 | -0.0005197 | -0.00050442 | -0.00014173 | 0.00051978 | 0.00038373 | -0.00059133 | 0.00020885 | -0.00038365 | 0.00059142 | -0.00020876 | -39.7055 | -39.7054 | -39.7054 | 140.2941 | 140.2941 | 140.2941 |  | 0.94925 | 0.91068 | 0.83879 | 0.94908 | 0.91077 | 0.83885 | -2.4485 | -116.2203 | 118.401 | -2.4501 | -116.2295 | 118.412
Line2_1_4 | 0.0029305 | 0.028073 | 0.026221 | 0.0029305 | 0.028073 | 0.026221 | 0.00067678 | 0.0064832 | 0.0060554 | 0.00067678 | 0.0064832 | 0.0060554 | 0.00051664 | 0.0045218 | 0.0032059 | -0.00051631 | -0.0045088 | -0.0031916 | 0.00038184 | 0.0037963 | 0.0039396 | -0.0003815 | -0.0037799 | -0.0039277 | -38.9158 | -156.236 | 67.5378 | 141.0837 | 23.764 | -112.4621 |  | 0.94925 | 0.91068 | 0.83879 | 0.94856 | 0.90752 | 0.83578 | -2.4485 | -116.2203 | 118.401 | -2.4554 | -116.2616 | 118.4407
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.3553e-09 | -9.3156e-09 | 3.0189e-09 | -3.3519e-09 | 4.6156e-09 | -1.3223e-09 | -7.793e-09 | -2.5528e-09 | 8.3637e-09 | 3.7627e-09 | 1.4745e-09 | -4.2591e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.94925 | 0.91068 | 0.83879 | 0.94925 | 0.91068 | 0.83879 | -2.4485 | -116.2203 | 118.401 | -2.4485 | -116.2203 | 118.401
Line4_2_6 | 0.0029025 | 0.0029025 | 0.0029025 | 0.0029025 | 0.0029025 | 0.0029025 | 0.00067031 | 0.00067031 | 0.00067031 | 0.00067031 | 0.00067031 | 0.00067031 | 0.00050787 | 0.00013994 | -0.00052096 | -0.00050778 | -0.00013987 | 0.00052104 | 0.00038314 | -0.00059425 | 0.00021161 | -0.00038306 | 0.00059433 | -0.00021152 | -39.4811 | -39.4811 | -39.4811 | 140.5184 | 140.5184 | 140.5184 |  | 0.94908 | 0.91077 | 0.83885 | 0.94891 | 0.91087 | 0.83892 | -2.4502 | -116.2295 | 118.412 | -2.4518 | -116.2387 | 118.4231
Line5_6_7 | 0.0029025 | 0.0029025 | 0.0029025 | 0.0029025 | 0.0029025 | 0.0029025 | 0.00067031 | 0.00067031 | 0.00067031 | 0.00067031 | 0.00067031 | 0.00067031 | 0.00050778 | 0.00013987 | -0.00052104 | -0.0005077 | -0.00013979 | 0.00052112 | 0.00038306 | -0.00059433 | 0.00021152 | -0.00038298 | 0.00059441 | -0.00021143 | -39.4816 | -39.4816 | -39.4816 | 140.518 | 140.518 | 140.518 |  | 0.94891 | 0.91087 | 0.83892 | 0.94873 | 0.91096 | 0.83898 | -2.4518 | -116.2387 | 118.4231 | -2.4535 | -116.2479 | 118.4341
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.5411e-09 | -1.3876e-08 | 4.4215e-09 | -6.5332e-09 | 9.2078e-09 | -2.761e-09 | -1.156e-08 | -3.8843e-09 | 1.2506e-08 | 7.5727e-09 | 2.7862e-09 | -8.4128e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.94873 | 0.91096 | 0.83898 | 0.94873 | 0.91096 | 0.83898 | -2.4535 | -116.2479 | 118.4341 | -2.4535 | -116.2479 | 118.4341
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1804e-09 | -4.6254e-09 | 1.4738e-09 | -1.724e-10 | -4.3065e-11 | 1.8667e-10 | -3.8534e-09 | -1.2948e-09 | 4.1686e-09 | -1.3403e-10 | 1.9672e-10 | -7.5657e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.94873 | 0.91096 | 0.83898 | 0.94873 | 0.91096 | 0.83898 | -2.4535 | -116.2479 | 118.4341 | -2.4535 | -116.2479 | 118.4341
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1804e-09 | -4.6254e-09 | 1.4738e-09 | -1.724e-10 | -4.3065e-11 | 1.8667e-10 | -3.8534e-09 | -1.2948e-09 | 4.1686e-09 | -1.3403e-10 | 1.9672e-10 | -7.5657e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.94873 | 0.91096 | 0.83898 | 0.94873 | 0.91096 | 0.83898 | -2.4535 | -116.2479 | 118.4341 | -2.4535 | -116.2479 | 118.4341
Line9_3_11 | 0.0028914 | 0.0028914 | 0.0028914 | 0.0028914 | 0.0028914 | 0.0028914 | 0.00066774 | 0.00066774 | 0.00066774 | 0.00066774 | 0.00066774 | 0.00066774 | 0.00050442 | 0.00014173 | -0.00051978 | -0.00050434 | -0.00014165 | 0.00051986 | 0.00038365 | -0.00059142 | 0.00020876 | -0.00038357 | 0.0005915 | -0.00020868 | -39.7059 | -39.7059 | -39.7059 | 140.2936 | 140.2936 | 140.2936 |  | 0.94908 | 0.91077 | 0.83885 | 0.94891 | 0.91087 | 0.83892 | -2.4501 | -116.2295 | 118.412 | -2.4517 | -116.2387 | 118.4229