## LLL_max_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0_3ph | 0.24525 | 0.24525 | 0 | 0 | 0.16991 | 0.16991 | 0.14767 | -0.055376 | 0.099767 | -0.037413 | -34.1183 | 145.8817 | 1.0489 | 0.39332 | -0.074844 | -0.074842
Line_1_3-1ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.39332 | 0.39332 | -0.074842 | -0.07484
Line_2_3-1ph | 0.24525 | 0.24525 | 0 | 0.35783 | 0.16991 | 0.16991 | 0.055376 | -1e-07 | 0.037413 | -1e-07 | -34.1182 | 145.8818 | 0.39332 | 0 | -0.074842 | 0

## LLL_max_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0_3ph | 0.25691 | 0.25691 | 0 | 0 | 0.17799 | 0.17799 | 0.16205 | -0.060769 | 0.10948 | -0.041057 | -34.1218 | 145.8782 | 1.0987 | 0.41203 | -0.078404 | -0.078402
Line_1_3-1ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.41203 | 0.41203 | -0.078402 | -0.0784
Line_2_3-1ph | 0.25691 | 0.25691 | 0 | 0.37485 | 0.17799 | 0.17799 | 0.060769 | -1e-07 | 0.041057 | -1e-07 | -34.1218 | 145.8782 | 0.41203 | 0 | -0.078402 | 0

## LLL_max_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0_3ph | 0.030144 | 0.030144 | 0 | 0 | 0.020885 | 0.020885 | 0.015861 | -0.014467 | 0.015137 | -0.014195 | -43.6704 | 136.3296 | 1.0498 | 0.97048 | -0.0077914 | 0.78712
Line_1_3-1ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97048 | 0.97048 | 0.78712 | 0.78712
Line_2_3-1ph | 0.030144 | 0.030144 | 0 | 0.043982 | 0.020885 | 0.020885 | 0.014467 | -0.01363 | 0.014195 | -0.01363 | -43.6704 | 136.3296 | 0.97048 | 0.92298 | 0.78712 | 1.3296

## LLL_max_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0_3ph | 0.03158 | 0.03158 | 0 | 0 | 0.021879 | 0.021879 | 0.017407 | -0.015877 | 0.016613 | -0.015579 | -43.6708 | 136.3292 | 1.0998 | 1.0167 | -0.0081624 | 0.78675
Line_1_3-1ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0167 | 1.0167 | 0.78675 | 0.78675
Line_2_3-1ph | 0.03158 | 0.03158 | 0 | 0.046076 | 0.021879 | 0.021879 | 0.015877 | -0.014959 | 0.015579 | -0.014959 | -43.6708 | 136.3292 | 1.0167 | 0.96692 | 0.78675 | 1.3292

## LLL_min_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0_3ph | 0.13164 | 0.13164 | 0 | 0 | 0.091205 | 0.091205 | 0.081693 | -0.030635 | 0.028746 | -0.01078 | -19.4452 | 160.5548 | 0.94954 | 0.35608 | -0.059154 | -0.059152
Line_1_3-1ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35608 | 0.35608 | -0.059152 | -0.05915
Line_2_3-1ph | 0.13164 | 0.13164 | 0 | 0.18993 | 0.091205 | 0.091205 | 0.030635 | -1e-07 | 0.01078 | -1e-07 | -19.4451 | 160.5549 | 0.35608 | 0 | -0.059152 | 0

## LLL_min_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0_3ph | 0.12472 | 0.12472 | 0 | 0 | 0.086407 | 0.086407 | 0.073323 | -0.027496 | 0.025801 | -0.0096754 | -19.442 | 160.558 | 0.89959 | 0.33735 | -0.056042 | -0.05604
Line_1_3-1ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33735 | 0.33735 | -0.05604 | -0.056038
Line_2_3-1ph | 0.12472 | 0.12472 | 0 | 0.17994 | 0.086407 | 0.086407 | 0.027496 | -1e-07 | 0.0096754 | -1e-07 | -19.442 | 160.558 | 0.33735 | 0 | -0.05604 | 0

## LLL_min_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0_3ph | 0.025497 | 0.025497 | 0 | 0 | 0.017665 | 0.017665 | 0.012816 | -0.010901 | 0.01083 | -0.010156 | -40.2074 | 139.7926 | 0.94985 | 0.8434 | -0.0088029 | 2.7668
Line_1_3-1ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8434 | 0.8434 | 2.7668 | 2.7668
Line_2_3-1ph | 0.025497 | 0.025497 | 0 | 0.036786 | 0.017665 | 0.017665 | 0.010901 | -0.0097514 | 0.010156 | -0.0097514 | -40.2074 | 139.7926 | 0.8434 | 0.78068 | 2.7668 | 4.7926

## LLL_min_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0_3ph | 0.024155 | 0.024155 | 0 | 0 | 0.016735 | 0.016735 | 0.011503 | -0.0097835 | 0.0097199 | -0.009115 | -40.2069 | 139.7931 | 0.89986 | 0.79901 | -0.0083396 | 2.7672
Line_1_3-1ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.79901 | 0.79901 | 2.7672 | 2.7672
Line_2_3-1ph | 0.024155 | 0.024155 | 0 | 0.034851 | 0.016735 | 0.016735 | 0.0097835 | -0.0087521 | 0.009115 | -0.0087521 | -40.2069 | 139.7931 | 0.79901 | 0.7396 | 2.7672 | 4.7931

## LL_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0_3ph | 0 | 0.21239 | 0.21239 | 0 | 0.21239 | 0.21239 | 0 | 0.049049 | 0.049049 | 0 | 0.049049 | 0.049049 | 1.2143e-18 | 0.051361 | 0.022474 | -2.4286e-18 | -0.028288 | 0.00059968 | -2.4286e-18 | 0.0036232 | 0.046261 | -2.9474e-34 | 0.011965 | -0.030672 | 0 | -124.1183 | 55.8817 | 0 | 55.8817 | -124.1183 | 1.05 | 1.0497 | 1.0485 | 1.05 | 0.62619 | 0.62545 | 7.3173e-16 | -120.0831 | 119.9709 | 6.9534e-15 | -147.0462 | 147.0018
Line_1_3-1ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0418e-23 | -7.0943e-10 | -7.1114e-10 | -6.0418e-23 | 7.0943e-10 | 7.1114e-10 | -4.906e-25 | 1.0962e-09 | -1.0933e-09 | 4.906e-25 | -1.0962e-09 | 1.0933e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.62619 | 0.62545 | 1.05 | 0.62619 | 0.62545 | 6.9534e-15 | -147.0462 | 147.0018 | 6.9534e-15 | -147.0462 | 147.0018
Line_2_3-1ph | 0 | 0.21239 | 0.21239 | 0 | 0.21239 | 0.21239 | 0 | 0.049049 | 0.049049 | 0 | 0.049049 | 0.049049 | 6.0418e-23 | 0.028288 | -0.00059967 | -6.0418e-23 | -0.014444 | 0.014444 | -4.906e-25 | -0.011965 | 0.030672 | 4.906e-25 | 0.021319 | -0.021319 | 0 | -124.1182 | 55.8818 | 0 | 55.8818 | -124.1182 | 1.05 | 0.62619 | 0.62545 | 1.05 | 0.525 | 0.525 | 6.9534e-15 | -147.0462 | 147.0018 | 6.9534e-15 | -180 | 180

## LL_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0_3ph | 0 | 0.22249 | 0.22249 | 0 | 0.22249 | 0.22249 | 0 | 0.051382 | 0.051382 | 0 | 0.051382 | 0.051382 | 6.9252e-35 | 0.056366 | 0.02466 | -7.0891e-34 | -0.031045 | 0.00066036 | -5.0885e-18 | 0.0039758 | 0.050766 | 2.5443e-18 | 0.013131 | -0.033659 | 0 | -124.1218 | 55.8782 | 0 | 55.8782 | -124.1218 | 1.1 | 1.0997 | 1.0984 | 1.1 | 0.65602 | 0.6552 | 7.7977e-16 | -120.087 | 119.9695 | 1.5964e-14 | -147.0486 | 147.0021
Line_1_3-1ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.4293e-24 | -7.7854e-10 | -7.8051e-10 | 7.4293e-24 | 7.7854e-10 | 7.8051e-10 | -1.2362e-24 | 1.2032e-09 | -1.1998e-09 | 1.2362e-24 | -1.2032e-09 | 1.1998e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.65602 | 0.6552 | 1.1 | 0.65602 | 0.6552 | 1.5964e-14 | -147.0486 | 147.0021 | 1.5964e-14 | -147.0486 | 147.0021
Line_2_3-1ph | 0 | 0.22249 | 0.22249 | 0 | 0.22249 | 0.22249 | 0 | 0.051382 | 0.051382 | 0 | 0.051382 | 0.051382 | -7.4293e-24 | 0.031045 | -0.00066035 | 7.4293e-24 | -0.015853 | 0.015853 | -1.2362e-24 | -0.013131 | 0.033659 | 1.2362e-24 | 0.023395 | -0.023395 | 0 | -124.1218 | 55.8782 | 0 | 55.8782 | -124.1218 | 1.1 | 0.65602 | 0.6552 | 1.1 | 0.55 | 0.55 | 1.5964e-14 | -147.0486 | 147.0021 | 1.5964e-14 | -180 | 180

## LL_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0_3ph | 0 | 0.046559 | 0.046559 | 0 | 0.046559 | 0.046559 | 0 | 0.010752 | 0.010752 | 0 | 0.010752 | 0.010752 | -3.0358e-19 | 0.011017 | 0.0033705 | 3.0358e-19 | -0.0099078 | -0.0022617 | 9.1073e-19 | 0.0024646 | 0.010771 | -6.0715e-19 | -0.0017155 | -0.010022 | 0 | -132.6282 | 47.3718 | 0 | 47.3718 | -132.6282 | 1.05 | 1.0499 | 1.0497 | 1.05 | 0.93515 | 0.95554 | 1.8973e-16 | -120.0175 | 119.9963 | 1.5656e-15 | -122.8049 | 124.6551
Line_1_3-1ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3344e-23 | -3.8948e-10 | -3.1883e-10 | -1.3344e-23 | 3.8948e-10 | 3.1883e-10 | -1.1046e-25 | 1.7618e-10 | -2.9856e-10 | 1.1046e-25 | -1.7618e-10 | 2.9856e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.93515 | 0.95554 | 1.05 | 0.93515 | 0.95554 | 1.5656e-15 | -122.8049 | 124.6551 | 1.5656e-15 | -122.8049 | 124.6551
Line_2_3-1ph | 0 | 0.046559 | 0.046559 | 0 | 0.046559 | 0.046559 | 0 | 0.010752 | 0.010752 | 0 | 0.010752 | 0.010752 | 1.3344e-23 | 0.0099078 | 0.0022617 | -1.3344e-23 | -0.0092425 | -0.0015964 | -1.1046e-25 | 0.0017155 | 0.010022 | 1.1046e-25 | -0.001266 | -0.0095729 | 0 | -132.6282 | 47.3718 | 0 | 47.3718 | -132.6282 | 1.05 | 0.93515 | 0.95554 | 1.05 | 0.8676 | 0.90259 | 1.5656e-15 | -122.8049 | 124.6551 | 1.5656e-15 | -124.8283 | 127.904

## LL_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0_3ph | 0 | 0.048776 | 0.048776 | 0 | 0.048776 | 0.048776 | 0 | 0.011264 | 0.011264 | 0 | 0.011264 | 0.011264 | 6.3607e-19 | 0.012091 | 0.003699 | -3.1803e-19 | -0.010874 | -0.0024821 | 6.3607e-19 | 0.0027049 | 0.011821 | -6.3607e-19 | -0.0018827 | -0.010999 | 0 | -132.6289 | 47.3711 | 0 | 47.3711 | -132.6289 | 1.1 | 1.0999 | 1.0996 | 1.1 | 0.97968 | 1.001 | 1.995e-16 | -120.0184 | 119.9961 | 4.4897e-15 | -122.8057 | 124.655
Line_1_3-1ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.9717e-24 | -4.2747e-10 | -3.4996e-10 | 1.9717e-24 | 4.2747e-10 | 3.4996e-10 | -3.4766e-25 | 1.9342e-10 | -3.2766e-10 | 3.4766e-25 | -1.9342e-10 | 3.2766e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.97968 | 1.001 | 1.1 | 0.97968 | 1.001 | 4.4897e-15 | -122.8057 | 124.655 | 4.4897e-15 | -122.8057 | 124.655
Line_2_3-1ph | 0 | 0.048776 | 0.048776 | 0 | 0.048776 | 0.048776 | 0 | 0.011264 | 0.011264 | 0 | 0.011264 | 0.011264 | -1.9717e-24 | 0.010874 | 0.0024821 | 1.9717e-24 | -0.010144 | -0.0017519 | -3.4766e-25 | 0.0018827 | 0.010999 | 3.4766e-25 | -0.0013894 | -0.010506 | 0 | -132.6289 | 47.3711 | 0 | 47.3711 | -132.6289 | 1.1 | 0.97968 | 1.001 | 1.1 | 0.90891 | 0.94556 | 4.4897e-15 | -122.8057 | 124.655 | 4.4897e-15 | -124.8292 | 127.9039

## LL_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0_3ph | 0 | 0.11401 | 0.11401 | 0 | 0.11401 | 0.11401 | 0 | 0.026329 | 0.026329 | 0 | 0.026329 | 0.026329 | 5.4933e-19 | 0.024586 | 0.01626 | -2.7466e-19 | -0.011822 | -0.0034954 | 3.1377e-36 | -0.0046062 | 0.018979 | -5.7764e-35 | 0.0090978 | -0.014488 | 0 | -109.4452 | 70.5548 | 0 | 70.5548 | -109.4452 | 0.95 | 0.95008 | 0.94923 | 0.95 | 0.56659 | 0.56605 | 3.2726e-16 | -120.0564 | 119.9677 | 1.205e-14 | -147.0257 | 146.9906
Line_1_3-1ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.0368e-23 | -5.8102e-10 | -5.8213e-10 | 3.0368e-23 | 5.8102e-10 | 5.8213e-10 | -6.9594e-25 | 8.9679e-10 | -8.9487e-10 | 6.9594e-25 | -8.9679e-10 | 8.9487e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.56659 | 0.56605 | 0.95 | 0.56659 | 0.56605 | 1.205e-14 | -147.0257 | 146.9906 | 1.205e-14 | -147.0257 | 146.9906
Line_2_3-1ph | 0 | 0.11401 | 0.11401 | 0 | 0.11401 | 0.11401 | 0 | 0.026329 | 0.026329 | 0 | 0.026329 | 0.026329 | -3.0368e-23 | 0.011822 | 0.0034954 | 3.0368e-23 | -0.0041633 | 0.0041633 | -6.9594e-25 | -0.0090978 | 0.014488 | 6.9594e-25 | 0.011793 | -0.011793 | 0 | -109.4451 | 70.5549 | 0 | 70.5549 | -109.4451 | 0.95 | 0.56659 | 0.56605 | 0.95 | 0.475 | 0.475 | 1.205e-14 | -147.0257 | 146.9906 | 1.205e-14 | -180 | 180

## LL_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0_3ph | 0 | 0.10801 | 0.10801 | 0 | 0.10801 | 0.10801 | 0 | 0.024943 | 0.024943 | 0 | 0.024943 | 0.024943 | -5.2042e-19 | 0.022067 | 0.014595 | 5.2042e-19 | -0.01061 | -0.0031379 | -2.8974e-36 | -0.0041343 | 0.017035 | 7.7424e-35 | 0.0081657 | -0.013003 | 0 | -109.442 | 70.558 | 0 | 70.558 | -109.442 | 0.9 | 0.90007 | 0.89931 | 0.9 | 0.53676 | 0.53628 | 3.1899e-16 | -120.0534 | 119.9694 | 8.5241e-15 | -147.0241 | 146.9909
Line_1_3-1ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.6984e-23 | -5.215e-10 | -5.2245e-10 | 2.6984e-23 | 5.215e-10 | 5.2245e-10 | -4.4186e-25 | 8.0482e-10 | -8.0318e-10 | 4.4186e-25 | -8.0482e-10 | 8.0318e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.53676 | 0.53628 | 0.9 | 0.53676 | 0.53628 | 8.5241e-15 | -147.0241 | 146.9909 | 8.5241e-15 | -147.0241 | 146.9909
Line_2_3-1ph | 0 | 0.10801 | 0.10801 | 0 | 0.10801 | 0.10801 | 0 | 0.024944 | 0.024944 | 0 | 0.024944 | 0.024944 | -2.6984e-23 | 0.01061 | 0.0031379 | 2.6984e-23 | -0.0037361 | 0.0037361 | -4.4186e-25 | -0.0081657 | 0.013003 | 4.4186e-25 | 0.010585 | -0.010585 | 0 | -109.442 | 70.558 | 0 | 70.558 | -109.442 | 0.9 | 0.53676 | 0.53628 | 0.9 | 0.45 | 0.45 | 8.5241e-15 | -147.0241 | 146.9909 | 8.5241e-15 | -180 | 180

## LL_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0_3ph | 0 | 0.037327 | 0.037327 | 0 | 0.037327 | 0.037327 | 0 | 0.0086204 | 0.0086204 | 0 | 0.0086204 | 0.0086204 | -1.3733e-19 | 0.0081301 | 0.0032153 | 0 | -0.0067618 | -0.0018469 | -4.139e-37 | 0.00097844 | 0.007529 | 0 | -0.00049694 | -0.0070475 | 0 | -126.8805 | 53.1195 | 0 | 53.1195 | -126.8805 | 0.95 | 0.94993 | 0.94971 | 0.95 | 0.78651 | 0.84515 | 1.7268e-16 | -120.0181 | 119.9945 | -8.8317e-16 | -122.6772 | 128.4344
Line_1_3-1ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.1316e-23 | -4.685e-10 | -2.9308e-10 | 1.1316e-23 | 4.685e-10 | 2.9308e-10 | 5.1008e-26 | 1.2797e-10 | -4.3181e-10 | -5.1008e-26 | -1.2797e-10 | 4.3181e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.78651 | 0.84515 | 0.95 | 0.78651 | 0.84515 | -8.8317e-16 | -122.6772 | 128.4344 | -8.8316e-16 | -122.6772 | 128.4344
Line_2_3-1ph | 0 | 0.037327 | 0.037327 | 0 | 0.037327 | 0.037327 | 0 | 0.0086204 | 0.0086204 | 0 | 0.0086204 | 0.0086204 | -1.1316e-23 | 0.0067618 | 0.0018469 | 1.1316e-23 | -0.0059407 | -0.0010259 | 5.1008e-26 | 0.00049694 | 0.0070475 | -5.1008e-26 | -0.00020804 | -0.0067586 | 0 | -126.8805 | 53.1195 | 0 | 53.1195 | -126.8805 | 0.95 | 0.78651 | 0.84515 | 0.95 | 0.68957 | 0.79301 | -8.8317e-16 | -122.6772 | 128.4344 | -8.8316e-16 | -124.8749 | 134.4883

## LL_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0_3ph | 0 | 0.035363 | 0.035363 | 0 | 0.035363 | 0.035363 | 0 | 0.0081668 | 0.0081668 | 0 | 0.0081668 | 0.0081668 | 2.6021e-19 | 0.007297 | 0.0028859 | -1.301e-19 | -0.0060688 | -0.0016578 | 5.2042e-19 | 0.00087819 | 0.0067575 | -5.2042e-19 | -0.00044602 | -0.0063254 | 0 | -126.8796 | 53.1204 | 0 | 53.1204 | -126.8796 | 0.9 | 0.89994 | 0.89974 | 0.9 | 0.74511 | 0.80068 | 1.6492e-16 | -120.0171 | 119.9947 | 6.0375e-15 | -122.6763 | 128.4346
Line_1_3-1ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -9.2105e-24 | -4.2048e-10 | -2.6301e-10 | 9.2105e-24 | 4.2048e-10 | 2.6301e-10 | -3.1296e-25 | 1.1481e-10 | -3.8756e-10 | 3.1296e-25 | -1.1481e-10 | 3.8756e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.74511 | 0.80068 | 0.9 | 0.74511 | 0.80068 | 6.0375e-15 | -122.6763 | 128.4346 | 6.0375e-15 | -122.6763 | 128.4346
Line_2_3-1ph | 0 | 0.035363 | 0.035363 | 0 | 0.035363 | 0.035363 | 0 | 0.0081668 | 0.0081668 | 0 | 0.0081668 | 0.0081668 | -9.2105e-24 | 0.0060688 | 0.0016578 | 9.2105e-24 | -0.0053319 | -0.00092086 | -3.1296e-25 | 0.00044602 | 0.0063254 | 3.1296e-25 | -0.00018673 | -0.0060661 | 0 | -126.8796 | 53.1204 | 0 | 53.1204 | -126.8796 | 0.9 | 0.74511 | 0.80068 | 0.9 | 0.65328 | 0.75128 | 6.0375e-15 | -122.6763 | 128.4346 | 6.0375e-15 | -124.8739 | 134.4884

## LG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0_3ph | 0.15095 | 3.5922e-05 | 3.5922e-05 | 0.15093 | 0 | 0 | 0.03486 | 8.2959e-06 | 8.2959e-06 | 0.034855 | 0 | 0 | 0.030314 | 7.5467e-06 | -7.5406e-06 | -0.0069909 | -4.1199e-09 | -4.1318e-09 | 0.020471 | -4.3501e-06 | -4.3606e-06 | -0.0047231 | -4.0427e-09 | 4.0358e-09 | -34.0767 | -90.0397 | -90.0397 | 145.9346 | 0 | 0 |  | 1.0493 | 1.05 | 1.05 | 0.24205 | 1.2994 | 1.3003 | -0.046075 | -120 | 120 | -0.022028 | -135.6263 | 135.5888
Line_1_3-1ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.1708e-10 | 1.3733e-09 | 1.3773e-09 | 7.1708e-10 | -1.3733e-09 | -1.3773e-09 | 3.5827e-13 | 1.3476e-09 | -1.3453e-09 | -3.5821e-13 | -1.3476e-09 | 1.3453e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.24205 | 1.2994 | 1.3003 | 0.24205 | 1.2994 | 1.3003 | -0.022028 | -135.6263 | 135.5888 | -0.022024 | -135.6263 | 135.5888
Line_2_3-1ph | 0.15093 | 0 | 0 | 0.15093 | 0 | 0 | 0.034855 | 0 | 0 | 0.034855 | 0 | 0 | 0.0069909 | 1.3733e-09 | 1.3773e-09 | -8.2582e-18 | -1.3733e-09 | -1.3773e-09 | 0.0047231 | 1.3476e-09 | -1.3453e-09 | 1.2143e-15 | -1.3476e-09 | 1.3453e-09 | -34.0654 | 0 | 0 | 145.9346 | 0 | 0 |  | 0.24205 | 1.2994 | 1.3003 | 0 | 1.2994 | 1.3003 | -0.022028 | -135.6263 | 135.5888 | 0 | -135.6263 | 135.5888

## LG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0_3ph | 0.15813 | 3.7633e-05 | 3.7633e-05 | 0.15811 | 0 | 0 | 0.036519 | 8.691e-06 | 8.691e-06 | 0.036514 | 0 | 0 | 0.033267 | 8.2825e-06 | -8.276e-06 | -0.007672 | -4.5212e-09 | -4.5346e-09 | 0.022465 | -4.7744e-06 | -4.7857e-06 | -0.0051833 | -4.4368e-09 | 4.4291e-09 | -34.0789 | -90.039 | -90.039 | 145.9324 | 0 | 0 |  | 1.0992 | 1.1 | 1.1 | 0.25357 | 1.3613 | 1.3622 | -0.048267 | -120 | 120 | -0.024221 | -135.6264 | 135.5879
Line_1_3-1ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.8698e-10 | 1.5071e-09 | 1.5115e-09 | 7.8698e-10 | -1.5071e-09 | -1.5115e-09 | 4.3233e-13 | 1.4789e-09 | -1.4764e-09 | -4.3226e-13 | -1.4789e-09 | 1.4764e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.25357 | 1.3613 | 1.3622 | 0.25357 | 1.3613 | 1.3622 | -0.024221 | -135.6264 | 135.5879 | -0.024216 | -135.6264 | 135.5879
Line_2_3-1ph | 0.15811 | 0 | 0 | 0.15811 | 0 | 0 | 0.036514 | 0 | 0 | 0.036514 | 0 | 0 | 0.007672 | 1.5071e-09 | 1.5115e-09 | 4.0838e-17 | -1.5071e-09 | -1.5115e-09 | 0.0051833 | 1.4789e-09 | -1.4764e-09 | 1.3435e-15 | -1.4789e-09 | 1.4764e-09 | -34.0676 | 0 | 0 | 145.9324 | 0 | 0 |  | 0.25357 | 1.3613 | 1.3622 | 0 | 1.3613 | 1.3622 | -0.024221 | -135.6264 | 135.5879 | 0 | -135.6264 | 135.5879

## LG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0_3ph | 0.028024 | 6.6691e-06 | 6.6691e-06 | 0.028021 | 0 | 0 | 0.0064719 | 1.5402e-06 | 1.5402e-06 | 0.0064711 | 0 | 0 | 0.0049704 | 1.5093e-06 | -1.2576e-06 | -0.0041667 | -3.7213e-10 | -6.0678e-10 | 0.0046326 | -5.807e-07 | -1.0168e-06 | -0.0040885 | -8.0841e-10 | 6.7294e-10 | -42.9931 | -98.9561 | -98.9561 | 137.0182 | 0 | 0 |  | 1.0498 | 1.05 | 1.05 | 0.90211 | 1.0791 | 1.0987 | -0.0073427 | -120 | 120 | 1.4757 | -123.7188 | 123.0397
Line_1_3-1ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.8803e-10 | 1.2404e-10 | 2.0226e-10 | 4.8803e-10 | -1.2404e-10 | -2.0226e-10 | -8.9443e-11 | 2.6947e-10 | -2.2431e-10 | 8.9443e-11 | -2.6947e-10 | 2.2431e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.90211 | 1.0791 | 1.0987 | 0.90211 | 1.0791 | 1.0987 | 1.4757 | -123.7188 | 123.0397 | 1.4757 | -123.7188 | 123.0397
Line_2_3-1ph | 0.028021 | 0 | 0 | 0.028021 | 0 | 0 | 0.0064711 | 0 | 0 | 0.0064711 | 0 | 0 | 0.0041667 | 1.2404e-10 | 2.0226e-10 | -0.0039257 | -1.2404e-10 | -2.0226e-10 | 0.0040885 | 2.6947e-10 | -2.2431e-10 | -0.0039257 | -2.6947e-10 | 2.2431e-10 | -42.9818 | 0 | 0 | 137.0182 | 0 | 0 |  | 0.90211 | 1.0791 | 1.0987 | 0.85795 | 1.0791 | 1.0987 | 1.4757 | -123.7188 | 123.0397 | 2.0182 | -123.7188 | 123.0397

## LG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0_3ph | 0.029359 | 6.987e-06 | 6.987e-06 | 0.029355 | 0 | 0 | 0.0067801 | 1.6136e-06 | 1.6136e-06 | 0.0067792 | 0 | 0 | 0.0054549 | 1.6565e-06 | -1.3803e-06 | -0.0045729 | -4.0841e-10 | -6.6594e-10 | 0.0050843 | -6.3742e-07 | -1.1159e-06 | -0.0044871 | -8.8723e-10 | 7.3854e-10 | -42.9935 | -98.9536 | -98.9536 | 137.0178 | 0 | 0 |  | 1.0998 | 1.1 | 1.1 | 0.94506 | 1.1305 | 1.151 | -0.0076923 | -120 | 120 | 1.4753 | -123.7188 | 123.0397
Line_1_3-1ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.3564e-10 | 1.3614e-10 | 2.2198e-10 | 5.3564e-10 | -1.3614e-10 | -2.2198e-10 | -9.814e-11 | 2.9574e-10 | -2.4618e-10 | 9.814e-11 | -2.9574e-10 | 2.4618e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.94506 | 1.1305 | 1.151 | 0.94506 | 1.1305 | 1.151 | 1.4753 | -123.7188 | 123.0397 | 1.4753 | -123.7188 | 123.0397
Line_2_3-1ph | 0.029355 | 0 | 0 | 0.029355 | 0 | 0 | 0.0067792 | 0 | 0 | 0.0067792 | 0 | 0 | 0.0045729 | 1.3614e-10 | 2.2198e-10 | -0.0043085 | -1.3614e-10 | -2.2198e-10 | 0.0044871 | 2.9574e-10 | -2.4618e-10 | -0.0043085 | -2.9574e-10 | 2.4618e-10 | -42.9822 | 0 | 0 | 137.0178 | 0 | 0 |  | 0.94506 | 1.1305 | 1.151 | 0.8988 | 1.1305 | 1.151 | 1.4753 | -123.7188 | 123.0397 | 2.0178 | -123.7188 | 123.0397

## LG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0_3ph | 0.081002 | 3.2499e-05 | 3.2499e-05 | 0.080992 | 0 | 0 | 0.018707 | 7.5053e-06 | 7.5053e-06 | 0.018704 | 0 | 0 | 0.01676 | 6.1783e-06 | -6.1713e-06 | -0.0038652 | -3.374e-09 | -3.3852e-09 | 0.0058924 | -3.559e-06 | -3.571e-06 | -0.0013601 | -3.3112e-09 | 3.3048e-09 | -19.4062 | -90.0557 | -90.0557 | 160.6155 | 0 | 0 |  | 0.94972 | 0.95 | 0.95 | 0.21907 | 1.1757 | 1.1766 | -0.036403 | -120 | 120 | 0.0014678 | -135.6347 | 135.5917
Line_1_3-1ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.8713e-10 | 1.1247e-09 | 1.1284e-09 | 5.8713e-10 | -1.1247e-09 | -1.1284e-09 | -1.9563e-14 | 1.1037e-09 | -1.1016e-09 | 1.9609e-14 | -1.1037e-09 | 1.1016e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.21907 | 1.1757 | 1.1766 | 0.21907 | 1.1757 | 1.1766 | 0.0014678 | -135.6347 | 135.5917 | 0.0014723 | -135.6347 | 135.5917
Line_2_3-1ph | 0.080992 | 0 | 0 | 0.080992 | 0 | 0 | 0.018704 | 0 | 0 | 0.018704 | 0 | 0 | 0.0038652 | 1.1247e-09 | 1.1284e-09 | 2.4535e-18 | -1.1247e-09 | -1.1284e-09 | 0.0013601 | 1.1037e-09 | -1.1016e-09 | 3.1837e-16 | -1.1037e-09 | 1.1016e-09 | -19.3845 | 0 | 0 | 160.6155 | 0 | 0 |  | 0.21907 | 1.1757 | 1.1766 | 0 | 1.1757 | 1.1766 | 0.0014678 | -135.6347 | 135.5917 | 0 | -135.6347 | 135.5917

## LG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0_3ph | 0.07674 | 3.0788e-05 | 3.0788e-05 | 0.07673 | 0 | 0 | 0.017722 | 7.1102e-06 | 7.1102e-06 | 0.01772 | 0 | 0 | 0.015043 | 5.545e-06 | -5.5387e-06 | -0.0034692 | -3.0283e-09 | -3.0382e-09 | 0.0052886 | -3.1942e-06 | -3.2051e-06 | -0.0012207 | -2.9718e-09 | 2.9662e-09 | -19.4043 | -90.0563 | -90.0563 | 160.6174 | 0 | 0 |  | 0.89975 | 0.9 | 0.9 | 0.20755 | 1.1139 | 1.1147 | -0.034488 | -120 | 120 | 0.0033831 | -135.6345 | 135.5923
Line_1_3-1ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.2696e-10 | 1.0094e-09 | 1.0127e-09 | 5.2696e-10 | -1.0094e-09 | -1.0127e-09 | -4.0453e-14 | 9.9061e-10 | -9.8872e-10 | 4.0495e-14 | -9.9061e-10 | 9.8872e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.20755 | 1.1139 | 1.1147 | 0.20755 | 1.1139 | 1.1147 | 0.0033831 | -135.6345 | 135.5923 | 0.0033877 | -135.6345 | 135.5923
Line_2_3-1ph | 0.07673 | 0 | 0 | 0.07673 | 0 | 0 | 0.01772 | 0 | 0 | 0.01772 | 0 | 0 | 0.0034692 | 1.0094e-09 | 1.0127e-09 | -7.0408e-18 | -1.0094e-09 | -1.0127e-09 | 0.0012207 | 9.9061e-10 | -9.8872e-10 | 2.9862e-16 | -9.9061e-10 | 9.8872e-10 | -19.3826 | 0 | 0 | 160.6174 | 0 | 0 |  | 0.20755 | 1.1139 | 1.1147 | 0 | 1.1139 | 1.1147 | 0.0033831 | -135.6345 | 135.5923 | 0 | -135.6345 | 135.5923

## LG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0_3ph | 0.022891 | 9.1841e-06 | 9.1841e-06 | 0.022888 | 0 | 0 | 0.0052865 | 2.121e-06 | 2.121e-06 | 0.0052858 | 0 | 0 | 0.0039572 | 1.9756e-06 | -1.3311e-06 | -0.002928 | -3.2899e-10 | -9.2826e-10 | 0.0030912 | -3.9642e-07 | -1.5127e-06 | -0.0027279 | -1.0585e-09 | 7.1252e-10 | -38.004 | -108.6535 | -108.6535 | 142.0177 | 0 | 0 |  | 0.94987 | 0.95 | 0.95 | 0.7571 | 0.97552 | 1.0299 | -0.0082109 | -120 | 120 | 4.9918 | -125.96 | 123.7961
Line_1_3-1ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.255e-10 | 1.0966e-10 | 3.0942e-10 | 5.255e-10 | -1.0966e-10 | -3.0942e-10 | -2.2947e-10 | 3.5284e-10 | -2.3751e-10 | 2.2947e-10 | -3.5284e-10 | 2.3751e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.7571 | 0.97552 | 1.0299 | 0.7571 | 0.97552 | 1.0299 | 4.9918 | -125.96 | 123.7961 | 4.9918 | -125.96 | 123.7961
Line_2_3-1ph | 0.022888 | 0 | 0 | 0.022888 | 0 | 0 | 0.0052858 | 0 | 0 | 0.0052858 | 0 | 0 | 0.002928 | 1.0966e-10 | 3.0942e-10 | -0.0026193 | -1.0966e-10 | -3.0942e-10 | 0.0027279 | 3.5284e-10 | -2.3751e-10 | -0.0026193 | -3.5284e-10 | 2.3751e-10 | -37.9823 | 0 | 0 | 142.0177 | 0 | 0 |  | 0.7571 | 0.97552 | 1.0299 | 0.7008 | 0.97552 | 1.0299 | 4.9918 | -125.96 | 123.7961 | 7.0177 | -125.96 | 123.7961

## LG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0_3ph | 0.021686 | 8.7006e-06 | 8.7006e-06 | 0.021684 | 0 | 0 | 0.0050083 | 2.0093e-06 | 2.0093e-06 | 0.0050076 | 0 | 0 | 0.0035517 | 1.7731e-06 | -1.1946e-06 | -0.0026279 | -2.9528e-10 | -8.3312e-10 | 0.0027744 | -3.5572e-07 | -1.3577e-06 | -0.0024484 | -9.5002e-10 | 6.395e-10 | -38.0036 | -108.6556 | -108.6556 | 142.0181 | 0 | 0 |  | 0.89988 | 0.9 | 0.9 | 0.71726 | 0.92418 | 0.97565 | -0.0077788 | -120 | 120 | 4.9923 | -125.96 | 123.7962
Line_1_3-1ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.7162e-10 | 9.8425e-11 | 2.7771e-10 | 4.7162e-10 | -9.8425e-11 | -2.7771e-10 | -2.0597e-10 | 3.1667e-10 | -2.1317e-10 | 2.0597e-10 | -3.1667e-10 | 2.1317e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.71726 | 0.92418 | 0.97565 | 0.71726 | 0.92418 | 0.97565 | 4.9923 | -125.96 | 123.7962 | 4.9923 | -125.96 | 123.7962
Line_2_3-1ph | 0.021684 | 0 | 0 | 0.021684 | 0 | 0 | 0.0050076 | 0 | 0 | 0.0050076 | 0 | 0 | 0.0026279 | 9.8425e-11 | 2.7771e-10 | -0.0023509 | -9.8425e-11 | -2.7771e-10 | 0.0024484 | 3.1667e-10 | -2.1317e-10 | -0.0023509 | -3.1667e-10 | 2.1317e-10 | -37.9819 | 0 | 0 | 142.0181 | 0 | 0 |  | 0.71726 | 0.92418 | 0.97565 | 0.66392 | 0.92418 | 0.97565 | 4.9923 | -125.96 | 123.7962 | 7.0181 | -125.96 | 123.7962

## LLG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0_3ph | 2.5944e-05 | 0.21932 | 0.21923 | 0 | 0.21934 | 0.2192 | 5.9916e-06 | 0.050651 | 0.050628 | 0 | 0.050655 | 0.050622 | 1.7815e-09 | 0.050424 | 0.034362 | -4.3043e-09 | -0.014765 | -0.014746 | -6.2911e-06 | 0.016805 | 0.040474 | -3.5887e-12 | -0.0099755 | -0.0099627 | 89.9838 | -138.511 | 70.2812 | 0 | 41.494 | -109.7211 |  | 1.05 | 1.0493 | 1.0487 | 1.3417 | 0.35178 | 0.35155 | -1.0277e-06 | -120.0794 | 119.9506 | -0.013269 | -104.4626 | 104.3223
Line_1_3-1ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4348e-09 | -8.5111e-10 | -8.4996e-10 | -1.4348e-09 | 8.5111e-10 | 8.4996e-10 | 1.1962e-12 | -3.6278e-10 | 3.6574e-10 | -1.1962e-12 | 3.6278e-10 | -3.6574e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3417 | 0.35178 | 0.35155 | 1.3417 | 0.35178 | 0.35155 | -0.013269 | -104.4626 | 104.3223 | -0.013269 | -104.4626 | 104.3223
Line_2_3-1ph | 0 | 0.21934 | 0.2192 | 0 | 0.21934 | 0.2192 | 0 | 0.050655 | 0.050622 | 0 | 0.050655 | 0.050622 | 1.4348e-09 | 0.014765 | 0.014746 | -1.4348e-09 | -5.8049e-16 | -2.2595e-15 | 1.1962e-12 | 0.0099755 | 0.0099627 | -1.1962e-12 | 3.7081e-16 | 2.4081e-16 | 0 | -138.506 | 70.2789 | 0 | 41.494 | -109.7211 |  | 1.3417 | 0.35178 | 0.35155 | 1.3417 | 0 | 0 | -0.013269 | -104.4626 | 104.3223 | -0.013269 | 0 | 0

## LLG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0_3ph | 2.718e-05 | 0.22976 | 0.22965 | 0 | 0.22978 | 0.22963 | 6.277e-06 | 0.053061 | 0.053036 | 0 | 0.053065 | 0.05303 | 1.8026e-09 | 0.055336 | 0.037707 | -4.7238e-09 | -0.016204 | -0.016182 | -6.9047e-06 | 0.018442 | 0.044416 | -4.0407e-12 | -0.010947 | -0.010933 | 89.985 | -138.5149 | 70.2781 | 0 | 41.4902 | -109.7242 |  | 1.1 | 1.0993 | 1.0986 | 1.4055 | 0.36851 | 0.36827 | -1.0764e-06 | -120.0832 | 119.9482 | -0.013613 | -104.4664 | 104.3193
Line_1_3-1ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5746e-09 | -9.341e-10 | -9.3279e-10 | -1.5746e-09 | 9.341e-10 | 9.3279e-10 | 1.3469e-12 | -3.9804e-10 | 4.0146e-10 | -1.3469e-12 | 3.9804e-10 | -4.0146e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.4055 | 0.36851 | 0.36827 | 1.4055 | 0.36851 | 0.36827 | -0.013613 | -104.4664 | 104.3193 | -0.013613 | -104.4664 | 104.3193
Line_2_3-1ph | 0 | 0.22978 | 0.22963 | 0 | 0.22978 | 0.22963 | 0 | 0.053065 | 0.05303 | 0 | 0.053065 | 0.05303 | 1.5746e-09 | 0.016204 | 0.016182 | -1.5746e-09 | 7.3314e-17 | -1.674e-15 | 1.3469e-12 | 0.010947 | 0.010933 | -1.3469e-12 | 2.9539e-17 | 3.2547e-16 | 0 | -138.5098 | 70.2758 | 0 | 41.4902 | -109.7242 |  | 1.4055 | 0.36851 | 0.36827 | 1.4055 | 0 | 0 | -0.013613 | -104.4664 | 104.3193 | -0.013613 | 0 | 0

## LLG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0_3ph | 6.2295e-06 | 0.029461 | 0.028945 | 0 | 0.029464 | 0.028938 | 1.4386e-06 | 0.0068037 | 0.0066845 | 0 | 0.0068043 | 0.006683 | 2.1958e-07 | 0.0054689 | 0.0048054 | -8.5409e-10 | -0.004607 | -0.0044442 | -1.4945e-06 | 0.0045947 | 0.0051141 | -1.182e-10 | -0.0045205 | -0.0043608 | 81.6418 | -160.0435 | 73.2105 | 0 | 19.9672 | -106.7913 |  | 1.05 | 1.0498 | 1.0498 | 1.1193 | 0.94857 | 0.93166 | -6.0111e-07 | -120.0082 | 119.993 | -0.52385 | -115.5753 | 117.6662
Line_1_3-1ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.847e-10 | -3.4189e-10 | -4.0128e-10 | -2.847e-10 | 3.4189e-10 | 4.0128e-10 | 3.94e-11 | -2.8175e-10 | 1.4606e-10 | -3.94e-11 | 2.8175e-10 | -1.4606e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1193 | 0.94857 | 0.93166 | 1.1193 | 0.94857 | 0.93166 | -0.52385 | -115.5753 | 117.6662 | -0.52385 | -115.5753 | 117.6662
Line_2_3-1ph | 0 | 0.029464 | 0.028938 | 0 | 0.029464 | 0.028938 | 0 | 0.0068043 | 0.006683 | 0 | 0.0068043 | 0.006683 | 2.847e-10 | 0.004607 | 0.0044442 | -2.847e-10 | -0.0043405 | -0.0041871 | 3.94e-11 | 0.0045205 | 0.0043608 | -3.94e-11 | -0.0043405 | -0.0041871 | 0 | -160.0328 | 73.2087 | 0 | 19.9672 | -106.7913 |  | 1.1193 | 0.94857 | 0.93166 | 1.1193 | 0.90214 | 0.88605 | -0.52385 | -115.5753 | 117.6662 | -0.52385 | -115.0328 | 118.2087

## LLG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0_3ph | 6.5263e-06 | 0.030863 | 0.030323 | 0 | 0.030866 | 0.030316 | 1.5072e-06 | 0.0071276 | 0.0070027 | 0 | 0.0071283 | 0.0070012 | 2.4093e-07 | 0.006002 | 0.0052739 | -9.3737e-10 | -0.0050561 | -0.0048774 | -1.6403e-06 | 0.0050426 | 0.0056127 | -1.2973e-10 | -0.0049613 | -0.0047859 | 81.6443 | -160.0439 | 73.2102 | 0 | 19.9668 | -106.7917 |  | 1.1 | 1.0998 | 1.0998 | 1.1726 | 0.99374 | 0.97602 | -6.2965e-07 | -120.0085 | 119.9927 | -0.52387 | -115.5757 | 117.6659
Line_1_3-1ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1246e-10 | -3.7525e-10 | -4.4043e-10 | -3.1246e-10 | 3.7525e-10 | 4.4043e-10 | 4.3243e-11 | -3.0919e-10 | 1.6033e-10 | -4.3243e-11 | 3.0919e-10 | -1.6033e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1726 | 0.99374 | 0.97602 | 1.1726 | 0.99374 | 0.97602 | -0.52387 | -115.5757 | 117.6659 | -0.52387 | -115.5757 | 117.6659
Line_2_3-1ph | 0 | 0.030867 | 0.030316 | 0 | 0.030867 | 0.030316 | 0 | 0.0071283 | 0.0070012 | 0 | 0.0071283 | 0.0070012 | 3.1246e-10 | 0.0050561 | 0.0048774 | -3.1246e-10 | -0.0047637 | -0.0045953 | 4.3243e-11 | 0.0049613 | 0.0047859 | -4.3243e-11 | -0.0047637 | -0.0045953 | 0 | -160.0332 | 73.2083 | 0 | 19.9668 | -106.7917 |  | 1.1726 | 0.99374 | 0.97602 | 1.1726 | 0.94509 | 0.92824 | -0.52387 | -115.5757 | 117.6659 | -0.52387 | -115.0332 | 118.2084

## LLG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0_3ph | 2.3469e-05 | 0.11772 | 0.11768 | 0 | 0.11774 | 0.11765 | 5.4199e-06 | 0.027186 | 0.027176 | 0 | 0.027191 | 0.027171 | 2.5881e-09 | 0.025767 | 0.021132 | -3.5248e-09 | -0.0081686 | -0.0081566 | -5.1489e-06 | 0.0017003 | 0.014801 | -3.37e-12 | -0.0028744 | -0.0028702 | 89.9712 | -123.8329 | 84.948 | 0 | 56.1735 | -95.053 |  | 0.95 | 0.94984 | 0.94937 | 1.214 | 0.31847 | 0.31824 | -1.1646e-06 | -120.0576 | 119.9557 | -0.015221 | -104.4405 | 104.333
Line_1_3-1ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1749e-09 | -6.968e-10 | -6.96e-10 | -1.1749e-09 | 6.968e-10 | 6.96e-10 | 1.1234e-12 | -2.9757e-10 | 2.9935e-10 | -1.1234e-12 | 2.9757e-10 | -2.9935e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.214 | 0.31847 | 0.31824 | 1.214 | 0.31847 | 0.31824 | -0.015221 | -104.4405 | 104.333 | -0.015221 | -104.4405 | 104.333
Line_2_3-1ph | 0 | 0.11774 | 0.11765 | 0 | 0.11774 | 0.11765 | 0 | 0.027191 | 0.027171 | 0 | 0.027191 | 0.027171 | 1.1749e-09 | 0.0081686 | 0.0081566 | -1.1749e-09 | 1.9303e-16 | -4.6e-16 | 1.1234e-12 | 0.0028744 | 0.0028702 | -1.1233e-12 | -1.9044e-16 | 1.3346e-16 | 0 | -123.8265 | 84.947 | 0 | 56.1735 | -95.053 |  | 1.214 | 0.31847 | 0.31824 | 1.214 | 0 | 0 | -0.015221 | -104.4405 | 104.333 | -0.015221 | 0 | 0

## LLG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0_3ph | 2.2233e-05 | 0.11153 | 0.11149 | 0 | 0.11155 | 0.11146 | 5.1346e-06 | 0.025756 | 0.025747 | 0 | 0.02576 | 0.025742 | 2.4121e-09 | 0.023126 | 0.018968 | -3.1636e-09 | -0.0073316 | -0.0073211 | -4.6211e-06 | 0.001526 | 0.013285 | -2.9649e-12 | -0.0025799 | -0.0025761 | 89.9701 | -123.8297 | 84.9509 | 0 | 56.1767 | -95.0502 |  | 0.9 | 0.89986 | 0.89943 | 1.1501 | 0.30172 | 0.3015 | -1.1035e-06 | -120.0546 | 119.9581 | -0.01492 | -104.4373 | 104.3359
Line_1_3-1ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0545e-09 | -6.2537e-10 | -6.2469e-10 | -1.0545e-09 | 6.2537e-10 | 6.2469e-10 | 9.883e-13 | -2.6713e-10 | 2.6863e-10 | -9.883e-13 | 2.6713e-10 | -2.6863e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1501 | 0.30172 | 0.3015 | 1.1501 | 0.30172 | 0.3015 | -0.01492 | -104.4373 | 104.3359 | -0.01492 | -104.4373 | 104.3359
Line_2_3-1ph | 0 | 0.11155 | 0.11146 | 0 | 0.11155 | 0.11146 | 0 | 0.02576 | 0.025742 | 0 | 0.02576 | 0.025742 | 1.0545e-09 | 0.0073316 | 0.0073211 | -1.0545e-09 | 1.7792e-16 | -4.5393e-16 | 9.883e-13 | 0.0025799 | 0.0025761 | -9.8829e-13 | -1.0112e-16 | 1.6933e-16 | 0 | -123.8233 | 84.9499 | 0 | 56.1767 | -95.0501 |  | 1.1501 | 0.30172 | 0.3015 | 1.1501 | 0 | 0 | -0.01492 | -104.4373 | 104.3359 | -0.01492 | 0 | 0

## LLG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0_3ph | 8.3224e-06 | 0.025041 | 0.023734 | 0 | 0.025047 | 0.023725 | 1.922e-06 | 0.005783 | 0.005481 | 0 | 0.0057843 | 0.0054791 | 5.2907e-07 | 0.0045212 | 0.0037228 | -1.0324e-09 | -0.0035063 | -0.0031461 | -1.7475e-06 | 0.0031197 | 0.0036394 | -2.8411e-10 | -0.0032667 | -0.0029311 | 73.1563 | -154.6155 | 75.6416 | 0 | 25.3986 | -104.3576 |  | 0.95 | 0.94987 | 0.94985 | 1.0399 | 0.8285 | 0.78479 | -1.5839e-06 | -120.0095 | 119.9924 | -1.4981 | -111.6273 | 118.6166
Line_1_3-1ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4413e-10 | -3.3833e-10 | -4.746e-10 | -3.4413e-10 | 3.3833e-10 | 4.746e-10 | 9.4703e-11 | -4.2023e-10 | 6.5999e-11 | -9.4703e-11 | 4.2023e-10 | -6.5999e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0399 | 0.8285 | 0.78479 | 1.0399 | 0.8285 | 0.78479 | -1.4981 | -111.6273 | 118.6166 | -1.4981 | -111.6273 | 118.6166
Line_2_3-1ph | 0 | 0.025047 | 0.023725 | 0 | 0.025047 | 0.023725 | 0 | 0.0057843 | 0.0054791 | 0 | 0.0057843 | 0.0054791 | 3.4413e-10 | 0.0035063 | 0.0031461 | -3.4413e-10 | -0.0031367 | -0.0028144 | 9.4703e-11 | 0.0032667 | 0.0029311 | -9.4703e-11 | -0.0031367 | -0.0028144 | 0 | -154.6014 | 75.6424 | 0 | 25.3986 | -104.3576 |  | 1.0399 | 0.8285 | 0.78479 | 1.0399 | 0.76689 | 0.72643 | -1.4981 | -111.6273 | 118.6166 | -1.4981 | -109.6014 | 120.6424

## LLG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0_3ph | 7.8842e-06 | 0.023723 | 0.022485 | 0 | 0.023729 | 0.022477 | 1.8208e-06 | 0.0054787 | 0.0051926 | 0 | 0.0054799 | 0.0051908 | 4.7489e-07 | 0.0040579 | 0.0033413 | -9.2657e-10 | -0.003147 | -0.0028237 | -1.5684e-06 | 0.0028 | 0.0032664 | -2.5499e-10 | -0.002932 | -0.0026308 | 73.1542 | -154.615 | 75.642 | 0 | 25.3991 | -104.3572 |  | 0.9 | 0.89988 | 0.89987 | 0.98519 | 0.7849 | 0.74349 | -1.5007e-06 | -120.009 | 119.9928 | -1.4981 | -111.6268 | 118.617
Line_1_3-1ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0886e-10 | -3.0364e-10 | -4.2595e-10 | -3.0886e-10 | 3.0364e-10 | 4.2595e-10 | 8.4995e-11 | -3.7718e-10 | 5.9218e-11 | -8.4995e-11 | 3.7718e-10 | -5.9218e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.98519 | 0.7849 | 0.74349 | 0.98519 | 0.7849 | 0.74349 | -1.4981 | -111.6268 | 118.617 | -1.4981 | -111.6268 | 118.617
Line_2_3-1ph | 0 | 0.023729 | 0.022477 | 0 | 0.023729 | 0.022477 | 0 | 0.0054799 | 0.0051908 | 0 | 0.0054799 | 0.0051908 | 3.0886e-10 | 0.003147 | 0.0028237 | -3.0886e-10 | -0.0028152 | -0.002526 | 8.4995e-11 | 0.002932 | 0.0026308 | -8.4995e-11 | -0.0028152 | -0.002526 | 0 | -154.6009 | 75.6428 | 0 | 25.3991 | -104.3572 |  | 0.98519 | 0.7849 | 0.74349 | 0.98519 | 0.72654 | 0.68821 | -1.4981 | -111.6268 | 118.617 | -1.4981 | -109.6009 | 120.6428