## LLL_max_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0_3ph | 0.63684 | 0.63684 | 0 | 0 | 22.0607 | 22.0607 | 6.1122 | -5.4795 | 16.8634 | -16.1455 | -73.3297 | 106.6703 | 0.81307 | 0.77287 | -3.2529 | -2.076
Line_1_3-2ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.77287 | 0.77287 | -2.076 | -2.076
Line_2_3-2ph | 0.63684 | 0.63684 | 0 | 0 | 22.0607 | 22.0607 | 5.4795 | -1.4827 | 16.1455 | -14.7523 | -73.3297 | 106.6703 | 0.77287 | 0.67208 | -2.076 | 10.9311
Line_3_3-2ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.77287 | 0.77287 | -2.076 | -2.076

## LLL_max_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0_3ph | 0.64777 | 0.64777 | 0 | 0 | 22.4393 | 22.4393 | 6.3968 | -5.7422 | 18.174 | -17.4313 | -73.6512 | 106.3488 | 0.85862 | 0.81788 | -3.0421 | -1.8842
Line_1_3-2ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.81788 | 0.81788 | -1.8842 | -1.8842
Line_2_3-2ph | 0.64777 | 0.64777 | 0 | 0 | 22.4393 | 22.4393 | 5.7422 | -1.607 | 17.4313 | -15.9898 | -73.6512 | 106.3488 | 0.81788 | 0.71617 | -1.8842 | 10.6096
Line_3_3-2ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.81788 | 0.81788 | -1.8842 | -1.8842

## LLL_max_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0_3ph | 0.00068521 | 0.00068521 | 0 | 0 | 0.023736 | 0.023736 | 0.017614 | -0.017613 | 0.017626 | -0.017625 | -45.0293 | 134.9707 | 1.0498 | 1.0498 | -0.0090182 | -0.0091776
Line_1_3-2ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0498 | 1.0498 | -0.0091776 | -0.0091776
Line_2_3-2ph | 0.00068521 | 0.00068521 | 0 | 0 | 0.023736 | 0.023736 | 0.017613 | -0.017608 | 0.017625 | -0.017624 | -45.0293 | 134.9707 | 1.0498 | 1.0496 | -0.0091776 | -0.0042724
Line_3_3-2ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0498 | 1.0498 | -0.0091776 | -0.0091776

## LLL_max_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0_3ph | 0.00071782 | 0.00071782 | 0 | 0 | 0.024866 | 0.024866 | 0.01933 | -0.019329 | 0.019345 | -0.019344 | -45.0304 | 134.9696 | 1.0998 | 1.0997 | -0.0090177 | -0.0091771
Line_1_3-2ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0997 | 1.0997 | -0.0091771 | -0.0091771
Line_2_3-2ph | 0.00071782 | 0.00071782 | 0 | 0 | 0.024866 | 0.024866 | 0.019329 | -0.019324 | 0.019344 | -0.019342 | -45.0304 | 134.9696 | 1.0997 | 1.0995 | -0.0091771 | -0.0042718
Line_3_3-2ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0997 | 1.0997 | -0.0091771 | -0.0091771

## LLL_min_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0_3ph | 0.5111 | 0.5111 | 0 | 0 | 17.705 | 17.705 | 6.7282 | -5.9458 | 11.3404 | -10.878 | -64.9631 | 115.0369 | 0.74477 | 0.7002 | -5.6437 | -3.6237
Line_1_3-2ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7002 | 0.7002 | -3.6237 | -3.6237
Line_2_3-2ph | 0.5111 | 0.5111 | 0 | 0 | 17.705 | 17.705 | 5.9458 | -1.0031 | 10.878 | -9.9806 | -64.9631 | 115.0369 | 0.7002 | 0.56656 | -3.6237 | 19.2977
Line_3_3-2ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7002 | 0.7002 | -3.6237 | -3.6237

## LLL_min_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0_3ph | 0.4842 | 0.4842 | 0 | 0 | 16.7731 | 16.7731 | 6.0386 | -5.3364 | 10.1781 | -9.7631 | -64.9631 | 115.0369 | 0.70557 | 0.66334 | -5.6437 | -3.6237
Line_1_3-2ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.66334 | 0.66334 | -3.6237 | -3.6237
Line_2_3-2ph | 0.4842 | 0.4842 | 0 | 0 | 16.7731 | 16.7731 | 5.3364 | -0.90028 | 9.7631 | -8.9577 | -64.9631 | 115.0369 | 0.66334 | 0.53674 | -3.6237 | 19.2977
Line_3_3-2ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.66334 | 0.66334 | -3.6237 | -3.6237

## LLL_min_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0_3ph | 0.00061983 | 0.00061983 | 0 | 0 | 0.021472 | 0.021472 | 0.014417 | -0.014416 | 0.014424 | -0.014423 | -45.0237 | 134.9763 | 0.94979 | 0.94973 | -0.010247 | -0.0093114
Line_1_3-2ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94973 | 0.94973 | -0.0093114 | -0.0093114
Line_2_3-2ph | 0.00061983 | 0.00061983 | 0 | 0 | 0.021472 | 0.021472 | 0.014416 | -0.014409 | 0.014423 | -0.014422 | -45.0237 | 134.9763 | 0.94973 | 0.94945 | -0.0093114 | 0.0025169
Line_3_3-2ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94973 | 0.94973 | -0.0093114 | -0.0093114

## LLL_min_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0_3ph | 0.00058721 | 0.00058721 | 0 | 0 | 0.020341 | 0.020341 | 0.012939 | -0.012938 | 0.012945 | -0.012945 | -45.0237 | 134.9763 | 0.8998 | 0.89975 | -0.010247 | -0.0093114
Line_1_3-2ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89975 | 0.89975 | -0.0093114 | -0.0093114
Line_2_3-2ph | 0.00058721 | 0.00058721 | 0 | 0 | 0.020341 | 0.020341 | 0.012938 | -0.012932 | 0.012945 | -0.012944 | -45.0237 | 134.9763 | 0.89975 | 0.89948 | -0.0093114 | 0.0025169
Line_3_3-2ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89975 | 0.89975 | -0.0093114 | -0.0093114

## LL_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0_3ph | 0 | 0.55152 | 0.55152 | 0 | 0.55152 | 0.55152 | 0 | 6.3684 | 6.3684 | 0 | 6.3684 | 6.3684 | 2.2163e-14 | 4.7309 | -1.6748 | -2.2135e-14 | -4.5728 | 1.833 | -1.5723e-15 | 3.2567 | 5.1749 | 1.577e-15 | -3.0773 | -4.9955 | 0 | -163.3297 | 16.6703 | 0 | 16.6703 | -163.3297 | 1.05 | 0.90188 | 0.8541 | 1.05 | 0.86549 | 0.83556 | 1.1865e-13 | -128.7864 | 124.6042 | 1.074e-13 | -129.3908 | 126.8201
Line_1_3-2ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5029e-16 | -1.0818e-09 | -1.2684e-09 | -3.4656e-16 | 1.0818e-09 | 1.2684e-09 | 2.0105e-16 | 1.0874e-09 | -7.6403e-10 | -1.8591e-16 | -1.0874e-09 | 7.6403e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.86549 | 0.83556 | 1.05 | 0.86549 | 0.83556 | 1.074e-13 | -129.3908 | 126.8201 | 1.0665e-13 | -129.3908 | 126.8201
Line_2_3-2ph | 0 | 0.55152 | 0.55152 | 0 | 0.55152 | 0.55152 | 0 | 6.3684 | 6.3684 | 0 | 6.3684 | 6.3684 | 2.1409e-14 | 4.5728 | -1.833 | -2.2124e-14 | -3.5735 | 2.8322 | -1.0172e-15 | 3.0773 | 4.9955 | 1.043e-15 | -2.729 | -4.6472 | 0 | -163.3297 | 16.6703 | 0 | 16.6703 | -163.3297 | 1.05 | 0.86549 | 0.83556 | 1.05 | 0.70605 | 0.85457 | 1.074e-13 | -129.3908 | 126.8201 | 8.2437e-14 | -125.9623 | 138.0305
Line_3_3-2ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -9.6394e-17 | -1.0818e-09 | -1.2684e-09 | -1.7795e-19 | 1.0818e-09 | 1.2684e-09 | 1.534e-17 | 1.0874e-09 | -7.6403e-10 | -1.2596e-19 | -1.0874e-09 | 7.6403e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.86549 | 0.83556 | 1.05 | 0.86549 | 0.83556 | 1.074e-13 | -129.3908 | 126.8201 | 1.0742e-13 | -129.3908 | 126.8201

## LL_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0_3ph | 0 | 0.56098 | 0.56098 | 0 | 0.56098 | 0.56098 | 0 | 6.4777 | 6.4777 | 0 | 6.4777 | 6.4777 | -1.1164e-15 | 5.0179 | -1.8195 | 2.3674e-18 | -4.8542 | 1.9831 | 1.3195e-15 | 3.5406 | 5.5463 | -1.5247e-15 | -3.355 | -5.3607 | 0 | -163.6512 | 16.3488 | 0 | 16.3488 | -163.6512 | 1.1 | 0.94807 | 0.90112 | 1.1 | 0.91094 | 0.88237 | 1.5422e-13 | -128.4442 | 124.5108 | 1.5786e-13 | -129.0012 | 126.6501
Line_1_3-2ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.0217e-15 | -1.1725e-09 | -1.3603e-09 | 1.8e-16 | 1.1725e-09 | 1.3603e-09 | 5.9493e-17 | 1.1497e-09 | -8.2428e-10 | -1.8797e-16 | -1.1497e-09 | 8.2428e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.91094 | 0.88237 | 1.1 | 0.91094 | 0.88237 | 1.5786e-13 | -129.0012 | 126.6501 | 1.5739e-13 | -129.0012 | 126.6501
Line_2_3-2ph | 0 | 0.56098 | 0.56098 | 0 | 0.56098 | 0.56098 | 0 | 6.4777 | 6.4777 | 0 | 6.4777 | 6.4777 | 5.9634e-17 | 4.8542 | -1.9831 | -1.712e-15 | -3.8204 | 3.0169 | 6.3541e-16 | 3.355 | 5.3607 | -1.2222e-16 | -2.9946 | -5.0003 | 0 | -163.6512 | 16.3488 | 0 | 16.3488 | -163.6512 | 1.1 | 0.91094 | 0.88237 | 1.1 | 0.74937 | 0.90155 | 1.5786e-13 | -129.0012 | 126.6501 | 1.645e-13 | -125.5605 | 137.4533
Line_3_3-2ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.4358e-16 | -1.1725e-09 | -1.3603e-09 | 1.5789e-18 | 1.1725e-09 | 1.3603e-09 | -1.2898e-16 | 1.1497e-09 | -8.2428e-10 | 4.8249e-19 | -1.1497e-09 | 8.2428e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.91094 | 0.88237 | 1.1 | 0.91094 | 0.88237 | 1.5786e-13 | -129.0012 | 126.6501 | 1.582e-13 | -129.0012 | 126.6501

## LL_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0_3ph | 0 | 0.0011857 | 0.0011857 | 0 | 0.0011857 | 0.0011857 | 0 | 0.013691 | 0.013691 | 0 | 0.013691 | 0.013691 | 6.2279e-17 | 0.013881 | 0.0037059 | -6.2713e-17 | -0.013881 | -0.0037052 | -5.8876e-18 | 0.0037287 | 0.013884 | 5.2645e-18 | -0.0037279 | -0.013883 | 0 | -135.0585 | 44.9415 | 0 | 44.9415 | -135.0585 | 1.05 | 1.0498 | 1.0496 | 1.05 | 1.0498 | 1.0495 | 1.5793e-16 | -120.0231 | 119.996 | 1.2208e-16 | -120.0255 | 119.998
Line_1_3-2ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.1254e-18 | -1.7499e-12 | -3.9886e-12 | 6.4202e-19 | 1.7499e-12 | 3.9886e-12 | 1.0785e-18 | 3.5965e-12 | 2.811e-13 | -1.3946e-18 | -3.5965e-12 | -2.811e-13 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.0498 | 1.0495 | 1.05 | 1.0498 | 1.0495 | 1.2208e-16 | -120.0255 | 119.998 | 1.2007e-16 | -120.0255 | 119.998
Line_2_3-2ph | 0 | 0.0011857 | 0.0011857 | 0 | 0.0011857 | 0.0011857 | 0 | 0.013691 | 0.013691 | 0 | 0.013691 | 0.013691 | 6.3615e-17 | 0.013881 | 0.0037052 | -6.4796e-17 | -0.013876 | -0.0037006 | -5.1027e-18 | 0.0037279 | 0.013883 | 2.7956e-18 | -0.0037263 | -0.013881 | 0 | -135.0585 | 44.9415 | 0 | 44.9415 | -135.0585 | 1.05 | 1.0498 | 1.0495 | 1.05 | 1.0494 | 1.0493 | 1.2208e-16 | -120.0255 | 119.998 | 3.5232e-17 | -120.0269 | 120.0141
Line_3_3-2ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.8207e-19 | -1.7499e-12 | -3.9886e-12 | -1.3054e-21 | 1.7499e-12 | 3.9886e-12 | -3.1603e-19 | 3.5965e-12 | 2.811e-13 | -3.681e-22 | -3.5965e-12 | -2.811e-13 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.0498 | 1.0495 | 1.05 | 1.0498 | 1.0495 | 1.2208e-16 | -120.0255 | 119.998 | 1.2171e-16 | -120.0255 | 119.998

## LL_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0_3ph | 0 | 0.0012421 | 0.0012421 | 0 | 0.0012421 | 0.0012421 | 0 | 0.014342 | 0.014342 | 0 | 0.014342 | 0.014342 | -8.6947e-18 | 0.015234 | 0.0040664 | 5.6439e-18 | -0.015233 | -0.0040656 | 9.6098e-18 | 0.0040927 | 0.015237 | -8.9686e-18 | -0.0040918 | -0.015236 | 0 | -135.0608 | 44.9392 | 0 | 44.9392 | -135.0608 | 1.1 | 1.0998 | 1.0995 | 1.1 | 1.0998 | 1.0995 | 2.8047e-16 | -120.0231 | 119.996 | 2.937e-16 | -120.0255 | 119.998
Line_1_3-2ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.3714e-18 | -1.9206e-12 | -4.3773e-12 | 1.7144e-19 | 1.9206e-12 | 4.3773e-12 | 3.4333e-18 | 3.9469e-12 | 3.0831e-13 | -2.9562e-18 | -3.9469e-12 | -3.0832e-13 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0998 | 1.0995 | 1.1 | 1.0998 | 1.0995 | 2.937e-16 | -120.0255 | 119.998 | 2.9416e-16 | -120.0255 | 119.998
Line_2_3-2ph | 0 | 0.0012421 | 0.0012421 | 0 | 0.0012421 | 0.0012421 | 0 | 0.014342 | 0.014342 | 0 | 0.014342 | 0.014342 | 1.5237e-19 | 0.015233 | 0.0040656 | -2.2834e-18 | -0.015228 | -0.0040606 | 4.0278e-18 | 0.0040918 | 0.015236 | -1.2726e-18 | -0.00409 | -0.015234 | 0 | -135.0608 | 44.9392 | 0 | 44.9392 | -135.0608 | 1.1 | 1.0998 | 1.0995 | 1.1 | 1.0994 | 1.0992 | 2.937e-16 | -120.0255 | 119.998 | 3.0755e-16 | -120.0269 | 120.0141
Line_3_3-2ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.2037e-18 | -1.9206e-12 | -4.3773e-12 | 3.1071e-21 | 1.9206e-12 | 4.3773e-12 | 4.7847e-19 | 3.9469e-12 | 3.0831e-13 | 1.7542e-22 | -3.9469e-12 | -3.0832e-13 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.0998 | 1.0995 | 1.1 | 1.0998 | 1.0995 | 2.937e-16 | -120.0255 | 119.998 | 2.9602e-16 | -120.0255 | 119.998

## LL_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0_3ph | 0 | 0.44262 | 0.44262 | 0 | 0.44262 | 0.44262 | 0 | 5.111 | 5.111 | 0 | 5.111 | 5.111 | -8.96e-15 | 3.8817 | -0.51754 | 8.625e-15 | -3.6861 | 0.71314 | 4.2783e-16 | 1.8077 | 3.8625 | -6.8554e-16 | -1.6921 | -3.7469 | 0 | -154.9631 | 25.0369 | 0 | 25.0369 | -154.9631 | 0.95 | 0.83779 | 0.76248 | 0.95 | 0.79356 | 0.74627 | 1.7043e-13 | -129.9918 | 122.6685 | 1.7219e-13 | -130.3055 | 125.8129
Line_1_3-2ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.1943e-16 | -8.212e-10 | -1.0882e-09 | 6.7781e-18 | 8.212e-10 | 1.0882e-09 | 6.2638e-17 | 9.8903e-10 | -5.2656e-10 | -2.2343e-16 | -9.8903e-10 | 5.2656e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.79356 | 0.74627 | 0.95 | 0.79356 | 0.74627 | 1.7219e-13 | -130.3055 | 125.8129 | 1.7197e-13 | -130.3055 | 125.8129
Line_2_3-2ph | 0 | 0.44262 | 0.44262 | 0 | 0.44262 | 0.44262 | 0 | 5.111 | 5.111 | 0 | 5.111 | 5.111 | -7.623e-15 | 3.6861 | -0.71314 | 7.0143e-15 | -2.4504 | 1.9488 | 5.1789e-16 | 1.6921 | 3.7469 | -4.3368e-16 | -1.4677 | -3.5226 | 0 | -154.9631 | 25.0369 | 0 | 25.0369 | -154.9631 | 0.95 | 0.79356 | 0.74627 | 0.95 | 0.55886 | 0.78766 | 1.7219e-13 | -130.3055 | 125.8129 | 1.7819e-13 | -124.042 | 143.99
Line_3_3-2ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.1256e-16 | -8.212e-10 | -1.0882e-09 | 1.8617e-19 | 8.212e-10 | 1.0882e-09 | -1.6073e-16 | 9.8903e-10 | -5.2656e-10 | 7.9577e-20 | -9.8903e-10 | 5.2656e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.79356 | 0.74627 | 0.95 | 0.79356 | 0.74627 | 1.7219e-13 | -130.3055 | 125.8129 | 1.7168e-13 | -130.3055 | 125.8129

## LL_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0_3ph | 0 | 0.41933 | 0.41933 | 0 | 0.41933 | 0.41933 | 0 | 4.842 | 4.842 | 0 | 4.842 | 4.842 | -7.8814e-15 | 3.4838 | -0.4645 | 7.5692e-15 | -3.3083 | 0.64005 | 1.7838e-16 | 1.6224 | 3.4666 | -2.962e-16 | -1.5187 | -3.3629 | 0 | -154.9631 | 25.0369 | 0 | 25.0369 | -154.9631 | 0.9 | 0.7937 | 0.72235 | 0.9 | 0.7518 | 0.70699 | 1.704e-13 | -129.9918 | 122.6685 | 1.7226e-13 | -130.3055 | 125.8129
Line_1_3-2ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.242e-16 | -7.3703e-10 | -9.7667e-10 | 3.5604e-17 | 7.3703e-10 | 9.7667e-10 | -3.5635e-16 | 8.8766e-10 | -4.7259e-10 | 2.8515e-16 | -8.8766e-10 | 4.7259e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.7518 | 0.70699 | 0.9 | 0.7518 | 0.70699 | 1.7226e-13 | -130.3055 | 125.8129 | 1.724e-13 | -130.3055 | 125.8129
Line_2_3-2ph | 0 | 0.41933 | 0.41933 | 0 | 0.41933 | 0.41933 | 0 | 4.842 | 4.842 | 0 | 4.842 | 4.842 | -7.2538e-15 | 3.3083 | -0.64005 | 7.3067e-15 | -2.1992 | 1.7491 | 3.3054e-16 | 1.5187 | 3.3629 | 1.1865e-16 | -1.3173 | -3.1615 | 0 | -154.9631 | 25.0369 | 0 | 25.0369 | -154.9631 | 0.9 | 0.7518 | 0.70699 | 0.9 | 0.52945 | 0.74621 | 1.7226e-13 | -130.3055 | 125.8129 | 1.7697e-13 | -124.042 | 143.99
Line_3_3-2ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.8803e-16 | -7.3703e-10 | -9.7667e-10 | -4.4265e-20 | 7.3703e-10 | 9.7667e-10 | -7.1352e-17 | 8.8766e-10 | -4.7259e-10 | 2.2575e-19 | -8.8766e-10 | 4.7259e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.7518 | 0.70699 | 0.9 | 0.7518 | 0.70699 | 1.7226e-13 | -130.3055 | 125.8129 | 1.7211e-13 | -130.3055 | 125.8129

## LL_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0_3ph | 0 | 0.0010724 | 0.0010724 | 0 | 0.0010724 | 0.0010724 | 0 | 0.012382 | 0.012382 | 0 | 0.012382 | 0.012382 | -3.0563e-17 | 0.011359 | 0.0030346 | 2.9275e-17 | -0.011358 | -0.0030335 | -3.1576e-19 | 0.0030483 | 0.011359 | -6.8172e-19 | -0.0030476 | -0.011359 | 0 | -135.0474 | 44.9526 | 0 | 44.9526 | -135.0474 | 0.95 | 0.94984 | 0.94954 | 0.95 | 0.94973 | 0.94946 | 3.6867e-16 | -120.0262 | 119.9955 | 3.7243e-16 | -120.0279 | 120.0001
Line_1_3-2ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.8334e-19 | -1.8673e-12 | -3.7263e-12 | -1.6137e-19 | 1.8673e-12 | 3.7263e-12 | -1.0168e-18 | 3.2259e-12 | -6.0424e-15 | 4.2663e-19 | -3.2259e-12 | 6.0418e-15 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94973 | 0.94946 | 0.95 | 0.94973 | 0.94946 | 3.7243e-16 | -120.0279 | 120.0001 | 3.7146e-16 | -120.0279 | 120.0001
Line_2_3-2ph | 0 | 0.0010724 | 0.0010724 | 0 | 0.0010724 | 0.0010724 | 0 | 0.012382 | 0.012382 | 0 | 0.012382 | 0.012382 | -2.5536e-17 | 0.011358 | 0.0030335 | 2.5248e-17 | -0.011351 | -0.0030262 | -1.3397e-18 | 0.0030476 | 0.011359 | 2.8273e-18 | -0.0030463 | -0.011357 | 0 | -135.0474 | 44.9526 | 0 | 44.9526 | -135.0474 | 0.95 | 0.94973 | 0.94946 | 0.95 | 0.94914 | 0.94921 | 3.7243e-16 | -120.0279 | 120.0001 | 3.7773e-16 | -120.025 | 120.0326
Line_3_3-2ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.0432e-18 | -1.8673e-12 | -3.7263e-12 | -4.2938e-22 | 1.8673e-12 | 3.7263e-12 | -5.887e-19 | 3.2259e-12 | -6.0414e-15 | -3.9182e-22 | -3.2259e-12 | 6.0408e-15 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94973 | 0.94946 | 0.95 | 0.94973 | 0.94946 | 3.7243e-16 | -120.0279 | 120.0001 | 3.7067e-16 | -120.0279 | 120.0001

## LL_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0_3ph | 0 | 0.0010159 | 0.0010159 | 0 | 0.0010159 | 0.0010159 | 0 | 0.011731 | 0.011731 | 0 | 0.011731 | 0.011731 | -2.3318e-17 | 0.010195 | 0.0027236 | 2.3466e-17 | -0.010194 | -0.0027226 | -2.277e-18 | 0.0027358 | 0.010195 | 1.1559e-18 | -0.0027352 | -0.010194 | 0 | -135.0474 | 44.9526 | 0 | 44.9526 | -135.0474 | 0.9 | 0.89984 | 0.89957 | 0.9 | 0.89975 | 0.89949 | 3.5583e-16 | -120.0262 | 119.9955 | 3.5485e-16 | -120.0279 | 120.0001
Line_1_3-2ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.6068e-19 | -1.6759e-12 | -3.3444e-12 | 2.6209e-19 | 1.6759e-12 | 3.3444e-12 | -1.0531e-19 | 2.8952e-12 | -5.4205e-15 | -5.6517e-19 | -2.8952e-12 | 5.4207e-15 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89975 | 0.89949 | 0.9 | 0.89975 | 0.89949 | 3.5485e-16 | -120.0279 | 120.0001 | 3.5239e-16 | -120.0279 | 120.0001
Line_2_3-2ph | 0 | 0.0010159 | 0.0010159 | 0 | 0.0010159 | 0.0010159 | 0 | 0.011731 | 0.011731 | 0 | 0.011731 | 0.011731 | -2.2292e-17 | 0.010194 | 0.0027226 | 2.2811e-17 | -0.010188 | -0.002716 | -7.9894e-20 | 0.0027352 | 0.010194 | 1.9132e-18 | -0.002734 | -0.010193 | 0 | -135.0474 | 44.9526 | 0 | 44.9526 | -135.0474 | 0.9 | 0.89975 | 0.89949 | 0.9 | 0.89918 | 0.89925 | 3.5485e-16 | -120.0279 | 120.0001 | 3.6458e-16 | -120.025 | 120.0326
Line_3_3-2ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -9.7934e-20 | -1.6759e-12 | -3.3444e-12 | -6.5915e-22 | 1.6759e-12 | 3.3444e-12 | -6.7146e-19 | 2.8952e-12 | -5.4214e-15 | 1.2419e-21 | -2.8952e-12 | 5.4216e-15 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89975 | 0.89949 | 0.9 | 0.89975 | 0.89949 | 3.5485e-16 | -120.0279 | 120.0001 | 3.5159e-16 | -120.0279 | 120.0001

## LG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0_3ph | 0.57337 | 0.0018086 | 0.0018086 | 0.57295 | 0.0013629 | 0.0013629 | 6.6207 | 0.020883 | 0.020883 | 6.6158 | 0.015737 | 0.015737 | 2.6474 | 0.021018 | -0.01592 | -2.1267 | -0.015674 | 0.011582 | 4.9274 | -0.0062604 | -0.015094 | -4.6338 | 0.0042354 | 0.012966 | -66.3264 | -103.45 | -103.45 | 113.6926 | 72.2386 | 72.2386 |  | 0.84486 | 1.0501 | 1.0505 | 0.77066 | 1.0317 | 1.1048 | -4.5744 | -120.0369 | 120.0246 | -0.96059 | -122.8823 | 120.4655
Line_1_3-2ph | 0.00037806 | 0.00037806 | 0.00037806 | 0 | 0 | 0 | 0.0043655 | 0.0043655 | 0.0043655 | 0 | 0 | 0 | -0.00063324 | 0.0042028 | -0.0035685 | 1.578e-09 | 1.2913e-10 | -4.4522e-10 | 0.0033042 | -0.0016194 | -0.0032443 | -9.8239e-11 | -4.0029e-10 | 6.8687e-11 | -101.8096 | -101.8096 | -101.8096 | 0 | 0 | 0 |  | 0.77066 | 1.0317 | 1.1048 | 0.77063 | 1.0316 | 1.1049 | -0.96059 | -122.8823 | 120.4655 | -0.94862 | -122.8885 | 120.4626
Line_2_3-2ph | 0.57233 | 0.00061584 | 0.00061584 | 0.57193 | 0 | 0 | 6.6087 | 0.0071111 | 0.0071111 | 6.6041 | 0 | 0 | 2.128 | 0.0072686 | -0.004445 | -0.39861 | 1.4289e-10 | -1.4143e-09 | 4.6272 | -0.00099652 | -0.0064776 | -3.9661 | -1.2116e-09 | 3.1253e-10 | -66.2634 | -115.0758 | -115.0758 | 113.783 | 0 | 0 |  | 0.77066 | 1.0317 | 1.1048 | 0.60358 | 1.0183 | 1.2089 | -0.96059 | -122.8823 | 120.4655 | 18.0438 | -128.8894 | 121.924
Line_3_3-2ph | 0.00037806 | 0.00037806 | 0.00037806 | 0 | 0 | 0 | 0.0043655 | 0.0043655 | 0.0043655 | 0 | 0 | 0 | -0.00063324 | 0.0042028 | -0.0035685 | 1.578e-09 | 1.2913e-10 | -4.4522e-10 | 0.0033042 | -0.0016194 | -0.0032443 | -9.824e-11 | -4.0029e-10 | 6.8687e-11 | -101.8096 | -101.8096 | -101.8096 | 0 | 0 | 0 |  | 0.77066 | 1.0317 | 1.1048 | 0.77063 | 1.0316 | 1.1049 | -0.96059 | -122.8823 | 120.4655 | -0.94862 | -122.8885 | 120.4626

## LG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0_3ph | 0.58542 | 0.0018466 | 0.0018466 | 0.58499 | 0.0013915 | 0.0013915 | 6.7598 | 0.021322 | 0.021322 | 6.7548 | 0.016068 | 0.016068 | 2.7792 | 0.022536 | -0.016895 | -2.2366 | -0.016809 | 0.012267 | 5.334 | -0.0065099 | -0.016285 | -5.0279 | 0.0043675 | 0.013947 | -66.7998 | -103.9235 | -103.9235 | 113.2191 | 71.7652 | 71.7652 |  | 0.88977 | 1.1001 | 1.1005 | 0.81466 | 1.0809 | 1.156 | -4.3211 | -120.036 | 120.0237 | -0.76193 | -122.8002 | 120.4314
Line_1_3-2ph | 0.00038601 | 0.00038601 | 0.00038601 | 0 | 0 | 0 | 0.0044572 | 0.0044572 | 0.0044572 | 0 | 0 | 0 | -0.00072524 | 0.004512 | -0.0037857 | 1.7042e-09 | 1.4226e-10 | -4.762e-10 | 0.003558 | -0.0016885 | -0.0034951 | -8.6056e-11 | -4.268e-10 | 6.9733e-11 | -102.283 | -102.283 | -102.283 | 0 | 0 | 0 |  | 0.81466 | 1.0809 | 1.156 | 0.81463 | 1.0807 | 1.1561 | -0.76193 | -122.8002 | 120.4314 | -0.75035 | -122.8062 | 120.4284
Line_2_3-2ph | 0.58436 | 0.00062877 | 0.00062877 | 0.58394 | 0 | 0 | 6.7476 | 0.0072605 | 0.0072605 | 6.7428 | 0 | 0 | 2.238 | 0.0077847 | -0.0046956 | -0.43532 | 1.6885e-10 | -1.5102e-09 | 5.0207 | -0.00099047 | -0.0069565 | -4.3314 | -1.2929e-09 | 3.235e-10 | -66.7369 | -115.5492 | -115.5492 | 113.3095 | 0 | 0 |  | 0.81466 | 1.0809 | 1.156 | 0.6456 | 1.0659 | 1.2626 | -0.76193 | -122.8002 | 120.4314 | 17.5704 | -128.6484 | 121.8203
Line_3_3-2ph | 0.00038601 | 0.00038601 | 0.00038601 | 0 | 0 | 0 | 0.0044572 | 0.0044572 | 0.0044572 | 0 | 0 | 0 | -0.00072524 | 0.004512 | -0.0037857 | 1.7042e-09 | 1.4226e-10 | -4.762e-10 | 0.003558 | -0.0016885 | -0.0034951 | -8.6056e-11 | -4.268e-10 | 6.9732e-11 | -102.283 | -102.283 | -102.283 | 0 | 0 | 0 |  | 0.81466 | 1.0809 | 1.156 | 0.81463 | 1.0807 | 1.1561 | -0.76193 | -122.8002 | 120.4314 | -0.75035 | -122.8062 | 120.4284

## LG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0_3ph | 0.00068682 | 2.1664e-06 | 2.1664e-06 | 0.00068631 | 1.6325e-06 | 1.6325e-06 | 0.0079307 | 2.5015e-05 | 2.5015e-05 | 0.0079249 | 1.8851e-05 | 1.8851e-05 | 0.0058742 | 2.0771e-05 | -2.4309e-05 | -0.0058711 | -1.6518e-05 | 1.7704e-05 | 0.0058999 | -1.6078e-05 | -9.949e-06 | -0.0058933 | 1.0906e-05 | 8.8543e-06 | -45.1342 | -82.2579 | -82.2579 | 134.8848 | 93.4308 | 93.4308 |  | 1.0498 | 1.05 | 1.05 | 1.0497 | 1.05 | 1.0501 | -0.0090191 | -120 | 120 | -0.0073926 | -120.0036 | 120.0018
Line_1_3-2ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.9557e-07 | 4.2437e-06 | -5.1393e-06 | 2.3601e-12 | -3.8358e-15 | -4.4222e-13 | 5.4156e-06 | -3.4841e-06 | -1.9337e-06 | -1.0416e-12 | -5.1279e-13 | 2.5969e-13 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0497 | 1.05 | 1.0501 | 1.0497 | 1.05 | 1.0501 | -0.0073926 | -120.0036 | 120.0018 | -0.0073834 | -120.0036 | 120.0018
Line_2_3-2ph | 0.00068558 | 0 | 0 | 0.00068509 | 0 | 0 | 0.0079164 | 0 | 0 | 0.0079108 | 0 | 0 | 0.0058693 | 8.0306e-06 | -7.4253e-06 | -0.0058674 | -1.4672e-13 | -1.2259e-12 | 0.0058824 | -3.9376e-06 | -4.9868e-06 | -0.0058726 | -1.4998e-12 | 8.7672e-13 | -45.0713 | 0 | 0 | 134.9752 | 0 | 0 |  | 1.0497 | 1.05 | 1.0501 | 1.0494 | 1.05 | 1.0502 | -0.0073926 | -120.0036 | 120.0018 | 0.00014394 | -120.0106 | 120.0062
Line_3_3-2ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.9557e-07 | 4.2437e-06 | -5.1393e-06 | 2.36e-12 | -3.8357e-15 | -4.4222e-13 | 5.4156e-06 | -3.4841e-06 | -1.9337e-06 | -1.0416e-12 | -5.1279e-13 | 2.5969e-13 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0497 | 1.05 | 1.0501 | 1.0497 | 1.05 | 1.0501 | -0.0073926 | -120.0036 | 120.0018 | -0.0073834 | -120.0036 | 120.0018

## LG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0_3ph | 0.0007195 | 2.2695e-06 | 2.2695e-06 | 0.00071898 | 1.7102e-06 | 1.7102e-06 | 0.0083081 | 2.6206e-05 | 2.6206e-05 | 0.008302 | 1.9748e-05 | 1.9748e-05 | 0.0064467 | 2.2796e-05 | -2.6679e-05 | -0.0064433 | -1.8128e-05 | 1.9429e-05 | 0.0064752 | -1.7645e-05 | -1.0919e-05 | -0.0064679 | 1.1969e-05 | 9.7178e-06 | -45.1354 | -82.2591 | -82.2591 | 134.8836 | 93.4296 | 93.4296 |  | 1.0998 | 1.1 | 1.1 | 1.0997 | 1.1 | 1.1001 | -0.0090186 | -120 | 120 | -0.007392 | -120.0036 | 120.0018
Line_1_3-2ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.8275e-07 | 4.6575e-06 | -5.6402e-06 | 2.5901e-12 | -4.1974e-15 | -4.8533e-13 | 5.9435e-06 | -3.8237e-06 | -2.1223e-06 | -1.143e-12 | -5.6278e-13 | 2.8499e-13 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0997 | 1.1 | 1.1001 | 1.0997 | 1.1 | 1.1001 | -0.007392 | -120.0036 | 120.0018 | -0.0073829 | -120.0036 | 120.0018
Line_2_3-2ph | 0.00071821 | 0 | 0 | 0.0007177 | 0 | 0 | 0.0082931 | 0 | 0 | 0.0082872 | 0 | 0 | 0.0064413 | 8.8135e-06 | -8.149e-06 | -0.0064393 | -1.6099e-13 | -1.3454e-12 | 0.006456 | -4.3213e-06 | -5.4731e-06 | -0.0064451 | -1.646e-12 | 9.6215e-13 | -45.0725 | 0 | 0 | 134.974 | 0 | 0 |  | 1.0997 | 1.1 | 1.1001 | 1.0994 | 1.1 | 1.1002 | -0.007392 | -120.0036 | 120.0018 | 0.00014463 | -120.0106 | 120.0062
Line_3_3-2ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.8275e-07 | 4.6575e-06 | -5.6402e-06 | 2.5901e-12 | -4.1981e-15 | -4.8534e-13 | 5.9435e-06 | -3.8237e-06 | -2.1223e-06 | -1.143e-12 | -5.6278e-13 | 2.8499e-13 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0997 | 1.1 | 1.1001 | 1.0997 | 1.1 | 1.1001 | -0.007392 | -120.0036 | 120.0018 | -0.0073829 | -120.0036 | 120.0018

## LG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0_3ph | 0.43186 | 0.0019274 | 0.0019274 | 0.43151 | 0.0015155 | 0.0015155 | 4.9867 | 0.022256 | 0.022256 | 4.9826 | 0.0175 | 0.0175 | 2.6861 | 0.020514 | -0.014688 | -2.1188 | -0.015814 | 0.011141 | 2.9088 | -0.0051314 | -0.015229 | -2.743 | 0.0039488 | 0.014079 | -54.0847 | -106.0057 | -106.0057 | 125.9489 | 69.4024 | 69.4024 |  | 0.79398 | 0.95012 | 0.95066 | 0.69563 | 0.9314 | 1.0259 | -6.8049 | -120.0498 | 120.0312 | -1.7349 | -124.6178 | 121.0484
Line_1_3-2ph | 0.0003961 | 0.0003961 | 0.0003961 | 0 | 0 | 0 | 0.0045738 | 0.0045738 | 0.0045738 | 0 | 0 | 0 | -0.00068677 | 0.0039924 | -0.0033036 | 1.2955e-09 | 1.0763e-10 | -5.7447e-10 | 0.0031067 | -0.0014862 | -0.0033324 | -1.4455e-10 | -5.2341e-10 | 1.296e-10 | -104.2005 | -104.2005 | -104.2005 | 0 | 0 | 0 |  | 0.69563 | 0.9314 | 1.0259 | 0.69563 | 0.93114 | 1.0262 | -1.7349 | -124.6178 | 121.0484 | -1.7092 | -124.6281 | 121.0387
Line_2_3-2ph | 0.431 | 0.0007336 | 0.0007336 | 0.43067 | 0 | 0 | 4.9767 | 0.0084709 | 0.0084709 | 4.973 | 0 | 0 | 2.1202 | 0.0078291 | -0.0045334 | -0.23741 | -1.6332e-11 | -1.8727e-09 | 2.7368 | -0.00097649 | -0.0074143 | -2.3622 | -1.5279e-09 | 4.5608e-10 | -53.9703 | -117.5083 | -117.5083 | 126.1171 | 0 | 0 |  | 0.69563 | 0.9314 | 1.0259 | 0.4774 | 0.92534 | 1.1673 | -1.7349 | -124.6178 | 121.0484 | 30.3779 | -133.7099 | 123.2151
Line_3_3-2ph | 0.0003961 | 0.0003961 | 0.0003961 | 0 | 0 | 0 | 0.0045738 | 0.0045738 | 0.0045738 | 0 | 0 | 0 | -0.00068677 | 0.0039924 | -0.0033036 | 1.2955e-09 | 1.0763e-10 | -5.7447e-10 | 0.0031067 | -0.0014862 | -0.0033324 | -1.4455e-10 | -5.2341e-10 | 1.296e-10 | -104.2005 | -104.2005 | -104.2005 | 0 | 0 | 0 |  | 0.69563 | 0.9314 | 1.0259 | 0.69563 | 0.93114 | 1.0262 | -1.7349 | -124.6178 | 121.0484 | -1.7092 | -124.6281 | 121.0387

## LG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0_3ph | 0.40913 | 0.001826 | 0.001826 | 0.40879 | 0.0014358 | 0.0014358 | 4.7242 | 0.021084 | 0.021084 | 4.7204 | 0.016579 | 0.016579 | 2.4108 | 0.018411 | -0.013182 | -1.9016 | -0.014193 | 0.0099987 | 2.6107 | -0.0046055 | -0.013668 | -2.4619 | 0.0035441 | 0.012636 | -54.0847 | -106.0057 | -106.0057 | 125.9489 | 69.4024 | 69.4024 |  | 0.75219 | 0.90011 | 0.90062 | 0.65901 | 0.88238 | 0.97193 | -6.8049 | -120.0498 | 120.0312 | -1.7349 | -124.6178 | 121.0484
Line_1_3-2ph | 0.00037526 | 0.00037526 | 0.00037526 | 0 | 0 | 0 | 0.0043331 | 0.0043331 | 0.0043331 | 0 | 0 | 0 | -0.00061638 | 0.0035832 | -0.002965 | 1.1627e-09 | 9.6602e-11 | -5.1559e-10 | 0.0027883 | -0.0013338 | -0.0029908 | -1.2973e-10 | -4.6977e-10 | 1.1632e-10 | -104.2005 | -104.2005 | -104.2005 | 0 | 0 | 0 |  | 0.65901 | 0.88238 | 0.97193 | 0.65902 | 0.88213 | 0.97217 | -1.7349 | -124.6178 | 121.0484 | -1.7092 | -124.6281 | 121.0387
Line_2_3-2ph | 0.40831 | 0.00069499 | 0.00069499 | 0.408 | 0 | 0 | 4.7148 | 0.008025 | 0.008025 | 4.7112 | 0 | 0 | 1.9029 | 0.0070267 | -0.0040688 | -0.21308 | -1.4658e-11 | -1.6808e-09 | 2.4563 | -0.00087641 | -0.0066544 | -2.1201 | -1.3713e-09 | 4.0933e-10 | -53.9703 | -117.5083 | -117.5083 | 126.1171 | 0 | 0 |  | 0.65901 | 0.88238 | 0.97193 | 0.45228 | 0.87664 | 1.1058 | -1.7349 | -124.6178 | 121.0484 | 30.3779 | -133.7099 | 123.2151
Line_3_3-2ph | 0.00037526 | 0.00037526 | 0.00037526 | 0 | 0 | 0 | 0.0043331 | 0.0043331 | 0.0043331 | 0 | 0 | 0 | -0.00061638 | 0.0035832 | -0.002965 | 1.1627e-09 | 9.6602e-11 | -5.1559e-10 | 0.0027883 | -0.0013338 | -0.0029908 | -1.2973e-10 | -4.6977e-10 | 1.1632e-10 | -104.2005 | -104.2005 | -104.2005 | 0 | 0 | 0 |  | 0.65901 | 0.88238 | 0.97193 | 0.65902 | 0.88213 | 0.97217 | -1.7349 | -124.6178 | 121.0484 | -1.7092 | -124.6281 | 121.0387

## LG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0_3ph | 0.00062136 | 2.7732e-06 | 2.7732e-06 | 0.00062085 | 2.1806e-06 | 2.1806e-06 | 0.0071749 | 3.2022e-05 | 3.2022e-05 | 0.007169 | 2.5179e-05 | 2.5179e-05 | 0.0048015 | 2.8031e-05 | -2.4252e-05 | -0.0047992 | -2.2713e-05 | 1.7853e-05 | 0.0048358 | -1.182e-05 | -1.8365e-05 | -0.0048287 | 7.5024e-06 | 1.5924e-05 | -45.2146 | -97.1355 | -97.1355 | 134.819 | 78.2725 | 78.2725 |  | 0.94979 | 0.95 | 0.95 | 0.94964 | 0.94999 | 0.9501 | -0.010231 | -120.0001 | 120.0001 | -0.0052156 | -120.0067 | 120.0026
Line_1_3-2ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.8e-07 | 5.6808e-06 | -5.1008e-06 | 2.4892e-12 | 1.0064e-13 | -7.2416e-13 | 6.2225e-06 | -2.6101e-06 | -3.616e-06 | -5.9912e-13 | -7.7793e-13 | 3.0172e-13 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.94964 | 0.94999 | 0.9501 | 0.94964 | 0.94999 | 0.9501 | -0.0052156 | -120.0067 | 120.0026 | -0.0051886 | -120.0067 | 120.0026
Line_2_3-2ph | 0.00062012 | 1.0555e-06 | 1.0555e-06 | 0.00061966 | 0 | 0 | 0.0071606 | 1.2188e-05 | 1.2188e-05 | 0.0071552 | 0 | 0 | 0.0048004 | 1.1351e-05 | -7.6517e-06 | -0.0048001 | 1.656e-13 | -2.0333e-12 | 0.0048163 | -2.2823e-06 | -8.6916e-06 | -0.0048045 | -2.2509e-12 | 9.8135e-13 | -45.1001 | -108.6381 | -108.6381 | 134.9873 | 0 | 0 |  | 0.94964 | 0.94999 | 0.9501 | 0.94918 | 0.94998 | 0.95029 | -0.0052156 | -120.0067 | 120.0026 | 0.01351 | -120.0195 | 120.0085
Line_3_3-2ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.8e-07 | 5.6808e-06 | -5.1008e-06 | 2.4892e-12 | 1.0064e-13 | -7.2417e-13 | 6.2225e-06 | -2.6101e-06 | -3.616e-06 | -5.9912e-13 | -7.7793e-13 | 3.0173e-13 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.94964 | 0.94999 | 0.9501 | 0.94964 | 0.94999 | 0.9501 | -0.0052156 | -120.0067 | 120.0026 | -0.0051886 | -120.0067 | 120.0026

## LG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0_3ph | 0.00058866 | 2.6272e-06 | 2.6272e-06 | 0.00058818 | 2.0658e-06 | 2.0658e-06 | 0.0067972 | 3.0337e-05 | 3.0337e-05 | 0.0067917 | 2.3854e-05 | 2.3854e-05 | 0.0043093 | 2.5158e-05 | -2.1766e-05 | -0.0043073 | -2.0385e-05 | 1.6024e-05 | 0.0043402 | -1.0609e-05 | -1.6483e-05 | -0.0043338 | 6.7335e-06 | 1.4292e-05 | -45.2146 | -97.1355 | -97.1355 | 134.819 | 78.2725 | 78.2725 |  | 0.8998 | 0.9 | 0.9 | 0.89966 | 0.89999 | 0.9001 | -0.010231 | -120.0001 | 120.0001 | -0.0052156 | -120.0067 | 120.0026
Line_1_3-2ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.2055e-07 | 5.0986e-06 | -4.578e-06 | 2.2341e-12 | 9.0326e-14 | -6.4994e-13 | 5.5847e-06 | -2.3425e-06 | -3.2454e-06 | -5.3772e-13 | -6.982e-13 | 2.708e-13 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.89966 | 0.89999 | 0.9001 | 0.89966 | 0.89999 | 0.9001 | -0.0052156 | -120.0067 | 120.0026 | -0.0051886 | -120.0067 | 120.0026
Line_2_3-2ph | 0.00058749 | 0 | 0 | 0.00058704 | 0 | 0 | 0.0067837 | 0 | 0 | 0.0067786 | 0 | 0 | 0.0043084 | 1.0188e-05 | -6.8675e-06 | -0.0043082 | 1.4863e-13 | -1.8249e-12 | 0.0043226 | -2.0484e-06 | -7.8008e-06 | -0.0043121 | -2.0202e-12 | 8.8077e-13 | -45.1001 | 0 | 0 | 134.9873 | 0 | 0 |  | 0.89966 | 0.89999 | 0.9001 | 0.89922 | 0.89998 | 0.90028 | -0.0052156 | -120.0067 | 120.0026 | 0.01351 | -120.0195 | 120.0085
Line_3_3-2ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.2055e-07 | 5.0986e-06 | -4.578e-06 | 2.2341e-12 | 9.0326e-14 | -6.4994e-13 | 5.5847e-06 | -2.3425e-06 | -3.2454e-06 | -5.3772e-13 | -6.982e-13 | 2.708e-13 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.89966 | 0.89999 | 0.9001 | 0.89966 | 0.89999 | 0.9001 | -0.0052156 | -120.0067 | 120.0026 | -0.0051886 | -120.0067 | 120.0026

## LLG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0_3ph | 0.0016229 | 0.65791 | 0.55545 | 0.001223 | 0.65783 | 0.55519 | 0.01874 | 7.5969 | 6.4138 | 0.014122 | 7.596 | 6.4108 | 0.0026432 | 3.0778 | 1.4499 | -0.0027097 | -2.5678 | -1.292 | -0.01951 | 5.3818 | 5.1945 | 0.015092 | -5.3616 | -4.6961 | 82.2768 | 174.1798 | 43.6125 | -102.0346 | -5.7848 | -136.4209 |  | 1.0506 | 0.81609 | 0.84086 | 1.0858 | 0.78262 | 0.75974 | -0.0078352 | -125.5847 | 118.0169 | -1.8557 | -121.3752 | 118.1964
Line_1_3-2ph | 0.00033925 | 0.00033925 | 0.00033925 | 0 | 0 | 0 | 0.0039174 | 0.0039174 | 0.0039174 | 0 | 0 | 0 | 0.00031351 | -0.0027719 | 0.0024592 | -2.897e-10 | 1.5324e-09 | 1.6148e-09 | -0.0042418 | 0.0013098 | 0.0016763 | -2.7183e-10 | -1.4381e-10 | -1.8384e-10 | 83.9172 | 83.9172 | 83.9172 | 0 | 0 | 0 |  | 1.0858 | 0.78262 | 0.75974 | 1.0858 | 0.78272 | 0.75959 | -1.8557 | -121.3752 | 118.1964 | -1.8631 | -121.3673 | 118.1988
Line_2_3-2ph | 0.00055262 | 0.65784 | 0.55468 | 0 | 0.65797 | 0.55419 | 0.0063811 | 7.596 | 6.4049 | 0 | 7.5975 | 6.3992 | 0.0020826 | 2.5733 | 1.2871 | -1.0238e-09 | -0.52756 | -0.37426 | -0.006608 | 5.359 | 4.6927 | -7.2394e-10 | -5.2491 | -3.7238 | 70.651 | 174.2743 | 43.5337 | 0 | -5.6789 | -136.4923 |  | 1.0858 | 0.78262 | 0.75974 | 1.1663 | 0.69438 | 0.58485 | -1.8557 | -121.3752 | 118.1964 | -4.6239 | -101.4181 | 127.7685
Line_3_3-2ph | 0.00033925 | 0.00033925 | 0.00033925 | 0 | 0 | 0 | 0.0039174 | 0.0039174 | 0.0039174 | 0 | 0 | 0 | 0.00031351 | -0.0027719 | 0.0024592 | -2.897e-10 | 1.5324e-09 | 1.6148e-09 | -0.0042418 | 0.0013098 | 0.0016763 | -2.7183e-10 | -1.4381e-10 | -1.8384e-10 | 83.9172 | 83.9172 | 83.9172 | 0 | 0 | 0 |  | 1.0858 | 0.78262 | 0.75974 | 1.0858 | 0.78272 | 0.75959 | -1.8557 | -121.3752 | 118.1964 | -1.8631 | -121.3673 | 118.1988

## LLG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0_3ph | 0.0016627 | 0.66942 | 0.5665 | 0.001253 | 0.66934 | 0.56623 | 0.0192 | 7.7298 | 6.5414 | 0.014468 | 7.7289 | 6.5383 | 0.0030395 | 3.2177 | 1.5332 | -0.003068 | -2.688 | -1.3665 | -0.020912 | 5.8254 | 5.5931 | 0.016152 | -5.8063 | -5.073 | 81.722 | 173.6723 | 43.4503 | -102.5893 | -6.2921 | -136.5831 |  | 1.1006 | 0.86095 | 0.88658 | 1.1363 | 0.82785 | 0.80354 | -0.007973 | -125.2423 | 118.1209 | -1.8343 | -121.1335 | 118.3405
Line_1_3-2ph | 0.00034758 | 0.00034758 | 0.00034758 | 0 | 0 | 0 | 0.0040135 | 0.0040135 | 0.0040135 | 0 | 0 | 0 | 0.00038188 | -0.0030235 | 0.0026425 | -3.0767e-10 | 1.6505e-09 | 1.7448e-09 | -0.0045446 | 0.0013776 | 0.0018488 | -2.9457e-10 | -1.3124e-10 | -1.874e-10 | 83.3625 | 83.3625 | 83.3624 | 0 | 0 | 0 |  | 1.1363 | 0.82785 | 0.80354 | 1.1364 | 0.82796 | 0.8034 | -1.8343 | -121.1335 | 118.3405 | -1.8415 | -121.1259 | 118.3429
Line_2_3-2ph | 0.00056618 | 0.66934 | 0.5657 | 0 | 0.66948 | 0.56519 | 0.0065377 | 7.7289 | 6.5321 | 0 | 7.7305 | 6.5263 | 0.0023042 | 2.694 | 1.3613 | -1.0876e-09 | -0.57218 | -0.40781 | -0.0070624 | 5.8036 | 5.0693 | -7.86e-10 | -5.6932 | -4.0577 | 70.0963 | 173.7674 | 43.3717 | 0 | -6.1855 | -136.6541 |  | 1.1363 | 0.82785 | 0.80354 | 1.2182 | 0.74017 | 0.62487 | -1.8343 | -121.1335 | 118.3405 | -4.5876 | -101.9247 | 127.6067
Line_3_3-2ph | 0.00034758 | 0.00034758 | 0.00034758 | 0 | 0 | 0 | 0.0040135 | 0.0040135 | 0.0040135 | 0 | 0 | 0 | 0.00038188 | -0.0030235 | 0.0026425 | -3.0767e-10 | 1.6505e-09 | 1.7448e-09 | -0.0045446 | 0.0013776 | 0.0018488 | -2.9457e-10 | -1.3124e-10 | -1.874e-10 | 83.3625 | 83.3625 | 83.3624 | 0 | 0 | 0 |  | 1.1363 | 0.82785 | 0.80354 | 1.1364 | 0.82796 | 0.8034 | -1.8343 | -121.1335 | 118.3405 | -1.8415 | -121.1259 | 118.3429

## LLG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0_3ph | 2.166e-06 | 0.00068493 | 0.0006871 | 1.6323e-06 | 0.00068487 | 0.00068665 | 2.5011e-05 | 0.0079088 | 0.007934 | 1.8848e-05 | 0.0079082 | 0.0079288 | -3.5399e-06 | 0.0058514 | 0.005894 | 1.1865e-06 | -0.0058551 | -0.005887 | -2.6022e-05 | 0.0058903 | 0.0058851 | 1.9756e-05 | -0.0058852 | -0.0058832 | 97.7465 | -165.1984 | 75.0345 | -86.5648 | 14.8476 | -104.9923 |  | 1.05 | 1.0498 | 1.0498 | 1.0501 | 1.0498 | 1.0497 | 1.6001e-06 | -120.009 | 119.9909 | -0.0017838 | -120.0056 | 119.989
Line_1_3-2ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.9562e-07 | -4.2416e-06 | 5.1372e-06 | -4.4597e-13 | 1.9183e-12 | 2.3563e-12 | -5.4166e-06 | 3.4832e-06 | 1.9312e-06 | -2.5303e-13 | -7.8237e-13 | -1.554e-12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0501 | 1.0498 | 1.0497 | 1.0501 | 1.0498 | 1.0497 | -0.0017838 | -120.0056 | 119.989 | -0.001793 | -120.0055 | 119.989
Line_2_3-2ph | 0 | 0.00068496 | 0.00068583 | 0 | 0.0006852 | 0.0006851 | 0 | 0.0079092 | 0.0079193 | 0 | 0.007912 | 0.0079109 | 6.0474e-07 | 0.0058636 | 0.0058767 | -1.3722e-12 | -0.0058692 | -0.0058677 | -8.9225e-06 | 0.0058782 | 0.0058793 | -6.2287e-13 | -0.0058743 | -0.0058728 | 0 | -165.077 | 74.9765 | 0 | 14.9814 | -105.0355 |  | 1.0501 | 1.0498 | 1.0497 | 1.0502 | 1.0495 | 1.0494 | -0.0017838 | -120.0056 | 119.989 | -0.0044133 | -119.9936 | 119.9895
Line_3_3-2ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.9562e-07 | -4.2416e-06 | 5.1372e-06 | -4.4597e-13 | 1.9183e-12 | 2.3563e-12 | -5.4166e-06 | 3.4832e-06 | 1.9312e-06 | -2.5303e-13 | -7.8237e-13 | -1.554e-12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0501 | 1.0498 | 1.0497 | 1.0501 | 1.0498 | 1.0497 | -0.0017838 | -120.0056 | 119.989 | -0.001793 | -120.0055 | 119.989

## LLG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0_3ph | 2.2691e-06 | 0.00071752 | 0.0007198 | 1.7099e-06 | 0.00071746 | 0.00071933 | 2.6202e-05 | 0.0082852 | 0.0083116 | 1.9745e-05 | 0.0082846 | 0.0083061 | -3.8843e-06 | 0.0064217 | 0.0064684 | 1.3017e-06 | -0.0064257 | -0.0064607 | -2.8559e-05 | 0.0064646 | 0.0064589 | 2.1681e-05 | -0.006459 | -0.0064568 | 97.7454 | -165.1996 | 75.0333 | -86.566 | 14.8464 | -104.9935 |  | 1.1 | 1.0998 | 1.0998 | 1.1001 | 1.0997 | 1.0997 | 1.5991e-06 | -120.009 | 119.9909 | -0.0017839 | -120.0056 | 119.989
Line_1_3-2ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -9.828e-07 | -4.6552e-06 | 5.638e-06 | -4.8944e-13 | 2.1054e-12 | 2.586e-12 | -5.9446e-06 | 3.8226e-06 | 2.1195e-06 | -2.777e-13 | -8.5859e-13 | -1.7054e-12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1001 | 1.0997 | 1.0997 | 1.1001 | 1.0997 | 1.0997 | -0.0017839 | -120.0056 | 119.989 | -0.001793 | -120.0055 | 119.989
Line_2_3-2ph | 0 | 0.00071756 | 0.00071847 | 0 | 0.00071781 | 0.00071771 | 0 | 0.0082856 | 0.0082961 | 0 | 0.0082885 | 0.0082874 | 6.6389e-07 | 0.006435 | 0.0064495 | -1.5059e-12 | -0.0064412 | -0.0064395 | -9.7922e-06 | 0.0064513 | 0.0064526 | -6.8362e-13 | -0.0064471 | -0.0064454 | 0 | -165.0782 | 74.9753 | 0 | 14.9802 | -105.0367 |  | 1.1001 | 1.0997 | 1.0997 | 1.1002 | 1.0995 | 1.0994 | -0.0017839 | -120.0056 | 119.989 | -0.0044134 | -119.9936 | 119.9895
Line_3_3-2ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -9.828e-07 | -4.6552e-06 | 5.638e-06 | -4.8944e-13 | 2.1054e-12 | 2.586e-12 | -5.9446e-06 | 3.8226e-06 | 2.1195e-06 | -2.777e-13 | -8.5859e-13 | -1.7054e-12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1001 | 1.0997 | 1.0997 | 1.1001 | 1.0997 | 1.0997 | -0.0017839 | -120.0056 | 119.989 | -0.001793 | -120.0055 | 119.989

## LLG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0_3ph | 0.0016276 | 0.52991 | 0.42177 | 0.0012798 | 0.5299 | 0.42153 | 0.018794 | 6.1189 | 4.8702 | 0.014778 | 6.1188 | 4.8674 | 0.0025285 | 3.2723 | 1.4412 | -0.0026764 | -2.7093 | -1.2735 | -0.017687 | 3.3092 | 3.4814 | 0.014573 | -3.4201 | -3.0587 | 81.8543 | -174.0587 | 49.3063 | -102.7377 | 5.981 | -130.7312 |  | 0.95068 | 0.76057 | 0.77368 | 1.0026 | 0.71308 | 0.6807 | -0.010172 | -128.7369 | 116.8191 | -2.3308 | -122.4039 | 116.6647
Line_1_3-2ph | 0.00033449 | 0.00033449 | 0.00033449 | 0 | 0 | 0 | 0.0038624 | 0.0038624 | 0.0038624 | 0 | 0 | 0 | 0.00027079 | -0.0024741 | 0.0022048 | -3.9289e-10 | 1.2339e-09 | 1.3371e-09 | -0.003863 | 0.0012101 | 0.0014321 | -2.859e-10 | -2.073e-10 | -2.7513e-10 | 83.6594 | 83.6594 | 83.6594 | 0 | 0 | 0 |  | 1.0026 | 0.71308 | 0.6807 | 1.0026 | 0.71329 | 0.68045 | -2.3308 | -122.4039 | 116.6647 | -2.3457 | -122.3909 | 116.6728
Line_2_3-2ph | 0.00061949 | 0.53004 | 0.42097 | 0 | 0.53031 | 0.4204 | 0.0071533 | 6.1204 | 4.861 | 0 | 6.1235 | 4.8543 | 0.0021348 | 2.7142 | 1.2691 | -1.3471e-09 | -0.35998 | -0.22622 | -0.0068468 | 3.4177 | 3.0558 | -7.6429e-10 | -3.5817 | -2.2508 | 70.3517 | -173.9484 | 49.2174 | 0 | 6.1119 | -130.813 |  | 1.0026 | 0.71308 | 0.6807 | 1.1107 | 0.58786 | 0.46602 | -2.3308 | -122.4039 | 116.6647 | -5.6683 | -89.6273 | 133.4478
Line_3_3-2ph | 0.00033449 | 0.00033449 | 0.00033449 | 0 | 0 | 0 | 0.0038624 | 0.0038624 | 0.0038624 | 0 | 0 | 0 | 0.00027079 | -0.0024741 | 0.0022048 | -3.9289e-10 | 1.2339e-09 | 1.3371e-09 | -0.003863 | 0.0012101 | 0.0014321 | -2.859e-10 | -2.073e-10 | -2.7513e-10 | 83.6594 | 83.6594 | 83.6594 | 0 | 0 | 0 |  | 1.0026 | 0.71308 | 0.6807 | 1.0026 | 0.71329 | 0.68045 | -2.3308 | -122.4039 | 116.6647 | -2.3457 | -122.3909 | 116.6728

## LLG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0_3ph | 0.001542 | 0.50202 | 0.39957 | 0.0012125 | 0.50201 | 0.39934 | 0.017805 | 5.7969 | 4.6138 | 0.014 | 5.7967 | 4.6112 | 0.0022693 | 2.9369 | 1.2934 | -0.0024021 | -2.4316 | -1.1429 | -0.015875 | 2.97 | 3.1246 | 0.013079 | -3.0696 | -2.7452 | 81.8543 | -174.0587 | 49.3063 | -102.7377 | 5.981 | -130.7312 |  | 0.90065 | 0.72054 | 0.73296 | 0.94983 | 0.67555 | 0.64487 | -0.010172 | -128.7369 | 116.8191 | -2.3308 | -122.4039 | 116.6647
Line_1_3-2ph | 0.00031689 | 0.00031689 | 0.00031689 | 0 | 0 | 0 | 0.0036591 | 0.0036591 | 0.0036591 | 0 | 0 | 0 | 0.00024303 | -0.0022205 | 0.0019788 | -3.5262e-10 | 1.1074e-09 | 1.2e-09 | -0.003467 | 0.0010861 | 0.0012853 | -2.5659e-10 | -1.8605e-10 | -2.4693e-10 | 83.6594 | 83.6594 | 83.6594 | 0 | 0 | 0 |  | 0.94983 | 0.67555 | 0.64487 | 0.94987 | 0.67575 | 0.64464 | -2.3308 | -122.4039 | 116.6647 | -2.3457 | -122.3909 | 116.6728
Line_2_3-2ph | 0.00058689 | 0.50215 | 0.39882 | 0 | 0.5024 | 0.39827 | 0.0067768 | 5.7983 | 4.6052 | 0 | 5.8012 | 4.5988 | 0.001916 | 2.436 | 1.139 | -1.209e-09 | -0.32308 | -0.20303 | -0.006145 | 3.0674 | 2.7426 | -6.8596e-10 | -3.2146 | -2.0202 | 70.3517 | -173.9484 | 49.2174 | 0 | 6.1119 | -130.813 |  | 0.94983 | 0.67555 | 0.64487 | 1.0523 | 0.55692 | 0.44149 | -2.3308 | -122.4039 | 116.6647 | -5.6683 | -89.6273 | 133.4478
Line_3_3-2ph | 0.00031689 | 0.00031689 | 0.00031689 | 0 | 0 | 0 | 0.0036591 | 0.0036591 | 0.0036591 | 0 | 0 | 0 | 0.00024303 | -0.0022205 | 0.0019788 | -3.5262e-10 | 1.1074e-09 | 1.2e-09 | -0.003467 | 0.0010861 | 0.0012853 | -2.5659e-10 | -1.8605e-10 | -2.4693e-10 | 83.6594 | 83.6594 | 83.6594 | 0 | 0 | 0 |  | 0.94983 | 0.67555 | 0.64487 | 0.94987 | 0.67575 | 0.64464 | -2.3308 | -122.4039 | 116.6647 | -2.3457 | -122.3909 | 116.6728

## LLG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0_3ph | 2.7724e-06 | 0.00061881 | 0.00062239 | 2.18e-06 | 0.00061887 | 0.00062182 | 3.2013e-05 | 0.0071454 | 0.0071867 | 2.5172e-05 | 0.0071461 | 0.0071801 | 3.7719e-06 | 0.0047794 | 0.0048277 | -4.8549e-06 | -0.0047838 | -0.0048206 | -3.0178e-05 | 0.0048182 | 0.0048255 | 2.3418e-05 | -0.0048143 | -0.0048221 | 82.8755 | -165.242 | 75.0029 | -101.7165 | 14.8155 | -105.0206 |  | 0.95 | 0.94979 | 0.94979 | 0.95009 | 0.94975 | 0.94963 | -1.6084e-05 | -120.0102 | 119.9897 | -0.004093 | -120.0026 | 119.9881
Line_1_3-2ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.7903e-07 | -5.6775e-06 | 5.0984e-06 | -6.2335e-13 | 1.7663e-12 | 2.5897e-12 | -6.2238e-06 | 2.6093e-06 | 3.6109e-06 | -4.7595e-13 | -2.982e-13 | -1.3764e-12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.95009 | 0.94975 | 0.94963 | 0.95009 | 0.94975 | 0.94963 | -0.004093 | -120.0026 | 119.9881 | -0.00412 | -120.0026 | 119.9881
Line_2_3-2ph | 1.0552e-06 | 0.00061926 | 0.00062069 | 0 | 0.00061985 | 0.00061964 | 1.2185e-05 | 0.0071506 | 0.0071671 | 0 | 0.0071574 | 0.007155 | 3.6968e-06 | 0.0047952 | 0.0048104 | -1.8666e-12 | -0.0048031 | -0.0047999 | -1.097e-05 | 0.0048091 | 0.0048149 | -1.2688e-12 | -0.0048075 | -0.0048043 | 71.3729 | -165.0855 | 74.9617 | 0 | 14.9958 | -105.0322 |  | 0.95009 | 0.94975 | 0.94963 | 0.95027 | 0.94947 | 0.94916 | -0.004093 | -120.0026 | 119.9881 | -0.010981 | -119.978 | 119.994
Line_3_3-2ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.7903e-07 | -5.6775e-06 | 5.0984e-06 | -6.2335e-13 | 1.7663e-12 | 2.5897e-12 | -6.2238e-06 | 2.6093e-06 | 3.6109e-06 | -4.7595e-13 | -2.982e-13 | -1.3764e-12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.95009 | 0.94975 | 0.94963 | 0.95009 | 0.94975 | 0.94963 | -0.004093 | -120.0026 | 119.9881 | -0.00412 | -120.0026 | 119.9881

## LLG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0_3ph | 2.6265e-06 | 0.00058624 | 0.00058963 | 2.0652e-06 | 0.0005863 | 0.00058909 | 3.0328e-05 | 0.0067693 | 0.0068084 | 2.3847e-05 | 0.00677 | 0.0068022 | 3.3853e-06 | 0.0042895 | 0.0043329 | -4.3573e-06 | -0.0042935 | -0.0043266 | -2.7085e-05 | 0.0043244 | 0.0043309 | 2.1018e-05 | -0.0043209 | -0.0043279 | 82.8755 | -165.242 | 75.0029 | -101.7165 | 14.8155 | -105.0206 |  | 0.9 | 0.8998 | 0.8998 | 0.90008 | 0.89976 | 0.89965 | -1.6084e-05 | -120.0102 | 119.9897 | -0.004093 | -120.0026 | 119.9881
Line_1_3-2ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.1969e-07 | -5.0956e-06 | 4.5759e-06 | -5.5946e-13 | 1.5852e-12 | 2.3243e-12 | -5.5859e-06 | 2.3419e-06 | 3.2408e-06 | -4.2717e-13 | -2.6764e-13 | -1.2354e-12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.90008 | 0.89976 | 0.89965 | 0.90008 | 0.89976 | 0.89965 | -0.004093 | -120.0026 | 119.9881 | -0.00412 | -120.0026 | 119.9881
Line_2_3-2ph | 0 | 0.00058667 | 0.00058802 | 0 | 0.00058722 | 0.00058703 | 0 | 0.0067743 | 0.0067899 | 0 | 0.0067807 | 0.0067784 | 3.3179e-06 | 0.0043037 | 0.0043174 | -1.6753e-12 | -0.0043108 | -0.004308 | -9.8459e-06 | 0.0043162 | 0.0043214 | -1.1388e-12 | -0.0043148 | -0.0043119 | 0 | -165.0855 | 74.9617 | 0 | 14.9958 | -105.0322 |  | 0.90008 | 0.89976 | 0.89965 | 0.90025 | 0.8995 | 0.8992 | -0.004093 | -120.0026 | 119.9881 | -0.010981 | -119.978 | 119.994
Line_3_3-2ph | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.1969e-07 | -5.0956e-06 | 4.5759e-06 | -5.5946e-13 | 1.5852e-12 | 2.3243e-12 | -5.5859e-06 | 2.3419e-06 | 3.2408e-06 | -4.2717e-13 | -2.6764e-13 | -1.2354e-12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.90008 | 0.89976 | 0.89965 | 0.90008 | 0.89976 | 0.89965 | -0.004093 | -120.0026 | 119.9881 | -0.00412 | -120.0026 | 119.9881