## LLL_max_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 3.6881 | 3.6881 | 0 | 0 | 127.7608 | 127.7608 | 35.7117 | -14.492 | 40.4916 | -16.4154 | -73.4178 | 106.5822 | 0.42258 | 0.17139 | -24.8286 | -24.8568
Line_1 | 2.5165 | 2.5165 | 5.0352 | 0 | 87.1726 | 87.1726 | -1e-07 | 9.8788 | -1e-07 | 11.2086 | 106.5347 | -73.4653 | 0 | 0.17139 | 0 | -24.8568
Line_2 | 1.1717 | 1.1717 | 0 | 0 | 40.5883 | 40.5883 | -2.4716 | 4.6132 | -2.7769 | 5.2068 | 106.6843 | -73.3157 | 0.091591 | 0.17139 | -24.9872 | -24.8568
Line_3 | 1.3448 | 1.3448 | 2.64 | 0 | 46.5845 | 46.5845 | -1e-07 | 2.8212 | -1e-07 | 3.2009 | 106.4044 | -73.5956 | 0 | 0.091591 | 0 | -24.9872

## LLL_max_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 3.6881 | 3.6881 | 0 | 0 | 127.7608 | 127.7608 | 35.7117 | -14.492 | 40.4916 | -16.4154 | -73.4178 | 106.5822 | 0.42258 | 0.17139 | -24.8286 | -24.8568
Line_1 | 2.5165 | 2.5165 | 5.0352 | 0 | 87.1726 | 87.1726 | -1e-07 | 9.8788 | -1e-07 | 11.2086 | 106.5347 | -73.4653 | 0 | 0.17139 | 0 | -24.8568
Line_2 | 1.1717 | 1.1717 | 0 | 0 | 40.5883 | 40.5883 | -2.4716 | 4.6132 | -2.7769 | 5.2068 | 106.6843 | -73.3157 | 0.091591 | 0.17139 | -24.9872 | -24.8568
Line_3 | 1.3448 | 1.3448 | 2.64 | 0 | 46.5845 | 46.5845 | -1e-07 | 2.8212 | -1e-07 | 3.2009 | 106.4044 | -73.5956 | 0 | 0.091591 | 0 | -24.9872

## LLL_max_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 1.0373 | 1.0373 | 0 | 0 | 35.932 | 35.932 | 26.3132 | -24.6348 | 21.7282 | -19.8239 | -47.5823 | 132.4177 | 0.94971 | 0.88001 | -8.034 | -8.7583
Line_1 | 0.74302 | 0.74302 | 1.5452 | 0 | 25.7391 | 25.7391 | -16.2572 | 17.1185 | -13.8556 | 14.8328 | 130.3335 | -49.6665 | 0.82989 | 0.88001 | -9.2264 | -8.7583
Line_2 | 0.29597 | 0.29597 | 0 | 0 | 10.2527 | 10.2527 | -7.3796 | 7.5163 | -4.836 | 4.9911 | 137.6561 | -42.3439 | 0.86056 | 0.88001 | -9.1062 | -8.7583
Line_3 | 0.45105 | 0.45105 | 0.88584 | 0 | 15.6247 | 15.6247 | -9.1308 | 9.4482 | -9.2068 | 9.5669 | 125.536 | -54.464 | 0.82989 | 0.86056 | -9.2264 | -9.1062

## LLL_max_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 1.0373 | 1.0373 | 0 | 0 | 35.932 | 35.932 | 26.3132 | -24.6348 | 21.7282 | -19.8239 | -47.5823 | 132.4177 | 0.94971 | 0.88001 | -8.034 | -8.7583
Line_1 | 0.74302 | 0.74302 | 1.5452 | 0 | 25.7391 | 25.7391 | -16.2572 | 17.1185 | -13.8556 | 14.8328 | 130.3335 | -49.6665 | 0.82989 | 0.88001 | -9.2264 | -8.7583
Line_2 | 0.29597 | 0.29597 | 0 | 0 | 10.2527 | 10.2527 | -7.3796 | 7.5163 | -4.836 | 4.9911 | 137.6561 | -42.3439 | 0.86056 | 0.88001 | -9.1062 | -8.7583
Line_3 | 0.45105 | 0.45105 | 0.88584 | 0 | 15.6247 | 15.6247 | -9.1308 | 9.4482 | -9.2068 | 9.5669 | 125.536 | -54.464 | 0.82989 | 0.86056 | -9.2264 | -9.1062

## LLL_min_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 3.0092 | 3.0092 | 0 | 0 | 104.2421 | 104.2421 | 45.2043 | -18.0817 | 26.7133 | -10.6853 | -62.3733 | 117.6267 | 0.50371 | 0.20148 | -31.7926 | -31.7926
Line_1 | 2.0061 | 2.0061 | 3.4722 | 0 | 69.4947 | 69.4947 | -1e-07 | 12.0545 | -1e-07 | 7.1235 | 117.6267 | -62.3733 | 0 | 0.20148 | 0 | -31.7926
Line_2 | 1.0031 | 1.0031 | 0 | 0 | 34.7474 | 34.7474 | -3.0136 | 6.0272 | -1.7809 | 3.5618 | 117.6267 | -62.3733 | 0.10074 | 0.20148 | -31.7926 | -31.7926
Line_3 | 1.0031 | 1.0031 | 1.7361 | 0 | 34.7474 | 34.7474 | -1e-07 | 3.0136 | -1e-07 | 1.7809 | 117.6267 | -62.3733 | 0 | 0.10074 | 0 | -31.7926

## LLL_min_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 3.0092 | 3.0092 | 0 | 0 | 104.2421 | 104.2421 | 45.2043 | -18.0817 | 26.7133 | -10.6853 | -62.3733 | 117.6267 | 0.50371 | 0.20148 | -31.7926 | -31.7926
Line_1 | 2.0061 | 2.0061 | 3.4722 | 0 | 69.4947 | 69.4947 | -1e-07 | 12.0545 | -1e-07 | 7.1235 | 117.6267 | -62.3733 | 0 | 0.20148 | 0 | -31.7926
Line_2 | 1.0031 | 1.0031 | 0 | 0 | 34.7474 | 34.7474 | -3.0136 | 6.0272 | -1.7809 | 3.5618 | 117.6267 | -62.3733 | 0.10074 | 0.20148 | -31.7926 | -31.7926
Line_3 | 1.0031 | 1.0031 | 1.7361 | 0 | 34.7474 | 34.7474 | -1e-07 | 3.0136 | -1e-07 | 1.7809 | 117.6267 | -62.3733 | 0 | 0.10074 | 0 | -31.7926

## LLL_min_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 1.0697 | 1.0697 | 0 | 0 | 37.0569 | 37.0569 | 22.8777 | -19.4502 | 20.541 | -18.5155 | -51.0933 | 128.9067 | 0.8297 | 0.72467 | -9.1739 | -7.5036
Line_1 | 0.71316 | 0.71316 | 1.2343 | 0 | 24.7046 | 24.7046 | -11.4434 | 12.9668 | -11.4434 | 12.3437 | 128.9067 | -51.0933 | 0.65508 | 0.72467 | -6.0933 | -7.5036
Line_2 | 0.35658 | 0.35658 | 0 | 0 | 12.3523 | 12.3523 | -6.1026 | 6.4834 | -5.9468 | 6.1718 | 128.9067 | -51.0933 | 0.68982 | 0.72467 | -6.834 | -7.5036
Line_3 | 0.35658 | 0.35658 | 0.61717 | 0 | 12.3523 | 12.3523 | -5.7217 | 6.1026 | -5.7217 | 5.9468 | 128.9067 | -51.0933 | 0.65508 | 0.68982 | -6.0933 | -6.834

## LLL_min_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 1.0697 | 1.0697 | 0 | 0 | 37.0569 | 37.0569 | 22.8777 | -19.4502 | 20.541 | -18.5155 | -51.0933 | 128.9067 | 0.8297 | 0.72467 | -9.1739 | -7.5036
Line_1 | 0.71316 | 0.71316 | 1.2343 | 0 | 24.7046 | 24.7046 | -11.4434 | 12.9668 | -11.4434 | 12.3437 | 128.9067 | -51.0933 | 0.65508 | 0.72467 | -6.0933 | -7.5036
Line_2 | 0.35658 | 0.35658 | 0 | 0 | 12.3523 | 12.3523 | -6.1026 | 6.4834 | -5.9468 | 6.1718 | 128.9067 | -51.0933 | 0.68982 | 0.72467 | -6.834 | -7.5036
Line_3 | 0.35658 | 0.35658 | 0.61717 | 0 | 12.3523 | 12.3523 | -5.7217 | 6.1026 | -5.7217 | 5.9468 | 128.9067 | -51.0933 | 0.65508 | 0.68982 | -6.0933 | -6.834

## LL_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.34636 | 3.202 | 3.1954 | 0.34636 | 3.202 | 3.1954 | 3.9994 | 36.9732 | 36.8978 | 3.9994 | 36.9732 | 36.8978 | -1.1886 | 29.9053 | -12.6438 | 1.251 | -24.574 | 17.9534 | -4.5163 | 2.6474 | 15.3402 | 4.587 | 3.4016 | -9.3158 | 105.4999 | -160.318 | 13.4761 | -74.5001 | 19.682 | -166.5239 | 1.1677 | 0.812 | 0.53877 | 1.1888 | 0.67098 | 0.54818 | 0.75518 | -155.259 | 142.9723 | 0.24528 | -168.199 | 166.0518
Line_1 | 0.17318 | 2.1821 | 2.18 | 0.17318 | 2.1821 | 2.18 | 1.9997 | 25.1967 | 25.1721 | 1.9997 | 25.1967 | 25.1721 | 0.65428 | -14.3042 | 14.6313 | -0.63869 | 16.7802 | -12.1601 | 2.3076 | 4.872 | -3.7182 | -2.2899 | -2.0627 | 6.522 | -74.1703 | 18.8087 | -165.7416 | 105.8297 | -161.1913 | 14.2584 | 1.1995 | 0.59973 | 0.59973 | 1.1888 | 0.67098 | 0.54818 | -8.1967e-06 | 180 | 180 | 0.24528 | -168.199 | 166.0518
Line_2 | 0.17318 | 1.0207 | 1.0161 | 0.17318 | 1.0207 | 1.0161 | 1.9997 | 11.7857 | 11.7331 | 1.9997 | 11.7857 | 11.7331 | 0.62788 | -7.2521 | 6.3302 | -0.61228 | 7.7938 | -5.7933 | 2.3148 | 1.9536 | -2.1846 | -2.2971 | -1.339 | 2.7938 | -74.8299 | 21.5492 | -168.2026 | 105.1701 | -158.4508 | 11.7974 | 1.1994 | 0.63726 | 0.57074 | 1.1888 | 0.67098 | 0.54818 | -0.0058437 | -173.5277 | 172.7571 | 0.24528 | -168.199 | 166.0518
Line_3 | 0.0019937 | 1.1636 | 1.1656 | 0.0019937 | 1.1636 | 1.1656 | 0.023021 | 13.4363 | 13.4593 | 0.023021 | 13.4363 | 13.4593 | 0.026608 | -7.73 | 7.7433 | -0.026606 | 8.4341 | -7.0368 | -0.0073793 | 2.2758 | -2.2795 | 0.0073817 | -1.477 | 3.0811 | 15.5004 | 16.4052 | -163.5964 | -164.4996 | -163.5948 | 16.4036 | 1.1995 | 0.59973 | 0.59973 | 1.1994 | 0.63726 | 0.57074 | -8.1967e-06 | 180 | 180 | -0.0058437 | -173.5277 | 172.7571

## LL_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.34636 | 3.202 | 3.1954 | 0.34636 | 3.202 | 3.1954 | 3.9994 | 36.9732 | 36.8978 | 3.9994 | 36.9732 | 36.8978 | -1.1886 | 29.9053 | -12.6438 | 1.251 | -24.574 | 17.9534 | -4.5163 | 2.6474 | 15.3402 | 4.587 | 3.4016 | -9.3158 | 105.4999 | -160.318 | 13.4761 | -74.5001 | 19.682 | -166.5239 | 1.1677 | 0.812 | 0.53877 | 1.1888 | 0.67098 | 0.54818 | 0.75518 | -155.259 | 142.9723 | 0.24528 | -168.199 | 166.0518
Line_1 | 0.17318 | 2.1821 | 2.18 | 0.17318 | 2.1821 | 2.18 | 1.9997 | 25.1967 | 25.1721 | 1.9997 | 25.1967 | 25.1721 | 0.65428 | -14.3042 | 14.6313 | -0.63869 | 16.7802 | -12.1601 | 2.3076 | 4.872 | -3.7182 | -2.2899 | -2.0627 | 6.522 | -74.1703 | 18.8087 | -165.7416 | 105.8297 | -161.1913 | 14.2584 | 1.1995 | 0.59973 | 0.59973 | 1.1888 | 0.67098 | 0.54818 | -8.1967e-06 | 180 | 180 | 0.24528 | -168.199 | 166.0518
Line_2 | 0.17318 | 1.0207 | 1.0161 | 0.17318 | 1.0207 | 1.0161 | 1.9997 | 11.7857 | 11.7331 | 1.9997 | 11.7857 | 11.7331 | 0.62788 | -7.2521 | 6.3302 | -0.61228 | 7.7938 | -5.7933 | 2.3148 | 1.9536 | -2.1846 | -2.2971 | -1.339 | 2.7938 | -74.8299 | 21.5492 | -168.2026 | 105.1701 | -158.4508 | 11.7974 | 1.1994 | 0.63726 | 0.57074 | 1.1888 | 0.67098 | 0.54818 | -0.0058437 | -173.5277 | 172.7571 | 0.24528 | -168.199 | 166.0518
Line_3 | 0.0019937 | 1.1636 | 1.1656 | 0.0019937 | 1.1636 | 1.1656 | 0.023021 | 13.4363 | 13.4593 | 0.023021 | 13.4363 | 13.4593 | 0.026608 | -7.73 | 7.7433 | -0.026606 | 8.4341 | -7.0368 | -0.0073793 | 2.2758 | -2.2795 | 0.0073817 | -1.477 | 3.0811 | 15.5004 | 16.4052 | -163.5964 | -164.4996 | -163.5948 | 16.4036 | 1.1995 | 0.59973 | 0.59973 | 1.1994 | 0.63726 | 0.57074 | -8.1967e-06 | 180 | 180 | -0.0058437 | -173.5277 | 172.7571

## LL_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.34636 | 1.5527 | 1.4433 | 0.34636 | 1.5527 | 1.4433 | 3.9994 | 17.9294 | 16.6655 | 3.9994 | 17.9294 | 16.6655 | -1.1886 | 18.2857 | -1.0226 | 1.251 | -17.032 | 2.1058 | -4.5163 | 1.1452 | 13.5061 | 4.587 | 0.27727 | -12.2771 | 105.4999 | -139.8929 | 27.5046 | -74.5001 | 40.1071 | -152.4954 | 1.1677 | 1.0219 | 0.81274 | 1.1888 | 0.95008 | 0.74743 | 0.75519 | -136.3092 | 121.8343 | 0.24528 | -140.8255 | 127.2372
Line_1 | 0.17318 | 1.0688 | 1.0175 | 0.17318 | 1.0688 | 1.0175 | 1.9997 | 12.3418 | 11.7495 | 1.9997 | 12.3418 | 11.7495 | 0.65428 | -11.127 | 1.8792 | -0.63869 | 11.721 | -1.3408 | 2.3076 | 0.34217 | -8.0681 | -2.2899 | 0.33185 | 8.679 | -74.1703 | 37.5527 | -151.5445 | 105.8297 | -142.4473 | 28.4555 | 1.1995 | 0.90199 | 0.70506 | 1.1888 | 0.95008 | 0.74743 | -5.8121e-06 | -144.2086 | 131.5665 | 0.24528 | -140.8255 | 127.2372
Line_2 | 0.17318 | 0.48729 | 0.42622 | 0.17318 | 0.48729 | 0.42622 | 1.9997 | 5.6267 | 4.9215 | 1.9997 | 5.6267 | 4.9215 | 0.62788 | -5.1875 | 0.85947 | -0.61228 | 5.311 | -0.76501 | 2.3148 | 0.74921 | -3.4909 | -2.2971 | -0.60912 | 3.5981 | -74.8299 | 45.7171 | -154.7659 | 105.1701 | -134.2829 | 25.2341 | 1.1994 | 0.93151 | 0.7305 | 1.1888 | 0.95008 | 0.74743 | -0.0058413 | -142.501 | 129.0653 | 0.24528 | -140.8255 | 127.2372
Line_3 | 0.0019937 | 0.59055 | 0.59248 | 0.0019937 | 0.59055 | 0.59248 | 0.023021 | 6.8191 | 6.8413 | 0.023021 | 6.8191 | 6.8413 | 0.026608 | -6.1277 | 0.90336 | -0.026606 | 6.309 | -0.72083 | -0.0073792 | -0.53266 | -4.7382 | 0.0073815 | 0.73843 | 4.9453 | 15.5002 | 30.8233 | -149.2277 | -164.4998 | -149.1767 | 30.7723 | 1.1995 | 0.90199 | 0.70506 | 1.1994 | 0.93151 | 0.7305 | -5.8121e-06 | -144.2086 | 131.5665 | -0.0058413 | -142.501 | 129.0653

## LL_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.34636 | 1.5527 | 1.4433 | 0.34636 | 1.5527 | 1.4433 | 3.9994 | 17.9294 | 16.6655 | 3.9994 | 17.9294 | 16.6655 | -1.1886 | 18.2857 | -1.0226 | 1.251 | -17.032 | 2.1058 | -4.5163 | 1.1452 | 13.5061 | 4.587 | 0.27727 | -12.2771 | 105.4999 | -139.8929 | 27.5046 | -74.5001 | 40.1071 | -152.4954 | 1.1677 | 1.0219 | 0.81274 | 1.1888 | 0.95008 | 0.74743 | 0.75519 | -136.3092 | 121.8343 | 0.24528 | -140.8255 | 127.2372
Line_1 | 0.17318 | 1.0688 | 1.0175 | 0.17318 | 1.0688 | 1.0175 | 1.9997 | 12.3418 | 11.7495 | 1.9997 | 12.3418 | 11.7495 | 0.65428 | -11.127 | 1.8792 | -0.63869 | 11.721 | -1.3408 | 2.3076 | 0.34217 | -8.0681 | -2.2899 | 0.33185 | 8.679 | -74.1703 | 37.5527 | -151.5445 | 105.8297 | -142.4473 | 28.4555 | 1.1995 | 0.90199 | 0.70506 | 1.1888 | 0.95008 | 0.74743 | -5.8121e-06 | -144.2086 | 131.5665 | 0.24528 | -140.8255 | 127.2372
Line_2 | 0.17318 | 0.48729 | 0.42622 | 0.17318 | 0.48729 | 0.42622 | 1.9997 | 5.6267 | 4.9215 | 1.9997 | 5.6267 | 4.9215 | 0.62788 | -5.1875 | 0.85947 | -0.61228 | 5.311 | -0.76501 | 2.3148 | 0.74921 | -3.4909 | -2.2971 | -0.60912 | 3.5981 | -74.8299 | 45.7171 | -154.7659 | 105.1701 | -134.2829 | 25.2341 | 1.1994 | 0.93151 | 0.7305 | 1.1888 | 0.95008 | 0.74743 | -0.0058413 | -142.501 | 129.0653 | 0.24528 | -140.8255 | 127.2372
Line_3 | 0.0019937 | 0.59055 | 0.59248 | 0.0019937 | 0.59055 | 0.59248 | 0.023021 | 6.8191 | 6.8413 | 0.023021 | 6.8191 | 6.8413 | 0.026608 | -6.1277 | 0.90336 | -0.026606 | 6.309 | -0.72083 | -0.0073792 | -0.53266 | -4.7382 | 0.0073815 | 0.73843 | 4.9453 | 15.5002 | 30.8233 | -149.2277 | -164.4998 | -149.1767 | 30.7723 | 1.1995 | 0.90199 | 0.70506 | 1.1994 | 0.93151 | 0.7305 | -5.8121e-06 | -144.2086 | 131.5665 | -0.0058413 | -142.501 | 129.0653

## LL_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 2.6061 | 2.6061 | 0 | 2.6061 | 2.6061 | 0 | 30.0921 | 30.0921 | 0 | 30.0921 | 30.0921 | 5.9212e-15 | 24.6317 | -2.0295 | -5.9212e-15 | -17.851 | 8.8102 | -2.8422e-14 | -0.29866 | 13.6553 | 2.6053e-14 | 4.3057 | -9.6483 | 0 | -152.3733 | 27.6267 | 0 | 27.6267 | -152.3733 | 1 | 0.8186 | 0.45877 | 1 | 0.61023 | 0.43419 | 4.1861e-13 | -153.068 | 126.0805 | 3.8166e-13 | -165.934 | 160.0269
Line_1 | 0 | 1.7374 | 1.7374 | 0 | 1.7374 | 1.7374 | 0 | 20.0614 | 20.0614 | 0 | 20.0614 | 20.0614 | -1.1842e-15 | -8.8871 | 8.8871 | 3.5527e-15 | 11.9007 | -5.8735 | 7.1054e-15 | 4.6513 | -4.6513 | -9.4739e-15 | -2.8704 | 6.4322 | 0 | 27.6267 | -152.3733 | 0 | -152.3733 | 27.6267 | 1 | 0.5 | 0.5 | 1 | 0.61023 | 0.43419 | 3.6606e-13 | -180 | 180 | 3.8166e-13 | -165.934 | 160.0269
Line_2 | 0 | 0.86868 | 0.86868 | 0 | 0.86868 | 0.86868 | 0 | 10.0307 | 10.0307 | 0 | 10.0307 | 10.0307 | -3.5527e-15 | -5.1969 | 3.6901 | 3.5527e-15 | 5.9503 | -2.9367 | 2.3685e-15 | 1.8804 | -2.7709 | -4.737e-15 | -1.4352 | 3.2161 | 0 | 27.6267 | -152.3733 | 0 | -152.3733 | 27.6267 | 1 | 0.55098 | 0.46005 | 1 | 0.61023 | 0.43419 | 3.6905e-13 | -172.2653 | 170.7242 | 3.8166e-13 | -165.934 | 160.0269
Line_3 | 0 | 0.86868 | 0.86868 | 0 | 0.86868 | 0.86868 | 0 | 10.0307 | 10.0307 | 0 | 10.0307 | 10.0307 | 4.737e-15 | -4.4435 | 4.4435 | 3.0511e-29 | 5.1969 | -3.6901 | 4.737e-15 | 2.3257 | -2.3257 | -4.737e-15 | -1.8804 | 2.7709 | 0 | 27.6267 | -152.3733 | 0 | -152.3733 | 27.6267 | 1 | 0.5 | 0.5 | 1 | 0.55098 | 0.46005 | 3.6606e-13 | -180 | 180 | 3.6905e-13 | -172.2653 | 170.7242

## LL_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 2.6061 | 2.6061 | 0 | 2.6061 | 2.6061 | 0 | 30.0921 | 30.0921 | 0 | 30.0921 | 30.0921 | 5.9212e-15 | 24.6317 | -2.0295 | -5.9212e-15 | -17.851 | 8.8102 | -2.8422e-14 | -0.29866 | 13.6553 | 2.6053e-14 | 4.3057 | -9.6483 | 0 | -152.3733 | 27.6267 | 0 | 27.6267 | -152.3733 | 1 | 0.8186 | 0.45877 | 1 | 0.61023 | 0.43419 | 4.1861e-13 | -153.068 | 126.0805 | 3.8166e-13 | -165.934 | 160.0269
Line_1 | 0 | 1.7374 | 1.7374 | 0 | 1.7374 | 1.7374 | 0 | 20.0614 | 20.0614 | 0 | 20.0614 | 20.0614 | -1.1842e-15 | -8.8871 | 8.8871 | 3.5527e-15 | 11.9007 | -5.8735 | 7.1054e-15 | 4.6513 | -4.6513 | -9.4739e-15 | -2.8704 | 6.4322 | 0 | 27.6267 | -152.3733 | 0 | -152.3733 | 27.6267 | 1 | 0.5 | 0.5 | 1 | 0.61023 | 0.43419 | 3.6606e-13 | -180 | 180 | 3.8166e-13 | -165.934 | 160.0269
Line_2 | 0 | 0.86868 | 0.86868 | 0 | 0.86868 | 0.86868 | 0 | 10.0307 | 10.0307 | 0 | 10.0307 | 10.0307 | -3.5527e-15 | -5.1969 | 3.6901 | 3.5527e-15 | 5.9503 | -2.9367 | 2.3685e-15 | 1.8804 | -2.7709 | -4.737e-15 | -1.4352 | 3.2161 | 0 | 27.6267 | -152.3733 | 0 | -152.3733 | 27.6267 | 1 | 0.55098 | 0.46005 | 1 | 0.61023 | 0.43419 | 3.6905e-13 | -172.2653 | 170.7242 | 3.8166e-13 | -165.934 | 160.0269
Line_3 | 0 | 0.86868 | 0.86868 | 0 | 0.86868 | 0.86868 | 0 | 10.0307 | 10.0307 | 0 | 10.0307 | 10.0307 | 4.737e-15 | -4.4435 | 4.4435 | 3.0511e-29 | 5.1969 | -3.6901 | 4.737e-15 | 2.3257 | -2.3257 | -4.737e-15 | -1.8804 | 2.7709 | 0 | 27.6267 | -152.3733 | 0 | -152.3733 | 27.6267 | 1 | 0.5 | 0.5 | 1 | 0.55098 | 0.46005 | 3.6606e-13 | -180 | 180 | 3.6905e-13 | -172.2653 | 170.7242

## LL_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 1.3721 | 1.3721 | 0 | 1.3721 | 1.3721 | 0 | 15.8432 | 15.8432 | 0 | 15.8432 | 15.8432 | 1.1842e-15 | 14.2512 | 1.4266 | -2.3685e-15 | -12.3717 | 0.45296 | -1.6579e-14 | 1.9064 | 11.2087 | 1.6579e-14 | -0.79565 | -10.098 | 0 | -144.0449 | 35.9551 | 0 | 35.9551 | -144.0449 | 1 | 0.90753 | 0.71319 | 1 | 0.7825 | 0.63801 | 2.0589e-13 | -136.4258 | 118.7019 | 1.8912e-13 | -140.3651 | 128.5235
Line_1 | 0 | 0.9147 | 0.9147 | 0 | 0.9147 | 0.9147 | 0 | 10.5621 | 10.5621 | 0 | 10.5621 | 10.5621 | -2.9606e-15 | -7.4125 | 1.1373 | 2.9606e-15 | 8.2478 | -0.30197 | 4.737e-15 | -0.036791 | -6.2383 | -4.737e-15 | 0.53044 | 6.732 | 0 | 35.9551 | -144.0449 | 0 | -144.0449 | 35.9551 | 1 | 0.70181 | 0.60037 | 1 | 0.7825 | 0.63801 | 1.8122e-13 | -143.7605 | 136.2873 | 1.8912e-13 | -140.3651 | 128.5235
Line_2 | 0 | 0.45735 | 0.45735 | 0 | 0.45735 | 0.45735 | 0 | 5.2811 | 5.2811 | 0 | 5.2811 | 5.2811 | -5.3291e-15 | -3.9151 | 0.35982 | 2.3685e-15 | 4.1239 | -0.15099 | 2.3685e-15 | -0.14181 | -3.2426 | -2.3685e-15 | 0.26522 | 3.366 | 0 | 35.9551 | -144.0449 | 0 | -144.0449 | 35.9551 | 1 | 0.74183 | 0.61777 | 1 | 0.7825 | 0.63801 | 1.8205e-13 | -141.9705 | 132.2872 | 1.8912e-13 | -140.3651 | 128.5235
Line_3 | 0 | 0.45735 | 0.45735 | 0 | 0.45735 | 0.45735 | 0 | 5.2811 | 5.2811 | 0 | 5.2811 | 5.2811 | 1.7764e-15 | -3.7062 | 0.56866 | -2.3685e-15 | 3.9151 | -0.35982 | 2.3685e-15 | -0.018396 | -3.1192 | -2.3685e-15 | 0.14181 | 3.2426 | 0 | 35.9551 | -144.0449 | 0 | -144.0449 | 35.9551 | 1 | 0.70181 | 0.60037 | 1 | 0.74183 | 0.61777 | 1.8122e-13 | -143.7605 | 136.2873 | 1.8205e-13 | -141.9705 | 132.2872

## LL_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0 | 1.3721 | 1.3721 | 0 | 1.3721 | 1.3721 | 0 | 15.8432 | 15.8432 | 0 | 15.8432 | 15.8432 | 1.1842e-15 | 14.2512 | 1.4266 | -2.3685e-15 | -12.3717 | 0.45296 | -1.6579e-14 | 1.9064 | 11.2087 | 1.6579e-14 | -0.79565 | -10.098 | 0 | -144.0449 | 35.9551 | 0 | 35.9551 | -144.0449 | 1 | 0.90753 | 0.71319 | 1 | 0.7825 | 0.63801 | 2.0589e-13 | -136.4258 | 118.7019 | 1.8912e-13 | -140.3651 | 128.5235
Line_1 | 0 | 0.9147 | 0.9147 | 0 | 0.9147 | 0.9147 | 0 | 10.5621 | 10.5621 | 0 | 10.5621 | 10.5621 | -2.9606e-15 | -7.4125 | 1.1373 | 2.9606e-15 | 8.2478 | -0.30197 | 4.737e-15 | -0.036791 | -6.2383 | -4.737e-15 | 0.53044 | 6.732 | 0 | 35.9551 | -144.0449 | 0 | -144.0449 | 35.9551 | 1 | 0.70181 | 0.60037 | 1 | 0.7825 | 0.63801 | 1.8122e-13 | -143.7605 | 136.2873 | 1.8912e-13 | -140.3651 | 128.5235
Line_2 | 0 | 0.45735 | 0.45735 | 0 | 0.45735 | 0.45735 | 0 | 5.2811 | 5.2811 | 0 | 5.2811 | 5.2811 | -5.3291e-15 | -3.9151 | 0.35982 | 2.3685e-15 | 4.1239 | -0.15099 | 2.3685e-15 | -0.14181 | -3.2426 | -2.3685e-15 | 0.26522 | 3.366 | 0 | 35.9551 | -144.0449 | 0 | -144.0449 | 35.9551 | 1 | 0.74183 | 0.61777 | 1 | 0.7825 | 0.63801 | 1.8205e-13 | -141.9705 | 132.2872 | 1.8912e-13 | -140.3651 | 128.5235
Line_3 | 0 | 0.45735 | 0.45735 | 0 | 0.45735 | 0.45735 | 0 | 5.2811 | 5.2811 | 0 | 5.2811 | 5.2811 | 1.7764e-15 | -3.7062 | 0.56866 | -2.3685e-15 | 3.9151 | -0.35982 | 2.3685e-15 | -0.018396 | -3.1192 | -2.3685e-15 | 0.14181 | 3.2426 | 0 | 35.9551 | -144.0449 | 0 | -144.0449 | 35.9551 | 1 | 0.70181 | 0.60037 | 1 | 0.74183 | 0.61777 | 1.8122e-13 | -143.7605 | 136.2873 | 1.8205e-13 | -141.9705 | 132.2872

## LG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 3.0198 | 0.34521 | 0.35464 | 3.0193 | 0.34522 | 0.3537 | 34.8702 | 3.9861 | 4.095 | 34.8641 | 3.9863 | 4.0842 | 26.0245 | -0.64896 | -1.9761 | -10.4721 | 1.9236 | 1.8093 | 13.0109 | -3.9642 | -4.5042 | -5.2425 | 3.6319 | 5.8468 | -46.68 | -15.9627 | -133.9651 | 133.3373 | 164.2118 | 45.9568 | 0.8344 | 1.0077 | 1.2011 | 0.33591 | 1.031 | 1.4985 | -20.1173 | -115.2599 | 112.3467 | -20.0695 | -133.696 | 118.7624
Line_1 | 2.0621 | 0.17295 | 0.17451 | 2.0632 | 0.17257 | 0.17696 | 23.811 | 1.9971 | 2.0151 | 23.8233 | 1.9927 | 2.0434 | 6.57e-11 | 1.4138 | 0.83666 | 7.1088 | -0.97097 | -0.92215 | -1.1752e-10 | 1.6769 | 3.3216 | 3.6747 | -1.8105 | -2.9199 | 132.6614 | 165.3677 | 45.9914 | -47.4051 | -15.4915 | -133.7108 | 0 | 1.0983 | 1.6999 | 0.33591 | 1.031 | 1.4985 | 0 | -144.7666 | 121.8536 | -20.0695 | -133.696 | 118.7624
Line_2 | 0.95585 | 0.17294 | 0.1746 | 0.95672 | 0.17266 | 0.17675 | 11.0372 | 1.997 | 2.0161 | 11.0472 | 1.9937 | 2.0409 | -1.7404 | 1.1938 | 0.83968 | 3.3634 | -0.95265 | -0.88711 | -0.80324 | 1.7607 | 3.1235 | 1.5678 | -1.8214 | -2.9268 | 135.0664 | 164.6733 | 45.3469 | -45.0615 | -16.0849 | -134.3759 | 0.17367 | 1.0652 | 1.6043 | 0.33591 | 1.031 | 1.4985 | -20.159 | -139.466 | 120.3002 | -20.0695 | -133.696 | 118.7624
Line_3 | 1.1072 | 0.0033973 | 0.0019956 | 1.1085 | 0.00055619 | 0.0028978 | 12.7853 | 0.039228 | 0.023043 | 12.7999 | 0.0064223 | 0.033461 | 3.7474e-11 | 0.034676 | 0.022366 | 1.938 | -0.003214 | -0.052034 | -6.1825e-11 | -0.025571 | -0.032158 | 1.0889 | 0.0060394 | -0.013193 | 130.6473 | -108.3602 | 177.0352 | -49.4896 | 102.5135 | -73.9268 | 0 | 1.0983 | 1.6999 | 0.17367 | 1.0652 | 1.6043 | 0 | -144.7666 | 121.8536 | -20.159 | -139.466 | 120.3002

## LG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 3.0198 | 0.34521 | 0.35464 | 3.0193 | 0.34522 | 0.3537 | 34.8702 | 3.9861 | 4.095 | 34.8641 | 3.9863 | 4.0842 | 26.0245 | -0.64896 | -1.9761 | -10.4721 | 1.9236 | 1.8093 | 13.0109 | -3.9642 | -4.5042 | -5.2425 | 3.6319 | 5.8468 | -46.68 | -15.9627 | -133.9651 | 133.3373 | 164.2118 | 45.9568 | 0.8344 | 1.0077 | 1.2011 | 0.33591 | 1.031 | 1.4985 | -20.1173 | -115.2599 | 112.3467 | -20.0695 | -133.696 | 118.7624
Line_1 | 2.0621 | 0.17295 | 0.17451 | 2.0632 | 0.17257 | 0.17696 | 23.811 | 1.9971 | 2.0151 | 23.8233 | 1.9927 | 2.0434 | 6.57e-11 | 1.4138 | 0.83666 | 7.1088 | -0.97097 | -0.92215 | -1.1752e-10 | 1.6769 | 3.3216 | 3.6747 | -1.8105 | -2.9199 | 132.6614 | 165.3677 | 45.9914 | -47.4051 | -15.4915 | -133.7108 | 0 | 1.0983 | 1.6999 | 0.33591 | 1.031 | 1.4985 | 0 | -144.7666 | 121.8536 | -20.0695 | -133.696 | 118.7624
Line_2 | 0.95585 | 0.17294 | 0.1746 | 0.95672 | 0.17266 | 0.17675 | 11.0372 | 1.997 | 2.0161 | 11.0472 | 1.9937 | 2.0409 | -1.7404 | 1.1938 | 0.83968 | 3.3634 | -0.95265 | -0.88711 | -0.80324 | 1.7607 | 3.1235 | 1.5678 | -1.8214 | -2.9268 | 135.0664 | 164.6733 | 45.3469 | -45.0615 | -16.0849 | -134.3759 | 0.17367 | 1.0652 | 1.6043 | 0.33591 | 1.031 | 1.4985 | -20.159 | -139.466 | 120.3002 | -20.0695 | -133.696 | 118.7624
Line_3 | 1.1072 | 0.0033973 | 0.0019956 | 1.1085 | 0.00055619 | 0.0028978 | 12.7853 | 0.039228 | 0.023043 | 12.7999 | 0.0064223 | 0.033461 | 3.7474e-11 | 0.034676 | 0.022366 | 1.938 | -0.003214 | -0.052034 | -6.1825e-11 | -0.025571 | -0.032158 | 1.0889 | 0.0060394 | -0.013193 | 130.6473 | -108.3602 | 177.0352 | -49.4896 | 102.5135 | -73.9268 | 0 | 1.0983 | 1.6999 | 0.17367 | 1.0652 | 1.6043 | 0 | -144.7666 | 121.8536 | -20.159 | -139.466 | 120.3002

## LG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.94247 | 0.34606 | 0.34936 | 0.94231 | 0.34605 | 0.34903 | 10.8827 | 3.996 | 4.0341 | 10.8809 | 3.9959 | 4.0302 | 9.6465 | -0.99507 | -1.4801 | -7.9096 | 1.5132 | 1.4345 | 5.8317 | -4.3083 | -4.525 | -5.1841 | 4.2437 | 5.0562 | -36.8837 | -15.0442 | -134.275 | 143.1381 | 165.0204 | 45.6927 | 1.0358 | 1.1065 | 1.1802 | 0.86914 | 1.1275 | 1.3041 | -5.7288 | -118.0495 | 117.6122 | -3.6204 | -124.6051 | 119.8534
Line_1 | 0.67381 | 0.17312 | 0.17366 | 0.67413 | 0.17301 | 0.17456 | 7.7805 | 1.999 | 2.0053 | 7.7842 | 1.9978 | 2.0156 | -4.6182 | 0.94602 | 0.70371 | 5.4547 | -0.76831 | -0.73204 | -3.6354 | 2.0863 | 2.6843 | 4.0024 | -2.1175 | -2.5245 | 140.1879 | 165.6574 | 45.8977 | -39.8901 | -14.6622 | -133.9759 | 0.7554 | 1.146 | 1.3838 | 0.86914 | 1.1275 | 1.3041 | -1.6029 | -128.7341 | 121.2078 | -3.6204 | -124.6051 | 119.8534
Line_2 | 0.27134 | 0.17312 | 0.1737 | 0.27147 | 0.17304 | 0.17448 | 3.1332 | 1.999 | 2.0057 | 3.1347 | 1.9981 | 2.0147 | -2.2962 | 0.84655 | 0.69186 | 2.4549 | -0.74493 | -0.70246 | -1.1351 | 2.1188 | 2.6163 | 1.1817 | -2.1262 | -2.5317 | 150.8542 | 164.9849 | 45.2443 | -29.3239 | -15.297 | -134.6389 | 0.81752 | 1.1414 | 1.3493 | 0.86914 | 1.1275 | 1.3041 | -2.84 | -126.7936 | 120.4318 | -3.6204 | -124.6051 | 119.8534
Line_3 | 0.41003 | 0.0025155 | 0.0018489 | 0.4105 | 0.0014358 | 0.002275 | 4.7346 | 0.029047 | 0.02135 | 4.7401 | 0.016579 | 0.026269 | -2.521 | 0.030671 | 0.025744 | 2.7838 | -0.017154 | -0.035424 | -2.5369 | -0.012933 | -0.014496 | 2.6958 | 0.0079902 | 0.0011779 | 133.2171 | -105.8699 | 150.5916 | -46.9199 | 78.1824 | -57.6637 | 0.7554 | 1.146 | 1.3838 | 0.81752 | 1.1414 | 1.3493 | -1.6029 | -128.7341 | 121.2078 | -2.84 | -126.7936 | 120.4318

## LG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.94247 | 0.34606 | 0.34936 | 0.94231 | 0.34605 | 0.34903 | 10.8827 | 3.996 | 4.0341 | 10.8809 | 3.9959 | 4.0302 | 9.6465 | -0.99507 | -1.4801 | -7.9096 | 1.5132 | 1.4345 | 5.8317 | -4.3083 | -4.525 | -5.1841 | 4.2437 | 5.0562 | -36.8837 | -15.0442 | -134.275 | 143.1381 | 165.0204 | 45.6927 | 1.0358 | 1.1065 | 1.1802 | 0.86914 | 1.1275 | 1.3041 | -5.7288 | -118.0495 | 117.6122 | -3.6204 | -124.6051 | 119.8534
Line_1 | 0.67381 | 0.17312 | 0.17366 | 0.67413 | 0.17301 | 0.17456 | 7.7805 | 1.999 | 2.0053 | 7.7842 | 1.9978 | 2.0156 | -4.6182 | 0.94602 | 0.70371 | 5.4547 | -0.76831 | -0.73204 | -3.6354 | 2.0863 | 2.6843 | 4.0024 | -2.1175 | -2.5245 | 140.1879 | 165.6574 | 45.8977 | -39.8901 | -14.6622 | -133.9759 | 0.7554 | 1.146 | 1.3838 | 0.86914 | 1.1275 | 1.3041 | -1.6029 | -128.7341 | 121.2078 | -3.6204 | -124.6051 | 119.8534
Line_2 | 0.27134 | 0.17312 | 0.1737 | 0.27147 | 0.17304 | 0.17448 | 3.1332 | 1.999 | 2.0057 | 3.1347 | 1.9981 | 2.0147 | -2.2962 | 0.84655 | 0.69186 | 2.4549 | -0.74493 | -0.70246 | -1.1351 | 2.1188 | 2.6163 | 1.1817 | -2.1262 | -2.5317 | 150.8542 | 164.9849 | 45.2443 | -29.3239 | -15.297 | -134.6389 | 0.81752 | 1.1414 | 1.3493 | 0.86914 | 1.1275 | 1.3041 | -2.84 | -126.7936 | 120.4318 | -3.6204 | -124.6051 | 119.8534
Line_3 | 0.41003 | 0.0025155 | 0.0018489 | 0.4105 | 0.0014358 | 0.002275 | 4.7346 | 0.029047 | 0.02135 | 4.7401 | 0.016579 | 0.026269 | -2.521 | 0.030671 | 0.025744 | 2.7838 | -0.017154 | -0.035424 | -2.5369 | -0.012933 | -0.014496 | 2.6958 | 0.0079902 | 0.0011779 | 133.2171 | -105.8699 | 150.5916 | -46.9199 | 78.1824 | -57.6637 | 0.7554 | 1.146 | 1.3838 | 0.81752 | 1.1414 | 1.3493 | -1.6029 | -128.7341 | 121.2078 | -2.84 | -126.7936 | 120.4318

## LG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.9064 | 0.009021 | 0.009021 | 1.9061 | 0.0079999 | 0.0079999 | 22.0137 | 0.10417 | 0.10417 | 22.01 | 0.092374 | 0.092374 | 18.3831 | 0.091164 | -0.080777 | -7.3424 | -0.077464 | 0.074589 | 5.2779 | -0.018978 | -0.073635 | -2.1286 | 0.047365 | 0.097155 | -32.137 | -107.6345 | -107.6345 | 147.8922 | 71.8691 | 71.8691 | 0.86881 | 0.89395 | 1.0493 | 0.34733 | 0.98292 | 1.326 | -16.118 | -119.3942 | 114.7173 | -15.9409 | -139.5747 | 124.3542
Line_1 | 1.2698 | 0.0014431 | 0.0014431 | 1.2705 | 0.0041094 | 0.0041094 | 14.6625 | 0.016663 | 0.016663 | 14.6699 | 0.047451 | 0.047451 | -2.3443e-11 | -0.013625 | 0.01377 | 4.8951 | 0.039815 | -0.038267 | 6.7148e-12 | 0.012244 | 0.021327 | 1.4142 | -0.024292 | -0.049944 | 148.0625 | 71.6564 | 71.6564 | -32.0543 | -108.1867 | -108.1867 | 0 | 1.0993 | 1.5235 | 0.34733 | 0.98292 | 1.326 | 0 | -150.2873 | 128.8071 | -15.9409 | -139.5747 | 124.3542
Line_2 | 0.6351 | 0.0015526 | 0.0015526 | 0.63568 | 0.0038905 | 0.0038905 | 7.3335 | 0.017927 | 0.017927 | 7.3401 | 0.044923 | 0.044923 | -1.2212 | -0.014874 | 0.014576 | 2.4473 | 0.037648 | -0.036323 | -0.35807 | 0.011123 | 0.020964 | 0.71443 | -0.023073 | -0.04721 | 147.9895 | 71.5236 | 71.5236 | -32.2148 | -108.0719 | -108.0719 | 0.17353 | 1.036 | 1.4243 | 0.34733 | 0.98292 | 1.326 | -15.6684 | -145.266 | 126.712 | -15.9409 | -139.5747 | 124.3542
Line_3 | 0.6344 | 0.0014431 | 0.0014431 | 0.6351 | 0.0015526 | 0.0015526 | 7.3254 | 0.016663 | 0.016663 | 7.3335 | 0.017927 | 0.017927 | -1.1701e-11 | 0.013625 | -0.01377 | 1.2212 | 0.014874 | -0.014576 | 3.3936e-12 | -0.012244 | -0.021327 | 0.35807 | -0.011123 | -0.020964 | 148.2525 | -108.3436 | -108.3436 | -32.0105 | -108.4764 | -108.4764 | 0 | 1.0993 | 1.5235 | 0.17353 | 1.036 | 1.4243 | 0 | -150.2873 | 128.8071 | -15.6684 | -145.266 | 126.712

## LG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.9064 | 0.009021 | 0.009021 | 1.9061 | 0.0079999 | 0.0079999 | 22.0137 | 0.10417 | 0.10417 | 22.01 | 0.092374 | 0.092374 | 18.3831 | 0.091164 | -0.080777 | -7.3424 | -0.077464 | 0.074589 | 5.2779 | -0.018978 | -0.073635 | -2.1286 | 0.047365 | 0.097155 | -32.137 | -107.6345 | -107.6345 | 147.8922 | 71.8691 | 71.8691 | 0.86881 | 0.89395 | 1.0493 | 0.34733 | 0.98292 | 1.326 | -16.118 | -119.3942 | 114.7173 | -15.9409 | -139.5747 | 124.3542
Line_1 | 1.2698 | 0.0014431 | 0.0014431 | 1.2705 | 0.0041094 | 0.0041094 | 14.6625 | 0.016663 | 0.016663 | 14.6699 | 0.047451 | 0.047451 | -2.3443e-11 | -0.013625 | 0.01377 | 4.8951 | 0.039815 | -0.038267 | 6.7148e-12 | 0.012244 | 0.021327 | 1.4142 | -0.024292 | -0.049944 | 148.0625 | 71.6564 | 71.6564 | -32.0543 | -108.1867 | -108.1867 | 0 | 1.0993 | 1.5235 | 0.34733 | 0.98292 | 1.326 | 0 | -150.2873 | 128.8071 | -15.9409 | -139.5747 | 124.3542
Line_2 | 0.6351 | 0.0015526 | 0.0015526 | 0.63568 | 0.0038905 | 0.0038905 | 7.3335 | 0.017927 | 0.017927 | 7.3401 | 0.044923 | 0.044923 | -1.2212 | -0.014874 | 0.014576 | 2.4473 | 0.037648 | -0.036323 | -0.35807 | 0.011123 | 0.020964 | 0.71443 | -0.023073 | -0.04721 | 147.9895 | 71.5236 | 71.5236 | -32.2148 | -108.0719 | -108.0719 | 0.17353 | 1.036 | 1.4243 | 0.34733 | 0.98292 | 1.326 | -15.6684 | -145.266 | 126.712 | -15.9409 | -139.5747 | 124.3542
Line_3 | 0.6344 | 0.0014431 | 0.0014431 | 0.6351 | 0.0015526 | 0.0015526 | 7.3254 | 0.016663 | 0.016663 | 7.3335 | 0.017927 | 0.017927 | -1.1701e-11 | 0.013625 | -0.01377 | 1.2212 | 0.014874 | -0.014576 | 3.3936e-12 | -0.012244 | -0.021327 | 0.35807 | -0.011123 | -0.020964 | 148.2525 | -108.3436 | -108.3436 | -32.0105 | -108.4764 | -108.4764 | 0 | 1.0993 | 1.5235 | 0.17353 | 1.036 | 1.4243 | 0 | -150.2873 | 128.8071 | -15.6684 | -145.266 | 126.712

## LG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.88591 | 0.004192 | 0.004192 | 0.88576 | 0.0037174 | 0.0037174 | 10.2296 | 0.048405 | 0.048405 | 10.2278 | 0.042925 | 0.042925 | 7.8711 | 0.045912 | -0.030255 | -5.4884 | -0.039981 | 0.027292 | 5.0772 | -0.0037501 | -0.038787 | -4.3945 | 0.0097178 | 0.041373 | -39.2053 | -114.7028 | -114.7028 | 140.8239 | 64.8008 | 64.8008 | 0.91563 | 0.95167 | 1.0163 | 0.68743 | 0.95854 | 1.1547 | -6.3817 | -119.3723 | 117.3426 | -0.49235 | -128.8604 | 121.3898
Line_1 | 0.59007 | 0.00067058 | 0.00067058 | 0.59037 | 0.0019096 | 0.0019096 | 6.8135 | 0.0077432 | 0.0077432 | 6.8169 | 0.02205 | 0.02205 | -2.6078 | -0.0071365 | 0.0049775 | 3.6608 | 0.020543 | -0.013999 | -2.6135 | 0.0025362 | 0.0082914 | 2.9255 | -0.0049719 | -0.021266 | 140.9942 | 64.5881 | 64.5881 | -39.1226 | -115.255 | -115.255 | 0.54187 | 0.97812 | 1.2489 | 0.68743 | 0.95854 | 1.1547 | 6.0575 | -134.9766 | 123.6111 | -0.49235 | -128.8604 | 121.3898
Line_2 | 0.29512 | 0.00072146 | 0.00072146 | 0.29539 | 0.0018079 | 0.0018079 | 3.4078 | 0.0083306 | 0.0083306 | 3.4109 | 0.020875 | 0.020875 | -1.5663 | -0.0077242 | 0.0052944 | 1.8276 | 0.019439 | -0.013293 | -1.3861 | 0.0022757 | 0.0084977 | 1.4689 | -0.0047459 | -0.020107 | 140.9212 | 64.4553 | 64.4553 | -39.2831 | -115.1402 | -115.1402 | 0.61376 | 0.96661 | 1.2018 | 0.68743 | 0.95854 | 1.1547 | 2.4293 | -131.9604 | 122.5306 | -0.49235 | -128.8604 | 121.3898
Line_3 | 0.2948 | 0.00067058 | 0.00067058 | 0.29512 | 0.00072146 | 0.00072146 | 3.404 | 0.0077432 | 0.0077432 | 3.4078 | 0.0083306 | 0.0083306 | -1.3072 | 0.0071365 | -0.0049775 | 1.5663 | 0.0077242 | -0.0052944 | -1.3014 | -0.0025362 | -0.0082914 | 1.3861 | -0.0022757 | -0.0084977 | 141.1842 | -115.4119 | -115.4119 | -39.0788 | -115.5447 | -115.5447 | 0.54187 | 0.97812 | 1.2489 | 0.61376 | 0.96661 | 1.2018 | 6.0575 | -134.9766 | 123.6111 | 2.4293 | -131.9604 | 122.5306

## LG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.88591 | 0.004192 | 0.004192 | 0.88576 | 0.0037174 | 0.0037174 | 10.2296 | 0.048405 | 0.048405 | 10.2278 | 0.042925 | 0.042925 | 7.8711 | 0.045912 | -0.030255 | -5.4884 | -0.039981 | 0.027292 | 5.0772 | -0.0037501 | -0.038787 | -4.3945 | 0.0097178 | 0.041373 | -39.2053 | -114.7028 | -114.7028 | 140.8239 | 64.8008 | 64.8008 | 0.91563 | 0.95167 | 1.0163 | 0.68743 | 0.95854 | 1.1547 | -6.3817 | -119.3723 | 117.3426 | -0.49235 | -128.8604 | 121.3898
Line_1 | 0.59007 | 0.00067058 | 0.00067058 | 0.59037 | 0.0019096 | 0.0019096 | 6.8135 | 0.0077432 | 0.0077432 | 6.8169 | 0.02205 | 0.02205 | -2.6078 | -0.0071365 | 0.0049775 | 3.6608 | 0.020543 | -0.013999 | -2.6135 | 0.0025362 | 0.0082914 | 2.9255 | -0.0049719 | -0.021266 | 140.9942 | 64.5881 | 64.5881 | -39.1226 | -115.255 | -115.255 | 0.54187 | 0.97812 | 1.2489 | 0.68743 | 0.95854 | 1.1547 | 6.0575 | -134.9766 | 123.6111 | -0.49235 | -128.8604 | 121.3898
Line_2 | 0.29512 | 0.00072146 | 0.00072146 | 0.29539 | 0.0018079 | 0.0018079 | 3.4078 | 0.0083306 | 0.0083306 | 3.4109 | 0.020875 | 0.020875 | -1.5663 | -0.0077242 | 0.0052944 | 1.8276 | 0.019439 | -0.013293 | -1.3861 | 0.0022757 | 0.0084977 | 1.4689 | -0.0047459 | -0.020107 | 140.9212 | 64.4553 | 64.4553 | -39.2831 | -115.1402 | -115.1402 | 0.61376 | 0.96661 | 1.2018 | 0.68743 | 0.95854 | 1.1547 | 2.4293 | -131.9604 | 122.5306 | -0.49235 | -128.8604 | 121.3898
Line_3 | 0.2948 | 0.00067058 | 0.00067058 | 0.29512 | 0.00072146 | 0.00072146 | 3.404 | 0.0077432 | 0.0077432 | 3.4078 | 0.0083306 | 0.0083306 | -1.3072 | 0.0071365 | -0.0049775 | 1.5663 | 0.0077242 | -0.0052944 | -1.3014 | -0.0025362 | -0.0082914 | 1.3861 | -0.0022757 | -0.0084977 | 141.1842 | -115.4119 | -115.4119 | -39.0788 | -115.5447 | -115.5447 | 0.54187 | 0.97812 | 1.2489 | 0.61376 | 0.96661 | 1.2018 | 6.0575 | -134.9766 | 123.6111 | 2.4293 | -131.9604 | 122.5306

## LLG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.3527 | 4.0931 | 2.5203 | 0.35193 | 4.0932 | 2.5198 | 4.0727 | 47.2626 | 29.102 | 4.0637 | 47.2637 | 29.0963 | -1.5144 | 32.3485 | -1.2901 | 2.1393 | -13.0351 | 0.4854 | -4.1662 | 8.7334 | 16.0655 | 5.0545 | -3.5649 | -6.4702 | 105.0625 | -175.1099 | 35.7971 | -74.8997 | 4.9014 | -144.2176 | 1.0885 | 0.70895 | 0.55382 | 1.3506 | 0.28592 | 0.223 | -4.9137 | -160.0014 | 130.3882 | -7.8398 | -159.8029 | 130.0728
Line_1 | 0.17418 | 2.7836 | 1.7349 | 0.17603 | 2.7832 | 1.7363 | 2.0112 | 32.1423 | 20.0329 | 2.0326 | 32.1372 | 20.0493 | 1.2865 | 6.9228e-11 | 4.8196e-11 | -1.0838 | 8.8463 | -0.3137 | 2.7793 | -3.6839e-11 | 4.3825e-13 | -2.5223 | 2.4851 | 4.4599 | -74.3195 | 4.5467 | -143.9985 | 105.4125 | -175.494 | 36.0493 | 1.5228 | 0 | 0 | 1.3506 | 0.28592 | 0.223 | -9.1588 | 0 | 0 | -7.8398 | -159.8029 | 130.0728
Line_2 | 0.17426 | 1.3106 | 0.78235 | 0.1759 | 1.3102 | 0.78356 | 2.0121 | 15.1337 | 9.0337 | 2.0311 | 15.1289 | 9.0478 | 1.1636 | -2.1744 | 0.060341 | -1.0555 | 4.1887 | -0.1717 | 2.6587 | -0.58349 | -1.0457 | -2.5321 | 1.0798 | 2.0103 | -74.9876 | 5.8172 | -144.9046 | 104.7879 | -174.2586 | 35.191 | 1.4423 | 0.14876 | 0.11595 | 1.3506 | 0.28592 | 0.223 | -8.6254 | -159.1614 | 128.3979 | -7.8398 | -159.8029 | 130.0728
Line_3 | 0.0026377 | 1.4738 | 0.95202 | 0.0018488 | 1.4733 | 0.95364 | 0.030457 | 17.0181 | 10.993 | 0.021348 | 17.0125 | 11.0117 | 0.031691 | 3.7018e-11 | 2.6448e-11 | -0.030201 | 2.4141 | -0.035647 | -0.033863 | -1.8803e-11 | -8.3083e-14 | -0.0059999 | 0.75975 | 1.2763 | 37.7388 | 3.4552 | -143.2975 | 160.138 | -176.631 | 36.798 | 1.5228 | 0 | 0 | 1.4423 | 0.14876 | 0.11595 | -9.1588 | 0 | 0 | -8.6254 | -159.1614 | 128.3979

## LLG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.3527 | 4.0931 | 2.5203 | 0.35193 | 4.0932 | 2.5198 | 4.0727 | 47.2626 | 29.102 | 4.0637 | 47.2637 | 29.0963 | -1.5144 | 32.3485 | -1.2901 | 2.1393 | -13.0351 | 0.4854 | -4.1662 | 8.7334 | 16.0655 | 5.0545 | -3.5649 | -6.4702 | 105.0625 | -175.1099 | 35.7971 | -74.8997 | 4.9014 | -144.2176 | 1.0885 | 0.70895 | 0.55382 | 1.3506 | 0.28592 | 0.223 | -4.9137 | -160.0014 | 130.3882 | -7.8398 | -159.8029 | 130.0728
Line_1 | 0.17418 | 2.7836 | 1.7349 | 0.17603 | 2.7832 | 1.7363 | 2.0112 | 32.1423 | 20.0329 | 2.0326 | 32.1372 | 20.0493 | 1.2865 | 6.9228e-11 | 4.8196e-11 | -1.0838 | 8.8463 | -0.3137 | 2.7793 | -3.6839e-11 | 4.3825e-13 | -2.5223 | 2.4851 | 4.4599 | -74.3195 | 4.5467 | -143.9985 | 105.4125 | -175.494 | 36.0493 | 1.5228 | 0 | 0 | 1.3506 | 0.28592 | 0.223 | -9.1588 | 0 | 0 | -7.8398 | -159.8029 | 130.0728
Line_2 | 0.17426 | 1.3106 | 0.78235 | 0.1759 | 1.3102 | 0.78356 | 2.0121 | 15.1337 | 9.0337 | 2.0311 | 15.1289 | 9.0478 | 1.1636 | -2.1744 | 0.060341 | -1.0555 | 4.1887 | -0.1717 | 2.6587 | -0.58349 | -1.0457 | -2.5321 | 1.0798 | 2.0103 | -74.9876 | 5.8172 | -144.9046 | 104.7879 | -174.2586 | 35.191 | 1.4423 | 0.14876 | 0.11595 | 1.3506 | 0.28592 | 0.223 | -8.6254 | -159.1614 | 128.3979 | -7.8398 | -159.8029 | 130.0728
Line_3 | 0.0026377 | 1.4738 | 0.95202 | 0.0018488 | 1.4733 | 0.95364 | 0.030457 | 17.0181 | 10.993 | 0.021348 | 17.0125 | 11.0117 | 0.031691 | 3.7018e-11 | 2.6448e-11 | -0.030201 | 2.4141 | -0.035647 | -0.033863 | -1.8803e-11 | -8.3083e-14 | -0.0059999 | 0.75975 | 1.2763 | 37.7388 | 3.4552 | -143.2975 | 160.138 | -176.631 | 36.798 | 1.5228 | 0 | 0 | 1.4423 | 0.14876 | 0.11595 | -9.1588 | 0 | 0 | -8.6254 | -159.1614 | 128.3979

## LLG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.34897 | 1.1192 | 0.85221 | 0.34865 | 1.1193 | 0.85186 | 4.0296 | 12.923 | 9.8404 | 4.0258 | 12.925 | 9.8364 | -1.3024 | 11.6774 | 6.4187 | 1.6451 | -10.0838 | -5.9331 | -4.3505 | 6.2955 | 6.7981 | 4.7439 | -6.5565 | -5.3242 | 105.2608 | -158.5918 | 70.5059 | -74.7166 | 21.424 | -109.4989 | 1.127 | 1.0266 | 0.95011 | 1.2472 | 0.9306 | 0.81043 | -1.405 | -130.262 | 117.15 | -3.8418 | -125.5439 | 112.4049
Line_1 | 0.17359 | 0.79385 | 0.61905 | 0.17435 | 0.79336 | 0.61992 | 2.0045 | 9.1666 | 7.1481 | 2.0132 | 9.161 | 7.1582 | 0.94694 | -6.1529 | -3.9214 | -0.83595 | 6.9393 | 4.1557 | 2.4807 | -5.0294 | -3.3102 | -2.3677 | 4.9522 | 4.0478 | -74.2501 | 18.9957 | -111.852 | 105.6045 | -161.0573 | 68.1585 | 1.3247 | 0.86694 | 0.71791 | 1.2472 | 0.9306 | 0.81043 | -5.143 | -121.7414 | 108.3167 | -3.8418 | -125.5439 | 112.4049
Line_2 | 0.17362 | 0.32903 | 0.23306 | 0.1743 | 0.32851 | 0.23384 | 2.0048 | 3.7993 | 2.6912 | 2.0126 | 3.7934 | 2.7001 | 0.87288 | -3.0142 | -1.7235 | -0.80912 | 3.1445 | 1.7774 | 2.4374 | -1.6449 | -1.1465 | -2.3762 | 1.6043 | 1.2764 | -74.9146 | 27.5265 | -103.2762 | 104.9622 | -152.5747 | 76.7219 | 1.2914 | 0.90382 | 0.76917 | 1.2472 | 0.9306 | 0.81043 | -4.6181 | -123.8509 | 110.3561 | -3.8418 | -125.5439 | 112.4049
Line_3 | 0.0022707 | 0.4712 | 0.38971 | 0.0017889 | 0.47074 | 0.39067 | 0.02622 | 5.441 | 4.5 | 0.020657 | 5.4356 | 4.5111 | 0.029757 | -3.3259 | -2.2726 | -0.026534 | 3.5836 | 2.353 | -0.017914 | -3.3449 | -2.296 | 0.0027439 | 3.3605 | 2.5501 | 25.9049 | 13.0951 | -116.9767 | -178.7142 | -167.0108 | 63.0534 | 1.3247 | 0.86694 | 0.71791 | 1.2914 | 0.90382 | 0.76917 | -5.143 | -121.7414 | 108.3167 | -4.6181 | -123.8509 | 110.3561

## LLG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.34897 | 1.1192 | 0.85221 | 0.34865 | 1.1193 | 0.85186 | 4.0296 | 12.923 | 9.8404 | 4.0258 | 12.925 | 9.8364 | -1.3024 | 11.6774 | 6.4187 | 1.6451 | -10.0838 | -5.9331 | -4.3505 | 6.2955 | 6.7981 | 4.7439 | -6.5565 | -5.3242 | 105.2608 | -158.5918 | 70.5059 | -74.7166 | 21.424 | -109.4989 | 1.127 | 1.0266 | 0.95011 | 1.2472 | 0.9306 | 0.81043 | -1.405 | -130.262 | 117.15 | -3.8418 | -125.5439 | 112.4049
Line_1 | 0.17359 | 0.79385 | 0.61905 | 0.17435 | 0.79336 | 0.61992 | 2.0045 | 9.1666 | 7.1481 | 2.0132 | 9.161 | 7.1582 | 0.94694 | -6.1529 | -3.9214 | -0.83595 | 6.9393 | 4.1557 | 2.4807 | -5.0294 | -3.3102 | -2.3677 | 4.9522 | 4.0478 | -74.2501 | 18.9957 | -111.852 | 105.6045 | -161.0573 | 68.1585 | 1.3247 | 0.86694 | 0.71791 | 1.2472 | 0.9306 | 0.81043 | -5.143 | -121.7414 | 108.3167 | -3.8418 | -125.5439 | 112.4049
Line_2 | 0.17362 | 0.32903 | 0.23306 | 0.1743 | 0.32851 | 0.23384 | 2.0048 | 3.7993 | 2.6912 | 2.0126 | 3.7934 | 2.7001 | 0.87288 | -3.0142 | -1.7235 | -0.80912 | 3.1445 | 1.7774 | 2.4374 | -1.6449 | -1.1465 | -2.3762 | 1.6043 | 1.2764 | -74.9146 | 27.5265 | -103.2762 | 104.9622 | -152.5747 | 76.7219 | 1.2914 | 0.90382 | 0.76917 | 1.2472 | 0.9306 | 0.81043 | -4.6181 | -123.8509 | 110.3561 | -3.8418 | -125.5439 | 112.4049
Line_3 | 0.0022707 | 0.4712 | 0.38971 | 0.0017889 | 0.47074 | 0.39067 | 0.02622 | 5.441 | 4.5 | 0.020657 | 5.4356 | 4.5111 | 0.029757 | -3.3259 | -2.2726 | -0.026534 | 3.5836 | 2.353 | -0.017914 | -3.3449 | -2.296 | 0.0027439 | 3.3605 | 2.5501 | 25.9049 | 13.0951 | -116.9767 | -178.7142 | -167.0108 | 63.0534 | 1.3247 | 0.86694 | 0.71791 | 1.2914 | 0.90382 | 0.76917 | -5.143 | -121.7414 | 108.3167 | -4.6181 | -123.8509 | 110.3561

## LLG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.0060552 | 3.0748 | 2.2247 | 0.0053698 | 3.075 | 2.2243 | 0.069919 | 35.5046 | 25.6891 | 0.062005 | 35.5073 | 25.6838 | 0.0015502 | 27.3351 | 2.1935 | -0.00031032 | -10.9406 | -0.86575 | -0.068134 | 2.4338 | 12.524 | 0.074481 | -0.99672 | -4.993 | 84.8147 | -161.2201 | 39.8988 | -95.6818 | 18.7919 | -140.1145 | 0.97471 | 0.77295 | 0.49494 | 1.2012 | 0.3094 | 0.1973 | -3.8819 | -156.1321 | 119.9643 | -5.443 | -156.0026 | 120.0487
Line_1 | 0.00096864 | 2.0511 | 1.481 | 0.0027584 | 2.0504 | 1.4823 | 0.011185 | 23.684 | 17.1011 | 0.031851 | 23.6754 | 17.1158 | 6.549e-05 | -1.0598e-10 | -1.6108e-11 | 0.00019669 | 7.2952 | 0.57564 | 0.015125 | -9.6729e-11 | -1.0235e-10 | -0.038259 | 0.66193 | 3.3276 | -95.8944 | 18.8583 | -140.1853 | 84.2624 | -161.1872 | 39.8632 | 1.3523 | 0 | 0 | 1.2012 | 0.3094 | 0.1973 | -6.1425 | 0 | 0 | -5.443 | -156.0026 | 120.0487
Line_2 | 0.0010421 | 1.0253 | 0.7409 | 0.0026114 | 1.0247 | 0.74201 | 0.012033 | 11.8393 | 8.5552 | 0.030154 | 11.8319 | 8.568 | -5.0707e-05 | -1.8256 | -0.14092 | 0.00011363 | 3.6454 | 0.29011 | 0.015365 | -0.17144 | -0.82769 | -0.036221 | 0.3348 | 1.6654 | -96.0272 | 18.8301 | -140.1553 | 84.3772 | -161.25 | 39.9301 | 1.2769 | 0.15487 | 0.09814 | 1.2012 | 0.3094 | 0.1973 | -5.8381 | -155.8051 | 120.1825 | -5.443 | -156.0026 | 120.0487
Line_3 | 0.00096864 | 1.0262 | 0.73946 | 0.0010421 | 1.0253 | 0.7409 | 0.011185 | 11.849 | 8.5385 | 0.012033 | 11.8393 | 8.5552 | -6.5492e-05 | -5.3084e-11 | -7.9728e-12 | 5.0706e-05 | 1.8256 | 0.14092 | -0.015125 | -4.8325e-11 | -5.1116e-11 | -0.015365 | 0.17144 | 0.82769 | 84.1056 | 18.932 | -140.2639 | 83.9728 | -161.1699 | 39.8447 | 1.3523 | 0 | 0 | 1.2769 | 0.15487 | 0.09814 | -6.1425 | 0 | 0 | -5.8381 | -155.8051 | 120.1825

## LLG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.0060552 | 3.0748 | 2.2247 | 0.0053698 | 3.075 | 2.2243 | 0.069919 | 35.5046 | 25.6891 | 0.062005 | 35.5073 | 25.6838 | 0.0015502 | 27.3351 | 2.1935 | -0.00031032 | -10.9406 | -0.86575 | -0.068134 | 2.4338 | 12.524 | 0.074481 | -0.99672 | -4.993 | 84.8147 | -161.2201 | 39.8988 | -95.6818 | 18.7919 | -140.1145 | 0.97471 | 0.77295 | 0.49494 | 1.2012 | 0.3094 | 0.1973 | -3.8819 | -156.1321 | 119.9643 | -5.443 | -156.0026 | 120.0487
Line_1 | 0.00096864 | 2.0511 | 1.481 | 0.0027584 | 2.0504 | 1.4823 | 0.011185 | 23.684 | 17.1011 | 0.031851 | 23.6754 | 17.1158 | 6.549e-05 | -1.0598e-10 | -1.6108e-11 | 0.00019669 | 7.2952 | 0.57564 | 0.015125 | -9.6729e-11 | -1.0235e-10 | -0.038259 | 0.66193 | 3.3276 | -95.8944 | 18.8583 | -140.1853 | 84.2624 | -161.1872 | 39.8632 | 1.3523 | 0 | 0 | 1.2012 | 0.3094 | 0.1973 | -6.1425 | 0 | 0 | -5.443 | -156.0026 | 120.0487
Line_2 | 0.0010421 | 1.0253 | 0.7409 | 0.0026114 | 1.0247 | 0.74201 | 0.012033 | 11.8393 | 8.5552 | 0.030154 | 11.8319 | 8.568 | -5.0707e-05 | -1.8256 | -0.14092 | 0.00011363 | 3.6454 | 0.29011 | 0.015365 | -0.17144 | -0.82769 | -0.036221 | 0.3348 | 1.6654 | -96.0272 | 18.8301 | -140.1553 | 84.3772 | -161.25 | 39.9301 | 1.2769 | 0.15487 | 0.09814 | 1.2012 | 0.3094 | 0.1973 | -5.8381 | -155.8051 | 120.1825 | -5.443 | -156.0026 | 120.0487
Line_3 | 0.00096864 | 1.0262 | 0.73946 | 0.0010421 | 1.0253 | 0.7409 | 0.011185 | 11.849 | 8.5385 | 0.012033 | 11.8393 | 8.5552 | -6.5492e-05 | -5.3084e-11 | -7.9728e-12 | 5.0706e-05 | 1.8256 | 0.14092 | -0.015125 | -4.8325e-11 | -5.1116e-11 | -0.015365 | 0.17144 | 0.82769 | 84.1056 | 18.932 | -140.2639 | 83.9728 | -161.1699 | 39.8447 | 1.3523 | 0 | 0 | 1.2769 | 0.15487 | 0.09814 | -6.1425 | 0 | 0 | -5.8381 | -155.8051 | 120.1825

## LLG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.0034817 | 1.1076 | 0.87246 | 0.0030876 | 1.1078 | 0.87207 | 0.040203 | 12.789 | 10.0743 | 0.035652 | 12.7915 | 10.0698 | 0.0097663 | 10.1889 | 4.881 | -0.0084281 | -7.7589 | -4.2224 | -0.038074 | 5.4371 | 6.7286 | 0.038341 | -5.8748 | -4.9609 | 73.6118 | -159.3111 | 62.2897 | -106.8846 | 20.706 | -117.7171 | 0.9777 | 0.90304 | 0.82512 | 1.1011 | 0.76083 | 0.64694 | -2.0014 | -131.2253 | 116.3321 | -4.487 | -122.1622 | 111.8803
Line_1 | 0.00055695 | 0.73943 | 0.57991 | 0.001586 | 0.7388 | 0.58092 | 0.0064312 | 8.5382 | 6.6962 | 0.018314 | 8.531 | 6.7079 | -0.0014893 | -4.1001 | -2.5203 | 0.0043486 | 5.1766 | 2.8122 | 0.0074692 | -4.105 | -2.5194 | -0.019691 | 3.9154 | 3.3051 | -107.0973 | 20.7983 | -117.7452 | 73.0595 | -159.2649 | 62.274 | 1.1843 | 0.67953 | 0.53218 | 1.1011 | 0.76083 | 0.64694 | -5.8207 | -114.1677 | 107.2446 | -4.487 | -122.1622 | 111.8803
Line_2 | 0.00059921 | 0.36952 | 0.29027 | 0.0015015 | 0.36897 | 0.29116 | 0.0069191 | 4.2668 | 3.3517 | 0.017338 | 4.2605 | 3.362 | -0.0016485 | -2.3194 | -1.3324 | 0.0040795 | 2.5823 | 1.4102 | 0.007732 | -2.0063 | -1.4558 | -0.01865 | 1.9594 | 1.6558 | -107.2301 | 20.7592 | -117.7338 | 73.1743 | -159.3523 | 62.3006 | 1.1426 | 0.71873 | 0.58879 | 1.1011 | 0.76083 | 0.64694 | -5.1943 | -118.3808 | 109.8015 | -4.487 | -122.1622 | 111.8803
Line_3 | 0.00055695 | 0.37023 | 0.28913 | 0.00059921 | 0.36952 | 0.29027 | 0.0064312 | 4.275 | 3.3386 | 0.0069191 | 4.2668 | 3.3517 | 0.0014893 | -2.0566 | -1.2559 | 0.0016485 | 2.3194 | 1.3324 | -0.0074692 | -2.0517 | -1.2568 | -0.007732 | 2.0063 | 1.4558 | 72.9027 | 20.9003 | -117.7758 | 72.7699 | -159.2408 | 62.2662 | 1.1843 | 0.67953 | 0.53218 | 1.1426 | 0.71873 | 0.58879 | -5.8207 | -114.1677 | 107.2446 | -5.1943 | -118.3808 | 109.8015

## LLG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.0034817 | 1.1076 | 0.87246 | 0.0030876 | 1.1078 | 0.87207 | 0.040203 | 12.789 | 10.0743 | 0.035652 | 12.7915 | 10.0698 | 0.0097663 | 10.1889 | 4.881 | -0.0084281 | -7.7589 | -4.2224 | -0.038074 | 5.4371 | 6.7286 | 0.038341 | -5.8748 | -4.9609 | 73.6118 | -159.3111 | 62.2897 | -106.8846 | 20.706 | -117.7171 | 0.9777 | 0.90304 | 0.82512 | 1.1011 | 0.76083 | 0.64694 | -2.0014 | -131.2253 | 116.3321 | -4.487 | -122.1622 | 111.8803
Line_1 | 0.00055695 | 0.73943 | 0.57991 | 0.001586 | 0.7388 | 0.58092 | 0.0064312 | 8.5382 | 6.6962 | 0.018314 | 8.531 | 6.7079 | -0.0014893 | -4.1001 | -2.5203 | 0.0043486 | 5.1766 | 2.8122 | 0.0074692 | -4.105 | -2.5194 | -0.019691 | 3.9154 | 3.3051 | -107.0973 | 20.7983 | -117.7452 | 73.0595 | -159.2649 | 62.274 | 1.1843 | 0.67953 | 0.53218 | 1.1011 | 0.76083 | 0.64694 | -5.8207 | -114.1677 | 107.2446 | -4.487 | -122.1622 | 111.8803
Line_2 | 0.00059921 | 0.36952 | 0.29027 | 0.0015015 | 0.36897 | 0.29116 | 0.0069191 | 4.2668 | 3.3517 | 0.017338 | 4.2605 | 3.362 | -0.0016485 | -2.3194 | -1.3324 | 0.0040795 | 2.5823 | 1.4102 | 0.007732 | -2.0063 | -1.4558 | -0.01865 | 1.9594 | 1.6558 | -107.2301 | 20.7592 | -117.7338 | 73.1743 | -159.3523 | 62.3006 | 1.1426 | 0.71873 | 0.58879 | 1.1011 | 0.76083 | 0.64694 | -5.1943 | -118.3808 | 109.8015 | -4.487 | -122.1622 | 111.8803
Line_3 | 0.00055695 | 0.37023 | 0.28913 | 0.00059921 | 0.36952 | 0.29027 | 0.0064312 | 4.275 | 3.3386 | 0.0069191 | 4.2668 | 3.3517 | 0.0014893 | -2.0566 | -1.2559 | 0.0016485 | 2.3194 | 1.3324 | -0.0074692 | -2.0517 | -1.2568 | -0.007732 | 2.0063 | 1.4558 | 72.9027 | 20.9003 | -117.7758 | 72.7699 | -159.2408 | 62.2662 | 1.1843 | 0.67953 | 0.53218 | 1.1426 | 0.71873 | 0.58879 | -5.8207 | -114.1677 | 107.2446 | -5.1943 | -118.3808 | 109.8015